## Forecast
[5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-03 | Saturday
|  | Date (day): | 2021-04-03 |  | Saturday
| Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14767.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15846 | MW
Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-02 | 2021-04-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[8 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[5 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
| Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 100 | 100 | 100
5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 323 | 370 | 412 | 412
7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 212 | 257 | 360 | 360
8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 450 | 450
9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 9 | 50 | 100 | 100
10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 265 | 270 | 270 |  | 35 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 175 | 200 | 200
17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 70 | 100 | 100
18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 215 | 221 | 222 | 222 |  | 113 | ST under maint
19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 40 | 100 | 100
20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 148 | 149 | 149
23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35
25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 40 | 55 | 58 | 58 |  | 22 | Engine problem
27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 3 | 80 | 300 | 300
32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 85 | 149 | 149 | 149
36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 86 | 104 | 104 | 104
38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 41 | 108 | 144 | 144 |  | 18 | Engine problem
| Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 30 | 0 | 30 | 0
| Dhaka area Total |  |  |  |  | 6171 | 5972 | 2563 | 3278 | 4504 | 4724 | 108 | 851
39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 110 | 105 | 106 | 106 | 124 |  | Low water lavel
44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 50 | 200
45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 120 | 120 | 120 |  | 30 | Machine problem
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98
48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 7 | 68 | 85 | 85 |  | 17 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 86 | 100 | 100
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
* | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 26 | 20 | 35
52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 92 | 92 |  | 16 | Engine problem
53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 33 | 88 | 300 | 300
55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 84 | 110 | 116 | 116
| Chattogram area Total |  |  |  |  | 2442 | 2382 | 664 | 954 | 1525 | 1715 | 484 | 161
59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 0 | 80 | 55 |  | Gas shortage
| Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
| Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 211 | 225 | 225
61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 320 | 190 | 340
62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 305 | 330 | 330
63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 | 19 |  | Gas shortage
64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 51 | 50 | 50 | 5 |  | Gas shortage
65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | under maint.
68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 140 | 140 | 140 |  | 23 | Machine problem
70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 68 | 152 | 200 | 200
71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 48 | 162 | 151 | 168
73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 12 | 52 | 43 | 43 |  | 9 | Engine problem
75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 99 | 111 | 113 | 113
| Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 37 | 37 | 37 | 37
| Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1431 | 1821 | 1893 | 2290 | 449 | 37
79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 117 | 142 | 165 | 165
80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 16 | 16 | 16
81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 32 | 32 | 32 |  | 63 | Engine problem
82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 178 | 200 | 200 | 200
84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 115 | 115 | 115
85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 47 | 0 | 50 | 0
86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 18 | 22 | 22
| Mymensingh Area Total |  |  |  |  | 717 | 709 | 486 | 523 | 601.6 | 550 | 0 | 63
87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 44 | 44 |  | 26 | Engine problem
88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 20 | 43 | 43 | 43 |  | 47 | Under maint.
89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0
90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 290 | 288 | 165 | 165 |  | 165
91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 34 | 34 |  | 32 | Under maint.
95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 80 | 80 | 80
| Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 163 | 151 | 165 | 176 |  | 55 | Machine problem
97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 315 | 341 | 341 |  |  | FGMO
101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 366 | 372 | 400 | 400
102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 10 | 10
103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 351 | 400 | 350 | 350
| Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1715 | 1799 | 1730 | 1741 | 0 | 444
104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 836 | 837 | 853 | 853
105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 99 | 99 |  | 16 | Engine problem
106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 7 | 4 | 20 | 20 |  | 34 | Engine problem
107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 375 | 400 | 400
110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 80 | 50 | 100
112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 100 | 100
113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| Khulna Area Total |  |  |  |  | 2288 | 2284 | 1334 | 1540 | 1722 | 2008 | 0 | 99
114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 48 | 0 | 110 | 110
115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 30 | 33 | 33
116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 62 | 68 | 70 | 70 |  | 124 | GT-2 under maint
117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 82 | 95 | 95
118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 250 | 540 | 622 | 622
| Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 74 | 75 | 75 |  |  | On Test
119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
| Barisal Area Total |  |  |  |  | 1826 | 1826 | 472 | 794 | 1155 | 1155 | 0 | 124
120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 65 | 65 | 65
| Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 140 | 144 | 150 | 150 | 60 |  | Gas shortage
127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 190 | 197 | 200 | 200 |  |  | FGMO
128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 200 | 200 | 200 |  |  | FGMO
129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 0 | 0 | 0 | 0 |  | 414 | Under maint.
130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34
131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 100 | 100
136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 818 | 1023 | 1356 | 1390 | 160 | 414
139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 5 | 0 | 0 | 0 |  | 20 | Engine problem
143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
| Rangpur Area Total |  |  |  |  | 685 | 605 | 262 | 263 | 281 | 273 | 124 | 200
| Total |  |  |  |  | 21778 | 21312 | 9745 | 11995 | 14767.6 | 15846 | 1325 | 2393
| Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9134.0588 | 11243 | 13841.778 | 14852.5701
A. |  | 2021-04-02 | (Yesterday) |  |  |  |  | Friday
1 | Highest Generation : |  |  | 11995 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
2 | Minimum Generation : |  |  | 9352 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11995 | MW
3 | Day peak Generation : |  |  | 9745 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11243 | MW
4 | Evening peak Generation : |  |  | 11995 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
5 | Total Energy Generation : |  | 254.4667 | MKWHr | By Solar | 0.76363 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
| By Gas : | 150.9742 | MKWHr |  | By Oil: | 65.3631 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
| By Coal : | 12.3316 | MKWHr |  | By Hydro: | 2.5542 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1325 | MW | Dhaka | 3792 | 3792 |  | 0
|  |  | For Plants S/D or M/C prob = |  |  | 2393 | MW | Chittagong | 1152 | 1152 |  | 0 |  | 18:00 |  | 0
|  |  | Total = |  |  | 3718 | MW | Khulna | 1476 | 1476 |  | 0 |  | 18:30 |  | 0
7 | Total Gas Supplied : |  |  | 1234.7 | MMCFD |  |  | Rajshahi | 1274 | 1274 |  | 0 |  | 19:00 |  | 0
8 | Fuel Cost : | i) Gas : | Taka | 162898201.47 | ii) Oil : | Taka | 443613644.34 | Comilla | 1154 | 1154 |  | 0 |  | 19:30 |  | 0
|  | iii) Coal : |  | 57910983 | Total | Taka | 664422828.81 | Mymensingh | 1008 | 1008 |  | 0 |  | 20:00 |  | 0
9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 4.0985 | MKWHr. | Sylhet | 373 | 373 |  | 0 |  | 21:00 |  | 0
| ii) During Peak Demand : |  |  | -320 | MW (E to W) at | 21:00 | hrs | Barisal | 309 | 309 |  | 0 |  | 22:00 |  | 0
| iii) Maximum : |  |  | -438 | MW at | 19:00 | hrs | Rangpur | 705 | 705 |  | 0 |  | 23:00 |  | 0
10 | Maximum Temperature in Dhaka was |  |  |  | 37° C |  |  | Total | 11243 | 11243 |  | 0
B. |  | 2021-04-03 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
2 | Maximum Generation (Generation end) |  |  |  | 15846 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
3 | Maximum Demand* Day (Generation end) |  |  |  | 11300 | MW
4 | Reserve(Generation end) |  |  |  | 3046 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
5 | Total Energy Generation |  |  |  | 271.5443 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9463 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.2153 | MKWHr. | ii) HVDC Flow at Peak Time |  | 837 | MW at | 21:00 | hrs.
* Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.2646 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.58 |  | (b) Today: | 84.1 |  | (c) Rule Curve: |  | 87.6
.
|  |  |  | Sub Divisional Engineer | [6 empty] | Executive Engineer
|  |  |  | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 342 | 181 |  | 0 | 320 | 225 | 100 | 0 | 55 | 222 | 0 | 145 | 100 | 102 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 68 | 88 | 0 | 0 | 22 | 38 | 70 | 0 | 80 | 260 | 265 | 213 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 68 | 146 | 32 | 17 | 0 | 44 | 22 | 50 | 0 | 130 | 290 | 0 | 80 | 0 | 163 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 184 | 0 | 149 | 0 | 100 | 68 | 0 | 365 | 115 | 35 | 0 | 0 | 107 | 54 | 0 | 88 | 103 | 100 | 330 | 104 | 0 | 144 | 111 | 0 | 37 | 0 |  | 843 | 0 | 195 | 0 | 99 | 0 | 0 | 0 | 9 | 0 | 33 | 68 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 180 | 0 | 64 | 50 | 179 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 8217 | 3202 | 11419 | 4710 | 843 | 1330 | 3414 | 730 | 107 | 217 | 68 | 0 | 0 | 84.68
2:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 342 | 206 |  | 0 | 320 | 225 | 100 | 0 | 55 | 221 | 0 | 145 | 100 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 22 | 0 | 68 | 88 | 0 | 0 | 22 | 38 | 70 | 0 | 80 | 260 | 265 | 215 | 8 | 135 | 26 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 66 | 147 | 32 | 17 | 0 | 44 | 22 | 22 | 0 | 130 | 289 | 0 | 80 | 0 | 163 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 68 | 0 | 367 | 115 | 0 | 0 | 0 | 69 | 54 | 0 | 50 | 105 | 100 | 330 | 104 | 0 | 144 | 111 | 0 | 37 | 0 |  | 836 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 33 | 58 | 31 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 186 | 0 | 63 | 30 | 189 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 7974 | 3188 | 11162 | 4769 | 836 | 1326 | 3174 | 730 | 107 | 154 | 66 | 0 | 0 | 84.66
3:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 341 | 221 |  | 0 | 320 | 225 | 73 | 0 | 55 | 221 | 0 | 145 | 100 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 22 | 0 | 51 | 88 | 0 | 0 | 0 | 38 | 70 | 0 | 80 | 260 | 265 | 215 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 66 | 147 | 32 | 17 | 0 | 44 | 22 | 22 | 0 | 130 | 290 | 0 | 80 | 0 | 162 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 149 | 0 | 100 | 68 | 0 | 365 | 115 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 105 | 100 | 330 | 104 | 0 | 108 | 111 | 0 | 37 | 0 |  | 837 | 0 | 295 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 62 | 29 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 192 | 0 | 64 | 0 | 194 | 0 | 0 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 0 |  | 7622 | 3161 | 10783 | 4809 | 837 | 1346 | 2825 | 690 | 107 | 103 | 66 | 0 | 0 | 84.64
4:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 341 | 226 |  | 0 | 320 | 225 | 0 | 0 | 55 | 221 | 0 | 145 | 70 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 0 | 22 | 39 | 70 | 0 | 80 | 260 | 265 | 214 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 64 | 147 | 24 | 17 | 0 | 44 | 22 | 22 | 0 | 130 | 290 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 142 | 0 | 100 | 68 | 0 | 366 | 115 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 111 | 100 | 335 | 104 | 0 | 72 | 111 | 0 | 37 | 0 |  | 836 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 67 | 28 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 204 | 0 | 63 | 0 | 209 | 0 | 0 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 0 | 0 | 0 |  | 7377 | 3107 | 10484 | 4910 | 836 | 1350 | 2548 | 600 | 105 | 71 | 64 | 0 | 0 | 84.62
5:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 342 | 227 |  | 0 | 320 | 225 | 0 | 0 | 55 | 221 | 0 | 145 | 30 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 0 | 22 | 39 | 70 | 0 | 80 | 260 | 265 | 214 | 8 | 138 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 62 | 146 | 24 | 17 | 0 | 44 | 22 | 22 | 0 | 130 | 290 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 130 | 0 | 100 | 68 | 0 | 365 | 115 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 111 | 100 | 355 | 104 | 0 | 35 | 112 | 0 | 37 | 0 |  | 836 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 68 | 26 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 211 | 0 | 63 | 0 | 204 | 0 | 0 | 35 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 350 | 0 | 0 | 0 |  | 7310 | 2983 | 10293 | 4960 | 836 | 1354 | 2405 | 500 | 105 | 71 | 62 | 0 | 0 | 84.6
6:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 346 | 221 |  | 0 | 320 | 225 | 0 | 0 | 55 | 220 | 0 | 145 | 7 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 25 | 0 | 0 | 36 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 0 | 22 | 39 | 70 | 0 | 80 | 260 | 265 | 215 | 8 | 140 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 58 | 162 | 24 | 17 | 0 | 44 | 22 | 22 | 0 | 80 | 288 | 0 | 77 | 0 | 163 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 130 | 0 | 100 | 68 | 0 | 366 | 115 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 111 | 100 | 330 | 104 | 0 | 35 | 111 | 0 | 37 | 0 |  | 837 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 62 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 210 | 0 | 63 | 0 | 172 | 0 | 0 | 35 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 250 | 0 | 0 | 0 |  | 7230 | 2820 | 10050 | 4957 | 837 | 1302 | 2319 | 400 | 106 | 71 | 58 | 0 | 0 | 84.58
7:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 350 | 215 |  | 0 | 320 | 230 | 0 | 0 | 55 | 220 | 0 | 150 | 7 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 28 | 25 | 0 | 0 | 38 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 17 | 20 | 0 | 0 | 22 | 38 | 70 | 0 | 80 | 260 | 265 | 216 | 8 | 135 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 56 | 162 | 24 | 17 | 0 | 44 | 22 | 22 | 0 | 0 | 288 | 0 | 77 | 0 | 163 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 130 | 3 | 90 | 68 | 0 | 366 | 115 | 0 | 0 | 1 | 16 | 54 | 0 | 0 | 111 | 100 | 330 | 104 | 7 | 17 | 112 | 0 | 37 | 3 |  | 836 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 163 | 0 | 64 | 0 | 169 | 0 | 0 | 17 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 200 | 0 | 0 | 0 |  | 7007 | 2654 | 9661 | 4915 | 836 | 1201 | 2143 | 350 | 108 | 37 | 56 | 15 | 0 | 84.56
8:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 345 | 207 |  | 0 | 320 | 230 | 0 | 0 | 55 | 222 | 0 | 145 | 7 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 38 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 17 | 20 | 0 | 0 | 22 | 24 | 80 | 0 | 80 | 265 | 265 | 215 | 8 | 134 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 54 | 142 | 24 | 17 | 1 | 44 | 22 | 22 | 0 | 0 | 288 | 0 | 77 | 0 | 163 | 18 | 0 | 9 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 133 | 8 | 90 | 68 | 0 | 366 | 115 | 0 | 0 | 2 | 16 | 54 | 0 | 0 | 111 | 100 | 330 | 104 | 18 | 17 | 111 | 0 | 37 | 9 |  | 836 | 0 | 415 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 63 | 18 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 155 | 0 | 63 | 0 | 168 | 0 | 0 | 17 | 0 | 94 | 0 | 106 | 0 | 2 | 113 | 100 | 0 | 0 | 0 |  | 6976 | 2582 | 9558 | 4891 | 836 | 1165 | 2177 | 250 | 108 | 37 | 54 | 40 | 0 | 84.54
9:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 336 | 213 |  | 0 | 320 | 230 | 0 | 0 | 55 | 222 | 0 | 68 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 30 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 23 | 0 | 0 | 20 | 0 | 0 | 22 | 24 | 80 | 0 | 80 | 265 | 265 | 180 | 8 | 134 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 44 | 142 | 24 | 17 | 2 | 44 | 22 | 22 | 0 | 0 | 290 | 0 | 77 | 0 | 163 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 182 | 0 | 117 | 14 | 100 | 68 | 0 | 367 | 115 | 0 | 0 | 3 | 16 | 54 | 0 | 0 | 84 | 100 | 347 | 104 | 31 | 17 | 112 | 0 | 36 | 17 |  | 836 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 53 | 19 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 156 | 0 | 85 | 0 | 168 | 0 | 0 | 17 | 0 | 94 | 0 | 106 | 0 | 4 | 113 | 5 | 0 | 0 | 0 |  | 6830 | 2522 | 9352 | 4787 | 836 | 1182 | 2173 | 155 | 100 | 4 | 44 | 71 | 0 | 84.52
10:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 333 | 205 |  | 0 | 320 | 225 | 0 | 0 | 55 | 221 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 22 | 0 | 0 | 20 | 0 | 0 | 22 | 10 | 80 | 0 | 80 | 270 | 280 | 190 | 8 | 141 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 44 | 125 | 16 | 17 | 2 | 44 | 22 | 47 | 0 | 0 | 291 | 0 | 77 | 0 | 163 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 179 | 0 | 81 | 18 | 100 | 68 | 0 | 366 | 85 | 0 | 0 | 4 | 16 | 54 | 0 | 0 | 84 | 100 | 347 | 72 | 41 | 17 | 73 | 0 | 37 | 23 |  | 837 | 0 | 375 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 18 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 75 | 0 | 160 | 0 | 95 | 0 | 180 | 0 | 0 | 17 | 0 | 94 | 0 | 70 | 0 | 5 | 113 | 100 | 0 | 0 | 0 |  | 6657 | 2552 | 9209 | 4726 | 837 | 1211 | 1934 | 250 | 110 | 4 | 44 | 93 | 0 | 84.5
11:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 324 | 213 |  | 0 | 320 | 265 | 0 | 0 | 55 | 217 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 80 | 0 | 80 | 260 | 265 | 181 | 8 | 139 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 21 | 11 | 33 | 20 | 44 | 118 | 16 | 17 | 2 | 42 | 20 | 50 | 0 | 0 | 290 | 0 | 77 | 0 | 163 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 179 | 0 | 80 | 18 | 100 | 68 | 0 | 367 | 85 | 0 | 0 | 5 | 33 | 54 | 0 | 0 | 84 | 90 | 360 | 70 | 52 | 17 | 73 | 0 | 37 | 28 |  | 836 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 17 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 125 | 0 | 193 | 0 | 92 | 0 | 190 | 0 | 0 | 17 | 0 | 94 | 0 | 70 | 0 | 6 | 113 | 220 | 0 | 0 | 0 |  | 6689 | 2761 | 9450 | 4763 | 836 | 1234 | 1978 | 370 | 110 | 4 | 44 | 111 | 0 | 84.48
12:00 | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 323 | 212 |  | 0 | 320 | 265 | 9 | 0 | 55 | 215 | 0 | 0 | 16 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 7 | 0 | 0 | 0 | 22 | 5 | 80 | 0 | 80 | 265 | 265 | 208 | 8 | 141 | 23 | 20 | 0 | 0 | 0 | 0 | 12 | 21 | 11 | 25 | 20 | 48 | 117 | 16 | 17 | 2 | 42 | 20 | 50 | 0 | 0 | 290 | 0 | 76 | 0 | 163 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 3 | 0 | 0 | 178 | 0 | 85 | 19 | 100 | 68 | 0 | 366 | 85 | 0 | 0 | 5 | 33 | 54 | 0 | 0 | 99 | 90 | 351 | 86 | 47 | 41 | 84 | 0 | 37 | 30 |  | 836 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 7 | 0 | 0 | 62 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 140 | 0 | 190 | 0 | 92 | 0 | 198 | 0 | 0 | 17 | 0 | 94 | 0 | 100 | 0 | 7 | 113 | 250 | 0 | 0 | 0 |  | 6859 | 2886 | 9745 | 4786 | 836 | 1232 | 2172 | 400 | 110 | 51 | 48 | 110 | 0 | 84.46
13:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 327 | 222 |  | 0 | 320 | 265 | 50 | 0 | 55 | 215 | 0 | 32 | 100 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 11 | 33 | 25 | 0 | 0 | 30 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 22 | 15 | 80 | 0 | 80 | 360 | 265 | 209 | 8 | 133 | 26 | 48 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 108 | 117 | 24 | 17 | 2 | 42 | 22 | 50 | 0 | 0 | 290 | 0 | 77 | 0 | 176 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 15 | 0 | 0 | 178 | 0 | 106 | 18 | 100 | 68 | 0 | 366 | 85 | 0 | 0 | 2 | 33 | 54 | 0 | 0 | 105 | 100 | 330 | 104 | 53 | 72 | 116 | 0 | 37 | 30 |  | 837 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 40 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 135 | 0 | 187 | 0 | 92 | 0 | 191 | 0 | 0 | 17 | 0 | 94 | 0 | 106 | 0 | 7 | 113 | 250 | 28 | 0 | 0 |  | 7362 | 2881 | 10243 | 4874 | 837 | 1298 | 2473 | 400 | 100 | 41 | 108 | 112 | 10243 | 84.44
14:00 | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 347 | 232 |  | 0 | 320 | 225 | 50 | 0 | 55 | 150 | 0 | 70 | 50 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 11 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 80 | 0 |  | 18 | 0 | 0 | 40 | 0 | 0 | 22 | 6 | 80 | 0 | 80 | 260 | 265 | 208 | 8 | 141 | 26 | 47 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 106 | 117 | 24 | 17 | 2 | 41 | 22 | 50 | 0 | 0 | 291 | 0 | 77 | 0 | 143 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 178 | 0 | 79 | 16 | 100 | 68 | 0 | 366 | 85 | 0 | 0 | 4 | 16 | 54 | 0 | 0 | 65 | 100 | 330 | 104 | 37 | 54 | 116 | 0 | 36 | 26 |  | 836 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 60 | 21 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 140 | 0 | 92 | 0 | 161 | 0 | 0 | 17 | 0 | 94 | 0 | 106 | 0 | 6 | 70 | 250 | 28 | 0 | 0 |  | 7006 | 2710 | 9716 | 4619 | 836 | 1284 | 2234 | 400 | 110 | 36 | 106 | 91 | 0 | 84.42
15:00 | 0 | 0 | 0 | 170 | 300 | 94 | 0 | 363 | 256 |  | 0 | 320 | 225 | 50 | 0 | 55 | 209 | 0 | 120 | 50 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 18 | 0 | 0 | 40 | 0 | 0 | 22 | 9 | 80 | 0 | 80 | 280 | 290 | 206 | 8 | 141 | 26 | 46 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 112 | 117 | 24 | 17 | 2 | 41 | 22 | 53 | 0 | 0 | 294 | 0 | 77 | 0 | 145 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 175 | 0 | 65 | 12 | 100 | 68 | 0 | 380 | 85 | 0 | 0 | 3 | 16 | 54 | 0 | 0 | 65 | 100 | 360 | 104 | 35 | 54 | 116 | 0 | 37 | 20 |  | 837 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 167 | 0 | 93 | 0 | 184 | 0 | 0 | 17 | 0 | 94 | 0 | 106 | 0 | 5 | 70 | 210 | 48 | 0 | 0 |  | 7260 | 2751 | 10011 | 4930 | 837 | 1352 | 2198 | 360 | 110 | 35 | 112 | 77 | 0 | 84.4
16:00 | 0 | 0 | 0 | 170 | 300 | 94 | 0 | 367 | 263 |  | 0 | 320 | 225 | 50 | 0 | 55 | 211 | 0 | 150 | 50 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 18 | 0 | 0 | 40 | 0 | 0 | 22 | 14 | 80 | 0 | 80 | 260 | 265 | 208 | 8 | 138 | 23 | 48 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 108 | 134 | 24 | 16 | 1 | 41 | 22 | 53 | 0 | 0 | 290 | 0 | 79 | 0 | 143 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 179 | 0 | 65 | 7 | 100 | 68 | 0 | 367 | 85 | 0 | 0 | 2 | 16 | 42 | 0 | 0 | 65 | 100 | 340 | 104 | 22 | 54 | 116 | 0 | 36 | 12 |  | 836 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 20 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 133 | 0 | 193 | 0 | 94 | 0 | 193 | 0 | 0 | 53 | 0 | 93 | 20 | 106 | 0 | 4 | 70 | 30 | 68 | 0 | 0 |  | 7194 | 2713 | 9907 | 4932 | 836 | 1387 | 2276 | 180 | 105 | 35 | 108 | 48 | 0 | 84.38
17:00 | 0 | 0 | 0 | 170 | 300 | 94 | 0 | 377 | 263 |  | 0 | 320 | 265 | 26 | 0 | 55 | 216 | 0 | 110 | 24 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 18 | 0 | 0 | 40 | 0 | 0 | 22 | 18 | 80 | 0 | 80 | 260 | 265 | 182 | 8 | 138 | 26 | 47 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 98 | 157 | 24 | 16 | 0 | 42 | 20 | 53 | 0 | 0 | 290 | 0 | 79 | 0 | 143 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 180 | 0 | 80 | 2 | 100 | 68 | 0 | 319 | 45 | 0 | 0 | 1 | 16 | 54 | 0 | 0 | 65 | 100 | 330 | 62 | 8 | 54 | 116 | 0 | 37 | 5 |  | 837 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 60 | 18 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 139 | 0 | 169 | 0 | 81 | 0 | 179 | 0 | 0 | 53 | 0 | 93 | 22 | 106 | 0 | 2 | 70 | 30 | 68 | 0 | 0 |  | 6996 | 2615 | 9611 | 4811 | 837 | 1377 | 2150 | 180 | 105 | 35 | 98 | 18 | 0 | 84.36
18:00 | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 325 | 275 |  | 0 | 320 | 260 | 24 | 0 | 55 | 170 | 0 | 70 | 24 | 24 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 70 | 0 |  | 18 | 0 | 39 | 40 | 0 | 0 | 22 | 22 | 80 | 0 | 80 | 260 | 265 | 182 | 8 | 136 | 26 | 48 | 0 | 0 | 0 | 0 | 34 | 21 | 11 | 33 | 20 | 132 | 158 | 24 | 16 | 0 | 43 | 32 | 53 | 0 | 0 | 288 | 0 | 79 | 0 | 122 | 18 | 0 | 9 | 270 | 16 | 11 | 0 | 15 | 0 | 0 | 183 | 0 | 94 | 0 | 100 | 68 | 0 | 319 | 45 | 6 | 0 | 0 | 16 | 54 | 0 | 0 | 65 | 100 | 320 | 53 | 1 | 54 | 116 | 0 | 37 | 0 |  | 837 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 3 | 7 | 0 | 52 | 22 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 17 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 116 | 0 | 165 | 0 | 43 | 0 | 169 | 0 | 0 | 53 | 0 | 93 | 0 | 113 | 0 | 1 | 70 | 170 | 74 | 0 | 0 |  | 6852 | 2612 | 9464 | 4487 | 837 | 1341 | 2142 | 320 | 105 | 98 | 132 | 2 | 0 | 84.34
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.32
19:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 322 | 290 |  | 0 | 320 | 260 | 54 | 0 | 55 | 221 | 0 | 175 | 62 | 64 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 16 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 18 | 0 | 68 | 86 | 0 | 14 | 22 | 20 | 80 | 0 | 80 | 260 | 265 | 212 | 8 | 138 | 26 | 49 | 0 | 0 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 164 | 141 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 290 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 172 | 0 | 0 | 192 | 0 | 97 | 0 | 100 | 99 | 0 | 361 | 85 | 34 | 0 | 0 | 84 | 54 | 0 | 0 | 102 | 100 | 370 | 87 | 0 | 78 | 116 | 0 | 37 | 0 |  | 837 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 19 | 12 | 40 | 67 | 27 | 48 | 0 | 0 | 65 | 50 | 0 | 92 | 0 | 0 | 0 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 122 | 0 | 178 | 0 | 62 | 0 | 182 | 0 | 0 | 105 | 0 | 93 | 0 | 113 | 0 | 0 | 100 | 310 | 74 | 0 | 0 |  | 8043 | 3318 | 11361 | 5040 | 837 | 1403 | 2944 | 460 | 105 | 408 | 164 | 0 | 0 | 84.28
19:30 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 367 | 286 |  | 0 | 320 | 260 | 100 | 0 | 55 | 221 | 0 | 175 | 80 | 64 | 147 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 86 | 0 | 40 | 22 | 26 | 80 | 0 | 80 | 260 | 265 | 211 | 8 | 140 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 143 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 291 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 120 | 0 | 0 | 193 | 0 | 115 | 0 | 100 | 150 | 0 | 366 | 115 | 50 | 0 | 0 | 83 | 54 | 0 | 0 | 112 | 100 | 370 | 104 | 0 | 108 | 116 | 0 | 37 | 0 |  | 837 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 18 | 12 | 40 | 58 | 29 | 48 | 0 | 0 | 70 | 50 | 0 | 92 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 5 | 144 | 0 | 186 | 0 | 78 | 50 | 184 | 0 | 0 | 105 | 0 | 93 | 0 | 113 | 0 | 0 | 113 | 460 | 74 | 0 | 0 |  | 8343 | 3575 | 11918 | 5139 | 837 | 1415 | 3226 | 609 | 105 | 425 | 162 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 363 | 281 |  | 0 | 320 | 265 | 80 | 0 | 55 | 221 | 0 | 175 | 70 | 40 | 148 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 86 | 0 | 47 | 22 | 26 | 80 | 0 | 80 | 285 | 290 | 210 | 8 | 140 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 158 | 142 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 290 | 0 | 80 | 0 | 163 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 80 | 0 | 0 | 194 | 0 | 144 | 0 | 100 | 152 | 0 | 380 | 115 | 17 | 0 | 0 | 83 | 54 | 0 | 0 | 110 | 100 | 400 | 104 | 0 | 108 | 115 | 0 | 37 | 0 |  | 836 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 4 | 12 | 40 | 67 | 29 | 48 | 0 | 0 | 65 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 189 | 0 | 82 | 50 | 187 | 0 | 0 | 105 | 0 | 93 | 0 | 113 | 0 | 0 | 113 | 490 | 74 | 0 | 0 |  | 8347 | 3585 | 11932 | 5272 | 836 | 1424 | 3140 | 640 | 105 | 357 | 158 | 0 | 0 | 84.3
21:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 370 | 257 |  | 0 | 320 | 265 | 50 | 0 | 55 | 221 | 0 | 175 | 70 | 40 | 148 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 86 | 0 | 50 | 22 | 26 | 80 | 0 | 80 | 320 | 305 | 211 | 8 | 140 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 142 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 288 | 0 | 80 | 0 | 151 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 152 | 0 | 372 | 115 | 17 | 0 | 0 | 88 | 54 | 0 | 0 | 111 | 100 | 400 | 104 | 0 | 108 | 110 | 0 | 37 | 0 |  | 837 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 40 | 68 | 30 | 0 | 0 | 0 | 65 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 197 | 0 | 82 | 80 | 200 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 74 | 0 | 0 |  | 8375 | 3620 | 11995 | 5321 | 837 | 1427 | 3108 | 690 | 105 | 345 | 162 | 0 | 0 | 84.28
22:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 378 | 255 |  | 0 | 320 | 265 | 50 | 0 | 55 | 222 | 0 | 180 | 70 | 40 | 140 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 86 | 0 | 50 | 22 | 26 | 80 | 0 | 80 | 315 | 300 | 213 | 8 | 140 | 26 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 142 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 290 | 0 | 80 | 0 | 135 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 152 | 0 | 360 | 115 | 17 | 0 | 0 | 89 | 54 | 0 | 0 | 112 | 100 | 400 | 104 | 0 | 108 | 111 | 0 | 37 | 0 |  | 836 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 40 | 68 | 30 | 16 | 0 | 0 | 65 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 196 | 0 | 78 | 80 | 197 | 0 | 0 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 75 | 0 | 0 |  | 8349 | 3637 | 11986 | 5287 | 836 | 1423 | 3116 | 720 | 105 | 337 | 162 | 0 | 0 | 84.26
23:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 379 | 242 |  | 0 | 320 | 225 | 50 | 0 | 55 | 222 | 0 | 180 | 70 | 40 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 65 | 0 | 50 | 22 | 26 | 80 | 0 | 80 | 310 | 300 | 213 | 8 | 139 | 26 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 142 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 288 | 0 | 80 | 0 | 135 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 80 | 0 | 0 | 194 | 0 | 149 | 0 | 100 | 152 | 0 | 366 | 115 | 17 | 0 | 0 | 89 | 54 | 0 | 0 | 110 | 100 | 390 | 104 | 0 | 108 | 111 | 0 | 37 | 0 |  | 837 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 40 | 68 | 31 | 32 | 0 | 0 | 65 | 0 | 0 | 18 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 145 | 0 | 192 | 0 | 73 | 80 | 194 | 0 | 0 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 75 | 0 | 0 |  | 8250 | 3516 | 11766 | 5265 | 837 | 1406 | 3047 | 720 | 107 | 222 | 162 | 0 | 0 | 84.24
24:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 382 | 242 |  | 0 | 320 | 225 | 40 | 0 | 55 | 222 | 0 | 180 | 70 | 24 | 62 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 |  | 18 | 0 | 68 | 65 | 0 | 50 | 22 | 36 | 80 | 0 | 80 | 315 | 300 | 215 | 8 | 139 | 26 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 144 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 290 | 0 | 80 | 0 | 136 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 45 | 0 | 0 | 185 | 0 | 149 | 0 | 100 | 175 | 0 | 366 | 115 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 112 | 100 | 398 | 104 | 0 | 54 | 111 | 0 | 37 | 0 |  | 837 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 33 | 68 | 31 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 146 | 0 | 186 | 0 | 73 | 80 | 188 | 0 | 0 | 94 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 75 | 0 | 0 |  | 8052 | 3459 | 11511 | 5272 | 837 | 1416 | 2871 | 720 | 107 | 134 | 154 | 0 | 0 | 84.22
KWH | 0 | 0 | 0 | 4063500 | 7177791 | 2275954 | 0 | 8833822 | 5592000 |  | 0 | 7079750 | 5739462 | 917760 | 0 | 1337883 | 5240657 | 0 | 3100000 | 1268467 | 751824 | 1309920 | 0 | 0 | 0 | 0 | 1296720 | 1228036 | 937819 | 482076 | 600000 | 561240 | 804300 | 624500 | 0 | 0 | 878225 | 1676000 | 0 | 0 | 614188 | 0 | 0 | 2513374 | 0 |  | 507120 | 0 | 809717 | 1285920 | 0 | 266400 | 535488 | 611520 | 1947542 | 0 | 1923456 | 6947600 | 6681000 | 5003000 | 200727 | 3281370 | 586944 | 845280 | 0 | 0 | 0 | 0 | 773760 | 504468 | 250560 | 812000 | 493320 | 2264640 | 3255120 | 624960 | 341964 | 16000 | 1016000 | 630000 | 1019400 | 0 | 788481 | 6551000 | 0 | 1893120 | 0 | 3753110 | 424000 | 0 | 192240 | 7244000 | 383832 | 246000 | 0 | 1196835 | 0 | 0 | 4375200 | 0 | 2833490 | 125280 | 2397120 | 2145120 | 0 | 8762000 | 2425200 | 207600 | 0 | 28080 | 1098982 | 1287994 | 0 | 188100 | 2441040 | 2361600 | 8453000 | 2428800 | 339420 | 1716480 | 2625764 | 0 | 887760 | 204320 |  | 20215273 | 0 | 8662464 | 0 | 2291520 | 0 | 0 | 0 | 114240 | 27904 | 389625 | 1524000 | 569292 | 1427040 | 0 | 0 | 365000 | 64032 | 0 | 373224 | 0 | 0 | 10055 | 812640 | 216848 | 477840 | 0 | 246780 | 0 | 0 | 3665300 | 0 | 6000 | 2778900 | 0 | 4592909 | 0 | 1812760 | 526080 | 4693855 | 0 | 0 | 1335360 | 0 | 2355072 | 36432 | 2565120 | 0 | 50528 | 2524896 | 8666300 | 723873 | 0 | 0 |  | 180345512 | 74121162 | 254466674 | 119647942 | 20215273 | 31326237 | 62431189 | 12331600 | 2554225 | 2931940 | 2264640 | 763628 | 0
Fuel Cost | 0 | 0 | 0 | 5973345 | 7967348.01 | 3004259.28 | 0 | 8922160.22 | 5759760 |  | 0 | 7716927.5 | 6370802.82 | 6965798.4 | 0 | 11318490.18 | 5450283.28 | 0 | 5363000 | 9551556.51 | 6856634.88 | 12889612.8 | 0 | 0 | 0 | 0 | 9466056 | 9492718.28 | 9246895.34 | 361557 | 450000 | 0 | 0 | 0 | 0 | 0 | 237120.75 | 452520 | 0 | 0 | 5705806.52 | 0 | 0 | 4272735.8 | 0 |  | 0 | 0 | 7854254.9 | 12280536 | 0 | 2109888 | 674714.88 | 1816214.4 | 2882362.16 | 0 | 2827480.32 | 5141224 | 6681000 | 4602760 | 258937.83 | 3773575.5 | 663246.72 | 1183392 | 0 | 0 | 0 | 0 | 7389408 | 640674.36 | 187920 | 1421000 | 369990 | 16984800 | 3450427.2 | 5674636.8 | 434294.28 | 255040 | 1666240 | 1008000 | 1814532 | 0 | 898868.34 | 6813040 | 0 | 3615859.2 | 0 | 6492880.3 | 928560 | 0 | 392169.6 | 7316440 | 287874 | 186960 | 0 | 9048072.6 | 0 | 0 | 22751040 | 0 | 27881541.6 | 1464523.2 | 19536528 | 23274552 | 0 | 8148660 | 22117824 | 1961820 | 0 | 0 | 8308303.92 | 11218427.74 | 0 | 1877238 | 20919712.8 | 15728256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 116439972.48 | 0 | 9095587.2 | 0 | 18011347.2 | 0 | 0 | 0 | 1198377.6 | 292433.92 | 4059892.5 | 1722120 | 882402.6 | 13927910.4 | 0 | 0 | 748250 | 630074.88 | 0 | 3303032.4 | 0 | 0 | 97432.95 | 7874481.6 | 2103425.6 | 917452.8 | 0 | 186812.46 | 0 | 0 | 19865926 | 0 | 171180 | 3251313 | 0 | 6062639.88 | 0 | 2719140 | 8948620.8 | 5491810.35 | 0 | 0 | 13941158.4 | 0 | 22349633.28 | 343918.08 | 19905331.2 | 0 | 558334.4 | 18658981.44 | 38045057 | 0 | 0 | 0 |  | 459011089.22 | 341804050.42 | 800815139.64 | 124601845.92 | 116439972.48 | 38296355.55 | 415073819.29 | 57910983 | 689640.75 | 28539825.05 | 16984800 | 2277897.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 323 | 212 |  | 0 | 320 | 265 | 9 | 0 | 55 | 215 | 0 | 0 | 16 | 40 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 15 | 33 | 25 | 0 | 0 | 40 | 70 | 0 | 0 | 25 | 0 | 0 | 110 | 0 |  | 24 | 0 | 7 | 0 | 0 | 0 | 22 | 5 | 80 | 0 | 80 | 265 | 265 | 208 | 8 | 141 | 23 | 20 | 0 | 0 | 0 | 0 | 12 | 21 | 11 | 25 | 20 | 48 | 117 | 16 | 17 | 2 | 42 | 20 | 50 | 0 | 0 | 290 | 0 | 76 | 0 | 163 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 3 | 0 | 0 | 178 | 0 | 85 | 19 | 100 | 68 | 0 | 366 | 85 | 0 | 0 | 5 | 33 | 54 | 0 | 0 | 99 | 90 | 351 | 86 | 47 | 41 | 84 | 0 | 37 | 30 |  | 836 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 7 | 0 | 0 | 62 | 20 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 140 | 0 | 190 | 0 | 92 | 0 | 198 | 0 | 0 | 17 | 0 | 94 | 0 | 100 | 0 | 7 | 113 | 250 | 0 | 0 | 0 |  | 9745 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 370 | 257 | 0 | 0 | 320 | 265 | 50 | 0 | 55 | 221 | 0 | 175 | 70 | 40 | 148 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 18 | 0 | 68 | 86 | 0 | 50 | 22 | 26 | 80 | 0 | 80 | 320 | 305 | 211 | 8 | 140 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 162 | 142 | 32 | 16 | 0 | 43 | 43 | 53 | 0 | 0 | 288 | 0 | 80 | 0 | 151 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 80 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 152 | 0 | 372 | 115 | 17 | 0 | 0 | 88 | 54 | 0 | 0 | 111 | 100 | 400 | 104 | 0 | 108 | 110 | 0 | 37 | 0 |  | 837 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 40 | 68 | 30 | 0 | 0 | 0 | 65 | 0 | 0 | 92 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 197 | 0 | 82 | 80 | 200 | 0 | 0 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 74 | 0 | 0 |  | 11995 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 270 | 100 | 0 | 55 | 222 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 36 | 70 | 0 | 0 | 25 | 200 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 92 | 50 | 22 | 35 | 80 | 0 | 80 | 340 | 330 | 225 | 8 | 140 | 26 | 50 | 0 | 0 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 168 | 165 | 32 | 16 | 0 | 44 | 43 | 51 | 0 | 0 | 165 | 34 | 80 | 0 | 176 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 350 | 104 | 0 | 144 | 116 | 0 | 37 |  |  | 853 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 40 | 70 | 33 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 150 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 0 | 100 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 75 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 412 | 360 | 0 | 0 | 450 | 270 | 100 | 0 | 55 | 222 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 36 | 70 | 0 | 0 | 25 | 50 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 92 | 50 | 22 | 20 | 0 | 0 | 80 | 190 | 330 | 225 | 8 | 140 | 26 | 50 | 0 | 0 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 151 | 165 | 32 | 16 | 1.6 | 44 | 43 | 51 | 0 | 0 | 165 | 34 | 80 | 0 | 165 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 350 | 104 | 50 | 144 | 116 | 0 | 37 | 30 |  | 853 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 40 | 70 | 33 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 150 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 0 | 100 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 75 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 302 | 287 | 0 | 0 | 320 | 225 | 0 | 0 | 15 | 190 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 26 | 22 | 25 | 30 | 33 |  | 0 | 0 | 36 | 70 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 1 | 0 | 0 | 100 | 0 | 0 | 22 | 3 | 0 | 0 | 80 | 190 | 295 | 216 | 0 | 140 | 23 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 28 | 20 | 164 | 165 | 32 | 16 | 1 | 44 | 43 | 53 | 0 | 0 | 162 | 34 | 80 | 0 | 136 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 187 | 0 | 111 | 0 | 70 | 197 | 0 | 366 | 65 | 0 | 0 | 2 | 0 | 54 | 0 | 0 | 0 | 100 | 370 | 22 | 12 | 0 | 112 | 0 | 0 | 0 | 0 | 838 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 184 | 0 | 34 | 0 | 186 | 0 | 0 | 53 | 0 | 94 | 0 | 50 | 0 | 2 | 95 | 370 | 75 | 0 | 0 | 0
199
| Minimum Generation |  | 9352 | 9:00
| Highest Generation |  | 11995 | 21:00
| Day Peak Generation |  | 9745 | 12:00
| Evening Peak Generation |  | 11995 | 21:00
| HVDC Max Flow |  | 843 | 1:00
| HVDC EvPeak Flow |  | 837 | 21:00
| Load factor L.F |  | 88.39%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-03
Till now the maximum generation is : - |  |  | 12893 MW | 21:00 | Hrs on | 2019-05-29
The Summary of Yesterday's |  | 2021-04-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9745 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9463 | MW
Evening Peak Generation : |  | 11995 | MW Hour : | 21:00 | Available Max Generation : |  | 15846 | MW
E.P. Demand (at gen end) : |  | 11995 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 11995 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3046 | MW
Total Gen. (MKWH) : |  | 254.4667 | System Load Factor : | 88.39% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -438 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-03
Actual : | 84.1 | Ft.(MSL) , | Rule curve : | 87.6 | Ft.( MSL )
Gas Consumed : | Total = | 1234.7 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 162898201.47
: |  | Coal : | 57910983 | Oil : | 443613644.34 | Total : | 664422828.81
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4461.8017 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1520.985 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1363.416 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1232.1971 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1113.3887 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 898.4747 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 497.5887 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 231.2062 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 692.9712 |  |  | 0 | 0%
Total | 0 |  | 12012.0292 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100, 71 MW
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Sirajganj #4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bheramara-Faridpur 132 kV Ckt-1 was under shut down from 08:55 to 19:43 for D/W.
b) Hathazari-Baraulia 132 kV Ckt-2 was under shut down from 09:09 to 13:28 for D/W.
c) Julda S/S-Julda Unit-1 P.P. 132 kV Ckt was under shut down from 10:30 to 12:39 due to R/H maintenance
at Julda Unit-1 P.P. end.
d) Rampura-Mogbazar 132 kV Ckt-1 was under shut down from 08:37 to 21:53 for D/W.
e) Netrokona 132/33 kV T-4 transformer was under shut down from 09:04 to 11:59 for Oil filling.
f) Shahjibazar 132/33 kV T-4 & T-6 transformers was under shut down from 08:35 to 10:54 for C/M.
g) Khulna-Satkhira 132 kV Ckt-2 was under shut down from 07:52 to 12:02 for C/M.
h) Bogura-Barapukuria S/S 230 kV Ckt-1 was under shut down from 11:36 to 14:16 for C/M.
i) Cumilla(S) 132/33 kV T-1 & T-2 transformers shifted to Tripura side at 12:26.
j) Payra-Gopalganj New 400 kV Ckt-2 was under shut down from 08:18 to 08:39 due to Gopalganj New 400/132 kV
ATR-02 transformer shutdown.
k) Gopalganj New 400/132 kV ATR-02 transformer was under shut down from 08:22 to 16:16 for C/M.
l) After parallel with T-4 Kishoreganj 132/33 kV T-3 transformer was switched on at 14:35.
m) Gopalganj-Madaripur 132 kV Ckt-3 was under shut down from 15:32 to 17:40 for C/M.
n) Mohasthanghar 132/33 kV T-2 transformer & its associated 33 kV Bus section-2 was under shutdown |  |  |  |  | About 22 MW power interruption occurred under Mohasthanghar S/S area
from 15:08 to 16:08 due to 33 kV feeder maintenance. |  |  |  |  | from 15:08 to 16:08.
o) Payra Unit-1 was shutdown and synchronized at 16:00 and 16:29 respectively for Gopalganj New 400/132 kV
ATR-2 normalization.
p) Rampur 230/132 kV T-02 transformer was energized at 16:31.
q) Saidpur-Purbasadipur 132 kV Ckt-2 tripped at 01:20(03/04/2021) from Saidpur end showing Dist. C-phase
and was switched on at 01:32(03/04/2021) & again tripped at 01:45(03/04/2021) and was switched on
at 02:02(03/04/2021).
r) Saidpur-Purbasadipur 132 kV Ckt-2 tripped at 04:18(03/04/2021) from Saidpur end showing Dist. C-phase |  |  |  |  | About 110 MW power interruption occurred under Purbasadipur, Thakurgaon
and was switched on at 04:31(03/04/2021) & again tripped at 05:06(03/04/2021) from both ends showing |  |  |  |  | & Panchagar S/S area from 04:18(03/04/2021) to 04:28(03/04/2021).
Dist. C-phase at Saidpur end & Dist. B-phase at Purbasadipur end.
s) Saidpur-Purbasadipur 132 kV Ckt-1 tripped at 04:18(03/04/2021) from Saidpur end showing Dist.B & C-phase
and was switched on at 04:28(03/04/2021).
t) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 04:36(03/04/2021) from both ends showing no relay
and was switched on at 06:15(03/04/2021).
u) Ashuganj-Sirajganj 230 kV Ckt-2 tripped at 04:36(03/04/2021) from both ends showing General trip at
Ashuganj end & Dist. B-phase, Z1, SOTF at Sirajganj end and was switched on at 05:53(03/04/2021).
v) Ashuganj 230/132 kV OAT-12 transformer tripped at 04:36(03/04/2021) showing master trip, E/F and
was switched on at 06:08(03/04/2021).
w) Ashuganj Unit-3 tripped at 04:36(03/04/2021) showing E/F, Master trip.
x) Ashuganj(S)-Ghorashal 230 kV Ckt-2 tripped at 05:10(03/04/2021) from both ends showing Dist. Z1 at
Ashuganj(S) end & Dist. A,B-phase, Z1 at Ghorashal end and was switched on at 06:18(03/04/2021).
y) Ashuganj(N) 450 MW CCPP ST tripped at 04:36(03/04/2021) due to voltage fluctuation.
z) Shahjibazar Unit-8 was synchronized at 00:40(03/04/2021).
aa) Shahjibazar 330 MW CCPP GT-1 was shutdown at 00:32(03/04/2021) for air filter replacement.
ab) Dohazari-(Matarbari)-Cox'sbazar 132 kV Ckt-1 is under shut down since 06:24(03/04/2021) for D/W.
ac) Baroirhat-PHP 132 kV Ckt is under shut down since 07:24(03/04/2021) for D/W.
ad) Mymensingh-Kishoreganj 132 kV Ckt-1 is under shut down since 07:35(03/04/2021) for D/W.
ae) Bheramara-Faridpur 132 kV Ckt-2 is under shut down since 07:18(03/04/2021) for D/W.
af) Bhandaria 132/33 kV T-1 transformer is under shut down since 06:57(03/04/2021) for C/M.
ag) Gopalganj Old 132/33 kV T-1 transformer is under shut down since 07:03(03/04/2021) for C/M. |  |  |  |  | About 15 MW power interruption has been running under Gopalganj S/S area
since 07:03(03/04/2021).
ah) Madaripur 132/33 kV T-2 transformer is under shut down since 07:30(03/04/2021) for C/M.
ai) Halishahar 132/33 kV T-2 transformer is under shut down since 07:50(03/04/2021) for C/M. |  |  |  |  | About 10 MW power interruption has been running under Halishahar S/S area
since 07:50(03/04/2021).
aj) Satkhira all 132/33 transformers tripped at 07:42(03/04/2021) from 33 kV side due to fault at Auxiliary |  |  |  |  | Full power interruption occurred under Satkhira S/S area from 07:42(03/04/2021)
transformer and was switched on at 08:14(03/04/2021). |  |  |  |  | to 08:14(03/04/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4063500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7177791 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2275954
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8833822 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 257 | 5592000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7079750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 50 | 917760 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 265 | 5739462
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1337883
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 482076
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 175 | 3100000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 70 | 1268467 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 5240657 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 751824 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1296720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 148 | 1309920
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1228036
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 937819 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1161240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 804300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 624500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 80 | 1196835 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2833490
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 207600 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2428800
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 1716480 | Engine problem
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 204320
| Dhaka area Total |  |  |  | 5972 | 3278 | 69811006
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 614188
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 125280
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 266400
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 105 | 2554225 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2513374 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Transformer O/L
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Reserve.
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 809717 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 86 | 1285920 | Engine problem
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2397120
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 535488
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 611520
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28080
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 88 | 1098982 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1287994
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2361600
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 2625764
| Chattogram area Total |  |  |  | 2382 | 954 | 19115652
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1947542 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 5003000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 320 | 6947600 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6681000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 586944 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 845280
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3281370 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 152 | 2145120 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 504468
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 2264640
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 812000
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 773760
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 493320
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 188100 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 111 | 2441040
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 37 | 887760 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1821 | 38177687
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 142 | 3255120 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 341964 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 32 | 624960 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 16000
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 4375200
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2425200 | #REF!
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 339420
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 507120
| Mymensingh Area Total |  |  |  | 709 | 523 | 11884984
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1016000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 630000 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 788481 | Under maint.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 288 | 6551000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1019400
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 246000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 80 | 1893120
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 151 | 3753110 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 424000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 383832 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7244000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 372 | 8762000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 192240
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8453000
| Sylhet Area Total |  |  |  | 2371 | 1799 | 41356183
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 837 | 20215273
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2291520 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 114240 | Machine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 27904 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 375 | 8662464 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 389625
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 80 | 526080 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1335360
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 36432 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1540 | 33598898
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 1427040 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 569292
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1524000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 82 | 1812760 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 8666300
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 74 | 723873 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L.
| Barisal Area Total |  |  |  | 1826 | 794 | 14723265
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 65 | 365000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 64032 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 10055 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 144 | 2778900 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 197 | 4592909 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 200 | 4693855 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 0 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 216848 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 477840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246780
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 812640
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 373224 | Engine problem
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2355072 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2524896
| Rajshahi Area Total |  |  |  | 2183 | 1023 | 19512051
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3665300 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 6000 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2565120
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50528
| Rangpur Area Total |  |  |  | 605 | 263 | 6286948
| Total |  |  |  | 21312 | 11995 | 254466674
| Eastern Grid Total |  |  |  | 14414 | 8375 | 180345512
| Western Grid Total |  |  |  | 6898 | 3620 | 74121162
| National Grid Total |  |  |  | 21312 | 11995 | 254466674
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-02
(a) ENTIRE EASTERN GRID : |  | 7479 | MW | (b) ENTIRE WESTERN GRID : |  | 3764 | MW
i) Dhaka area |  | 3792 | MW | i) Khulna area |  | 1476 | MW
ii) Chittagong area |  | 1152 | MW | ii) Rajshahi area |  | 1274 | MW
iii) Comilla area |  | 1154 | MW | iii) Barisal area |  | 309 | MW
iv) Mymensingh area |  | 1008 | MW | iv) Rangpur area |  | 705 | MW
v) Sylhet area |  | 373 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11243 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 23:00 | Jamalpur | 151 | 19:00 | Jhenida | 115 | 20:00
Munsiganj | 132 | 21:00 | Sherpur | 130 | 19:00 | Bottail | 108 | 19:30
Sonargaon | 84 | 23:00 | Srimongal | 36 | 19:00 | G.K Project | 51 | 20:00
Shyampur | 196 | 24:00 | Shahjibazar | 105 | 21:00 | Faridpur | 178 | 1:00
Bhulta | 183 | 1:00 | Fenchuganj | 28 | 18:30 | Madaripur | 100 | 22:00
Madanganj | 50 | 24:00 | Kulawara | 36 | 20:00 | Sariatpur | 62 | 21:00
Shitalakhya | 100 | 9:00 | Sylhet | 88 | 19:30 | Gopalganj | 83 | 1:00
Rahim steel | 8 | 1:00 | Chatak | 23 | 21:00 | Bagerhat | 105 | 19:30
Matuail | 62 | 7:00 | Sunamganj | 32 | 21:00 | Mongla | 28 | 8:00
Ghorasal | 82 | 1:00 | Biani Bazar | 44 | 20:00 | Satkhira | 111 | 21:00
Narsingdi | 167 | 20:00 | Comilla (S) | 164 | 19:00 | Gallamari | 38 | 1:00
Haripur (SBU) | 110 | 10:00 | Comilla(N) | 137 | 19:00 | Magura | 54 | 19:30
Sreenagar |  |  | Chandpur | 76 | 21:00 | Norail | 39 | 20:00
Ullon | 85 | 18:30 | Feni | 131 | 19:00 | Chuadanga | 86 | 20:00
Hasnabad | 98 | 1:00 | Chowmuhani | 179 | 21:00 | Borguna | 16 | 1:00
Magbazar | 66 | 1:00 | Ashuganj | 20 | 19:00 | Barisal(N) | 42 | 20:00
Maniknagar | 77 | 18:30 | Daudkandi | 132 | 1:00 | Barisal (S) | 96 | 1:00
Bangabhaban | 8 | 15:00 | B.Baria | 160 | 21:00 | Patuakhali | 103 | 1:00
Narinda | 76 | 12:00 | Ramganj | 84 | 19:00 | Bhandaria | 47 | 1:00
Dhanmondi | 145 | 18:30 | Chaddagram | 44 | 18:30 | Borhan Uddin | 42 | 23:00
Lalbag | 71 | 1:00 | PHP | 11 | 21:00 | Ishurdi | 54 | 1:00
Madartek | 78 | 1:00 | Kochua | 63 | 19:30 | Ruppur Paromanobik | 3 | 7:00
Dhaka University | 23 | 18:30 | Madunaghat | 56 | 18:30 | Natore | 123 | 19:30
Aftabnagar | 11 | 1:00 | Hathazari | 91 | 19:30 | Bogra | 155 | 1:00
Fatullah | 62 | 1:00 | Khulshi | 184 | 16:00 | Noagaon | 107 | 20:00
Nawabganj | 50 | 1:00 | Halishahar | 128 | 19:30 | Rajshahi | 140 | 22:00
Mirpur | 102 | 19:00 | Baraulia | 155 | 5:00 | Rajshahi New | 19 | 20:00
Kalyanpur | 90 | 19:00 | Sikalbaha | 22 | 20:00 | C.Nawabganj | 75 | 20:00
Gulshan | 100 | 18:30 | Dohazari | 90 | 21:00 | Amnura | 60 | 20:00
Uttara | 92 | 18:30 | Cox'sbazar | 111 | 18:30 | Pabna | 98 | 21:00
Uttara New | 26 | 18:30 | Chandraghona | 28 | 19:00 | Shahjadpur | 104 | 21:00
Kamrangirchar | 77 | 1:00 | Kaptai | 5.5 | 0.77083 | Serajganj | 96 | 19:30
Savar | 163 | 1:00 | A. Khaer Stl. | 10 | 12:00 | Niyamatpur | 90 | 19:00
Bhasantec | 140 | 19:00 | Bakulia | 95 | 19:00 | Joypurhat | 57 | 21:00
Agargaon | 64 | 19:00 | Julda | 22 | 1:00 | Sherpur(Bogura) | 52 | 19:30
Satmosjid | 91 | 19:30 | TK chemical | 28.6 | 19:30 | Mohastangor | 56 | 21:00
Tongi | 88 | 1:00 | Modern Steel | 0 | #N/A | Bangura | 29 | 20:00
Kabirpur | 199 | 1:00 | Shahmirpur | 26.5 | 1:00 | Rangpur | 122 | 19:00
Basundhara | 151 | 19:30 | Khagrachhari | 24 | 0:00 | Lalmonirhat | 44 | 19:00
Manikganj | 72 | 1:00 | Matarbari | 34 | 23:00 | Saidpur | 97 | 12:00
Joydevpur | 125 | 19:00 | Baroiar Hat | 24 | 1:00 | Purbasadipur | 93 | 19:30
New Tongi | 83 | 12:00 | Rangamati | 13 | 19:00 | Thakurgaon | 75 | 19:00
Kodda | 225 | 11:00 | Abul Khair 230 | 7 | 5:00 | Palashbari | 112 | 19:30
Dhamrai | 92 | 1:00 | BSRM | 143 | 21:00 | Barapukuria | 48 | 19:00
Rajendrapur | 92 | 1:00 | GPH Ispat | 79 | 6:00 | Panchagar | 49 | 19:00
Valuka | 110 | 22:00 | Goalpara | 32 | 1:00 | Joldhaka | 62 | 19:00
Tangail | 226 | 21:00 | Central s/s | 80 | 20:00 | Kurigram | 58 | 19:30
Mymensing | 213 | 18:30 | Noapara | 46 | 0.91667 | Mithapukur | 27 | 19:00
Kishorganj | 132 | 22:00 | Jessore | 125 | 20:00
Netrokona | 104 | 19:30 | Benapol | 64 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 18:00 | 400 | 10:00 | Kaliakoir | 388 | 0.41667 | 382 | 0.41667
| Bheramara | 401 | 13:00 | 396 | 19:00 | Bhulta | 385 | 0.54167 | 375 | 0.45833
| Ashuganj(N) | 389 | 1:00 | 382 | 10:00 | Gopalganj | 409 | 0.625 | 383 | 0.91667
| Payra | 414 | 2:00 | 395 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 8:00 | 230 | 1:00 | Hathazari | 225 | 1:00 | 214 | 15:00
| Ishurdi | 235 | 6:00 | 225 | 15:00 | Megnaghat | 230 | 2:00 | 226 | 5:00
| Ashuganj | 235 | 1:00 | 230 | 11:00 | Fenchuganj | 239 | 18:00 | 234 | 15:00
| Serajganj | 235 | 2:00 | 225 | 7:00 | Siddhirganj | 229 | 13:00 | 225 | 9:00
| Baghabari | 232 | 1:00 | 227 | 11:00 | Maniknagar | 227 | 13:00 | 223 | 11:00
| Barapukuria | 238 | 5:00 | 226 | 19:00 | Agargaon | 224 | 10:00 | 219 | 11:00
| Bogra | 228 | 4:00 | 215 | 19:30 | Barisal | 253 | 18:00 | 235 | 22:00
| Rajshahi | 232 | 18:00 | 221 | 15:00 | Bhola 225 MW | 254 | 6:00 | 238 | 23:00
| Khulna South | 233 | 18:00 | 215 | 19:00 | AKSML | 225 | 18:00 | 219 | 2:00
| Rampura | 227 | 8:00 | 224 | 7:00 | BSRM | 226 | 6:00 | 217 | 15:00
| Haripur | 227 | 18:00 | 225 | 9:00 | Bibiyana | 240 | 4:00 | 233 | 20:00
| Hasnabad | 230 | 7:00 | 220 | 3:00 | Bhulta | 230 | 19:00 | 225 | 11:00
| Shyampur | 224 | 2:00 | 220 | 10:00 | Ashuganj (S) | 234 | 18:00 | 231 | 4:00
| Aminbazar | 226 | 1:00 | 221 | 2:00 | Kaliakoir | 226 | 1:00 | 221 | 10:00
| Tongi | 225 | 1:00 | 218 | 11:00 | GPH | 226 | 9:00 | 217 | 15:00
| Comilla (N) | 226 | 1:00 | 223 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 13:00 | 133 | 10:00 | Madanhat | 135 | 0.041667 | 131 | 0.45833
| Munsiganj | 136 | 13:00 | 133 | 3:00 | Hathazari | 134 | 0.041667 | 129 | 0.625
| Sonargaon | 135 | 1:00 | 132 | 7:00 | Khulshi | 134 | 0.16667 | 126 | 0.625
| Shyampur | 135 | 13:00 | 132 | 10:00 | Halishahar | 134 | 0.79167 | 129 | 0.45833
| Bhulta | 130 | 13:00 | 127 | 10:00 | Baraulia | 133 | 0.041667 | 127 | 0.625
| Madanganj | 137 | 2:00 | 131 | 23:00 | Sikalbaha | 136 | 0.83333 | 119 | 0.5
| Shitalakhya | 138 | 2:00 | 130 | 11:00 | Dohazari | 132 | 0.8125 | 125 | 0.625
| Rahim steal | 135 | 7:00 | 134 | 1:00 | Cox'sbazar | 124 | 0.79167 | 114 | 0
| Matuail | 136 | 13:00 | 133 | 10:00 | Chandraghona | 134 | 0.33333 | 129 | 0.625
| Ghorasal | 138 | 23:00 | 136 | 1:00 | Kaptai | 135 | 0.041667 | 132 | 0.29167
| Narsinghdi | 132 | 18:00 | 126 | 1:00 | A. Khaer Stl. | 133 | 0.8125 | 128 | 0.625
| Haripur (SBU) | 135 | 7:00 | 132 | 11:00 | Bakulia | 135 | 0.8125 | 128 | 0.625
| Sreenagar |  |  |  |  | Julda | 137 | 0.77083 | 131 | 0.375
| Ullon | 135 | 7:00 | 132 | 11:00 | TK Chemical | 135 | 0.041667 | 130 | 0.58333
| Hasnabad | 135 | 1:00 | 131 | 9:00 | Modern Steel
| Magbazar | 135 | 6:00 | 132 | 10:00 | Shahmirpur | 135 | 0.041667 | 128 | 0.625
| Maniknagar | 136 | 13:00 | 134 | 11:00 | Khagrachhari | 134 | 0 | 128 | 0.66667
| Bangabhaban | 136 | 13:00 | 134 | 11:00 | Matarbari | 128 | 0.75 | 118 | 0
| Narinda | 136 | 13:00 | 134 | 11:00 | Baroiar Hat | 132 | 0.375 | 129 | 0.625
| Dhanmondi | 135 | 7:00 | 132 | 11:00 | Rangamati | 133 | 0.25 | 128 | 0.625
| Lalbag | 134 | 2:00 | 129 | 11:00 | Goalpara S/S | 139 | 18:00 | 126 | 19:00
| Madartek | 135 | 6:00 | 132 | 10:00 | Khulna Central S/S | 139 | 18:00 | 126 | 19:00
| Dhaka University | 135 | 7:00 | 132 | 12:00 | Noapara | 135 | 18:00 | 121 | 0.79167
| Aftabnagar | 135 | 7:00 | 132 | 11:00 | Jessore | 131 | 18:00 | 113 | 0.79167
| Fatullah | 136 | 18:00 | 132 | 10:00 | Benapol | 130 | 18:00 | 130 | 0.79167
| Nawabganj | 129 | 1:00 | 125 | 11:00 | Jhenida | 127 | 18:00 | 109 | 0.79167
| Mirpur | 135 | 1:00 | 132 | 16:00 | Bottail | 134 | 0.75 | 122 | 0.79167
| Kalyanpur | 137 | 19:30 | 132 | 16:00 | G.K Project | 139 | 18:00 | 133 | 0.8125
| Gulshan | 134 | 6:00 | 132 | 10:00 | Faridpur | 138 | 0.75 | 126 | 0.8125
| Uttara | 135 | 1:00 | 131 | 10:00 | Madaripur | 141 | 0.75 | 130 | 0.875
| Uttara New | 135 | 19:00 | 130 | 10:00 | Shariyatpur S/S | 139 | 0.70833 | 128 | 0.875
| Kamrangirchar | 134 | 19:30 | 128 | 11:00 | Gopalganj | 145 | 0.25 | 130 | 0.875
| Savar | 137 | 1:00 | 131 | 10:00 | Bagerhat | 136 | 18:00 | 124 | 0.79167
| Bhasantec | 134 | 2:00 | 131 | 10:00 | Mongla | 135 | 0.33333 | 122 | 0.79167
| Agargaon | 135 | 2:00 | 132 | 10:00 | Satkhira | 137 | 18:00 | 122 | 0.79167
| Satmosjid | 134 | 2:00 | 131 | 11:00 | Gallamari | 140 | 18:00 | 125 | 0.77083
| Tongi | 138 | 1:00 | 131 | 17:00 | Magura | 126 | 18:00 | 105 | 19:00
| Kabirpur | 134 | 18:00 | 130 | 12:00 | Narail | 124 | 0.75 | 104 | 19:00
| Basundhara | 135 | 1:00 | 130 | 11:00 | Chuadanga | 122 | 18:00 | 98 | 0.79167
| Manikganj | 138 | 8:00 | 132 | 15:00 | Borguna | 141 | 0.375 | 126 | 0.875
| Joydevpur | 136 | 19:00 | 129 | 11:00 | Barisal(N) | 143 | 18:00 | 131 | 0.875
| New Tongi | 137 | 19:00 | 130 | 11:00 | Barisal (S) | 142 | 18:00 | 128 | 0.83333
| Kodda | 138 | 1:00 | 126 | 13:00 | Patuakhali(S) | 140 | 5:00 | 124 | 21:00
| Dhamrai | 132 | 2:00 | 128 | 20:00 | Bhandaria | 141 | 0.75 | 124 | 0.875
| Rajendrapur | 134 | 19:30 | 122 | 16:00 | Ishurdi | 137 | 0.25 | 131 | 0.79167
| Valuka | 125 | 6:00 | 110 | 19:00 | Ruppur Paromanobik | 136 | 0.25 | 132 | 0.625
| Tangail | 130 | 3:00 | 123 | 22:00 | Natore | 136 | 6:00 | 129 | 19:00
| Mymensing | 128 | 6:00 | 115 | 18:30 | Bogra | 137 | 6:00 | 127 | 19:00
| Kishorganj | 130 | 8:00 | 120 | 18:30 | Noagaon | 129 | 6:00 | 119 | 19:00
| Netrokona | 127 | 6:00 | 112 | 19:00 | Rajshahi | 135 | 6:00 | 128 | 18:30
| Jamalpur | 138 | 3:00 | 125 | 19:00 | Rajshahi New | 137 | 18:00 | 130 | 7:00
| Sherpur | 138 | 3:00 | 122 | 19:00 | C.Nawabganj | 136 | 15:00 | 126 | 19:00
| Srimongal | 140 | 9:00 | 135 | 21:00 | Amnura | 132 | 18:00 | 125 | 7:00
| Shahjibazar | 137 | 9:00 | 132 | 18:30 | Pabna | 135 | 6:00 | 130 | 19:30
| Fenchuganj | 138 | 9:00 | 135 | 15:00 | Shahjadpur | 138 | 17:00 | 133 | 18:30
| Khulawara | 137 | 4:00 | 134 | 20:00 | Serajganj | 133 | 4:00 | 125 | 19:30
| Sylhet | 136 | 1:00 | 133 | 23:00 | Niyamatpur | 126 | 18:00 | 116 | 19:00
| Chatak | 136 | 8:00 | 132 | 19:00 | Joypurhat | 129 | 2:00 | 116 | 19:30
| Sunamganj | 135 | 4:00 | 131 | 20:00 | Sherpur(Bogura) | 135 | 1:00 | 127 | 19:00
| Biani Bazar | 138 | 6:00 | 131 | 20:00 | Mohastangor | 135 | 4:00 | 125 | 19:00
| Comilla(s) | 131 | 4:00 | 120 | 18:30 | Bangura | 136 | 18:00 | 130 | 20:00
| Comilla(n) | 135 | 19:00 | 132 | 3:00 | Rangpur | 135 | 5:00 | 120 | 19:00
| Chandpur | 135 | 23:00 | 128 | 15:00 | Lalmonirhat | 135 | 4:00 | 120 | 18:30
| Feni | 132 | 8:00 | 124 | 15:00 | Saidpur | 134 | 3:00 | 120 | 12:00
| Chowmuhani | 133 | 7:00 | 125 | 15:00 | Purbasadipur | 134 | 3:00 | 115 | 19:00
| Ashuganj | 138 | 18:00 | 135 | 12:00 | Thakurgaon | 131 | 3:00 | 111 | 19:00
| Daudkandi | 134 | 18:00 | 129 | 4:00 | Palashbari | 135 | 3:00 | 121 | 19:30
| B.Baria | 133 | 5:00 | 129 | 19:00 | Barapukuria | 138 | 5:00 | 126 | 19:00

## L-Curve
Date | 2021-04-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 160 | 8052 | 3459 | 11511 |  |  |  | QF-LDC-11
0:30 | 240 | 8134.5 | 3330.5 | 11465 | Date: | 2021-04-02
1:00 | 320 | 8217 | 3202 | 11419
1:30 | 280 | 8095.5 | 3195 | 11290.5
2:00 | 240 | 7974 | 3188 | 11162
2:30 | 202 | 7798 | 3174.5 | 10972.5 | [5 empty] | Gen. at Eve. Peak | 11995 | 11995 MW (21:00 )
3:00 | 164 | 7622 | 3161 | 10783 | [6 empty] | 21:00
3:30 | 164 | 7499.5 | 3134 | 10633.5 | [5 empty] | Gen. at Day Peak | 9745 | 9745 MW (12:00 )
4:00 | 164 | 7377 | 3107 | 10484 | [6 empty] | 12:00
4:30 | 171 | 7343.5 | 3045 | 10388.5 | [5 empty] | Highest Generation | 11995
5:00 | 178 | 7310 | 2983 | 10293 | [6 empty] | 21:00
5:30 | 183 | 7270 | 2901.5 | 10171.5
6:00 | 188 | 7230 | 2820 | 10050
6:30 | 290 | 7118.5 | 2737 | 9855.5
7:00 | 392 | 7007 | 2654 | 9661
7:30 | 394 | 6991.5 | 2618 | 9609.5
8:00 | 396 | 6976 | 2582 | 9558
8:30 | 348 | 6903 | 2552 | 9455
9:00 | 300 | 6830 | 2522 | 9352
9:30 | 229 | 6743.5 | 2537 | 9280.5
10:00 | 158 | 6657 | 2552 | 9209
10:30 | 142 | 6673 | 2656.5 | 9329.5
11:00 | 126 | 6689 | 2761 | 9450
11:30 | 153 | 6774 | 2823.5 | 9597.5
12:00 | 180 | 6859 | 2886 | 9745
12:30 | 252.5 | 7110.5 | 2883.5 | 9994
13:00 | 325 | 7362 | 2881 | 10243
13:30 | 288.5 | 7184 | 2795.5 | 9979.5
14:00 | 252 | 7006 | 2710 | 9716
14:30 | 247 | 7133 | 2730.5 | 9863.5
15:00 | 242 | 7260 | 2751 | 10011
15:30 | 242 | 7227 | 2732 | 9959
16:00 | 242 | 7194 | 2713 | 9907
16:30 | 197 | 7095 | 2664 | 9759
17:00 | 152 | 6996 | 2615 | 9611
17:30 | 129 | 6924 | 2613.5 | 9537.5
18:00 | 106 | 6852 | 2612 | 9464
18:30 | 272 | 7447.5 | 2965 | 10412.5
19:00 | 438 | 8043 | 3318 | 11361
19:30 | 392 | 8343 | 3575 | 11918
20:00 | 320 | 8347 | 3585 | 11932 |  |  |  | Executive Engineer
20:30 | 320 | 8361 | 3602.5 | 11963.5 |  |  |  | Network Operation Division
21:00 | 320 | 8375 | 3620 | 11995
21:30 | 301 | 8362 | 3628.5 | 11990.5
22:00 | 282 | 8349 | 3637 | 11986 |  |  |  |  | Page 6 of 7
22:30 | 261 | 8299.5 | 3576.5 | 11876
23:00 | 240 | 8250 | 3516 | 11766
23:30 | 200 | 8151 | 3487.5 | 11638.5
24:00 | 160 | 8052 | 3459 | 11511
11995 MW (21:00 )
9745 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-02 |  | Energy | 254466674
[11 empty] | 2021-04-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 5272 | 837 | 1416 | 3047 | 720 | 107 | 134 | 0 | 154 | 0
0:30 | 4991 | 840 | 1373 | 3230.5 | 725 | 107 | 175.5 | 0 | 111 | 0 | Date: | 2021-04-02
1:00 | 4710 | 843 | 1330 | 3414 | 730 | 107 | 217 | 0 | 68 | 0
1:30 | 4739.5 | 839.5 | 1328 | 3294 | 730 | 107 | 185.5 | 0 | 67 | 0 | [7 empty] | Total Energy | 254.4667 | Total Energy Gen 254.467 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.467 MKWHr
2:00 | 4769 | 836 | 1326 | 3174 | 730 | 107 | 154 | 0 | 66 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4789 | 836.5 | 1336 | 2999.5 | 710 | 107 | 128.5 | 0 | 66 | 0 | [7 empty] | Energy Requirement | 254.4667
3:00 | 4809 | 837 | 1346 | 2825 | 690 | 107 | 103 | 0 | 66 | 0
3:30 | 4859.5 | 836.5 | 1348 | 2686.5 | 645 | 106 | 87 | 0 | 65 | 0 | [6 empty] | Shortage
4:00 | 4910 | 836 | 1350 | 2548 | 600 | 105 | 71 | 0 | 64 | 0
4:30 | 4935 | 836 | 1352 | 2476.5 | 550 | 105 | 71 | 0 | 63 | 0
5:00 | 4960 | 836 | 1354 | 2405 | 500 | 105 | 71 | 0 | 62 | 0
5:30 | 4958.5 | 836.5 | 1328 | 2362 | 450 | 105.5 | 71 | 0 | 60 | 0
6:00 | 4957 | 837 | 1302 | 2319 | 400 | 106 | 71 | 0 | 58 | 0
6:30 | 4936 | 836.5 | 1251.5 | 2231 | 375 | 107 | 54 | 0 | 57 | 7.5 |  |  |  |  | Coal
7:00 | 4915 | 836 | 1201 | 2143 | 350 | 108 | 37 | 0 | 56 | 15
7:30 | 4903 | 836 | 1183 | 2160 | 300 | 108 | 37 | 0 | 55 | 27.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4891 | 836 | 1165 | 2177 | 250 | 108 | 37 | 0 | 54 | 40
8:30 | 4839 | 836 | 1173.5 | 2175 | 202.5 | 104 | 20.5 | 0 | 49 | 55.5
9:00 | 4787 | 836 | 1182 | 2173 | 155 | 100 | 4 | 0 | 44 | 71
9:30 | 4756.5 | 836.5 | 1196.5 | 2053.5 | 202.5 | 105 | 4 | 0 | 44 | 82
10:00 | 4726 | 837 | 1211 | 1934 | 250 | 110 | 4 | 0 | 44 | 93
10:30 | 4744.5 | 836.5 | 1222.5 | 1956 | 310 | 110 | 4 | 0 | 44 | 102
11:00 | 4763 | 836 | 1234 | 1978 | 370 | 110 | 4 | 0 | 44 | 111
11:30 | 4774.5 | 836 | 1233 | 2075 | 385 | 110 | 27.5 | 0 | 46 | 110.5
12:00 | 4786 | 836 | 1232 | 2172 | 400 | 110 | 51 | 0 | 48 | 110
12:30 | 4830 | 836.5 | 1265 | 2322.5 | 400 | 105 | 46 | 0 | 78 | 111
13:00 | 4874 | 837 | 1298 | 2473 | 400 | 100 | 41 | 0 | 108 | 112
13:30 | 4874 | 837 | 1298 | 2473 | 400 | 100 | 41 | 0 | 108 | 112
14:00 | 4874 | 837 | 1298 | 2473 | 400 | 100 | 41 | 0 | 108 | 112
14:30 | 4902 | 837 | 1325 | 2335.5 | 380 | 105 | 38 | 0 | 110 | 94.5
15:00 | 4930 | 837 | 1352 | 2198 | 360 | 110 | 35 | 0 | 112 | 77
15:30 | 4931 | 836.5 | 1369.5 | 2237 | 270 | 107.5 | 35 | 0 | 110 | 62.5
16:00 | 4932 | 836 | 1387 | 2276 | 180 | 105 | 35 | 0 | 108 | 48
16:30 | 4871.5 | 836.5 | 1382 | 2213 | 180 | 105 | 35 | 0 | 103 | 33
17:00 | 4811 | 837 | 1377 | 2150 | 180 | 105 | 35 | 0 | 98 | 18
17:30 | 4649 | 837 | 1359 | 2146 | 250 | 105 | 66.5 | 0 | 115 | 10
18:00 | 4487 | 837 | 1341 | 2142 | 320 | 105 | 98 | 0 | 132 | 2
18:30 | 4763.5 | 837 | 1372 | 2543 | 390 | 105 | 253 | 0 | 148 | 1
19:00 | 5040 | 837 | 1403 | 2944 | 460 | 105 | 408 | 0 | 164 | 0
19:30 | 5139 | 837 | 1415 | 3226 | 609 | 105 | 425 | 0 | 162 | 0
20:00 | 5272 | 836 | 1424 | 3140 | 640 | 105 | 357 | 0 | 158 | 0
20:30 | 5296.5 | 836.5 | 1425.5 | 3124 | 665 | 105 | 351 | 0 | 160 | 0
21:00 | 5321 | 837 | 1427 | 3108 | 690 | 105 | 345 | 0 | 162 | 0
21:30 | 5304 | 836.5 | 1425 | 3112 | 705 | 105 | 341 | 0 | 162 | 0
22:00 | 5287 | 836 | 1423 | 3116 | 720 | 105 | 337 | 0 | 162 | 0
22:30 | 5276 | 836.5 | 1414.5 | 3081.5 | 720 | 106 | 279.5 | 0 | 162 | 0
23:00 | 5265 | 837 | 1406 | 3047 | 720 | 107 | 222 | 0 | 162 | 0
23:30 | 5268.5 | 837 | 1411 | 3047 | 720 | 107 | 178 | 0 | 158 | 0 | Max Temp. in Dhaka |  | 37° C
24:00 | 5272 | 837 | 1416 | 3047 | 720 | 107 | 134 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 254.467 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.467 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 37 | 37 | 37 | 35 | 35 | 36 | 38 | 38 | 30 | 40 | 40 | 40 | 30 | 40 | 40 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 37 | 37 | 878225
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1676000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614188
| Teknaf 20MW PP (Solartech) | [6 empty] | 3 | 8 | 14 | 18 | 18 | 19 | 18 | 16 | 12 | 7 | 2 | [9 empty] | 125280
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 80 | 110 | 110 | 110 | 70 |  | 110 | 120 | 120 | 120 | 120 | 120 | 120 | 2513374
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 51 | 51 | 51 | 51 | 17 | 17 |  |  |  | 7 | [5 empty] | 39 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 809717
12 | Hathazari 100 MW peaking PP
Sikalbaha 105 MW PP (Baraka Sikalbaha)
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 145 | 145 | 145 | 145 | 145 | 145 | 150 | 145 | 68 |  |  |  | 32 | 70 | 120 | 150 | 110 | 70 |  | 175 | 175 | 175 | 175 | 180 | 180 | 180 | 3100000
17 | Siddhirganj 335 MW CCPP | 222 | 221 | 221 | 221 | 221 | 220 | 220 | 222 | 222 | 221 | 217 | 215 | 215 | 150 | 209 | 211 | 216 | 170 |  | 221 | 221 | 221 | 221 | 222 | 222 | 222 | 5240657
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 95 | [9 empty] | 3 | 15 | 15 | 15 | 15 | 15 | 15 |  | 172 | 120 | 80 | 80 | 80 | 80 | 45 | 1196835
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4063500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7177791
26
28 | Ashuganj TPP Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1947542
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 26 | 26 | 26 | 23 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 586944
33 | Ashuganj 225 MW CCPP | 213 | 215 | 215 | 214 | 214 | 215 | 216 | 215 | 180 | 190 | 181 | 208 | 209 | 208 | 206 | 208 | 182 | 182 |  | 212 | 211 | 210 | 211 | 213 | 213 | 215 | 5003000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 280 | 265 | 265 | 265 | 265 | 290 | 265 | 265 | 265 |  | 265 | 265 | 290 | 305 | 300 | 300 | 300 | 6681000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 265 | 265 | 270 | 260 | 265 | 360 | 260 | 280 | 260 | 260 | 260 |  | 260 | 260 | 285 | 320 | 315 | 310 | 315 | 6947600
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 48 | 47 | 46 | 48 | 47 | 48 |  | 49 | 50 | 50 | 51 | 52 | 52 | 52 | 845280
36 | Chandpur 150 MW CCPP | 140 | 135 | 140 | 140 | 138 | 140 | 135 | 134 | 134 | 141 | 139 | 141 | 133 | 141 | 141 | 138 | 138 | 136 |  | 138 | 140 | 140 | 140 | 140 | 139 | 139 | 3281370
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 342 | 341 | 341 | 342 | 346 | 350 | 345 | 336 | 333 | 324 | 323 | 327 | 347 | 363 | 367 | 377 | 325 |  | 322 | 367 | 363 | 370 | 378 | 379 | 382 | 8833822
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7079750
41 | Haripur 360MW CCPP(HPL) | 181 | 206 | 221 | 226 | 227 | 221 | 215 | 207 | 213 | 205 | 213 | 212 | 222 | 232 | 256 | 263 | 263 | 275 |  | 290 | 286 | 281 | 257 | 255 | 242 | 242 | 5592000
42 | RPCL 210MW CCPP | 146 | 147 | 147 | 147 | 146 | 162 | 162 | 142 | 142 | 125 | 118 | 117 | 117 | 117 | 117 | 134 | 157 | 158 |  | 141 | 143 | 142 | 142 | 142 | 142 | 144 | 3255120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 7 | 18 | 31 | 41 | 52 | 47 | 53 | 37 | 35 | 22 | 8 | 1 | [8 empty] | 339420
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 42 | 42 | 41 | 41 | 41 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1016000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 22 | 22 | 22 | 22 | 20 | 32 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 630000
46 | Shajibazar 330 MW CCPP | 290 | 289 | 290 | 290 | 290 | 288 | 288 | 288 | 290 | 291 | 290 | 290 | 290 | 291 | 294 | 290 | 290 | 288 |  | 290 | 291 | 290 | 288 | 290 | 288 | 290 | 6551000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 77 | 77 | 77 | 79 | 79 | 79 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1893120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 163 | 163 | 162 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 176 | 143 | 145 | 143 | 143 | 122 |  | 163 | 163 | 163 | 151 | 135 | 135 | 136 | 3753110
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 424000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 8 | 8 | 9 | 9 | 9 | 9 | 8 | 9 | 7 | 7 | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 192240
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 47 | 50 | 50 | 50 | 50 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1019400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 383832
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 285 | 285 | 290 | 300 | 290 | 280 | 270 | 290 | 305 | 305 | 295 | 280 | 300 | 300 | 300 | 270 |  | 290 | 280 | 290 | 315 | 315 | 315 | 315 | 7244000
| Bibiyana South 400 MW | 330 | 330 | 330 | 335 | 355 | 330 | 330 | 330 | 347 | 347 | 360 | 351 | 330 | 330 | 360 | 340 | 330 | 320 |  | 370 | 370 | 400 | 400 | 400 | 390 | 398 | 8453000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 937819
59 | Tangail Palli Power Gen 22 MW | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 24 | 24 | 24 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 507120
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 535488
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 482076
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 341964
63 | Impoprt (Tripura) | 68 | 66 | 66 | 64 | 62 | 58 | 56 | 54 | 44 | 44 | 44 | 48 | 108 | 106 | 112 | 108 | 98 | 132 |  | 164 | 162 | 158 | 162 | 162 | 162 | 154 | 2264640
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 39 | 39 | 39 | 38 | 24 | 24 | 10 | 10 | 5 | 15 | 6 | 9 | 14 | 18 | 22 |  | 20 | 26 | 26 | 26 | 26 | 26 | 36 | 611520
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 504468
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250560
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812000
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 493320
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 18 | 15 | 11 | 11 | 15 | 15 | 15 | 15 |  | 16 | 28 | 29 | 30 | 30 | 30 | 30 | 561240
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 804300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 624500
73 | Ghorashal 108MW PP (Regent) | 98 | 98 | 98 | 98 | 98 | 98 | 98 | 96 | 96 | 93 | 95 | 97 | 96 | 97 | 94 | 94 | 94 | 97 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2275954
| Feni Lanka Power | 88 | 50 | [24 empty] | 188100
| Chowmuhani 113 MW | 103 | 105 | 105 | 111 | 111 | 111 | 111 | 111 | 84 | 84 | 84 | 99 | 105 | 65 | 65 | 65 | 65 | 65 |  | 102 | 112 | 110 | 111 | 112 | 110 | 112 | 2441040
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 108 | 72 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 41 | 72 | 54 | 54 | 54 | 54 | 54 |  | 78 | 108 | 108 | 108 | 108 | 108 | 54 | 1716480
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 70 | 30 | 7 | 7 | 7 | 7 | 7 | 7 | 16 | 100 | 50 | 50 | 50 | 24 | 24 |  | 62 | 80 | 70 | 70 | 70 | 70 | 70 | 1268467
78 | Gazipur 52 MW PP
79 | Kodda 150MW PP | 98 | 82 | 48 | 16 | 16 | 16 | 16 | 16 |  |  |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 133 | 147 | 148 | 148 | 140 | 132 | 62 | 1309920
80 | Jamalpur 95 MW PP(Powerpac) | 32 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 24 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 624960
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 34 | 34 | 34 | 34 | 34 | 34 |  | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 773760
| Gazipur 100 MW PP | 35 | [16 empty] | 6 |  | 34 | 50 | 17 | 17 | 17 | 17 | 0 | 207600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 2 | 4 | 3 | 2 | 1 | [9 empty] | 28080
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 42 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1287994
Karnaphuli Power Ltd.
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP(Summit) | 225 | 225 | 225 | 225 | 225 | 225 | 230 | 230 | 230 | 225 | 265 | 265 | 265 | 225 | 225 | 225 | 265 | 260 |  | 260 | 260 | 265 | 265 | 265 | 225 | 225 | 5739462
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 73 | [8 empty] | 9 | 50 | 50 | 50 | 50 | 26 | 24 |  | 54 | 100 | 80 | 50 | 50 | 50 | 40 | 917760
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 72 | 70 | 86 | 104 | 104 | 104 | 104 | 62 | 53 |  | 87 | 104 | 104 | 104 | 104 | 104 | 104 | 2428800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 88 | 88 | 88 | 88 | 88 | 88 | 20 | 20 | 20 | 20 |  |  | 10 | 40 | 40 | 40 | 40 | 40 |  | 86 | 86 | 86 | 86 | 86 | 65 | 65 | 1285920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 16 | [5 empty] | 7 | 7 | 7 | 40 | 40 | 40 | 40 | 40 | 24 | 24 |  | 64 | 64 | 40 | 40 | 40 | 40 | 24 | 751824
95 | Patenga 50MW PP (Baraka) | [19 empty] | 14 | 40 | 47 | 50 | 50 | 50 | 50 | 266400
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1337883
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1228036
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 80 | [20 empty] | 788481
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 16000
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1296720
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 184 | 175 | 184 | 184 | 184 | 184 | 184 | 183 | 182 | 179 | 179 | 178 | 178 | 178 | 175 | 179 | 180 | 183 |  | 192 | 193 | 194 | 200 | 200 | 194 | 185 | 4375200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 142 | 130 | 130 | 130 | 133 | 117 | 81 | 80 | 85 | 106 | 79 | 65 | 65 | 80 | 94 |  | 97 | 115 | 144 | 149 | 149 | 149 | 149 | 2833490
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2397120
116 | Chandpur 200MW (Desh energy) | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 99 | 150 | 152 | 152 | 152 | 152 | 175 | 2145120
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 365 | 367 | 365 | 366 | 365 | 366 | 366 | 366 | 367 | 366 | 367 | 366 | 366 | 366 | 380 | 367 | 319 | 319 |  | 361 | 366 | 380 | 372 | 360 | 366 | 366 | 8762000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 45 | 45 |  | 85 | 115 | 115 | 115 | 115 | 115 | 115 | 2425200
| Anwara 300 MW PP (United) | 107 | 69 | 52 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 33 | 33 | 33 | 16 | 16 | 16 | 16 | 16 |  | 84 | 83 | 83 | 88 | 89 | 89 | 52 | 1098982
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2361600
| Anlima Energy Ltd. | 111 | 111 | 111 | 111 | 112 | 111 | 112 | 111 | 112 | 73 | 73 | 84 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 115 | 110 | 111 | 111 | 111 | 2625764
| Bhairob 54.5 MW | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 37 | 37 | 37 | 37 | 36 | 37 | 36 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 887760
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 9 | 17 | 23 | 28 | 30 | 30 | 26 | 20 | 12 | 5 | 0 | [8 empty] | 204320
120 | Eastern Zone Total | 8217 | 7974 | 7622 | 7377 | 7310 | 7230 | 7007 | 6976 | 6830 | 6657 | 6689 | 6859 | 7362 | 7006 | 7260 | 7194 | 6996 | 6852 |  | 8043 | 8343 | 8347 | 8375 | 8349 | 8250 | 8052 | 180345512
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 83 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 83 | 83 | 2291520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 9 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 4 | 4 | 3 | 3 | 3 | 3 |  | 19 | 18 | 4 | 4 | 4 | 4 | 4 | 114240
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 70 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 53 |  | 105 | 105 | 105 | 105 | 94 | 94 | 94 | 1335360
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | [12 empty] | 28 | 28 | 48 | 68 | 68 | 74 |  | 74 | 74 | 74 | 74 | 75 | 75 | 75 | 723873
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 48 |  | 40 | 80 | 64 | 48 | 48 | 48 | 48 | 48 | 80 | 48 | 48 |  | 48 | 48 | 48 |  | 16 | 32 | 16 | 1427040
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 64 | 63 | 64 | 63 | 63 | 63 | 64 | 63 | 85 | 95 | 92 | 92 | 92 | 92 | 93 | 94 | 81 | 43 |  | 62 | 78 | 82 | 82 | 78 | 73 | 73 | 1812760
| Bhola 225 MW CCPP | 68 | 58 | 62 | 67 | 68 | 62 | 65 | 63 | 53 | 64 | 65 | 62 | 40 | 60 | 65 | 65 | 60 | 52 |  | 67 | 58 | 67 | 68 | 68 | 68 | 68 | 1524000
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 29 | 28 | 26 | 23 | 20 | 18 | 19 | 18 | 17 | 20 | 21 | 21 | 23 | 20 | 18 | 22 |  | 27 | 29 | 29 | 30 | 30 | 31 | 31 | 569292
141 | Noapara 100 MW PP (Bangla Trac) | 50 | 30 | [18 empty] | 50 | 50 | 80 | 80 | 80 | 80 | 526080
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 16 | 16 | 16 | 16 | 16 | 16 | [11 empty] | 40 | 40 | 40 | 40 | 40 | 40 | 33 | 389625
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 0 | 7 |  | 12 | 12 | 12 |  |  |  |  | 27904
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [15 empty] | 20 | 22 | [9 empty] | 36432
146 | Bheramara HVDC | 843 | 836 | 837 | 836 | 836 | 837 | 836 | 836 | 836 | 837 | 836 | 836 | 837 | 836 | 837 | 836 | 837 | 837 |  | 837 | 837 | 836 | 837 | 836 | 837 | 837 | 20215273
147 | Bheramara 410 MW CCPP | 195 | 250 | 295 | 340 | 370 | 410 | 410 | 415 | 410 | 375 | 375 | 375 | 375 | 375 | 380 | 350 | 350 | 270 |  | 355 | 350 | 385 | 375 | 365 | 360 | 355 | 8662464
148 | Payra 1320 MW | 580 | 580 | 540 | 450 | 350 | 250 | 200 | 100 | 5 | 100 | 220 | 250 | 250 | 250 | 210 | 30 | 30 | 170 |  | 310 | 460 | 490 | 540 | 570 | 570 | 570 | 8666300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 3665300
153 | Baghabari 71 MW GTPP | [19 empty] | 65 | 70 | 65 | 65 | 65 | 65 | 65 | 365000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | [5 empty] | 64032
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 125 | 140 | 135 | 100 | 100 | 133 | 139 | 116 |  | 122 | 144 | 144 | 144 | 144 | 145 | 146 | 2778900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 180 | 186 | 192 | 204 | 211 | 210 | 163 | 155 | 156 | 160 | 193 | 190 | 187 | 140 | 167 | 193 | 169 | 165 |  | 178 | 186 | 189 | 197 | 196 | 192 | 186 | 4592909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 179 | 189 | 194 | 209 | 204 | 172 | 169 | 168 | 168 | 180 | 190 | 198 | 191 | 161 | 184 | 193 | 179 | 169 |  | 182 | 184 | 187 | 200 | 197 | 194 | 188 | 4693855
Sirajgonj 225MW CCPP Unit-3 (Oil)
Sirajgonj 400 MW CCPP Unit-4
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 20 | 20 | 19 | 17 | 16 | 17 | 19 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 477840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246780
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 9 | [25 empty] | 10055
168 | Santahar 50 MW Peaking PP | 33 | [16 empty] | 17 |  | 34 | 33 | 33 | 33 | 33 |  |  | 216848
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 52 | 52 | 25 | 25 | 25 | 8 | 8 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 812640
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 92 | 92 | 92 | 92 | 92 | 18 |  | 373224
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 93 | 93 | 93 |  | 93 | 93 | 93 | 94 | 94 | 94 | 94 | 2355072
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2524896
173 | Rangpur 20 MW GTPP | [11 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [11 empty] | 5 | 5 | [6 empty] | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 6000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 106 | 106 | 70 | 70 | 100 | 106 | 106 | 106 | 106 | 106 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2565120
177 | Sympa Solar Power 8MW | [6 empty] | 1 | 2 | 4 | 5 | 6 | 7 | 7 | 6 | 5 | 4 | 2 | 1 | [8 empty] | 50528
178
178