## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-06 | Tuesday
|  |  | Date (day): | 2021-04-06 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15314.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16000 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-05 | 2021-04-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170 | 20 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 78 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 99 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 325 | 272 | 300 | 300 | 112 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 232 | 195 | 250 | 250 | 110 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 400 | 400 | 50 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 160 | 240 | 270 | 270 | 35 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 42 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 97 | 185 | 180 | 180 | 30 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 60 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 220 | 221 | 222 | 222 |  | 113 | ST under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 32 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 82 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 40 |  | 15 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 54 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 16 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 29 | 95 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 17 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 72 | 17 | 144 | 144 |  | 18 | Engine problem
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 0 | 0 | 34 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6171 | 5972 | 2698 | 2899 | 4204 | 4429 | 465 | 839
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 9 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 15 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 18 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 70 | 70 | 70 | 160 |  | Low water lavel
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 204 | 225 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 82 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 50 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 80 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 15 | 15 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 53 | 17 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 726 | 904 | 1664 | 1697 | 520 | 133
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 100 | 100 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 214 | 225 | 225 |  |  | FGMO
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 15 | 310 | 360 | 360 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 230 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 50 | 50
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | Machine problem
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 155 | 180 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 140 | 151 | 168
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 0 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 17 | 17 | 17 |  | 8 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 65 | 113 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 0 | 0 | 6 | 18 | 37 | 37
|  | Cumilla Area Total |  |  |  |  | 3040 | 2980 | 1085 | 1577 | 2009 | 2176 | 564 | 81
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 134 | 158 | 160 | 160 | 42 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 17 | 17 | 17 |  | 5 | Engine problem
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 41 | 49 | 49 |  | 46 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 192 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 85 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 352 | 517 | 614.6 | 563 | 42 | 51
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 44 | 44 |  | 26 | Engine problem
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 43 | 43 |  | 47 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 70 | 163 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 165 | 164 | 165 | 165 |  | 165
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 44 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 33 | 33 | 33 | 33 |  | 33 | GT-9 Under maint.
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 75 | 75 | 75 |  | 11 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | Under maint |  | 20/04/2021
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 30 | 217 | 225 | 225
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 310 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 356 | 355 | 400 | 400
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 10 | 10
| 103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2416 | 2371 | 1561 | 1890 | 1997 | 1997 | 0 | 401
| 104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 837 | 836 | 843 | 843
| 105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 88 | 99 | 99 | 99 |  | 16 | Engine problem
| 106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 410 | 370 | 400 | 400
| 110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 40 | 40 | 40
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 70 | 100 | 100
| 113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1370 | 1515 | 1712 | 1998 | 0 | 99
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 32 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 14 | 25 | 25 | 25 |  | 8 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 67 | 70 | 70 |  | 124 | GT-2 under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 35 | 75 | 95 | 95
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 500 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 53 | 73 | 0 | 0 |  |  | On Test
| 119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 467 | 772 | 1072 | 1072 | 0 | 132
| 120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 65 | 65
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| 124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 |  |  | Fuel shortage
| 125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
| 126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 10 | 147 | 144 | 144
| 127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 36 | 207 | 220 | 220 |  |  | FGMO
| 128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 188 | 210 | 210 |  |  | FGMO
| 129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 7 | 47 | 400 | 400
| 130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34
| 131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 10 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 5 | 11 | 11
| 134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 52 | 52 | 52
| 135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 94 | 94 |  | 19 | Engine problem
| 138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2183 | 467 | 1009 | 1761 | 1795 | 100 | 19
| 139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 10 | 10 |  | 10 | Engine problem
| 142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 106 | 113 | 113
| 144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 270 | 264 | 281 | 273 | 124 | 200
|  | Total |  |  |  |  | 21778 | 21312 | 8996 | 11347 | 15314.6 | 16000 | 1815 | 1955
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8604.3525 | 10853 | 14647.8676 | 15303.4282
| A. |  | 2021-04-05 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 11347 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 6383 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11347 | MW
| 3 | Day peak Generation : |  |  | 8996 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10853 | MW
| 4 | Evening peak Generation : |  |  | 11347 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 214.116 | MKWHr | By Solar | 0.80527 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 143.6054 | MKWHr |  | By Oil: | 36.4562 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.5523 | MKWHr |  | By Hydro: | 1.196 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1815 | MW | Dhaka | 3765 | 3765 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1955 | MW | Chittagong | 1211 | 1211 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 3770 | MW | Khulna | 1327 | 1327 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1220.86 | MMCFD |  |  | Rajshahi | 1199 | 1199 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151893353.5 | ii) Oil : | Taka | 252048255.09 | Comilla | 1049 | 1049 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 58877075 | Total | Taka | 462818683.59 | Mymensingh | 870 | 870 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.862 | MKWHr. | Sylhet | 404 | 404 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -84 | MW (E to W) at | 19:30 | hrs | Barisal | 285 | 285 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -370 | MW at | 6:00 | hrs | Rangpur | 743 | 743 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.7° C |  |  | Total | 10853 | 10853 |  | 0
| B. |  | 2021-04-06 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 37.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 16000 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
| 4 | Reserve(Generation end) |  |  |  | 4000 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 226.438 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8101 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 836 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.495 | MKWHr. | iii) Maximum HVDC Flow : |  | 837 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.61 |  | (b) Today: | 83.49 |  | (c) Rule Curve: |  | 87.2
.

## YesterdayGen
2021-04-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 250 | 73 | 0 | 340 | 303 |  | 0 | 320 | 150 | 0 | 0 | 10 | 12 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 14 | 0 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 208 | 0 | 120 | 0 |  | 12 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 0 | 0 | 0 | 250 | 205 | 216 | 8 | 85 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 25 | 5 | 72 | 160 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 126 | 34 | 64 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 20 | 370 | 17 | 0 | 0 | 17 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 144 | 0 | 0 | 0 | 196 | 0 | 0 | 17 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 4916 | 1637 | 6553 | 3931 | 384 | 1195 | 587 | 349 | 35 | 0 | 72 | 0 | 0 | 83.66
2:00 | 0 | 0 | 0 | 110 | 250 | 73 | 0 | 346 | 323 |  | 0 | 320 | 150 | 0 | 0 | 15 | 145 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 206 | 0 | 120 | 0 |  | 19 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 0 | 0 | 0 | 255 | 200 | 216 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 25 | 5 | 74 | 164 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 128 | 35 | 64 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 370 | 17 | 0 | 0 | 14 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 70 | 0 | 34 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 5069 | 1618 | 6687 | 4080 | 384 | 1202 | 562 | 350 | 35 | 0 | 74 | 0 | 0 | 83.65
3:00 | 0 | 0 | 0 | 110 | 250 | 73 | 0 | 350 | 322 |  | 0 | 320 | 150 | 0 | 0 | 15 | 145 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 10 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 120 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 36 | 0 | 0 | 0 | 255 | 205 | 187 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 5 | 76 | 163 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 126 | 35 | 50 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 17 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 370 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 4986 | 1571 | 6557 | 4040 | 384 | 1202 | 470 | 350 | 35 | 0 | 76 | 0 | 0 | 83.64
4:00 | 0 | 0 | 0 | 110 | 250 | 73 | 0 | 350 | 322 |  | 0 | 320 | 150 | 0 | 0 | 15 | 144 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 22 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 120 | 0 |  | 18 | 0 | 0 | 0 | 0 | 0 | 18 | 37 | 0 | 0 | 0 | 260 | 200 | 180 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 5 | 74 | 165 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 127 | 35 | 50 | 0 | 0 | 0 | 0 | 9 | 290 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 370 | 17 | 0 | 0 | 0 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 4925 | 1541 | 6466 | 3996 | 384 | 1194 | 433 | 350 | 35 | 0 | 74 | 0 | 0 | 83.63
5:00 | 0 | 0 | 0 | 110 | 250 | 73 | 0 | 350 | 323 |  | 0 | 320 | 150 | 0 | 0 | 0 | 145 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 22 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 120 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 18 | 34 | 0 | 0 | 0 | 255 | 205 | 183 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 5 | 74 | 165 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 127 | 35 | 50 | 0 | 0 | 0 | 0 | 9 | 285 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 138 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 4894 | 1496 | 6390 | 3993 | 384 | 1187 | 368 | 349 | 35 | 0 | 74 | 0 | 0 | 83.62
6:00 | 0 | 0 | 0 | 110 | 250 | 72 | 0 | 350 | 323 |  | 0 | 320 | 150 | 0 | 0 | 0 | 145 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 22 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 215 | 0 | 120 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 18 | 18 | 0 | 0 | 0 | 255 | 205 | 188 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 5 | 72 | 165 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 126 | 35 | 50 | 0 | 0 | 0 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 370 | 0 | 1 | 0 | 0 | 0 | 0 | 0 |  | 384 | 0 | 330 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 0 | 164 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 200 | 0 | 0 | 0 |  | 4910 | 1473 | 6383 | 3988 | 384 | 1185 | 368 | 350 | 35 | 0 | 72 | 1 | 0 | 83.61
7:00 | 0 | 0 | 0 | 110 | 250 | 72 | 0 | 354 | 324 |  | 0 | 320 | 150 | 0 | 0 | 0 | 175 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 24 | 22 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 19 | 38 | 0 | 0 | 0 | 260 | 200 | 181 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 5 | 74 | 166 | 24 | 0 | 0 | 43 | 43 | 22 | 0 | 0 | 126 | 36 | 50 | 0 | 0 | 0 | 0 | 9 | 315 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 17 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 370 | 0 | 9 | 0 | 0 | 0 | 0 | 5 |  | 619 | 0 | 370 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 123 | 0 | 0 | 0 | 181 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 200 | 0 | 0 | 0 |  | 5091 | 1769 | 6860 | 4164 | 619 | 1212 | 392 | 349 | 35 | 0 | 74 | 15 | 0 | 83.6
8:00 | 0 | 0 | 0 | 110 | 250 | 72 | 0 | 346 | 293 |  | 0 | 320 | 150 | 0 | 0 | 9 | 221 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 25 | 32 | 0 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 216 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 0 | 0 | 0 | 250 | 200 | 201 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 3 | 78 | 163 | 24 | 16 | 1 | 43 | 43 | 22 | 0 | 0 | 126 | 34 | 50 | 0 | 0 | 0 | 0 | 7 | 280 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 10 | 17 | 0 | 361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 30 | 370 | 16 | 22 | 0 | 0 | 0 | 0 | 12 |  | 837 | 0 | 385 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 133 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 200 | 0 | 0 | 0 |  | 5079 | 2009 | 7088 | 4172 | 837 | 1122 | 457 | 350 | 35 | 0 | 78 | 37 | 0 | 83.6
9:00 | 0 | 0 | 0 | 110 | 300 | 89 | 0 | 334 | 281 |  | 0 | 320 | 150 | 0 | 0 | 16 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 20 | 3 | 0 | 0 | 0 | 250 | 240 | 181 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 3 | 84 | 161 | 24 | 16 | 2 | 43 | 43 | 48 | 0 | 10 | 125 | 34 | 69 | 0 | 0 | 0 | 0 | 7 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 50 | 34 | 0 | 332 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 8 | 90 | 370 | 42 | 35 | 0 | 0 | 0 | 0 | 21 |  | 837 | 0 | 410 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 52 | 0 | 34 | 0 | 3 | 70 | 220 | 28 | 0 | 0 |  | 5260 | 2231 | 7491 | 4168 | 837 | 1206 | 728 | 370 | 35 | 0 | 84 | 63 | 0 | 83.59
10:00 | 0 | 0 | 0 | 110 | 300 | 96 | 0 | 348 | 243 |  | 0 | 320 | 150 | 4 | 0 | 22 | 190 | 0 | 155 | 4 | 3 | 0 | 0 | 0 | 0 | 0 | 53 | 55 | 0 | 0 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 3 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 20 | 0 | 0 | 20 | 3 | 0 | 0 | 0 | 30 | 240 | 181 | 8 | 86 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 9 | 84 | 160 | 24 | 16 | 2 | 43 | 43 | 48 | 0 | 70 | 132 | 34 | 73 | 0 | 0 | 0 | 0 | 7 | 300 | 8 | 2 | 0 | 0 | 0 | 0 | 10 | 0 | 80 | 7 | 70 | 100 | 0 | 331 | 0 | 0 | 0 | 2 | 0 | 9 | 0 | 0 | 36 | 100 | 370 | 104 | 46 | 4 | 5 | 0 | 0 | 28 |  | 837 | 0 | 410 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 202 | 0 | 0 | 17 | 0 | 93 | 0 | 106 | 0 | 5 | 95 | 260 | 26 | 0 | 0 |  | 5606 | 2362 | 7968 | 3974 | 837 | 1259 | 1279 | 410 | 35 | 0 | 84 | 90 | 0 | 83.59
11:00 | 0 | 0 | 0 | 120 | 300 | 96 | 0 | 333 | 236 |  | 0 | 320 | 150 | 47 | 0 | 42 | 220 | 0 | 75 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 29 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 8 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 20 | 0 | 0 | 20 | 3 | 0 | 0 | 0 | 15 | 230 | 189 | 8 | 87 | 26 | 30 | 0 | 0 | 0 | 0 | 12 | 19 | 0 | 33 | 11 | 94 | 133 | 24 | 14 | 2 | 43 | 43 | 48 | 0 | 70 | 164 | 32 | 72 | 0 | 0 | 0 | 0 | 7 | 290 | 8 | 2 | 0 | 0 | 0 | 0 | 100 | 0 | 149 | 19 | 30 | 144 | 0 | 352 | 0 | 0 | 0 | 3 | 0 | 54 | 0 | 0 | 65 | 90 | 400 | 104 | 52 | 72 | 53 | 0 | 0 | 32 |  | 837 | 0 | 410 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 0 | 195 | 0 | 0 | 35 | 0 | 93 | 0 | 113 | 0 | 7 | 95 | 310 | 53 | 0 | 0 |  | 6111 | 2460 | 8571 | 3930 | 837 | 1278 | 1822 | 460 | 35 | 0 | 94 | 115 | 0 | 83.58
12:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 325 | 232 |  | 0 | 320 | 160 | 50 | 0 | 42 | 220 | 0 | 97 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 20 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 15 | 230 | 181 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 25 | 19 | 0 | 33 | 14 | 108 | 134 | 24 | 14 | 2 | 43 | 42 | 50 | 0 | 70 | 165 | 33 | 72 | 0 | 30 | 0 | 0 | 7 | 280 | 8 | 5 | 0 | 29 | 0 | 0 | 100 | 0 | 149 | 15 | 80 | 155 | 0 | 356 | 0 | 0 | 0 | 4 | 0 | 54 | 0 | 0 | 65 | 100 | 400 | 104 | 54 | 72 | 53 | 0 | 6 | 34 |  | 837 | 0 | 410 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 10 | 0 | 36 | 0 | 35 | 0 | 187 | 0 | 7 | 35 | 0 | 94 | 0 | 113 | 0 | 7 | 95 | 350 | 53 | 0 | 0 |  | 6422 | 2574 | 8996 | 4142 | 837 | 1297 | 1961 | 500 | 35 | 0 | 108 | 116 | 0 | 83.58
13:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 306 | 221 |  | 0 | 320 | 220 | 50 | 0 | 42 | 216 | 0 | 150 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 30 | 0 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 6 | 90 | 0 | 0 | 35 | 230 | 181 | 8 | 87 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 19 | 8 | 33 | 17 | 106 | 133 | 24 | 16 | 2 | 43 | 42 | 53 | 0 | 90 | 163 | 33 | 75 | 0 | 60 | 0 | 0 | 5 | 290 | 8 | 5 | 0 | 60 | 0 | 0 | 84 | 0 | 132 | 9 | 80 | 155 | 0 | 354 | 0 | 0 | 0 | 4 | 0 | 54 | 0 | 0 | 36 | 90 | 396 | 53 | 52 | 35 | 53 | 0 | 17 | 32 |  | 837 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 121 | 0 | 80 | 0 | 36 | 0 | 189 | 0 | 95 | 35 | 0 | 94 | 0 | 113 | 0 | 7 | 95 | 380 | 52 | 0 | 0 |  | 6425 | 2869 | 9294 | 4406 | 837 | 1413 | 1861 | 530 | 35 | 0 | 106 | 106 | 9294 | 83.57
14:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 301 | 221 |  | 0 | 320 | 220 | 28 | 0 | 42 | 217 | 0 | 185 | 20 | 16 | 6 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 22 | 25 | 24 | 0 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 5 | 90 | 0 | 0 | 40 | 230 | 180 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 20 | 8 | 33 | 17 | 112 | 130 | 24 | 16 | 2 | 42 | 42 | 53 | 0 | 163 | 164 | 32 | 75 | 0 | 160 | 0 | 0 | 5 | 300 | 15 | 5 | 0 | 30 | 0 | 0 | 100 | 0 | 115 | 13 | 100 | 153 | 0 | 356 | 0 | 0 | 0 | 4 | 0 | 54 | 0 | 0 | 8 | 90 | 400 | 53 | 47 | 35 | 53 | 0 | 18 | 29 |  | 837 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 144 | 0 | 162 | 0 | 35 | 0 | 188 | 0 | 227 | 35 | 0 | 94 | 0 | 113 | 0 | 5 | 95 | 390 | 48 | 0 | 0 |  | 6613 | 3133 | 9746 | 4678 | 837 | 1625 | 1779 | 539 | 70 | 6 | 112 | 100 | 0 | 83.57
15:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 296 | 241 |  | 0 | 320 | 220 | 24 | 0 | 42 | 216 | 0 | 177 | 20 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 5 | 22 | 25 | 27 | 0 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 4 | 90 | 0 | 0 | 58 | 230 | 213 | 8 | 129 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 20 | 11 | 33 | 17 | 124 | 129 | 24 | 16 | 1 | 42 | 42 | 50 | 0 | 163 | 165 | 33 | 75 | 0 | 188 | 0 | 0 | 5 | 300 | 15 | 5 | 0 | 30 | 0 | 0 | 125 | 0 | 115 | 13 | 100 | 166 | 0 | 355 | 0 | 0 | 0 | 3 | 0 | 54 | 0 | 0 | 8 | 90 | 401 | 53 | 36 | 35 | 53 | 0 | 18 | 23 |  | 837 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 143 | 0 | 214 | 0 | 34 | 0 | 190 | 0 | 340 | 35 | 0 | 94 | 0 | 113 | 0 | 3 | 95 | 390 | 68 | 0 | 0 |  | 6795 | 3272 | 10067 | 4795 | 837 | 1772 | 1818 | 540 | 70 | 32 | 124 | 79 | 0 | 83.56
16:00 | 0 | 0 | 0 | 170 | 300 | 93 | 0 | 291 | 234 |  | 0 | 320 | 220 | 24 | 0 | 30 | 215 | 0 | 175 | 20 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 22 | 25 | 27 | 0 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 5 | 132 | 0 | 0 | 140 | 230 | 212 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 18 | 11 | 33 | 17 | 122 | 132 | 24 | 17 | 1 | 42 | 42 | 50 | 0 | 163 | 165 | 33 | 72 | 0 | 217 | 0 | 0 | 5 | 290 | 15 | 5 | 0 | 15 | 0 | 0 | 140 | 0 | 102 | 8 | 60 | 136 | 0 | 355 | 0 | 0 | 0 | 2 | 0 | 54 | 0 | 0 | 8 | 90 | 398 | 17 | 23 | 35 | 17 | 0 | 18 | 15 |  | 836 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 213 | 0 | 34 | 0 | 195 | 0 | 338 | 35 | 0 | 94 | 0 | 109 | 0 | 2 | 70 | 390 | 74 | 0 | 0 |  | 6728 | 3260 | 9988 | 4916 | 836 | 1755 | 1650 | 540 | 70 | 48 | 122 | 51 | 0 | 83.56
17:00 | 0 | 0 | 0 | 170 | 300 | 52 | 0 | 300 | 222 |  | 0 | 320 | 260 | 24 | 0 | 30 | 180 | 0 | 108 | 20 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 20 | 22 | 25 | 27 | 0 | 17 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 9 | 135 | 0 | 0 | 165 | 240 | 212 | 8 | 50 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 21 | 11 | 33 | 17 | 116 | 152 | 24 | 17 | 0 | 42 | 42 | 22 | 0 | 130 | 165 | 33 | 75 | 0 | 202 | 0 | 0 | 5 | 280 | 15 | 5 | 0 | 15 | 0 | 0 | 140 | 0 | 100 | 2 | 60 | 136 | 0 | 355 | 0 | 0 | 0 | 1 | 0 | 54 | 0 | 0 | 8 | 100 | 400 | 17 | 9 | 35 | 17 | 0 | 18 | 6 |  | 836 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 5 | 0 | 54 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 201 | 0 | 35 | 0 | 187 | 0 | 280 | 35 | 0 | 94 | 0 | 109 | 0 | 1 | 70 | 390 | 63 | 0 | 0 |  | 6532 | 3156 | 9688 | 4768 | 836 | 1569 | 1717 | 540 | 70 | 53 | 116 | 19 | 0 | 83.55
18:00 | 0 | 0 | 0 | 170 | 300 | 52 | 0 | 291 | 212 |  | 0 | 320 | 260 | 24 | 0 | 30 | 180 | 0 | 70 | 20 | 32 | 48 | 9 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 25 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 4 | 10 | 0 | 1 | 20 | 4 | 100 | 0 | 0 | 255 | 240 | 181 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 21 | 11 | 33 | 17 | 112 | 153 | 24 | 17 | 0 | 43 | 43 | 22 | 0 | 110 | 165 | 33 | 75 | 0 | 182 | 0 | 0 | 7 | 270 | 16 | 11 | 0 | 17 | 0 | 0 | 140 | 0 | 100 | 0 | 60 | 136 | 0 | 355 | 7 | 5 | 0 | 0 | 10 | 54 | 0 | 0 | 8 | 100 | 400 | 17 | 1 | 35 | 17 | 0 | 12 | 1 |  | 837 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 0 | 9 | 0 | 65 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 158 | 0 | 45 | 0 | 187 | 0 | 48 | 35 | 0 | 94 | 0 | 110 | 0 | 0 | 70 | 390 | 73 | 0 | 0 |  | 6563 | 2886 | 9449 | 4707 | 837 | 1321 | 1777 | 540 | 70 | 83 | 112 | 2 | 0 | 83.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
19:00 | 0 | 0 | 0 | 170 | 300 | 94 | 0 | 280 | 201 |  | 0 | 320 | 260 | 24 | 0 | 45 | 221 | 0 | 175 | 25 | 32 | 98 | 20 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 25 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 191 | 0 | 130 | 0 |  | 24 | 0 | 85 | 50 | 0 | 17 | 20 | 12 | 135 | 0 | 0 | 310 | 245 | 216 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 17 | 140 | 159 | 41 | 17 | 0 | 44 | 43 | 53 | 0 | 163 | 164 | 34 | 75 | 0 | 217 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 115 | 0 | 0 | 161 | 0 | 120 | 0 | 100 | 143 | 0 | 355 | 64 | 40 | 0 | 0 | 16 | 54 | 0 | 0 | 75 | 100 | 400 | 68 | 0 | 35 | 17 | 0 | 15 | 0 |  | 837 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 6 | 40 | 57 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 31 | 34 | 33 | 22 | 0 | 5 | 0 | 0 | 150 | 10 | 0 | 136 | 0 | 177 | 0 | 75 | 29 | 189 | 0 | 48 | 105 | 0 | 94 | 0 | 109 | 0 | 0 | 100 | 420 | 65 | 0 | 0 |  | 7659 | 3381 | 11040 | 5086 | 837 | 1478 | 2496 | 570 | 70 | 363 | 140 | 0 | 0 | 83.53
19:30 | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 272 | 195 |  | 0 | 320 | 240 | 0 | 0 | 55 | 221 | 0 | 185 | 60 | 32 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 25 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 85 | 50 | 0 | 18 | 20 | 15 | 135 | 0 | 0 | 310 | 230 | 214 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 140 | 158 | 41 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 33 | 75 | 0 | 217 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 180 | 0 | 355 | 85 | 17 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 17 | 17 | 0 | 18 | 0 |  | 836 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 5 | 0 | 0 | 150 | 8 | 0 | 147 | 0 | 207 | 0 | 75 | 100 | 188 | 0 | 47 | 70 | 0 | 94 | 0 | 106 | 0 | 0 | 113 | 500 | 73 | 0 | 0 |  | 7787 | 3560 | 11347 | 5158 | 836 | 1516 | 2668 | 650 | 70 | 309 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 275 | 187 |  | 0 | 320 | 240 | 0 | 0 | 55 | 220 | 0 | 175 | 50 | 32 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 30 | 25 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 85 | 50 | 0 | 18 | 20 | 22 | 135 | 0 | 0 | 335 | 245 | 216 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 140 | 137 | 41 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 165 | 35 | 75 | 0 | 230 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 180 | 0 | 355 | 85 | 17 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 17 | 17 | 0 | 18 | 0 |  | 837 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 63 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 5 | 0 | 0 | 150 | 5 | 0 | 147 | 0 | 213 | 0 | 75 | 100 | 189 | 0 | 72 | 70 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 500 | 71 | 0 | 0 |  | 7775 | 3565 | 11340 | 5170 | 837 | 1508 | 2659 | 650 | 70 | 306 | 140 | 0 | 0 | 83.54
21:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 264 | 176 |  | 0 | 320 | 240 | 0 | 0 | 30 | 220 | 0 | 185 | 16 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 85 | 20 | 0 | 18 | 20 | 29 | 135 | 0 | 0 | 365 | 230 | 215 | 8 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 142 | 136 | 41 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 34 | 75 | 0 | 224 | 0 | 0 | 9 | 290 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 180 | 0 | 362 | 55 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 0 | 17 | 0 | 18 | 0 |  | 837 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 68 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 219 | 0 | 64 | 100 | 193 | 0 | 105 | 70 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 520 | 74 | 0 | 0 |  | 7532 | 3641 | 11173 | 5220 | 837 | 1542 | 2409 | 670 | 70 | 283 | 142 | 0 | 0 | 83.53
22:00 | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 255 | 176 |  | 0 | 320 | 230 | 0 | 0 | 30 | 220 | 0 | 180 | 16 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 24 | 0 | 85 | 20 | 0 | 18 | 20 | 35 | 135 | 0 | 0 | 310 | 240 | 216 | 8 | 89 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 142 | 139 | 49 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 34 | 73 | 0 | 224 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 179 | 0 | 352 | 55 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 0 | 17 | 0 | 18 | 0 |  | 837 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 69 | 27 | 40 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 220 | 0 | 77 | 100 | 193 | 0 | 0 | 70 | 0 | 94 | 0 | 107 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 7485 | 3464 | 10949 | 5134 | 837 | 1400 | 2414 | 670 | 70 | 282 | 142 | 0 | 0 | 83.53
23:00 | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 254 | 176 |  | 0 | 320 | 230 | 0 | 0 | 30 | 220 | 0 | 150 | 16 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 205 | 0 | 130 | 0 |  | 24 | 0 | 19 | 20 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 320 | 240 | 199 | 8 | 86 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 140 | 138 | 49 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 34 | 73 | 0 | 223 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 142 | 0 | 100 | 180 | 0 | 361 | 24 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 65 | 100 | 400 | 104 | 0 | 0 | 17 | 0 | 18 | 0 |  | 836 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 8 | 69 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 200 | 0 | 96 | 0 | 187 | 0 | 0 | 70 | 0 | 94 | 0 | 84 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 7148 | 3182 | 10330 | 5066 | 836 | 1381 | 2075 | 670 | 70 | 92 | 140 | 0 | 0 | 83.52
24:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 343 | 192 |  | 0 | 320 | 230 | 0 | 0 | 30 | 221 | 0 | 150 | 16 | 7 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 31 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 17 | 20 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 310 | 70 | 218 | 8 | 88 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 114 | 139 | 49 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 35 | 73 | 0 | 223 | 0 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 116 | 0 | 100 | 181 | 0 | 367 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 65 | 100 | 370 | 104 | 0 | 0 | 17 | 0 | 15 | 0 |  | 837 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 148 | 0 | 185 | 0 | 97 | 0 | 188 | 0 | 0 | 70 | 0 | 94 | 0 | 47 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6992 | 3016 | 10008 | 4944 | 837 | 1416 | 1912 | 650 | 70 | 65 | 114 | 0 | 0 | 83.52
KWH | 0 | 0 | 0 | 3465000 | 6753500 | 1994727 | 0 | 7661570 | 6048000 |  | 0 | 7073500 | 4597324 | 321600 | 0 | 650740 | 4475384 | 0 | 3612000 | 462720 | 365904 | 548640 | 36440 | 0 | 0 | 0 | 1147320 | 922804 | 301828 | 223056 | 600000 | 610920 | 370700 | 585300 | 39360 | 0 | 0 | 1196000 | 0 | 0 | 344745 | 4927178 | 0 | 3034988 | 0 |  | 547200 | 0 | 380411 | 279480 | 0 | 82560 | 446880 | 484800 | 1423584 | 0 | 0 | 5198600 | 5344000 | 4820000 | 200727 | 2148670 | 591192 | 738240 | 0 | 0 | 0 | 0 | 100440 | 490752 | 118440 | 797500 | 2995700 | 2495040 | 3455840 | 686400 | 238932 | 15100 | 1020000 | 1013280 | 918000 | 0 | 2047418 | 3511000 | 813984 | 1632960 | 0 | 2269320 | 0 | 0 | 172080 | 7282000 | 337536 | 167000 | 0 | 607200 | 0 | 0 | 2071200 | 0 | 1926720 | 89775 | 1312320 | 2559840 | 0 | 8508000 | 354000 | 79200 | 0 | 28201 | 40145 | 802537 | 0 | 0 | 1042440 | 1694400 | 9138800 | 1330560 | 386400 | 452160 | 505582 | 0 | 217800 | 239239 |  | 17005818 | 0 | 8964576 | 0 | 1758720 | 0 | 0 | 0 | 0 | 13696 | 165750 | 703000 | 368900 | 200064 | 0 | 0 | 0 | 0 | 0 | 446840 | 0 | 0 | 18925 | 324480 | 149465 | 491520 | 0 | 60930 | 0 | 0 | 3662600 | 15000 | 0 | 1755300 | 0 | 3783082 | 0 | 685216 | 369600 | 4679145 | 0 | 1591181 | 764160 | 0 | 1942752 | 0 | 1659840 | 0 | 46557 | 1814880 | 8889700 | 761509 | 0 | 0 |  | 151022833 | 63093206 | 214116039 | 111114639 | 17005818 | 32490778 | 34883215 | 12552300 | 1196000 | 1572977 | 2495040 | 805272 | 0
Fuel Cost | 0 | 0 | 0 | 5093550 | 7496385 | 2633039.64 | 0 | 7738185.7 | 6229440 |  | 0 | 7710115 | 5103029.64 | 2440944 | 0 | 5505260.4 | 4654399.36 | 0 | 6248760 | 3484281.6 | 3337044.48 | 5398617.6 | 335976.8 | 0 | 0 | 0 | 8375436 | 7133274.92 | 2976024.08 | 167292 | 450000 | 0 | 0 | 0 | 380611.2 | 0 | 0 | 322920 | 0 | 0 | 3202681.05 | 5370624.02 | 0 | 5159479.6 | 0 |  | 0 | 0 | 3689986.7 | 2669034 | 0 | 653875.2 | 563068.8 | 1439856 | 2106904.32 | 0 | 0 | 3846964 | 5344000 | 4434400 | 258937.83 | 2470970.5 | 668046.96 | 1033536 | 0 | 0 | 0 | 0 | 959202 | 623255.04 | 88830 | 1395625 | 2246775 | 18712800 | 3663190.4 | 6232512 | 303443.64 | 240694 | 1672800 | 1621248 | 1634040 | 0 | 2334056.52 | 3651440 | 1603548.48 | 3118953.6 | 0 | 3925923.6 | 0 | 0 | 351043.2 | 7354820 | 253152 | 126920 | 0 | 4590432 | 0 | 0 | 10770240 | 0 | 18958924.8 | 1049469.75 | 10695408 | 27774264 | 0 | 7912440 | 3228480 | 748440 | 0 | 0 | 303496.2 | 6990097.27 | 0 | 0 | 8933710.8 | 11284704 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97953511.68 | 0 | 9412804.8 | 0 | 13823539.2 | 0 | 0 | 0 | 0 | 143534.08 | 1727115 | 794390 | 571795 | 1952624.64 | 0 | 0 | 0 | 0 | 0 | 3954534 | 0 | 0 | 183383.25 | 3144211.2 | 1449810.5 | 943718.4 | 0 | 46124.01 | 0 | 0 | 19851292 | 519750 | 0 | 2053701 | 0 | 4993668.24 | 0 | 1027824 | 6286896 | 5474599.65 | 0 | 1575269.19 | 7977830.4 | 0 | 18436716.48 | 0 | 12880358.4 | 0 | 514454.85 | 13411963.2 | 39025783 | 0 | 0 | 0 |  | 311481331.7 | 270131202.17 | 581612533.87 | 113676909.12 | 97953511.68 | 38216444.38 | 236708638.96 | 58877075 | 322920 | 15339616.13 | 18712800 | 1804618.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 325 | 232 |  | 0 | 320 | 160 | 50 | 0 | 42 | 220 | 0 | 97 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 24 | 25 | 25 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 20 | 0 | 0 | 20 | 3 | 80 | 0 | 0 | 15 | 230 | 181 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 25 | 19 | 0 | 33 | 14 | 108 | 134 | 24 | 14 | 2 | 43 | 42 | 50 | 0 | 70 | 165 | 33 | 72 | 0 | 30 | 0 | 0 | 7 | 280 | 8 | 5 | 0 | 29 | 0 | 0 | 100 | 0 | 149 | 15 | 80 | 155 | 0 | 356 | 0 | 0 | 0 | 4 | 0 | 54 | 0 | 0 | 65 | 100 | 400 | 104 | 54 | 72 | 53 | 0 | 6 | 34 |  | 837 | 0 | 410 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 20 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 10 | 0 | 36 | 0 | 35 | 0 | 187 | 0 | 7 | 35 | 0 | 94 | 0 | 113 | 0 | 7 | 95 | 350 | 53 | 0 | 0 |  | 8996 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 272 | 195 | 0 | 0 | 320 | 240 | 0 | 0 | 55 | 221 | 0 | 185 | 60 | 32 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 25 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 25 | 204 | 0 | 130 | 0 | 0 | 24 | 0 | 85 | 50 | 0 | 18 | 20 | 15 | 135 | 0 | 0 | 310 | 230 | 214 | 8 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 140 | 158 | 41 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 164 | 33 | 75 | 0 | 217 | 0 | 0 | 9 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 180 | 0 | 355 | 85 | 17 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 17 | 17 | 0 | 18 | 0 |  | 836 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 40 | 67 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 5 | 0 | 0 | 150 | 8 | 0 | 147 | 0 | 207 | 0 | 75 | 100 | 188 | 0 | 47 | 70 | 0 | 94 | 0 | 106 | 0 | 0 | 113 | 500 | 73 | 0 | 0 |  | 11347 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 300 | 250 | 0 | 0 | 400 | 270 | 100 | 0 | 55 | 222 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 40 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 85 | 100 | 90 | 50 | 22 | 20 | 100 | 0 | 0 | 360 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 17 | 168 | 160 | 49 | 17 | 0 | 44 | 43 | 51 | 0 | 163 | 165 | 33 | 75 | 0 | 225 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 37 |  |  | 843 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 144 | 0 | 220 | 0 | 95 | 100 | 210 | 0 | 400 | 100 | 200 | 94 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 300 | 100 | 0 | 300 | 250 | 0 | 0 | 400 | 270 | 100 | 0 | 55 | 222 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 33 | 25 | 25 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 82 | 100 | 90 | 50 | 22 | 15 | 100 | 0 | 0 | 360 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 17 | 151 | 160 | 49 | 17 | 1.6 | 44 | 43 | 51 | 0 | 163 | 165 | 33 | 75 | 0 | 225 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 37 | 30 |  | 843 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 40 | 70 | 25 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 144 | 0 | 220 | 0 | 95 | 50 | 210 | 0 | 400 | 100 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 300 | 53 | 0 | 315 | 166 | 0 | 0 | 320 | 235 | 0 | 0 | 0 | 221 | 0 | 80 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 31 | 25 |  | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 10 | 100 | 0 | 0 | 270 | 250 | 181 | 8 | 89 | 26 | 53 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 16 | 92 | 162 | 16 | 17 | 1 | 43 | 43 | 50 | 0 | 110 | 165 | 34 | 67 | 0 | 169 | 0 | 0 | 9 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 157 | 0 | 70 | 7 | 10 | 0 | 0 | 325 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 70 | 340 | 0 | 21 | 0 | 0 | 0 | 0 | 12 | 0 | 842 | 0 | 355 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 148 | 0 | 130 | 0 | 33 | 0 | 155 | 0 | 365 | 0 | 0 | 70 | 0 | 105 | 0 | 0 | 25 | 380 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6383 | 6:00
| Highest Generation |  | 11347 | 19:30
| Day Peak Generation |  | 8996 | 12:00
| Evening Peak Generation |  | 11347 | 19:30
| HVDC Max Flow |  | 837 | 8:00
| HVDC EvPeak Flow |  | 836 | 19:30
| Load factor L.F |  | 78.62%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-06
Till now the maximum generation is : - |  |  | 13018 MW | 21:00 | Hrs on | 2021-04-03
The Summary of Yesterday's |  | 2021-04-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8996 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8101 | MW
Evening Peak Generation : |  | 11347 | MW Hour : | 19:30 | Available Max Generation : |  | 16000 | MW
E.P. Demand (at gen end) : |  | 11347 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11347 | MW Hour : | 19:30 | Reserve(Generation end) |  | 4000 | MW
Total Gen. (MKWH) : |  | 214.116 | System Load Factor : | 78.62% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -370 | MW at | 6:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-06
Actual : | 83.49 | Ft.(MSL) , | Rule curve : | 87.2 | Ft.( MSL )
Gas Consumed : | Total = | 1220.86 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151893353.5
: |  | Coal : | 58877075 | Oil : | 252048255.09 | Total : | 462818683.59
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4269.0084 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1454.0269 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1303.1746 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1177.6755 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1064.1671 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 858.7511 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 477.1759 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.026 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 662.3258 |  |  | 0 | 0%
Total | 0 |  | 11487.3313 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100 MW
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bakulia-Kulshi 132 kV Ckt-2 was under shut down from 08:53 to 13:30 for C/M.
b) Kabirpur 132/33 kV T-1 & T-2 transformers were switched off at 11:22 as fire originated from marshaling |  |  |  |  | About 140 MW power interruption occurred under Kabirpur S/S
box of T-2 and were switched on at 11:41 & 18:03 respectively. |  |  |  |  | area from 11:22 to 11:41.
c) Mymensing-Jamalpur 132 kV Ckt-1 was under shut down from 08:27 to 16:39 for C/M.
d) Naogaon 132/33 kV T-2 transformer tripped at 07:55 showing O/C & E/F relays and was switched |  |  |  |  | About 10 MW power interruption occurred under Naogaon S/S
on at 08:08. |  |  |  |  | area from 07:55 to 08:08.
e) Sikalbaha(O) 132/33 kV T-3 & T-4 transformers were shut down at 08:40 for C/M and were switched |  |  |  |  | About 10 MW power interruption occurred under Sikalbaha(O) S/S
on at 10:35. |  |  |  |  | area from 08:40 to 10:35.
f) Ashuganj #3 was synchronized at 11:06.
g) Sirajganj #4 CCPP GT & ST were synchronized at 11:29 & 13:29 respectively.
h) Sirajganj #1 CCPP GT was synchronized at 11:50.
i) Kushiara-163 MW CCPP GT & ST were synchronized at 08:50 & 11:37 respectively.
j) Summit Megnaghat-305 MW CCPP GT-2 was synchronized at 11:53.
k) Sirajganj #2 CCPP ST was synchronized at 12:01.
l) Sylhet-225 MW CCPP GT & ST were synchronized at 11:08 & 12:55 respectively.
m) Bhola-225 MW CCPP GT-1 was synchronized at 11:42.
n) Aminbazar-Agargaon 132 kV Ckt-2 was under shut down from 16:53 to 17:18 for C/M.
o) Ashuganj(N)-450 MW CCPP ST was synchronized at 14:55.
p) Ashuganj(S)-450 MW CCPP ST was synchronized at 03:47(6/4/21).
q) Sirajganj #4 CCPP GT tripped at 21:31 & ST was shut down at 17:37 and were synchronized at
01:47 & 02:54(6/4/21) respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 3465000 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6753500 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 78 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 1994727
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 272 | 7661570 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 195 | 6048000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7073500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 321600 | Reserve.
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 4597324 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 100 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 650740
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 36440 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 223056
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3612000 | Machine problem
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 60 | 462720 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 4475384 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 32 | 365904 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1147320
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 548640 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 922804
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 301828 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1210920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 370700 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 585300 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 16 | 39360 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 95 | 607200 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1926720
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 17 | 79200 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1330560
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 452160 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 0 | 0 | 239239
| Dhaka area Total |  |  |  | 5972 | 2899 | 57503416
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 344745
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 89775
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 18 | 82560 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1196000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4927178
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3034988 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 380411 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 279480 | Low demand
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1312320
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 446880
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 484800
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28201
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 40145 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 802537
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1694400
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 505582 | Low demand
| Chattogram area Total |  |  |  | 2382 | 904 | 15650002
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 1423584 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 214 | 4820000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 5198600 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 230 | 5344000 | ST Under maint.
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 591192 | Gas shortage
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 738240 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2148670 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 2559840 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 490752
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 118440
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2495040
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 797500
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 100440 | Reserve.
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 17 | 2995700 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1042440
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 0 | 18 | 217800 | Engine problem
| Cumilla Area Total |  |  |  | 2980 | 1577 | 31282965
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 158 | 3455840 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 238932
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 41 | 686400 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15100
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 2071200
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 85 | 354000 | Engine problem
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 386400
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 547200
| Mymensingh Area Total |  |  |  | 709 | 517 | 7755072
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1020000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1013280 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 2047418
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 164 | 3511000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 918000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 44 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 167000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 813984 | GT-9 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1632960
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 0 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 217 | 2269320
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 50 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 337536 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7282000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 355 | 8508000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 172080
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9138800
| Sylhet Area Total |  |  |  | 2371 | 1890 | 38831378
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 836 | 17005818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1758720 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 13696 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 8964576 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 40 | 165750
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 369600
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 70 | 764160 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1515 | 29042320
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 32 | 200064 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 25 | 368900
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 703000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 75 | 685216 | Machine problem
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 8889700
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 73 | 761509 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 772 | 11608389
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 18925 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 147 | 1755300 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 207 | 3783082 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 188 | 4679145 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 47 | 1591181 | ST Problem
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 149465 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 491520
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 10 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 60930
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 324480
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 446840
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1942752 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1814880
| Rajshahi Area Total |  |  |  | 2183 | 1009 | 17058500
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3662600 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 15000 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 106 | 1659840 | Engine problem
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46557
| Rangpur Area Total |  |  |  | 605 | 264 | 5383997
| Total |  |  |  | 21312 | 11347 | 214116039
| Eastern Grid Total |  |  |  | 14414 | 7787 | 151022833
| Western Grid Total |  |  |  | 6898 | 3560 | 63093206
| National Grid Total |  |  |  | 21312 | 11347 | 214116039
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-05
(a) ENTIRE EASTERN GRID : |  | 7299 | MW | (b) ENTIRE WESTERN GRID : |  | 3554 | MW
i) Dhaka area |  | 3765 | MW | i) Khulna area |  | 1327 | MW
ii) Chittagong area |  | 1211 | MW | ii) Rajshahi area |  | 1199 | MW
iii) Comilla area |  | 1049 | MW | iii) Barisal area |  | 285 | MW
iv) Mymensingh area |  | 870 | MW | iv) Rangpur area |  | 743 | MW
v) Sylhet area |  | 404 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10853 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 92 | 12:00 | Jamalpur | 133 | 21:00 | Jhenida | 104 | 19:30
Munsiganj | 118 | 21:00 | Sherpur | 80 | 22:00 | Bottail | 112 | 19:00
Sonargaon | 82 | 19:00 | Srimongal | 30 | 18:30 | G.K Project | 49 | 19:00
Shyampur | 198 | 10:00 | Shahjibazar | 111 | 19:00 | Faridpur | 160 | 20:00
Bhulta | 198 | 15:00 | Fenchuganj | 35 | 18:30 | Madaripur | 81 | 21:00
Madanganj | 56 | 10:00 | Kulawara | 37 | 20:00 | Sariatpur | 50 | 19:30
Shitalakhya | 118 | 16:00 | Sylhet | 100 | 19:00 | Gopalganj | 72 | 19:30
Rahim steel | 27 | 16:00 | Chatak | 24 | 18:30 | Bagerhat | 95 | 19:00
Matuail | 60 | 12:00 | Sunamganj | 34 | 21:00 | Mongla | 42 | 15:00
Ghorasal | 68 | 23:00 | Biani Bazar | 52 | 20:00 | Satkhira | 106 | 22:00
Narsingdi | 161 | 21:00 | Comilla (S) | 142 | 21:00 | Gallamari | 38 | 21:00
Haripur (SBU) | 127 | 17:00 | Comilla(N) | 125 | 19:30 | Magura | 44 | 19:30
Sreenagar |  |  | Chandpur | 63 | 19:30 | Norail | 32 | 19:00
Ullon | 73 | 15:00 | Feni | 113 | 19:00 | Chuadanga | 80 | 20:00
Hasnabad | 85 | 21:00 | Chowmuhani | 144 | 19:00 | Borguna | 14 | 19:30
Magbazar | 54 | 15:00 | Ashuganj | 32 | 1:00 | Barisal(N) | 32 | 20:00
Maniknagar | 89 | 12:00 | Daudkandi | 132 | 19:30 | Barisal (S) | 92 | 18:30
Bangabhaban | 22 | 14:00 | B.Baria | 145 | 22:00 | Patuakhali | 87 | 21:00
Narinda | 70 | 18:30 | Ramganj | 66 | 19:30 | Bhandaria | 42 | 20:00
Dhanmondi | 138 | 13:00 | Chaddagram | 39 | 18:30 | Borhan Uddin | 33 | 19:30
Lalbag | 76 | 13:00 | PHP | 6 | 11:00 | Ishurdi | 41 | 19:00
Madartek | 73 | 22:00 | Kochua | 55 | 21:00 | Ruppur Paromanobik | 3 | 22:00
Dhaka University | 28 | 12:00 | Madunaghat | 63 | 18:30 | Natore | 117 | 19:30
Aftabnagar | 8 | 10:00 | Hathazari | 77 | 19:00 | Bogra | 139 | 21:00
Fatullah | 58 | 24:00 | Khulshi | 188 | 12:00 | Noagaon | 106 | 20:00
Nawabganj | 42 | 19:30 | Halishahar | 124 | 15:00 | Rajshahi | 130 | 21:00
Mirpur | 90 | 15:00 | Baraulia | 143 | 1:00 | Rajshahi New | 19 | 21:00
Kalyanpur | 96 | 15:00 | Sikalbaha | 33 | 18:30 | C.Nawabganj | 76 | 20:00
Gulshan | 98 | 13:00 | Dohazari | 78 | 20:00 | Amnura | 60 | 19:30
Uttara | 78 | 15:00 | Cox'sbazar | 90 | 19:30 | Pabna | 101 | 19:00
Uttara New | 24 | 12:00 | Chandraghona | 28 | 19:00 | Shahjadpur | 96 | 20:00
Kamrangirchar | 79 | 19:00 | Kaptai | 5.2 | 18:30 | Serajganj | 86 | 20:00
Savar | 167 | 15:00 | A. Khaer Stl. | 9 | 18:30 | Niyamatpur | 94 | 19:30
Bhasantec | 124 | 14:00 | Bakulia | 100 | 19:00 | Joypurhat | 62 | 19:00
Agargaon | 58 | 14:00 | Julda | 23 | 19:00 | Sherpur(Bogura) | 52 | 20:00
Satmosjid | 72 | 13:00 | TK chemical | 24.2 | 19:00 | Mohastangor | 52 | 21:00
Tongi | 92 | 17:00 | Modern Steel | 0 | #N/A | Bangura | 20 | 19:30
Kabirpur | 237 | 19:00 | Shahmirpur | 28 | 15:00 | Rangpur | 118 | 19:00
Basundhara | 130 | 16:00 | Khagrachhari | 24 | 1:00 | Lalmonirhat | 44 | 19:00
Manikganj | 60 | 19:00 | Matarbari | 35.5 | 19:30 | Saidpur | 107 | 9:00
Joydevpur | 127 | 19:00 | Baroiar Hat | 34 | 14:00 | Purbasadipur | 95 | 12:00
New Tongi | 99 | 15:00 | Rangamati | 12 | 19:00 | Thakurgaon | 84 | 19:00
Kodda | 229 | 15:00 | Abul Khair 230 | 12 | 19:00 | Palashbari | 86 | 19:30
Dhamrai | 94 | 15:00 | BSRM | 151 | 8:00 | Barapukuria | 50 | 19:00
Rajendrapur | 100 | 19:30 | GPH Ispat | 84 | 13:00 | Panchagar | 47 | 19:00
Valuka | 112 | 14:00 | Goalpara | 28 | 19:00 | Joldhaka | 56 | 19:30
Tangail | 199 | 18:30 | Central s/s | 75 | 13:00 | Kurigram | 57 | 19:00
Mymensing | 182 | 20:00 | Noapara | 37 | 0.875 | Mithapukur | 27 | 19:00
Kishorganj | 110 | 21:00 | Jessore | 135 | 19:00
Netrokona | 107 | 19:30 | Benapol | 58 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 2:00 | 397 | 16:00 | Kaliakoir | 398 | 0.083333 | 375 | 0.66667
| Bheramara | 405 | 19:00 | 392 | 19:00 | Bhulta | 383 | 0.083333 | 363 | 0.625
| Ashuganj(N) | 389 | 1:00 | 370 | 15:00 | Gopalganj | 412 | 0.625 | 385 | 0.83333
| Payra | 415 | 1:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 230 | 15:00 | Hathazari | 224 | 19:00 | 216 | 13:00
| Ishurdi | 235 | 2:00 | 225 | 13:00 | Megnaghat | 232 | 12:00 | 223 | 13:00
| Ashuganj | 236 | 1:00 | 226 | 16:00 | Fenchuganj | 240 | 1:00 | 236 | 8:00
| Serajganj | 232 | 1:00 | 224 | 12:00 | Siddhirganj | 230 | 1:00 | 221 | 16:00
| Baghabari | 234 | 3:00 | 228 | 6:00 | Maniknagar | 229 | 1:00 | 219 | 16:00
| Barapukuria | 238 | 1:00 | 227 | 8:00 | Agargaon | 227 | 4:00 | 214 | 16:00
| Bogra | 227 | 1:00 | 215 | 8:00 | Barisal | 244 | 10:00 | 236 | 19:00
| Rajshahi | 231 | 4:00 | 220 | 8:00 | Bhola 225 MW | 247 | 24:00 | 239 | 18:30
| Khulna South | 236 | 4:00 | 219 | 13:00 | AKSML | 227 | 10:00 | 214 | 16:00
| Rampura | 230 | 1:00 | 220 | 15:00 | BSRM | 227 | 1:00 | 215 | 16:00
| Haripur | 229 | 1:00 | 221 | 16:00 | Bibiyana | 241 | 10:00 | 235 | 16:00
| Hasnabad | 230 | 1:00 | 217 | 15:00 | Bhulta | 230 | 1:00 | 221 | 16:00
| Shyampur | 226 | 1:00 | 220 | 16:00 | Ashuganj (S) | 236 | 2:00 | 225 | 15:00
| Aminbazar | 228 | 1:00 | 216 | 2:00 | Kaliakoir | 230 | 4:00 | 216 | 16:00
| Tongi | 228 | 1:00 | 213 | 15:00 | GPH | 225 | 10:00 | 216 | 8:00
| Comilla (N) | 229 | 1:00 | 220 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 1:00 | 130 | 16:00 | Madanhat | 136 | 0.041667 | 131 | 0.20833
| Munsiganj | 135 | 4:00 | 129 | 16:00 | Hathazari | 133 | 0.041667 | 129 | 0.54167
| Sonargaon | 135 | 10:00 | 128 | 15:00 | Khulshi | 139 | 0.75 | 126 | 0.66667
| Shyampur | 134 | 5:00 | 127 | 16:00 | Halishahar | 134 | 0.79167 | 128 | 0.33333
| Bhulta | 128 | 4:00 | 124 | 15:00 | Baraulia | 135 | 0.041667 | 126 | 0.66667
| Madanganj | 134 | 18:30 | 128 | 15:00 | Sikalbaha | 135 | 0.41667 | 130 | 0.625
| Shitalakhya | 136 | 1:00 | 128 | 14:00 | Dohazari | 134 | 0.041667 | 125 | 0.625
| Rahim steal | 136 | 1:00 | 130 | 16:00 | Cox'sbazar | 132 | 0.041667 | 115 | 0.77083
| Matuail | 136 | 1:00 | 130 | 16:00 | Chandraghona | 134 | 0.83333 | 129 | 0.66667
| Ghorasal | 140 | 1:00 | 133 | 15:00 | Kaptai | 135 | 0.041667 | 128 | 0.625
| Narsinghdi | 138 | 1:00 | 126 | 15:00 | A. Khaer Stl. | 132 | 0.41667 | 127 | 0.70833
| Haripur (SBU) | 136 | 4:00 | 130 | 16:00 | Bakulia | 136 | 0.041667 | 128 | 0.66667
| Sreenagar |  |  |  |  | Julda | 135 | 0.41667 | 129 | 0.625
| Ullon | 134 | 1:00 | 128 | 14:00 | TK Chemical | 134 | 0.041667 | 130 | 0.625
| Hasnabad | 135 | 1:00 | 129 | 16:00 | Modern Steel
| Magbazar | 134 | 1:00 | 126 | 15:00 | Shahmirpur | 135 | 0.41667 | 129 | 0.625
| Maniknagar | 137 | 1:00 | 131 | 16:00 | Khagrachhari | 132 | 0.041667 | 128 | 0.33333
| Bangabhaban | 137 | 1:00 | 131 | 16:00 | Matarbari | 133 | 0.041667 | 119 | 0.66667
| Narinda | 137 | 1:00 | 131 | 16:00 | Baroiar Hat | 136 | 0.41667 | 127 | 0.66667
| Dhanmondi | 134 | 1:00 | 128 | 14:00 | Rangamati | 133 | 0.041667 | 128 | 0.33333
| Lalbag | 136 | 2:00 | 127 | 16:00 | Goalpara S/S | 137 | 18:00 | 127 | 8:00
| Madartek | 134 | 19:00 | 127 | 15:00 | Khulna Central S/S | 135 | 3:00 | 124 | 13:00
| Dhaka University | 134 | 1:00 | 128 | 13:00 | Noapara | 133 | 1:00 | 122 | 0.54167
| Aftabnagar | 134 | 1:00 | 126 | 15:00 | Jessore | 130 | 1:00 | 120 | 0.625
| Fatullah | 134 | 2:00 | 127 | 15:00 | Benapol | 130 | 1:00 | 125 | 0.77083
| Nawabganj | 131 | 2:00 | 124 | 15:00 | Jhenida | 132 | 3:00 | 114 | 0.83333
| Mirpur | 135 | 1:00 | 127 | 16:00 | Bottail | 133 | 0.041667 | 123 | 0.54167
| Kalyanpur | 136 | 7:00 | 129 | 15:00 | G.K Project | 138 | 1:00 | 133 | 0.54167
| Gulshan | 134 | 3:00 | 126 | 15:00 | Faridpur | 140 | 0.041667 | 128 | 0.79167
| Uttara | 134 | 2:00 | 127 | 14:00 | Madaripur | 141 | 0.16667 | 132 | 0.83333
| Uttara New | 139 | 1:00 | 126 | 16:00 | Shariyatpur S/S | 142 | 0.20833 | 130 | 0.875
| Kamrangirchar | 133 | 7:00 | 126 | 16:00 | Gopalganj | 146 | 0.041667 | 133 | 0.83333
| Savar | 134 | 1:00 | 128 | 15:00 | Bagerhat | 135 | 1:00 | 120 | 0.54167
| Bhasantec | 132 | 7:00 | 124 | 16:00 | Mongla | 133 | 1;00 | 121 | 0.54167
| Agargaon | 132 | 1:00 | 125 | 16:00 | Satkhira | 134 | 4:00 | 121 | 0.54167
| Satmosjid | 132 | 2:00 | 125 | 16:00 | Gallamari | 136 | 22:00 | 125 | 0.54167
| Tongi | 138 | 1:00 | 126 | 16:00 | Magura | 132 | 2:00 | 112 | 20:00
| Kabirpur | 136 | 0:00 | 126 | 15:00 | Narail | 133 | 0.083333 | 113 | 20:00
| Basundhara | 136 | 1:00 | 123 | 18:00 | Chuadanga | 130 | 3:00 | 106 | 0.83333
| Manikganj | 138 | 144:00 | 126 | 16:00 | Borguna | 138 | 0.041667 | 130 | 0.625
| Joydevpur | 137 | 2:00 | 130 | 11:00 | Barisal(N) | 139 | 4:00 | 132 | 0.79167
| New Tongi | 137 | 1:00 | 125 | 15:00 | Barisal (S) | 138 | 2:00 | 131 | 0.77083
| Kodda | 137 | 1:00 | 123 | 15:00 | Patuakhali(S) | 137 | 4:00 | 127 | 13:00
| Dhamrai | 135 | 1:00 | 124 | 15:00 | Bhandaria | 137 | 0.041667 | 127 | 0.54167
| Rajendrapur | 134 | 1:00 | 116 | 16:00 | Ishurdi | 136 | 0.083333 | 130 | 0.54167
| Valuka | 136 | 1:00 | 114 | 14:00 | Ruppur Paromanobik | 135 | 0.125 | 130 | 0.54167
| Tangail | 138 | 1:00 | 125 | 14:00 | Natore | 136 | 3:00 | 129 | 13:00
| Mymensing | 136 | 1:00 | 119 | 15:00 | Bogra | 138 | 4:00 | 128 | 8:00
| Kishorganj | 138 | 1:00 | 122 | 15:00 | Noagaon | 132 | 4:00 | 121 | 8:00
| Netrokona | 134 | 1:00 | 117 | 13:00 | Rajshahi | 135 | 3:00 | 128 | 8:00
| Jamalpur | 140 | 10:00 | 123 | 14:00 | Rajshahi New | 136 | 4:00 | 129 | 8:00
| Sherpur | 139 | 10:00 | 128 | 8:00 | C.Nawabganj | 133 | 3:00 | 125 | 12:00
| Srimongal | 139 | 3:00 | 134 | 16:00 | Amnura | 133 | 22:00 | 124 | 8:00
| Shahjibazar | 138 | 4:00 | 131 | 15:00 | Pabna | 136 | 4:00 | 129 | 12:00
| Fenchuganj | 138 | 3:00 | 135 | 15:00 | Shahjadpur | 140 | 3:00 | 135 | 10:00
| Khulawara | 137 | 9:00 | 134 | 16:00 | Serajganj | 136 | 3:00 | 128 | 13:00
| Sylhet | 134 | 5:00 | 132 | 11:00 | Niyamatpur | 127 | 9:00 | 117 | 19:30
| Chatak | 134 | 4:00 | 130 | 11:00 | Joypurhat | 130 | 1:00 | 120 | 8:00
| Sunamganj | 134 | 4:00 | 130 | 21:00 | Sherpur(Bogura) | 137 | 3:00 | 128 | 8:00
| Biani Bazar | 134 | 6:00 | 130 | 11:00 | Mohastangor | 135 | 3:00 | 126 | 8:00
| Comilla(s) | 130 | 1:00 | 122 | 19:00 | Bangura | 138 | 4:00 | 132 | 10:00
| Comilla(n) | 139 | 10:00 | 132 | 16:00 | Rangpur | 133 | 3:00 | 119 | 8:00
| Chandpur | 140 | 10:00 | 134 | 17:00 | Lalmonirhat | 131 | 3:00 | 117 | 8:00
| Feni | 136 | 10:00 | 125 | 16:00 | Saidpur | 132 | 2:00 | 118 | 8:00
| Chowmuhani | 138 | 10:00 | 130 | 9:00 | Purbasadipur | 131 | 4:00 | 117 | 8:00
| Ashuganj | 140 | 1:00 | 133 | 15:00 | Thakurgaon | 130 | 3:00 | 112 | 19:00
| Daudkandi | 135 | 1:00 | 127 | 16:00 | Palashbari | 134 | 5:00 | 123 | 18:30
| B.Baria | 138 | 5:00 | 127 | 15:00 | Barapukuria | 138 | 3:00 | 127 | 8:00
| Ramganj | 140 | 10:00 | 127 | 16:00 | Panchagar | 130 | 4:00 | 111 | 19:00
| Chaddagram | 136 | 10:00 | 128 | 16:00 | Joldhaka | 132 | 3:00 | 114 | 19:00
| PHP | 136 | 10:00 | 124 | 16:00 | Kurigram | 131 | 3:00 | 115 | 8:00
| Kochua | 138 | 11:00 | 132 | 16:00 | Mithapukur | 134 | 0.16667 | 121 | 0.33333

## L-Curve
Date | 2021-04-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 34 | 6992 | 3016 | 10008 |  |  |  | QF-LDC-11
0:30 | 127 | 5954 | 2326.5 | 8280.5 | Date: | 2021-04-05
1:00 | 220 | 4916 | 1637 | 6553
1:30 | 230 | 4992.5 | 1627.5 | 6620
2:00 | 240 | 5069 | 1618 | 6687
2:30 | 245 | 5027.5 | 1594.5 | 6622 | [5 empty] | Gen. at Eve. Peak | 11347 | 11347 MW (19:30 )
3:00 | 250 | 4986 | 1571 | 6557 | [6 empty] | 19:30
3:30 | 275 | 4955.5 | 1556 | 6511.5 | [5 empty] | Gen. at Day Peak | 8996 | 8996 MW (12:00 )
4:00 | 300 | 4925 | 1541 | 6466 | [6 empty] | 12:00
4:30 | 315 | 4909.5 | 1518.5 | 6428 | [5 empty] | Highest Generation | 11347
5:00 | 330 | 4894 | 1496 | 6390 | [6 empty] | 19:30
5:30 | 350 | 4902 | 1484.5 | 6386.5
6:00 | 370 | 4910 | 1473 | 6383
6:30 | 325 | 5000.5 | 1621 | 6621.5
7:00 | 280 | 5091 | 1769 | 6860
7:30 | 245 | 5085 | 1889 | 6974
8:00 | 210 | 5079 | 2009 | 7088
8:30 | 145 | 5169.5 | 2120 | 7289.5
9:00 | 80 | 5260 | 2231 | 7491
9:30 | 63 | 5433 | 2296.5 | 7729.5
10:00 | 46 | 5606 | 2362 | 7968
10:30 | 46 | 5858.5 | 2411 | 8269.5
11:00 | 46 | 6111 | 2460 | 8571
11:30 | 57 | 6266.5 | 2517 | 8783.5
12:00 | 68 | 6422 | 2574 | 8996
12:30 | 110 | 6423.5 | 2721.5 | 9145
13:00 | 152 | 6425 | 2869 | 9294
13:30 | 173 | 6519 | 3001 | 9520
14:00 | 194 | 6613 | 3133 | 9746
14:30 | 247 | 6704 | 3202.5 | 9906.5
15:00 | 300 | 6795 | 3272 | 10067
15:30 | 323 | 6761.5 | 3266 | 10027.5
16:00 | 346 | 6728 | 3260 | 9988
16:30 | 297 | 6630 | 3208 | 9838
17:00 | 248 | 6532 | 3156 | 9688
17:30 | 145 | 6547.5 | 3021 | 9568.5
18:00 | 42 | 6563 | 2886 | 9449
18:30 | 69 | 7111 | 3133.5 | 10244.5
19:00 | 96 | 7659 | 3381 | 11040
19:30 | 84 | 7787 | 3560 | 11347
20:00 | 84 | 7775 | 3565 | 11340 |  |  |  | Executive Engineer
20:30 | 58 | 7653.5 | 3603 | 11256.5 |  |  |  | Network Operation Division
21:00 | 32 | 7532 | 3641 | 11173
21:30 | 28 | 7508.5 | 3552.5 | 11061
22:00 | 24 | 7485 | 3464 | 10949 |  |  |  |  | Page 6 of 7
22:30 | 15 | 7316.5 | 3323 | 10639.5
23:00 | 6 | 7148 | 3182 | 10330
23:30 | 20 | 7070 | 3099 | 10169
24:00 | 34 | 6992 | 3016 | 10008
11347 MW (19:30 )
8996 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-05 |  | Energy | 214116039
[11 empty] | 2021-04-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4944 | 837 | 1416 | 2075 | 650 | 70 | 65 | 0 | 114 | 0
0:30 | 4437.5 | 610.5 | 1305.5 | 1331 | 499.5 | 52.5 | 32.5 | 0 | 93 | 0 | Date: | 2021-04-05
1:00 | 3931 | 384 | 1195 | 587 | 349 | 35 | 0 | 0 | 72 | 0
1:30 | 4005.5 | 384 | 1198.5 | 574.5 | 349.5 | 35 | 0 | 0 | 73 | 0 | [7 empty] | Total Energy | 214.116 | Total Energy Gen 214.116 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 214.116 MKWHr
2:00 | 4080 | 384 | 1202 | 562 | 350 | 35 | 0 | 0 | 74 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4060 | 384 | 1202 | 516 | 350 | 35 | 0 | 0 | 75 | 0 | [7 empty] | Energy Requirement | 214.116
3:00 | 4040 | 384 | 1202 | 470 | 350 | 35 | 0 | 0 | 76 | 0
3:30 | 4018 | 384 | 1198 | 451.5 | 350 | 35 | 0 | 0 | 75 | 0 | [6 empty] | Shortage
4:00 | 3996 | 384 | 1194 | 433 | 350 | 35 | 0 | 0 | 74 | 0
4:30 | 3994.5 | 384 | 1190.5 | 400.5 | 349.5 | 35 | 0 | 0 | 74 | 0
5:00 | 3993 | 384 | 1187 | 368 | 349 | 35 | 0 | 0 | 74 | 0
5:30 | 3990.5 | 384 | 1186 | 368 | 349.5 | 35 | 0 | 0 | 73 | 0.5
6:00 | 3988 | 384 | 1185 | 368 | 350 | 35 | 0 | 0 | 72 | 1
6:30 | 4076 | 501.5 | 1198.5 | 380 | 349.5 | 35 | 0 | 0 | 73 | 8 |  |  |  |  | Coal
7:00 | 4164 | 619 | 1212 | 392 | 349 | 35 | 0 | 0 | 74 | 15
7:30 | 4168 | 728 | 1167 | 424.5 | 349.5 | 35 | 0 | 0 | 76 | 26 |  |  |  | Oil |  |  |  | ,
8:00 | 4172 | 837 | 1122 | 457 | 350 | 35 | 0 | 0 | 78 | 37
8:30 | 4170 | 837 | 1164 | 592.5 | 360 | 35 | 0 | 0 | 81 | 50
9:00 | 4168 | 837 | 1206 | 728 | 370 | 35 | 0 | 0 | 84 | 63
9:30 | 4071 | 837 | 1232.5 | 1003.5 | 390 | 35 | 0 | 0 | 84 | 76.5
10:00 | 3974 | 837 | 1259 | 1279 | 410 | 35 | 0 | 0 | 84 | 90
10:30 | 3952 | 837 | 1268.5 | 1550.5 | 435 | 35 | 0 | 0 | 89 | 102.5
11:00 | 3930 | 837 | 1278 | 1822 | 460 | 35 | 0 | 0 | 94 | 115
11:30 | 4036 | 837 | 1287.5 | 1891.5 | 480 | 35 | 0 | 0 | 101 | 115.5
12:00 | 4142 | 837 | 1297 | 1961 | 500 | 35 | 0 | 0 | 108 | 116
12:30 | 4274 | 837 | 1355 | 1911 | 515 | 35 | 0 | 0 | 107 | 111
13:00 | 4406 | 837 | 1413 | 1861 | 530 | 35 | 0 | 0 | 106 | 106
13:30 | 4406 | 837 | 1413 | 1861 | 530 | 35 | 0 | 0 | 106 | 106
14:00 | 4406 | 837 | 1413 | 1861 | 530 | 35 | 0 | 0 | 106 | 106
14:30 | 4600.5 | 837 | 1592.5 | 1839.5 | 535 | 52.5 | 16 | 0 | 115 | 92.5
15:00 | 4795 | 837 | 1772 | 1818 | 540 | 70 | 32 | 0 | 124 | 79
15:30 | 4855.5 | 836.5 | 1763.5 | 1734 | 540 | 70 | 40 | 0 | 123 | 65
16:00 | 4916 | 836 | 1755 | 1650 | 540 | 70 | 48 | 0 | 122 | 51
16:30 | 4842 | 836 | 1662 | 1683.5 | 540 | 70 | 50.5 | 0 | 119 | 35
17:00 | 4768 | 836 | 1569 | 1717 | 540 | 70 | 53 | 0 | 116 | 19
17:30 | 4737.5 | 836.5 | 1445 | 1747 | 540 | 70 | 68 | 0 | 114 | 10.5
18:00 | 4707 | 837 | 1321 | 1777 | 540 | 70 | 83 | 0 | 112 | 2
18:30 | 4896.5 | 837 | 1399.5 | 2136.5 | 555 | 70 | 223 | 0 | 126 | 1
19:00 | 5086 | 837 | 1478 | 2496 | 570 | 70 | 363 | 0 | 140 | 0
19:30 | 5158 | 836 | 1516 | 2668 | 650 | 70 | 309 | 0 | 140 | 0
20:00 | 5170 | 837 | 1508 | 2659 | 650 | 70 | 306 | 0 | 140 | 0
20:30 | 5195 | 837 | 1525 | 2534 | 660 | 70 | 294.5 | 0 | 141 | 0
21:00 | 5220 | 837 | 1542 | 2409 | 670 | 70 | 283 | 0 | 142 | 0
21:30 | 5177 | 837 | 1471 | 2411.5 | 670 | 70 | 282.5 | 0 | 142 | 0
22:00 | 5134 | 837 | 1400 | 2414 | 670 | 70 | 282 | 0 | 142 | 0
22:30 | 5100 | 836.5 | 1390.5 | 2244.5 | 670 | 70 | 187 | 0 | 141 | 0
23:00 | 5066 | 836 | 1381 | 2075 | 670 | 70 | 92 | 0 | 140 | 0
23:30 | 5005 | 836.5 | 1398.5 | 2075 | 660 | 70 | 78.5 | 0 | 127 | 0 | Max Temp. in Dhaka |  | 33.7° C
24:00 | 4944 | 837 | 1416 | 2075 | 650 | 70 | 65 | 0 | 114 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 214.116 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 214.116 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1196000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 8 | 8 | [7 empty] | 3 | 8 | 9 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 344745
| Teknaf 20MW PP (Solartech) | [9 empty] | 7 | 19 | 15 | 9 | 13 | 13 | 8 | 2 | [9 empty] | 89775
6 | Sikalbaha 225MW CCPP (Gas) | 208 | 206 | 203 | 202 | 202 | 215 | 202 | 216 | 203 | 203 | 204 | 203 | 204 | 204 | 204 | 204 | 204 | 204 |  | 191 | 204 | 204 | 204 | 204 | 205 | 203 | 4927178
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3034988
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [17 empty] | 4 |  | 85 | 85 | 85 | 85 | 85 | 19 | 17 | 380411
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [25 empty] | 0 | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 145 | 150 | 115 | 115 | 115 | 175 | 115 | 75 | 155 | 75 | 97 | 150 | 185 | 177 | 175 | 108 | 70 |  | 175 | 185 | 175 | 185 | 180 | 150 | 150 | 3612000
17 | Siddhirganj 335 MW CCPP | 12 | 145 | 145 | 144 | 145 | 145 | 175 | 221 | 180 | 190 | 220 | 220 | 216 | 217 | 216 | 215 | 180 | 180 |  | 221 | 221 | 220 | 220 | 220 | 220 | 221 | 4475384
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 29 | 60 | 30 | 30 | 15 | 15 | 17 |  | 115 | 95 | 95 | 45 | 45 |  | 0 | 607200
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 120 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3465000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6753500
26
28 | Ashuganj TPP Unit- 3 | [11 empty] | 80 | 90 | 90 | 90 | 132 | 135 | 100 |  | 135 | 135 | 135 | 135 | 135 | 100 | 100 | 1423584
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 23 | 26 | 26 | 591192
33 | Ashuganj 225 MW CCPP | 216 | 216 | 187 | 180 | 183 | 188 | 181 | 201 | 181 | 181 | 189 | 181 | 181 | 180 | 213 | 212 | 212 | 181 |  | 216 | 214 | 216 | 215 | 216 | 199 | 218 | 4820000
34 | Ashuganj 450 MW CCPP(South) | 205 | 200 | 205 | 200 | 205 | 205 | 200 | 200 | 240 | 240 | 230 | 230 | 230 | 230 | 230 | 230 | 240 | 240 |  | 245 | 230 | 245 | 230 | 240 | 240 | 70 | 5344000
| Ashuganj 450 MW CCPP(North) | 250 | 255 | 255 | 260 | 255 | 255 | 260 | 250 | 250 | 30 | 15 | 15 | 35 | 40 | 58 | 140 | 165 | 255 |  | 310 | 310 | 335 | 365 | 310 | 320 | 310 | 5198600
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 738240
36 | Chandpur 150 MW CCPP | 85 | 89 | 90 | 90 | 90 | 90 | 89 | 89 | 89 | 86 | 87 | 90 | 87 | 90 | 129 | 90 | 50 | 90 |  | 90 | 90 | 89 | 89 | 89 | 86 | 88 | 2148670
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 340 | 346 | 350 | 350 | 350 | 350 | 354 | 346 | 334 | 348 | 333 | 325 | 306 | 301 | 296 | 291 | 300 | 291 |  | 280 | 272 | 275 | 264 | 255 | 254 | 343 | 7661570
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7073500
41 | Haripur 360MW CCPP(HPL) | 303 | 323 | 322 | 322 | 323 | 323 | 324 | 293 | 281 | 243 | 236 | 232 | 221 | 221 | 241 | 234 | 222 | 212 |  | 201 | 195 | 187 | 176 | 176 | 176 | 192 | 6048000
42 | RPCL 210MW CCPP | 160 | 164 | 163 | 165 | 165 | 165 | 166 | 163 | 161 | 160 | 133 | 134 | 133 | 130 | 129 | 132 | 152 | 153 |  | 159 | 158 | 137 | 136 | 139 | 138 | 139 | 3455840
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 9 | 22 | 35 | 46 | 52 | 54 | 52 | 47 | 36 | 23 | 9 | 1 | [8 empty] | 386400
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 43 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1020000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1013280
46 | Shajibazar 330 MW CCPP | 126 | 128 | 126 | 127 | 127 | 126 | 126 | 126 | 125 | 132 | 164 | 165 | 163 | 164 | 165 | 165 | 165 | 165 |  | 164 | 164 | 165 | 164 | 164 | 164 | 164 | 3511000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 35 | 35 | 35 | 35 | 35 | 36 | 34 | 34 | 34 | 32 | 33 | 33 | 32 | 33 | 33 | 33 | 33 |  | 34 | 33 | 35 | 34 | 34 | 34 | 35 | 813984
48 | Shahjibazar 86MW PP (Shahjibazar) | 64 | 64 | 50 | 50 | 50 | 50 | 50 | 50 | 69 | 73 | 72 | 72 | 75 | 75 | 75 | 72 | 75 | 75 |  | 75 | 75 | 75 | 75 | 73 | 73 | 73 | 1632960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [11 empty] | 30 | 60 | 160 | 188 | 217 | 202 | 182 |  | 217 | 217 | 230 | 224 | 224 | 223 | 223 | 2269320
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 5 | 5 | 5 | 5 | 5 | 7 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 172080
54 | Hobiganj 11MW PP Cofidence-E | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 2 | 2 | 2 | 5 | 5 | 5 | 5 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 167000
55 | Fenchugonj 51 MW PP (Barakatullah) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 48 | 48 | 48 | 50 | 53 | 53 | 50 | 50 | 22 | 22 |  | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 918000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 15 | 15 | 15 | 15 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 337536
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 285 | 300 | 290 | 285 | 300 | 315 | 280 | 280 | 300 | 290 | 280 | 290 | 300 | 300 | 290 | 280 | 270 |  | 280 | 310 | 280 | 290 | 310 | 280 | 300 | 7282000
| Bibiyana South 400 MW | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 370 | 400 | 400 | 396 | 400 | 401 | 398 | 400 | 400 |  | 400 | 400 | 400 | 400 | 400 | 400 | 370 | 9138800
58 | Nababganj 55 MW PP (Southern power ) | [14 empty] | 5 | 17 | 20 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 301828
59 | Tangail Palli Power Gen 22 MW | 12 | 19 | 18 | 18 | 20 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 547200
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 446880
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 19 | 19 | 22 | 22 | 223056
62 | Tangail 22 MW PP (Doreen) | [7 empty] | 16 | 16 | 16 | 14 | 14 | 16 | 16 | 16 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 238932
63 | Impoprt (Tripura) | 72 | 74 | 76 | 74 | 74 | 72 | 74 | 78 | 84 | 84 | 94 | 108 | 106 | 112 | 124 | 122 | 116 | 112 |  | 140 | 140 | 140 | 142 | 142 | 140 | 114 | 2495040
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 36 | 37 | 34 | 18 | 38 | 10 | 3 | 3 | 3 | 3 | 6 | 5 | 4 | 5 | 9 | 4 |  | 12 | 15 | 22 | 29 | 35 | 30 | 30 | 484800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 18 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 490752
66 | Feni 11 MW PP (Doreen) | [12 empty] | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 118440
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 797500
68 | Cumilla 25 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 3 | 3 | 9 | 11 | 14 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 2995700
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 14 | 24 | 24 | 24 | 24 | 24 | 24 | 32 | 30 | 30 | 29 | 24 | 30 | 24 | 27 | 27 | 27 | 18 |  | 18 | 29 | 30 | 31 | 31 | 31 | 31 | 610920
71 | Maona 33 MW PP(Summit) |  | 25 | 10 | 22 | 22 | 22 | 22 |  | 25 | 25 | 25 | 25 | 0 | 0 | 0 |  | 0 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 370700
72 | Rupganj 33 MW PP(Summit) | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 585300
73 | Ghorashal 108MW PP (Regent) | 73 | 73 | 73 | 73 | 73 | 72 | 72 | 72 | 89 | 96 | 96 | 96 | 96 | 96 | 93 | 93 | 52 | 52 |  | 94 | 99 | 99 | 100 | 100 | 99 | 98 | 1994727
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | [7 empty] | 8 | 8 | 36 | 65 | 65 | 36 | 8 | 8 | 8 | 8 | 8 |  | 75 | 113 | 113 | 113 | 113 | 65 | 65 | 1042440
| Manikgonj 162MW PP(MPGL) | [9 empty] | 4 | 72 | 72 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 17 | 17 |  |  |  | 0 | 452160
77 | Siddhirganj 100 PP(Dutch Bangla) | [9 empty] | 4 | 50 | 50 | 40 | 20 | 20 | 20 | 20 | 20 |  | 25 | 60 | 50 | 16 | 16 | 16 | 16 | 462720
78 | Gazipur 52 MW PP | [17 empty] | 16 |  | 16 | 16 | 16 |  |  |  | 0 | 39360
79 | Kodda 150MW PP | [13 empty] | 6 | 32 | 48 | 48 | 48 |  | 98 | 82 | 82 | 64 | 64 | 48 | 48 | 548640
80 | Jamalpur 95 MW PP(Powerpac) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 41 | 41 | 41 | 41 | 49 | 49 | 49 | 686400
81 | Jangalia 52 MW PP (Lakdanavi) | [10 empty] | 12 | 25 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | [6 empty] | 100440
| Gazipur 100 MW PP | [17 empty] | 5 |  | 40 | 17 | 17 |  |  |  | 0 | 79200
| Kaptai 7 MW Solar PP | [8 empty] | 2 | 2 | 3 | 4 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 28201
| Jodiac Power | 17 | [8 empty] | 9 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 802537
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 9 |  | 20 | [5 empty] | 0 | 36440
86 | ` | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 160 | 220 | 220 | 220 | 220 | 260 | 260 |  | 260 | 240 | 240 | 240 | 230 | 230 | 230 | 4597324
87 | Meghnaghat 100 MW(IEL) | [9 empty] | 4 | 47 | 50 | 50 | 28 | 24 | 24 | 24 | 24 |  | 24 | [6 empty] | 321600
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 |  |  |  | 16 | 42 | 104 | 104 | 104 | 53 | 53 | 53 | 17 | 17 | 17 |  | 68 | 104 | 104 | 104 | 104 | 104 | 104 | 1330560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [9 empty] | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 50 | 50 | 20 | 20 | 20 | 20 | 279480
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 3 | 40 | 40 | 16 | 16 | 16 | 32 | 32 | 32 |  | 32 | 32 | 32 | 16 | 16 | 16 | 7 | 365904
95 | Patenga 50MW PP (Baraka) | [17 empty] | 1 |  | 17 | 18 | 18 | 18 | 18 |  | 0 | 82560
96 | Chattogram 108 MW PP (ECPV) | [20 empty] | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC) | [25 empty] | 0 | 0
99 | Madanganj-55 MW PP(Summit) | 10 | 15 | 15 | 15 |  |  |  | 9 | 16 | 22 | 42 | 42 | 42 | 42 | 42 | 30 | 30 | 30 |  | 45 | 55 | 55 | 30 | 30 | 30 | 30 | 650740
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | [5 empty] | 17 | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 922804
101 | Kushiara 163 MW CCPP (KP) | [8 empty] | 10 | 70 | 70 | 70 | 90 | 163 | 163 | 163 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 2047418
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15100
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 53 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1147320
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [9 empty] | 10 | 100 | 100 | 84 | 100 | 125 | 140 | 140 | 140 |  | 161 | 192 | 192 | 200 | 200 | 193 | 184 | 2071200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [7 empty] | 15 | 16 | 80 | 149 | 149 | 132 | 115 | 115 | 102 | 100 | 100 |  | 120 | 149 | 149 | 149 | 149 | 142 | 116 | 1926720
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 20 | 20 |  |  |  | 10 | 10 | 50 | 70 | 30 | 80 | 80 | 100 | 100 | 60 | 60 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1312320
116 | Chandpur 200MW (Desh energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 100 | 144 | 155 | 155 | 153 | 166 | 136 | 136 | 136 |  | 143 | 180 | 180 | 180 | 179 | 180 | 181 | 2559840
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 366 | 331 | 332 | 331 | 333 | 335 | 365 | 361 | 332 | 331 | 352 | 356 | 354 | 356 | 355 | 355 | 355 | 355 |  | 355 | 355 | 355 | 362 | 352 | 361 | 367 | 8508000
| Jamalpur 115 MW PP (United) | [17 empty] | 7 |  | 64 | 85 | 85 | 55 | 55 | 24 | 0 | 354000
| Anwara 300 MW PP (United) | [17 empty] | 10 |  | 16 | 16 | 16 |  |  |  | 0 | 40145
| Juldah unit-2 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 90 | 100 | 90 | 100 | 90 | 90 | 90 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1694400
| Anlima Energy Ltd. | 17 | 14 | [7 empty] | 5 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 505582
| Bhairob 54.5 MW | [11 empty] | 6 | 17 | 18 | 18 | 18 | 18 | 12 |  | 15 | 18 | 18 | 18 | 18 | 18 | 15 | 217800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 12 | 21 | 28 | 32 | 34 | 32 | 29 | 23 | 15 | 6 | 1 | [8 empty] | 239239
120 | Eastern Zone Total | 4916 | 5069 | 4986 | 4925 | 4894 | 4910 | 5091 | 5079 | 5260 | 5606 | 6111 | 6422 | 6425 | 6613 | 6795 | 6728 | 6532 | 6563 | 0 | 7659 | 7787 | 7775 | 7532 | 7485 | 7148 | 6992 | 151022833
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 49 | 49 | 49 | 32 | 32 | 32 | 32 | 32 | 66 | 72 | 83 | 88 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1758720
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [8 empty] | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 105 | 70 | 70 | 70 | 70 | 70 | 70 | 764160
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | [8 empty] | 28 | 26 | 53 | 53 | 52 | 48 | 68 | 74 | 63 | 73 |  | 65 | 73 | 71 | 74 |  |  | 0 | 761509
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [16 empty] | 16 | 16 |  | 32 | 32 | 32 | 32 | 40 | 32 | 0 | 200064
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | [10 empty] | 9 | 35 | 36 | 35 | 34 | 34 | 35 | 45 |  | 75 | 75 | 75 | 64 | 77 | 96 | 97 | 685216
| Bhola 225 MW CCPP | [11 empty] | 15 | 30 | 50 | 53 | 65 | 54 | 65 |  | 57 | 67 | 63 | 68 | 69 | 69 | 69 | 703000
140 | Bhola 33 MW PP (Venture) | 8 | 10 | 10 | 11 | 11 | 11 | 2 | 8 | 11 | 13 | 15 | 14 | 16 | 19 | 21 | 19 | 18 | 24 |  | 23 | 25 | 25 | 27 | 27 | 25 | 24 | 368900
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 29 | 100 | 100 | 100 | 100 |  | 0 | 369600
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 40 | 40 | 40 | 33 | 33 | 8 |  | 165750
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 5 | 9 |  | 6 | [6 empty] | 13696
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 384 | 384 | 384 | 384 | 384 | 384 | 619 | 837 | 837 | 837 | 837 | 837 | 837 | 837 | 837 | 836 | 836 | 837 |  | 837 | 836 | 837 | 837 | 837 | 836 | 837 | 17005818
147 | Bheramara 410 MW CCPP | 330 | 330 | 330 | 330 | 330 | 330 | 370 | 385 | 410 | 410 | 410 | 410 | 410 | 410 | 360 | 360 | 360 | 300 |  | 355 | 370 | 350 | 375 | 355 | 375 | 360 | 8964576
148 | Payra 1320 MW | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 220 | 260 | 310 | 350 | 380 | 390 | 390 | 390 | 390 | 390 |  | 420 | 500 | 500 | 520 | 520 | 520 | 500 | 8889700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 150 | 150 | 150 | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3662600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [11 empty] | 10 | 121 | 144 | 143 | 144 | 120 | 120 |  | 136 | 147 | 147 | 148 | 148 | 148 | 148 | 1755300
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 144 | 145 | 145 | 145 | 138 | 110 | 123 | 133 | 136 | 38 | 18 | 36 | 80 | 162 | 214 | 213 | 201 | 158 |  | 177 | 207 | 213 | 219 | 220 | 200 | 185 | 3783082
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 196 | 190 | 176 | 162 | 160 | 164 | 181 | 170 | 192 | 202 | 195 | 187 | 189 | 188 | 190 | 195 | 187 | 187 |  | 189 | 188 | 189 | 193 | 193 | 187 | 188 | 4679145
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [11 empty] | 7 | 95 | 227 | 340 | 338 | 280 | 48 |  | 48 | 47 | 72 | 105 |  |  | 0 | 1591181
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 491520
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [11 empty] | 2 | 2 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 60930
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 31 | [6 empty] | 18925
168 | Santahar 50 MW Peaking PP | [17 empty] | 22 |  | 33 | 34 | 34 | 34 | 34 |  | 0 | 149465
169 | Natore 52 MW PP (Rajlanka) | [9 empty] | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 |  | 34 | 52 | 52 | 52 | 52 | 24 | 8 | 324480
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 100 | 100 | 100 | 100 | 99 | 25 | 0 | 446840
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 52 | 93 | 93 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 1942752
172 | Confidence Power Bogura Unit-1 113 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 70 | 70 | 70 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1814880
173 | Rangpur 20 MW GTPP | [19 empty] | 10 | 8 | 5 | 0 | 0 | 0 | 0 | 15000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | [6 empty] | 34 | 106 | 113 | 113 | 113 | 113 | 113 | 109 | 109 | 110 |  | 109 | 106 | 107 | 107 | 107 | 84 | 47 | 1659840
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 7 | 7 | 7 | 5 | 3 | 2 | 1 | 0 | [8 empty] | 46557
178
178