## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-08 | Thursday
|  |  | Date (day): | 2021-04-08 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14882.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15688 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-07 | 2021-04-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170 | 20 |  | Gas shortage
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 103 | 104 | 104
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 40 | 0 | 0 | 412 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 188 | 146 | 250 | 250 | 110 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 400 | 400 | 50 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 63 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 260 | 270 | 270 | 35 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 5 | 61 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 175 | 177 | 180 | 180
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 80 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 222 | 220 | 220 |  | 115 | ST under maint
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 32 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 51 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 35 | 282 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 141 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 94 | 162 | 162 | 162
|  | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2627 | 3446 | 3952 | 4172 | 735 | 800
| 39 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 40 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 41 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 42 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 50 | 50 | 50
| 43 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 105 | 105 | 125 |  | Low water lavel
| 44 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 195 | 202 | 225 | 225
| 45 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 47 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98
| 48 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 82 | 85 |  | 17 | Engine problem
| 49 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 100 | 100 | 100
| 50 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 51 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 9 | 29 | 15 | 20
| 52 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 2 | 92 | 100 | 100
| 53 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 54 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 32 | 300 | 300
| 55 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 56 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 57 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 58 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 57 | 98 | 60 | 60 |  | 56 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 908 | 1187 | 1653 | 1686 | 485 | 171
| 59 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 60 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 171 | 212 | 225 | 225 |  |  | FGMO
| 61 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 275 | 360 | 360 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 270 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 64 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 51 | 50 | 50
| 65 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
| 66 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 67 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 68 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 69 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 89 | 90 | 90 |  | 73 | Machine problem
| 70 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 180 | 180 | 200 | 200
| 71 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 72 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 128 | 160 | 151 | 168
| 73 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 74 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 18 | 52 | 52 | 52
| 75 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 17 | 17 | 17 |  | 8 | Engine problem
| 76 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 77 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 114 | 114
| 78 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 93 | 111 | 113 | 113
|  | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 36 | 36
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1515 | 1747 | 1988 | 2155 | 584 | 81
| 79 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 116 | 114 | 160 | 160 | 42 |  | Gas shortage
| 80 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 14 | 17 | 17 |  | 5 | Engine problem
| 81 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 32 | 49 | 49 |  | 46 | Engine problem
| 82 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 83 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 183 | 191 | 200 | 200
| 84 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 85 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 86 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 520 | 490 | 614.6 | 563 | 42 | 51
| 87 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 44 | 44 |  | 26 | Engine problem
| 88 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Engine problem
| 89 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 90 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 164 | 332 | 330 | 330
| 91 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 92 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 93 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 94 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 33 | 33 |  | 33 | GT-9 Under maint.
| 95 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 75 | 78 |  | 8 | Engine problem
|  | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 20/04/2021
| 96 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 217 | 204 | 225 | 225
| 97 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 98 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 99 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 100 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 300 | 341 | 341 |  |  | FGMO
| 101 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 364 | 400 | 400
| 102 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 9 | 10 | 10
| 103 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1913 | 2066 | 2162 | 2165 | 0 | 223
| 104 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 830 | 830 | 727 | 848
| 105 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 99 | 99 |  | 16 | Engine problem
| 106 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 6 | 4 | 20 | 20 |  | 34 | Engine problem
| 107 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 108 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 109 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 160 | 200 | 400 | 400
| 110 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1165 | 1370 | 1593 | 2000 | 0 | 107
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 30 | 25 | 26 |  | 7 | Engine problem
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 66 | 68 | 70 | 70 |  | 124 | GT-2 under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 96 | 95 | 95
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 600 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 119 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 628 | 890 | 1072 | 1073 | 0 | 131
| 120 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 65 | 65
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 121 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 122 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 123 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 124 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 40 | 40
| 126 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 50 | 0 | 0 | 0
| 127 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 124 | 158 | 180 | 180 | 40 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 190 | 200 | 200 | 20 |  | Gas shortage
| 129 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 341 | 350 | 400 | 400
| 130 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34
| 131 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 132 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 133 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 5 | 11 | 11
| 134 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 135 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 136 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 137 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 94 | 94 |  | 19 | Engine problem
| 138 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 911 | 1192 | 1567 | 1601 | 260 | 19
| 139 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 140 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 141 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 142 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Engine problem
| 143 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 107 | 113 | 113 | 113
| 144 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 263 | 263 | 281 | 273 | 124 | 200
|  | Total |  |  |  |  | 21967 | 21219 | 10450 | 12651 | 14882.6 | 15688 | 2230 | 1783
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9889.9573 | 11973 | 14085.0028 | 14847.2393
| A. |  | 2021-04-07 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 12651 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8789 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12651 | MW
| 3 | Day peak Generation : |  |  | 10450 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11973 | MW
| 4 | Evening peak Generation : |  |  | 12651 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 254.6545 | MKWHr | By Solar | 0.73026 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 145.7019 | MKWHr |  | By Oil: | 66.6004 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.5441 | MKWHr |  | By Hydro: | 1.7742 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2230 | MW | Dhaka | 4193 | 4193 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1783 | MW | Chittagong | 1173 | 1173 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4013 | MW | Khulna | 1517 | 1517 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1188.93 | MMCFD |  |  | Rajshahi | 1357 | 1357 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 158329301.714 | ii) Oil : | Taka | 473023311.9 | Comilla | 1171 | 1171 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 76408390 | Total | Taka | 707761003.614 | Mymensingh | 997 | 997 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.1635 | MKWHr. | Sylhet | 469 | 469 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -430 | MW (E to W) at | 21:00 | hrs | Barisal | 333 | 333 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -430 | MW at | 21:00 | hrs | Rangpur | 763 | 763 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.2° C |  |  | Total | 11973 | 11973 |  | 0
| B. |  | 2021-04-08 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 37.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15688 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2788 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 259.6666 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9403 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.0531 | MKWHr. | ii) HVDC Flow at Peak Time |  | 830 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2506 | MKWHr. | iii) Maximum HVDC Flow : |  | 830 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.29 |  | (b) Today: | 83.05 |  | (c) Rule Curve: |  | 86.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 264 | 190 |  | 0 | 320 | 230 | 0 | 0 | 55 | 0 | 0 | 170 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 18 | 0 | 51 | 10 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 300 | 295 | 206 | 16 | 86 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 18 | 136 | 160 | 49 | 17 | 0 | 44 | 43 | 53 | 0 | 163 | 163 | 34 | 78 | 0 | 217 | 18 | 0 | 9 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 183 | 0 | 138 | 0 | 100 | 180 | 0 | 366 | 75 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 75 | 100 | 370 | 104 | 0 | 17 | 32 | 0 | 36 | 0 |  | 829 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 126 | 0 | 97 | 0 | 123 | 0 | 362 | 53 | 0 | 94 | 0 | 92 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 7142 | 3029 | 10171 | 4464 | 829 | 1803 | 2112 | 670 | 70 | 87 | 136 | 0 | 0 | 83.34
2:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 264 | 211 |  | 0 | 320 | 230 | 0 | 0 | 30 | 0 | 0 | 145 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 201 | 0 | 130 | 0 |  | 18 | 0 | 17 | 10 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 300 | 295 | 202 | 16 | 86 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 132 | 159 | 49 | 17 | 0 | 44 | 43 | 53 | 0 | 163 | 163 | 34 | 78 | 0 | 217 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 192 | 0 | 96 | 0 | 100 | 179 | 0 | 366 | 8 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 17 | 100 | 370 | 104 | 0 | 0 | 0 | 0 | 36 | 0 |  | 830 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 127 | 0 | 95 | 0 | 124 | 0 | 362 | 35 | 0 | 94 | 0 | 34 | 0 | 0 | 113 | 500 | 0 | 0 | 0 |  | 6814 | 2919 | 9733 | 4440 | 830 | 1825 | 1749 | 650 | 70 | 37 | 132 | 0 | 0 | 83.33
3:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 260 | 231 |  | 0 | 320 | 230 | 0 | 0 | 15 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 18 | 0 | 0 | 10 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 300 | 295 | 206 | 16 | 89 | 23 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 130 | 161 | 49 | 17 | 0 | 44 | 43 | 53 | 0 | 130 | 164 | 35 | 78 | 0 | 217 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 140 | 0 | 80 | 0 | 100 | 179 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 370 | 45 | 0 | 0 | 0 | 0 | 36 | 0 |  | 829 | 0 | 185 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 69 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 130 | 0 | 95 | 0 | 127 | 0 | 362 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 70 | 500 | 0 | 0 | 0 |  | 6510 | 2814 | 9324 | 4450 | 829 | 1814 | 1377 | 650 | 70 | 4 | 130 | 0 | 0 | 83.32
4:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 259 | 231 |  | 0 | 320 | 230 | 0 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 18 | 0 | 0 | 10 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 300 | 295 | 198 | 16 | 88 | 23 | 53 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 126 | 161 | 16 | 17 | 0 | 44 | 43 | 53 | 0 | 130 | 163 | 35 | 78 | 0 | 217 | 18 | 0 | 9 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 140 | 0 | 80 | 0 | 100 | 173 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 370 | 17 | 0 | 0 | 0 | 0 | 36 | 0 |  | 830 | 0 | 195 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 130 | 0 | 95 | 0 | 131 | 0 | 362 | 0 | 0 | 94 | 0 | 0 | 0 | 0 | 70 | 470 | 0 | 0 | 0 |  | 6418 | 2797 | 9215 | 4428 | 830 | 1827 | 1310 | 620 | 70 | 4 | 126 | 0 | 0 | 83.31
5:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 259 | 236 |  | 0 | 320 | 230 | 0 | 0 | 15 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 20 | 0 | 0 | 10 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 305 | 295 | 179 | 16 | 89 | 23 | 54 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 120 | 161 | 8 | 17 | 0 | 44 | 43 | 53 | 0 | 130 | 163 | 35 | 78 | 0 | 217 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 140 | 0 | 67 | 0 | 60 | 120 | 0 | 366 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 100 | 400 | 17 | 0 | 0 | 0 | 0 | 35 | 0 |  | 830 | 0 | 195 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 69 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 50 | 0 | 130 | 0 | 95 | 0 | 131 | 0 | 364 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 470 | 0 | 0 | 0 |  | 6314 | 2703 | 9017 | 4443 | 830 | 1829 | 1102 | 619 | 70 | 4 | 120 | 0 | 0 | 83.3
6:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 260 | 225 |  | 0 | 320 | 230 | 0 | 0 | 15 | 0 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 205 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 330 | 325 | 198 | 16 | 90 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 114 | 161 | 8 | 17 | 0 | 44 | 43 | 22 | 0 | 110 | 161 | 34 | 40 | 0 | 217 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 140 | 0 | 65 | 0 | 30 | 68 | 0 | 392 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 60 | 400 | 17 | 0 | 0 | 0 | 0 | 36 | 0 |  | 830 | 0 | 205 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 50 | 0 | 130 | 0 | 71 | 0 | 131 | 0 | 340 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 35 | 470 | 0 | 0 | 0 |  | 6145 | 2644 | 8789 | 4532 | 830 | 1654 | 966 | 619 | 70 | 4 | 114 | 0 | 0 | 83.29
7:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 264 | 213 |  | 0 | 320 | 230 | 0 | 0 | 15 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 217 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 0 | 20 | 33 | 80 | 0 | 0 | 340 | 335 | 154 | 16 | 90 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 104 | 159 | 8 | 17 | 0 | 44 | 43 | 22 | 0 | 110 | 164 | 34 | 40 | 0 | 217 | 18 | 0 | 9 | 325 | 16 | 5 | 0 | 0 | 0 | 0 | 175 | 0 | 67 | 0 | 30 | 68 | 0 | 402 | 17 | 0 | 0 | 1 | 0 | 35 | 0 | 0 | 0 | 60 | 400 | 17 | 5 | 0 | 0 | 0 | 36 | 4 |  | 830 | 0 | 205 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 50 | 0 | 130 | 0 | 54 | 0 | 134 | 0 | 403 | 17 | 0 | 60 | 0 | 58 | 0 | 1 | 70 | 470 | 0 | 0 | 0 |  | 6220 | 2811 | 9031 | 4539 | 830 | 1714 | 1140 | 619 | 70 | 4 | 104 | 11 | 0 | 83.28
8:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 261 | 160 |  | 0 | 320 | 235 | 0 | 0 | 15 | 0 | 0 | 150 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 22 | 25 | 0 | 25 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 3 | 20 | 8 | 80 | 0 | 0 | 300 | 300 | 161 | 16 | 89 | 23 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 108 | 139 | 8 | 17 | 1 | 44 | 43 | 22 | 0 | 110 | 162 | 33 | 50 | 0 | 216 | 18 | 0 | 9 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 185 | 0 | 124 | 0 | 30 | 68 | 0 | 363 | 103 | 0 | 0 | 2 | 0 | 35 | 0 | 0 | 0 | 60 | 385 | 17 | 16 | 0 | 0 | 0 | 36 | 13 |  | 830 | 0 | 190 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 66 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 130 | 0 | 55 | 0 | 137 | 0 | 419 | 35 | 0 | 92 | 0 | 102 | 0 | 1 | 95 | 470 | 0 | 0 | 0 |  | 6255 | 2967 | 9222 | 4381 | 830 | 1658 | 1470 | 620 | 70 | 52 | 108 | 33 | 0 | 83.27
9:00 | 0 | 0 | 0 | 170 | 300 | 98 | 0 | 0 | 183 |  | 0 | 320 | 235 | 3 | 0 | 20 | 0 | 0 | 150 | 4 | 2 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 40 | 22 | 25 | 0 | 25 | 25 | 22 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 18 | 20 | 3 | 80 | 0 | 0 | 300 | 300 | 171 | 16 | 90 | 20 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 122 | 137 | 16 | 17 | 1 | 44 | 43 | 50 | 0 | 163 | 164 | 33 | 75 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 185 | 0 | 114 | 12 | 100 | 96 | 0 | 365 | 115 | 0 | 0 | 3 | 0 | 35 | 0 | 0 | 27 | 90 | 384 | 60 | 21 | 7 | 2 | 0 | 36 | 21 |  | 830 | 0 | 180 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 128 | 0 | 55 | 0 | 130 | 0 | 401 | 35 | 0 | 94 | 0 | 113 | 0 | 2 | 95 | 450 | 0 | 0 | 0 |  | 6582 | 2950 | 9532 | 4109 | 830 | 1750 | 1837 | 600 | 70 | 154 | 122 | 60 | 0 | 83.26
10:00 | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 0 | 187 |  | 0 | 320 | 235 | 7 | 0 | 55 | 0 | 0 | 150 | 28 | 7 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 0 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 18 | 20 | 6 | 80 | 0 | 0 | 320 | 320 | 174 | 16 | 89 | 20 | 30 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 33 | 18 | 120 | 137 | 24 | 17 | 2 | 43 | 43 | 50 | 0 | 163 | 164 | 32 | 78 | 0 | 217 | 18 | 0 | 9 | 315 | 16 | 5 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 15 | 100 | 155 | 0 | 377 | 115 | 0 | 0 | 4 | 0 | 51 | 0 | 0 | 75 | 100 | 400 | 104 | 39 | 17 | 17 | 0 | 36 | 28 |  | 830 | 0 | 170 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 123 | 0 | 89 | 0 | 130 | 0 | 403 | 35 | 0 | 94 | 0 | 107 | 0 | 2 | 95 | 450 | 0 | 0 | 0 |  | 6930 | 2992 | 9922 | 4162 | 830 | 1800 | 2096 | 600 | 70 | 154 | 120 | 90 | 0 | 83.25
11:00 | 0 | 0 | 0 | 170 | 300 | 99 | 0 | 0 | 186 |  | 0 | 320 | 265 | 24 | 0 | 55 | 0 | 0 | 150 | 45 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 80 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 195 | 0 | 130 | 0 |  | 22 | 0 | 0 | 50 | 0 | 19 | 17 | 6 | 80 | 0 | 0 | 295 | 300 | 175 | 16 | 90 | 23 | 30 | 0 | 0 | 0 | 0 | 1 | 16 | 11 | 25 | 18 | 130 | 133 | 16 | 17 | 2 | 43 | 43 | 50 | 0 | 163 | 165 | 32 | 78 | 0 | 217 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 5 | 0 | 0 | 184 | 0 | 108 | 17 | 100 | 178 | 0 | 367 | 115 | 0 | 0 | 4 | 0 | 54 | 0 | 0 | 75 | 100 | 385 | 104 | 44 | 36 | 35 | 0 | 36 | 32 |  | 830 | 0 | 160 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 124 | 0 | 93 | 0 | 130 | 0 | 342 | 35 | 0 | 94 | 0 | 107 | 0 | 3 | 95 | 450 | 0 | 0 | 0 |  | 7210 | 2928 | 10138 | 4149 | 830 | 1730 | 2373 | 600 | 70 | 154 | 130 | 102 | 0 | 83.24
12:00 | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 0 | 188 |  | 0 | 320 | 265 | 63 | 0 | 55 | 0 | 0 | 175 | 80 | 32 | 150 | 5 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 8 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 195 | 0 | 130 | 0 |  | 22 | 0 | 0 | 100 | 2 | 21 | 17 | 9 | 80 | 0 | 0 | 260 | 300 | 171 | 16 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 18 | 16 | 11 | 25 | 18 | 128 | 116 | 16 | 17 | 2 | 42 | 43 | 50 | 0 | 163 | 164 | 31 | 78 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 35 | 0 | 0 | 183 | 0 | 141 | 18 | 90 | 180 | 0 | 367 | 115 | 0 | 0 | 4 | 16 | 54 | 0 | 17 | 93 | 100 | 400 | 104 | 49 | 94 | 57 | 0 | 36 | 33 |  | 830 | 0 | 160 | 0 | 99 | 0 | 0 | 0 | 6 | 0 | 0 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 124 | 0 | 94 | 0 | 130 | 0 | 341 | 70 | 0 | 94 | 0 | 107 | 0 | 6 | 95 | 450 | 0 | 0 | 0 |  | 7483 | 2967 | 10450 | 4060 | 830 | 1743 | 2751 | 600 | 70 | 156 | 128 | 112 | 0 | 83.23
13:00 | 0 | 0 | 0 | 170 | 300 | 95 | 0 | 0 | 188 |  | 0 | 320 | 265 | 92 | 0 | 55 | 0 | 0 | 175 | 95 | 70 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 201 | 0 | 130 | 0 |  | 24 | 0 | 0 | 100 | 38 | 42 | 17 | 9 | 80 | 0 | 0 | 260 | 300 | 181 | 16 | 88 | 26 | 30 | 0 | 0 | 0 | 0 | 50 | 17 | 11 | 25 | 18 | 134 | 111 | 16 | 17 | 2 | 43 | 43 | 53 | 0 | 163 | 164 | 32 | 77 | 0 | 208 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 144 | 0 | 0 | 183 | 0 | 149 | 18 | 90 | 180 | 0 | 367 | 115 | 0 | 0 | 4 | 33 | 54 | 0 | 17 | 110 | 100 | 370 | 104 | 44 | 162 | 60 | 0 | 36 | 31 |  | 830 | 0 | 150 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 61 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 124 | 0 | 95 | 0 | 130 | 0 | 341 | 70 | 0 | 94 | 0 | 107 | 0 | 6 | 95 | 450 | 0 | 0 | 0 |  | 7905 | 2952 | 10857 | 4030 | 830 | 1744 | 3191 | 600 | 70 | 153 | 134 | 105 | 10857 | 83.22
14:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 0 | 184 |  | 0 | 320 | 235 | 91 | 0 | 55 | 0 | 0 | 115 | 95 | 102 | 147 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 0 | 100 | 51 | 47 | 17 | 5 | 80 | 0 | 0 | 260 | 295 | 181 | 16 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 17 | 11 | 25 | 17 | 134 | 113 | 16 | 17 | 2 | 42 | 43 | 22 | 0 | 130 | 165 | 31 | 77 | 0 | 190 | 18 | 0 | 8 | 305 | 16 | 5 | 0 | 150 | 0 | 0 | 183 | 0 | 149 | 16 | 90 | 180 | 0 | 367 | 115 | 0 | 0 | 4 | 33 | 54 | 0 | 17 | 112 | 100 | 379 | 104 | 41 | 162 | 76 | 0 | 36 | 27 |  | 829 | 0 | 160 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 124 | 0 | 93 | 0 | 140 | 0 | 340 | 80 | 0 | 113 | 0 | 113 | 0 | 6 | 95 | 460 | 0 | 0 | 0 |  | 7751 | 2967 | 10718 | 3932 | 829 | 1666 | 3231 | 610 | 70 | 150 | 134 | 96 | 0 | 83.21
15:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 0 | 178 |  | 0 | 320 | 230 | 94 | 0 | 55 | 0 | 0 | 182 | 100 | 102 | 147 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 90 | 55 | 50 | 20 | 3 | 80 | 0 | 0 | 270 | 275 | 184 | 16 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 17 | 11 | 25 | 17 | 124 | 112 | 16 | 17 | 1 | 41 | 43 | 47 | 0 | 163 | 164 | 31 | 76 | 0 | 210 | 18 | 0 | 8 | 320 | 16 | 5 | 0 | 159 | 0 | 0 | 182 | 0 | 149 | 12 | 90 | 180 | 0 | 373 | 115 | 0 | 0 | 3 | 66 | 54 | 0 | 52 | 110 | 100 | 392 | 104 | 24 | 162 | 75 | 0 | 36 | 21 |  | 829 | 0 | 170 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 124 | 0 | 95 | 0 | 135 | 0 | 345 | 105 | 0 | 113 | 0 | 113 | 0 | 5 | 95 | 500 | 0 | 0 | 0 |  | 7969 | 3065 | 11034 | 4037 | 829 | 1732 | 3349 | 650 | 70 | 177 | 124 | 66 | 0 | 83.2
16:00 | 0 | 0 | 0 | 170 | 300 | 96 | 0 | 0 | 173 |  | 0 | 320 | 230 | 100 | 0 | 55 | 0 | 0 | 110 | 100 | 64 | 147 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 0 | 90 | 40 | 50 | 20 | 3 | 80 | 0 | 0 | 260 | 270 | 209 | 16 | 87 | 26 | 30 | 0 | 0 | 0 | 0 | 48 | 19 | 11 | 25 | 17 | 138 | 122 | 24 | 17 | 1 | 42 | 43 | 53 | 0 | 130 | 295 | 32 | 75 | 0 | 210 | 18 | 0 | 8 | 290 | 16 | 8 | 0 | 227 | 0 | 0 | 182 | 0 | 149 | 0 | 100 | 180 | 0 | 333 | 115 | 0 | 0 | 2 | 66 | 54 | 0 | 52 | 111 | 100 | 340 | 104 | 17 | 162 | 79 | 0 | 36 | 14 |  | 830 | 0 | 180 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 55 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 95 | 0 | 155 | 0 | 343 | 105 | 0 | 113 | 0 | 113 | 0 | 3 | 95 | 510 | 0 | 0 | 0 |  | 7917 | 3118 | 11035 | 4054 | 830 | 1665 | 3382 | 660 | 70 | 199 | 138 | 37 | 0 | 83.19
17:00 | 0 | 0 | 0 | 170 | 300 | 56 | 0 | 0 | 160 |  | 0 | 320 | 130 | 55 | 0 | 55 | 12 | 0 | 115 | 60 | 64 | 147 | 10 | 0 | 0 | 0 | 54 | 17 | 35 | 22 | 25 | 20 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 23 | 0 | 0 | 30 | 17 | 24 | 20 | 8 | 80 | 0 | 0 | 275 | 270 | 208 | 16 | 87 | 26 | 30 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 17 | 138 | 131 | 24 | 17 | 0 | 41 | 43 | 53 | 0 | 130 | 307 | 32 | 76 | 0 | 210 | 18 | 0 | 9 | 295 | 16 | 8 | 0 | 240 | 0 | 0 | 181 | 0 | 149 | 2 | 100 | 180 | 0 | 330 | 115 | 0 | 0 | 1 | 16 | 54 | 0 | 17 | 75 | 100 | 340 | 104 | 6 | 108 | 80 | 0 | 36 | 5 |  | 829 | 0 | 195 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 8 | 49 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 96 | 0 | 165 | 0 | 344 | 53 | 0 | 113 | 0 | 106 | 0 | 2 | 95 | 480 | 0 | 0 | 0 |  | 7356 | 3062 | 10418 | 4150 | 829 | 1633 | 2745 | 630 | 70 | 207 | 138 | 16 | 0 | 83.18
18:00 | 0 | 0 | 0 | 170 | 300 | 26 | 0 | 0 | 158 |  | 0 | 320 | 130 | 50 | 0 | 55 | 12 | 0 | 73 | 60 | 64 | 147 | 10 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 24 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 70 | 0 |  | 23 | 0 | 0 | 30 | 12 | 24 | 20 | 8 | 80 | 0 | 0 | 275 | 270 | 210 | 16 | 89 | 26 | 30 | 0 | 0 | 0 | 0 | 25 | 21 | 11 | 25 | 17 | 134 | 127 | 24 | 17 | 0 | 41 | 43 | 53 | 0 | 130 | 282 | 32 | 77 | 0 | 182 | 19 | 0 | 7 | 290 | 0 | 8 | 0 | 243 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 180 | 0 | 307 | 115 | 1 | 0 | 0 | 16 | 54 | 0 | 17 | 75 | 100 | 330 | 104 | 1 | 108 | 80 | 0 | 36 | 1 |  | 830 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 11 | 0 | 0 | 65 | 25 | 16 | 0 | 0 | 0 | 5 | 27 | 84 | 0 | 0 | 6 | 25 | 25 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 97 | 0 | 180 | 0 | 320 | 53 | 0 | 113 | 0 | 111 | 0 | 0 | 95 | 450 | 0 | 0 | 0 |  | 7127 | 3165 | 10292 | 3983 | 830 | 1578 | 2790 | 600 | 70 | 305 | 134 | 2 | 0 | 83.17
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
19:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 3 | 153 |  | 0 | 320 | 230 | 78 | 0 | 55 | 217 | 0 | 182 | 85 | 85 | 148 | 45 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 15 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 72 | 36 | 20 | 14 | 80 | 0 | 0 | 275 | 270 | 212 | 8 | 90 | 26 | 40 | 0 | 0 | 0 | 50 | 34 | 22 | 11 | 25 | 17 | 158 | 120 | 32 | 17 | 0 | 41 | 43 | 53 | 0 | 163 | 308 | 33 | 78 | 0 | 204 | 18 | 0 | 8 | 310 | 0 | 11 | 0 | 259 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 171 | 0 | 365 | 115 | 79 | 0 | 0 | 48 | 54 | 0 | 114 | 111 | 100 | 370 | 104 | 0 | 147 | 94 | 0 | 36 | 0 |  | 829 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 32 | 68 | 29 | 75 | 0 | 0 | 0 | 43 | 27 | 90 | 0 | 0 | 31 | 52 | 31 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 98 | 38 | 190 | 0 | 351 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 470 | 0 | 0 | 0 |  | 8643 | 3524 | 12167 | 4514 | 829 | 1748 | 3710 | 620 | 70 | 518 | 158 | 0 | 0 | 83.14
19:30 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 54 | 148 |  | 0 | 320 | 230 | 100 | 0 | 55 | 219 | 0 | 182 | 100 | 93 | 149 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 98 | 50 | 20 | 15 | 80 | 0 | 0 | 275 | 270 | 212 | 8 | 90 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 25 | 17 | 162 | 119 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 336 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 284 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 180 | 0 | 367 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 114 | 112 | 100 | 382 | 104 | 0 | 162 | 95 | 0 | 36 | 0 |  | 830 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 32 | 68 | 29 | 80 | 0 | 0 | 0 | 43 | 27 | 90 | 0 | 0 | 31 | 52 | 34 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 96 | 100 | 195 | 0 | 351 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 580 | 0 | 0 | 0 |  | 8936 | 3707 | 12643 | 4628 | 830 | 1745 | 3956 | 730 | 70 | 522 | 162 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 300 | 102 | 0 | 32 | 148 |  | 0 | 320 | 260 | 100 | 0 | 55 | 220 | 0 | 177 | 100 | 95 | 150 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 98 | 50 | 20 | 24 | 80 | 0 | 0 | 275 | 270 | 212 | 8 | 90 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 17 | 160 | 116 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 332 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 282 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 175 | 0 | 365 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 114 | 111 | 100 | 378 | 104 | 0 | 162 | 98 | 0 | 36 | 0 |  | 829 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 32 | 68 | 27 | 80 | 0 | 0 | 0 | 43 | 27 | 90 | 0 | 0 | 31 | 52 | 33 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 96 | 100 | 190 | 0 | 350 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 580 | 0 | 0 | 0 |  | 8951 | 3698 | 12649 | 4593 | 829 | 1762 | 3983 | 730 | 70 | 522 | 160 | 0 | 0 | 83.15
21:00 | 0 | 0 | 0 | 170 | 300 | 103 | 0 | 40 | 146 |  | 0 | 320 | 260 | 100 | 0 | 55 | 222 | 0 | 177 | 100 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 92 | 50 | 20 | 29 | 80 | 0 | 0 | 275 | 270 | 212 | 8 | 89 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 17 | 160 | 114 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 332 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 282 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 180 | 0 | 364 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 114 | 111 | 100 | 400 | 104 | 0 | 162 | 98 | 0 | 36 | 0 |  | 830 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 68 | 30 | 96 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 0 | 31 | 52 | 33 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 96 | 100 | 190 | 0 | 350 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 600 | 0 | 0 | 0 |  | 8936 | 3715 | 12651 | 4631 | 830 | 1758 | 4006 | 750 | 70 | 446 | 160 | 0 | 0 | 83.14
22:00 | 0 | 0 | 0 | 170 | 300 | 103 | 0 | 10 | 135 |  | 0 | 320 | 260 | 100 | 0 | 55 | 223 | 0 | 177 | 100 | 102 | 133 | 61 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 51 | 0 | 32 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 60 | 50 | 20 | 37 | 80 | 0 | 0 | 275 | 270 | 210 | 8 | 82 | 26 | 53 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 11 | 160 | 113 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 330 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 284 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 180 | 0 | 366 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 114 | 110 | 100 | 378 | 104 | 0 | 162 | 97 | 0 | 36 | 0 |  | 830 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 32 | 68 | 26 | 96 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 0 | 17 | 52 | 33 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 96 | 60 | 193 | 0 | 351 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 580 | 0 | 0 | 0 |  | 8857 | 3637 | 12494 | 4564 | 830 | 1759 | 3935 | 730 | 102 | 414 | 160 | 0 | 0 | 83.13
23:00 | 0 | 0 | 0 | 170 | 300 | 104 | 0 | 61 | 130 |  | 0 | 320 | 230 | 100 | 0 | 55 | 222 | 0 | 140 | 100 | 102 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 36 | 70 | 0 | 0 | 25 | 205 | 0 | 130 | 0 |  | 24 | 0 | 68 | 90 | 45 | 50 | 20 | 39 | 80 | 0 | 0 | 275 | 280 | 214 | 8 | 82 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 11 | 156 | 121 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 334 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 284 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 180 | 0 | 375 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 17 | 105 | 100 | 400 | 104 | 0 | 162 | 99 | 0 | 36 | 0 |  | 830 | 0 | 190 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 32 | 68 | 30 | 80 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 4 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 97 | 60 | 193 | 0 | 351 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 560 | 0 | 0 | 0 |  | 8619 | 3457 | 12076 | 4627 | 830 | 1755 | 3652 | 710 | 106 | 240 | 156 | 0 | 0 | 83.12
24:00 | 0 | 0 | 0 | 170 | 300 | 104 | 0 | 0 | 140 |  | 0 | 320 | 230 | 100 | 0 | 55 | 223 | 0 | 140 | 50 | 102 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 25 | 25 | 0 | 0 | 36 | 70 | 0 | 0 | 25 | 208 | 0 | 130 | 0 |  | 20 | 0 | 41 | 90 | 15 | 50 | 20 | 40 | 80 | 0 | 0 | 275 | 285 | 215 | 8 | 81 | 26 | 53 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 11 | 154 | 129 | 32 | 17 | 0 | 42 | 43 | 53 | 0 | 163 | 333 | 33 | 78 | 0 | 196 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 173 | 0 | 382 | 115 | 90 | 0 | 0 | 16 | 54 | 0 | 0 | 112 | 100 | 400 | 104 | 0 | 162 | 97 | 0 | 36 | 0 |  | 829 | 0 | 190 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 16 | 68 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 155 | 0 | 95 | 0 | 190 | 0 | 352 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 95 | 560 | 0 | 0 | 0 |  | 8207 | 3248 | 11455 | 4583 | 829 | 1775 | 3173 | 709 | 106 | 126 | 154 | 0 | 0 | 83.11
KWH | 0 | 0 | 0 | 4000500 | 7150127 | 2262363 | 0 | 2420740 | 4382000 |  | 0 | 7070050 | 5499927 | 1181760 | 0 | 1073093 | 1295528 | 0 | 3663000 | 1287360 | 1154448 | 2372160 | 415624 | 0 | 0 | 0 | 1188360 | 925518 | 1106978 | 463896 | 600000 | 482760 | 628800 | 598100 | 685488 | 0 | 86225 | 1688000 | 0 | 0 | 603532 | 4808156 | 0 | 3061632 | 0 |  | 543600 | 0 | 544091 | 1243320 | 624000 | 624480 | 456336 | 489120 | 1947542 | 0 | 0 | 7288000 | 7135000 | 4681000 | 384727 | 2093360 | 541008 | 984480 | 0 | 0 | 0 | 95592 | 514877 | 456408 | 232200 | 739000 | 401770 | 3250560 | 3128200 | 566400 | 336816 | 14350 | 1016000 | 1026600 | 1139400 | 0 | 3677072 | 5103000 | 791424 | 1777920 | 0 | 5047100 | 417000 | 0 | 194760 | 7408500 | 360768 | 163000 | 0 | 2860362 | 0 | 0 | 4281600 | 0 | 2911680 | 110835 | 2101440 | 3869280 | 0 | 8844000 | 2128800 | 618000 | 0 | 29520 | 411491 | 1181575 | 0 | 663480 | 1787520 | 2290560 | 9171500 | 2055360 | 301570 | 2047680 | 1225691 | 0 | 870840 | 234521 |  | 20053091 | 0 | 4545216 | 0 | 2278080 | 0 | 0 | 0 | 109440 | 0 | 205875 | 1515000 | 503084 | 501216 | 0 | 0 | 0 | 181689 | 92822 | 637504 | 0 | 0 | 109853 | 766080 | 166082 | 490560 | 0 | 124452 | 0 | 0 | 3669700 | 0 | 0 | 0 | 0 | 3496709 | 0 | 2142739 | 428160 | 3890345 | 0 | 8673100 | 938880 | 0 | 2398944 | 0 | 2083200 | 0 | 39464 | 2146560 | 12874400 | 0 | 0 | 0 |  | 179592211 | 75062245 | 254654456 | 104121993 | 20053091 | 41579875 | 62291119 | 16544100 | 1774225 | 4309233 | 3250560 | 730260 | 0
Fuel Cost | 0 | 0 | 0 | 5880735 | 7936640.97 | 2986319.16 | 0 | 2444947.4 | 4513460 |  | 0 | 7706354.5 | 6104918.97 | 8969558.4 | 0 | 9078366.78 | 1347349.12 | 0 | 6336990 | 9693820.8 | 10528565.76 | 23342054.4 | 3832053.28 | 0 | 0 | 0 | 8675028 | 7154254.14 | 10914803.08 | 347922 | 450000 | 0 | 0 | 0 | 6628668.96 | 0 | 23280.75 | 455760 | 0 | 0 | 5606812.28 | 5240890.04 | 0 | 5204774.4 | 0 |  | 0 | 0 | 5277682.7 | 11873706 | 5428800 | 4945881.6 | 574983.36 | 1452686.4 | 2882362.16 | 0 | 0 | 5393120 | 7135000 | 4306520 | 496297.83 | 2407364 | 611339.04 | 1378272 | 0 | 0 | 0 | 965479.2 | 4917075.35 | 579638.16 | 174150 | 1293250 | 301327.5 | 24379200 | 3315892 | 5142912 | 427756.32 | 228739 | 1666240 | 1642560 | 2028132 | 0 | 4191862.08 | 5307120 | 1559105.28 | 3395827.2 | 0 | 8731483 | 913230 | 0 | 397310.4 | 7482585 | 270576 | 123880 | 0 | 21624336.72 | 0 | 0 | 22264320 | 0 | 28650931.2 | 1295661.15 | 17126736 | 41981688 | 0 | 8224920 | 19414656 | 5840100 | 0 | 0 | 3110871.96 | 10291518.25 | 0 | 6621530.4 | 15319046.4 | 15255129.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115505804.16 | 0 | 4772476.8 | 0 | 17905708.8 | 0 | 0 | 0 | 1148025.6 | 0 | 2145217.5 | 1711950 | 779780.2 | 4891868.16 | 0 | 0 | 0 | 1787819.76 | 943071.52 | 5641910.4 | 0 | 0 | 1064475.57 | 7423315.2 | 1610995.4 | 941875.2 | 0 | 94210.164 | 0 | 0 | 19889774 | 0 | 0 | 0 | 0 | 4615655.88 | 0 | 3214108.5 | 7283001.6 | 4551703.65 | 0 | 8586369 | 9801907.2 | 0 | 22765978.56 | 0 | 16165632 | 0 | 436077.2 | 15863078.4 | 56518616 | 0 | 0 | 0 |  | 512025119.45 | 338060406.424 | 850085525.874 | 108778062.244 | 115505804.16 | 49551239.47 | 431241797.35 | 76408390 | 479040.75 | 41781514.55 | 24379200 | 1960477.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 300 | 97 | 0 | 0 | 188 |  | 0 | 320 | 265 | 63 | 0 | 55 | 0 | 0 | 175 | 80 | 32 | 150 | 5 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 8 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 195 | 0 | 130 | 0 |  | 22 | 0 | 0 | 100 | 2 | 21 | 17 | 9 | 80 | 0 | 0 | 260 | 300 | 171 | 16 | 90 | 26 | 30 | 0 | 0 | 0 | 0 | 18 | 16 | 11 | 25 | 18 | 128 | 116 | 16 | 17 | 2 | 42 | 43 | 50 | 0 | 163 | 164 | 31 | 78 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 35 | 0 | 0 | 183 | 0 | 141 | 18 | 90 | 180 | 0 | 367 | 115 | 0 | 0 | 4 | 16 | 54 | 0 | 17 | 93 | 100 | 400 | 104 | 49 | 94 | 57 | 0 | 36 | 33 |  | 830 | 0 | 160 | 0 | 99 | 0 | 0 | 0 | 6 | 0 | 0 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 124 | 0 | 94 | 0 | 130 | 0 | 341 | 70 | 0 | 94 | 0 | 107 | 0 | 6 | 95 | 450 | 0 | 0 | 0 |  | 10450 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 300 | 103 | 0 | 40 | 146 | 0 | 0 | 320 | 260 | 100 | 0 | 55 | 222 | 0 | 177 | 100 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 | 0 | 24 | 0 | 85 | 100 | 92 | 50 | 20 | 29 | 80 | 0 | 0 | 275 | 270 | 212 | 8 | 89 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 17 | 160 | 114 | 32 | 14 | 0 | 42 | 43 | 53 | 0 | 163 | 332 | 33 | 78 | 0 | 204 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 282 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 180 | 0 | 364 | 115 | 105 | 0 | 0 | 32 | 54 | 0 | 114 | 111 | 100 | 400 | 104 | 0 | 162 | 98 | 0 | 36 | 0 |  | 830 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 68 | 30 | 96 | 0 | 0 | 0 | 43 | 0 | 100 | 0 | 0 | 31 | 52 | 33 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 96 | 100 | 190 | 0 | 350 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 600 | 0 | 0 | 0 |  | 12651 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 300 | 104 | 0 | 0 | 250 | 0 | 0 | 400 | 270 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 35 | 70 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 85 | 100 | 100 | 50 | 22 | 20 | 80 | 0 | 0 | 360 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 17 | 168 | 160 | 49 | 17 | 0 | 44 | 43 | 51 | 0 | 163 | 330 | 33 | 78 | 0 | 225 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 60 | 0 | 36 |  |  | 848 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 70 | 26 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 180 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 170 | 300 | 104 | 0 | 0 | 250 | 0 | 0 | 400 | 270 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 35 | 70 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 82 | 100 | 100 | 50 | 22 | 15 | 80 | 0 | 0 | 360 | 300 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 17 | 151 | 160 | 49 | 17 | 1.6 | 44 | 43 | 51 | 0 | 163 | 330 | 33 | 75 | 0 | 225 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 60 | 0 | 36 | 30 |  | 727 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 70 | 25 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 300 | 104 | 0 | 0 | 158 | 0 | 0 | 320 | 230 | 0 | 0 | 55 | 170 | 0 | 76 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 24 | 25 |  | 51 | 0 | 35 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 4 | 20 | 8 | 80 | 0 | 0 | 280 | 275 | 160 | 8 | 89 | 26 | 52 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 120 | 121 | 32 | 17 | 1 | 43 | 43 | 53 | 0 | 110 | 331 | 33 | 72 | 0 | 150 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 174 | 0 | 15 | 8 | 100 | 180 | 0 | 313 | 115 | 105 | 0 | 1 | 0 | 54 | 0 | 0 | 17 | 100 | 370 | 104 | 17 | 0 | 35 | 0 | 36 | 12 | 0 | 713 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 32 | 66 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 65 | 0 | 184 | 0 | 353 | 53 | 0 | 94 | 0 | 25 | 0 | 1 | 95 | 450 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8789 | 6:00
| Highest Generation |  | 12651 | 21:00
| Day Peak Generation |  | 10450 | 12:00
| Evening Peak Generation |  | 12651 | 21:00
| HVDC Max Flow |  | 830 | 2:00
| HVDC EvPeak Flow |  | 830 | 21:00
| Load factor L.F |  | 83.87%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-08
Till now the maximum generation is : - |  |  | 13018 MW | 21:00 | Hrs on | 2021-04-03
The Summary of Yesterday's |  | 2021-04-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10450 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9403 | MW
Evening Peak Generation : |  | 12651 | MW Hour : | 21:00 | Available Max Generation : |  | 15688 | MW
E.P. Demand (at gen end) : |  | 12651 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12651 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2788 | MW
Total Gen. (MKWH) : |  | 254.6545 | System Load Factor : | 83.87% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -430 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-08
Actual : | 83.05 | Ft.(MSL) , | Rule curve : | 86.6 | Ft.( MSL )
Gas Consumed : | Total = | 1188.93 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 158329301.714
: |  | Coal : | 76408390 | Oil : | 473023311.9 | Total : | 707761003.614
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4538.5325 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1547.634 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1387.3918 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1253.8964 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1132.9786 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 914.2845 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 505.7129 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 235.2578 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 705.1679 |  |  | 0 | 0%
Total | 0 |  | 12220.8564 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100 MW
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Baghabari-Bhangura 132 kV Ckt-1 was under shut down from 10:16 to 18:04 for D/W.
b) Feni 132/33 kV T-2 transformer was under shutdown from 08:34 to 18:27 for C/M.
c) Hathazari-Baroirhat 132 kV Ckt-1 was under shut down from 10:04 to 11:13 for tree trimming.
d) Kabirpur-Tongi 132 kV Ckt-1 was under shut down from 09:59 to 15:59 for C/M.
e) Rampura-Mogbazar 132 kV Ckt-1 was under shut down from 08:37 to 19:59 for D/W at Mogbazar end.
f) Purbasadipur 132/33 kV T-3 transformer was under shutdown from 11:20 to 12:28 for C/M. |  |  |  |  | About 25 MW power interruption occurred under Purbasadipur S/S area
from 11:20 to 12:28.
g) Kodda 132 kV main Bus-1 was under shutdown from 09:23 to 17:12 for D/W.
h) Haripur 412 MW CCPP was shutdown at 08:52 due to dirty gas and was synchronized at 18:48 and
again was shutdown at 23:03 due to gas shortage.
i) B.Baria-Shahjibazar 132 kV Ckt-2 was under shut down from 13:15 to 14:35 for tree trimming.
j) Sirajganj unit-1 GT was shutdown at 13:11 due to low gas pressure.
k) Keraniganj 230/132 kV ATR-01 transformer was shutdown at 10:52 for C/M.
l) After maintenance Shahjibazar 330 MW GT-1 was synchronized at 15:01.
m) Kabirpur-Tongi 132 kV Ckt-2 was under shut down from 16:16 to 17:03 for protection test.
n) After maintenance Siddhirganj 335 MW GT was synchronized at 16:46.
o) Meghnaghat Summit 335 MW CCPP GT-2 tripped at 16:44 due to GBC problem and was synchronized
at 18:32.
p) Kabirpur-Manikganj 132 kV Ckt-1 was under shut down from 16:15 to 16:22 for CM.
q) Madaripur 132/33 kV T-3 transformer's 33 kV Bus section was under shutdown from 16:08 to 17:20 due |  |  |  |  | About 11 MW power interruption occurred under Madaripur S/S area
to Takerhat-1 33 kV feeder maintenance by PBS. |  |  |  |  | from 16:08 to 17:20.
r) Manikganj 132/33 kV T-3 transformer was under shutdown from 20:20 to 21:01 due to R/H.
s) Cumilla(N)-Shahjibazar 230 kV Ckt-2 tripped at 04:15(08/04/2021) from both ends showing E/F at both
ends and was switched on at 04:48(08/04/2021).
t) Cumilla(N)-Shahjibazar 230 kV Ckt-1 tripped at 04:15(08/04/2021) from Cumilla(N) end showing O/C
and was switched on at 04:48(08/04/2021).
u) Mohasthangarh 132/33 kV T-1 transformer's 33 kV Breaker was shutdown at 05:46(08/04/2021) due to
R/H at R-phase Bus isolator.
v) Kodda 132 kV main Bus-2 was shutdown at 07:11(08/04/2021) for D/W.
w) Ashuganj 132 kV Bus-2 was shutdown at 07:36(08/04/2021) for C/M.
x) Kaliakoir-Tangail 132 kV Ckt-2 was shutdown at 07:43(08/04/2021) for D/W.
y) Ashuganj-Kishoreganj 132 kV Ckt-1 was under shutdown from 07:56(08/04/2021) to 10:02(08/04/2021) for C/M.
z) Cumilla(N)-Shahjibazar 230 kV Ckt-2 tripped at 07:45(08/04/2021) from both ends showing Dist. Z1,E/F at
Cumilla(N) end & E/F at Shahjibazar end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4000500 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7150127 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2262363
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 40 | 2420740 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 146 | 4382000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7070050 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1181760
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 5499927 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1073093
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 61 | 415624 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 463896
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 177 | 3663000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1287360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 222 | 1295528 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1154448
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1188360
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2372160
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 925518
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1106978
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Machine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1082760 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 628800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 598100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 685488
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 282 | 2860362 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2911680
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 618000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2055360
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2047680
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 234521
| Dhaka area Total |  |  |  | 5829 | 3446 | 62636183
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 603532
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110835
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 624480
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1774225 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 4808156 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3061632 | Machine problem
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 544091 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1243320
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2101440
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 456336
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 29 | 489120
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 92 | 624000 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29520
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 32 | 411491 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1181575
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2290560
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 98 | 1225691 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1187 | 21580004
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1947542 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 4681000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7288000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7135000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 541008 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 984480
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 384727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 95592 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2093360 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 3869280 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 456408
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 232200
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3250560
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 739000
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 514877
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 17 | 401770 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 663480
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 111 | 1787520
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 870840 | 33 kV feeder fault
| Cumilla Area Total |  |  |  | 3034 | 1747 | 37936644
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 114 | 3128200 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 336816
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 32 | 566400 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14350
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 191 | 4281600 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2128800
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 301570
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 543600
| Mymensingh Area Total |  |  |  | 709 | 490 | 11301336
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1016000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1026600 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3677072
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 332 | 5103000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1139400
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 163000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 791424 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1777920
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 204 | 5047100
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 417000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 360768 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7408500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 364 | 8844000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 194760
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9171500
| Sylhet Area Total |  |  |  | 2377 | 2066 | 46138044
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 830 | 20053091
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2278080 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 4 | 109440
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 200 | 4545216 | Gas shortage.
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 205875 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 428160
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 938880
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1370 | 28558742
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 501216 | High voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 503084
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1515000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2142739
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 600 | 12874400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 890 | 17536439
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 181689
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 92822 | Engine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 109853 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 158 | 3496709 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 3890345 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 350 | 8673100
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 166082 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 490560
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 124452 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 766080
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 637504
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2398944
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 2146560 | Engine problem
| Rajshahi Area Total |  |  |  | 2173 | 1192 | 23174700
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3669700 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2083200
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 39464
| Rangpur Area Total |  |  |  | 605 | 263 | 5792364
| Total |  |  |  | 21219 | 12651 | 254654456
| Eastern Grid Total |  |  |  | 14331 | 8936 | 179592211
| Western Grid Total |  |  |  | 6888 | 3715 | 75062245
| National Grid Total |  |  |  | 21219 | 12651 | 254654456
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-07
(a) ENTIRE EASTERN GRID : |  | 8003 | MW | (b) ENTIRE WESTERN GRID : |  | 3970 | MW
i) Dhaka area |  | 4193 | MW | i) Khulna area |  | 1517 | MW
ii) Chittagong area |  | 1173 | MW | ii) Rajshahi area |  | 1357 | MW
iii) Comilla area |  | 1171 | MW | iii) Barisal area |  | 333 | MW
iv) Mymensingh area |  | 997 | MW | iv) Rangpur area |  | 763 | MW
v) Sylhet area |  | 469 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11973 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 112 | 21:00 | Jamalpur | 154 | 19:30 | Jhenida | 113 | 19:00
Munsiganj | 132 | 20:00 | Sherpur | 118 | 23:00 | Bottail | 124 | 20:00
Sonargaon | 94 | 21:00 | Srimongal | 46 | 19:00 | G.K Project | 57 | 20:00
Shyampur | 196 | 13:00 | Shahjibazar | 123 | 21:00 | Faridpur | 183 | 21:00
Bhulta | 213 | 0:00 | Fenchuganj | 36 | 18:30 | Madaripur | 99 | 22:00
Madanganj | 55 | 19:30 | Kulawara | 40 | 18:30 | Sariatpur | 62 | 20:00
Shitalakhya | 123 | 15:00 | Sylhet | 115 | 19:00 | Gopalganj | 87 | 19:30
Rahim steel | 24 | 20:00 | Chatak | 28 | 19:00 | Bagerhat | 99 | 21:00
Matuail | 60 | 10:00 | Sunamganj | 38 | 19:30 | Mongla | 42 | 15:00
Ghorasal | 82 | 22:00 | Biani Bazar | 55 | 19:00 | Satkhira | 104 | 21:00
Narsingdi | 167 | 21:00 | Comilla (S) | 162 | 19:30 | Gallamari | 33 | 22:00
Haripur (SBU) | 127 | 21:00 | Comilla(N) | 147 | 21:00 | Magura | 52 | 19:00
Sreenagar |  |  | Chandpur | 76 | 21:00 | Norail | 40 | 19:00
Ullon | 78 | 19:30 | Feni | 123 | 20:00 | Chuadanga | 85 | 19:30
Hasnabad | 94 | 21:00 | Chowmuhani | 175 | 20:00 | Borguna | 14 | 21:00
Magbazar | 63 | 15:00 | Ashuganj | 32 | 22:00 | Barisal(N) | 39 | 19:00
Maniknagar | 92 | 12:00 | Daudkandi | 146 | 21:00 | Barisal (S) | 102 | 21:00
Bangabhaban | 20 | 10:00 | B.Baria | 156 | 21:00 | Patuakhali | 96 | 21:00
Narinda | 76 | 16:00 | Ramganj | 88 | 20:00 | Bhandaria | 50 | 20:00
Dhanmondi | 159 | 13:00 | Chaddagram | 42 | 19:00 | Borhan Uddin | 36 | 21:00
Lalbag | 80 | 13:00 | PHP | 5 | 10:00 | Ishurdi | 60 | 19:30
Madartek | 76 | 21:00 | Kochua | 67 | 20:00 | Ruppur Paromanobik | 3 | 17:00
Dhaka University | 32 | 13:00 | Madunaghat | 59 | 19:00 | Natore | 132 | 20:00
Aftabnagar | 9 | 12:00 | Hathazari | 96 | 19:00 | Bogra | 158 | 21:00
Fatullah | 65 | 24:00 | Khulshi | 198 | 16:00 | Noagaon | 124 | 21:00
Nawabganj | 52 | 22:00 | Halishahar | 131 | 14:00 | Rajshahi | 148 | 21:00
Mirpur | 100 | 18:30 | Baraulia | 154 | 23:00 | Rajshahi New | 21 | 22:00
Kalyanpur | 108 | 20:00 | Sikalbaha | 36 | 20:00 | C.Nawabganj | 83 | 20:00
Gulshan | 114 | 13:00 | Dohazari | 78 | 22:00 | Amnura | 60 | 20:00
Uttara | 76 | 14:00 | Cox'sbazar | 98 | 20:00 | Pabna | 115 | 13:00
Uttara New | 27 | 15:00 | Chandraghona | 28 | 19:00 | Shahjadpur | 104 | 21:00
Kamrangirchar | 85 | 12:00 | Kaptai | 5.5 | 18:30 | Serajganj | 116 | 19:30
Savar | 167 | 15:00 | A. Khaer Stl. | 11 | 16:00 | Niyamatpur | 93 | 17:00
Bhasantec | 137 | 13:00 | Bakulia | 98 | 15:00 | Joypurhat | 60 | 21:00
Agargaon | 64 | 12:00 | Julda | 22 | 1:00 | Sherpur(Bogura) | 54 | 19:00
Satmosjid | 79 | 22:00 | TK chemical | 25.7 | 19:00 | Mohastangor | 60 | 20:00
Tongi | 117 | 11:00 | Modern Steel | 0 | #N/A | Bangura | 28 | 21:00
Kabirpur | 247 | 12:00 | Shahmirpur | 26 | 15:00 | Rangpur | 131 | 19:00
Basundhara | 141 | 15:00 | Khagrachhari | 26 | 13:00 | Lalmonirhat | 43 | 20:00
Manikganj | 68 | 19:30 | Matarbari | 38 | 18:30 | Saidpur | 106 | 19:00
Joydevpur | 147 | 19:30 | Baroiar Hat | 36 | 20:00 | Purbasadipur | 102 | 20:00
New Tongi | 105 | 12:00 | Rangamati | 12 | 18:30 | Thakurgaon | 81 | 19:00
Kodda | 270 | 21:00 | Abul Khair 230 | 11 | 18:00 | Palashbari | 104 | 21:00
Dhamrai | 114 | 21:00 | BSRM | 153 | 10:00 | Barapukuria | 55 | 21:00
Rajendrapur | 108 | 19:30 | GPH Ispat | 88 | 22:00 | Panchagar | 46 | 20:00
Valuka | 126 | 16:00 | Goalpara | 23 | 19:00 | Joldhaka | 57 | 18:30
Tangail | 210 | 19:00 | Central s/s | 93 | 20:00 | Kurigram | 56 | 19:00
Mymensing | 195 | 20:00 | Noapara | 55 | 0.83333 | Mithapukur | 28 | 19:00
Kishorganj | 132 | 20:00 | Jessore | 125 | 21:00
Netrokona | 111 | 22:00 | Benapol | 64 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 404 | 22:00 | 398 | 11:00 | Kaliakoir | 384 | 0.16667 | 377 | 0.41667
| Bheramara | 395 | 13:00 | 388 | 20:00 | Bhulta | 378 | 0.041667 | 367 | 0.41667
| Ashuganj(N) | 384 | 1:00 | 376 | 10:00 | Gopalganj | 405 | 0.625 | 383 | 0.8125
| Payra | 409 | 20:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 22:00 | 230 | 1:00 | Hathazari | 228 | 19:00 | 218 | 10:00
| Ishurdi | 235 | 9:00 | 227 | 19:30 | Megnaghat | 229 | 1:00 | 222 | 10:00
| Ashuganj | 232 | 4:00 | 230 | 8:00 | Fenchuganj | 239 | 19:00 | 237 | 7:00
| Serajganj | 230 | 1:00 | 222 | 19:00 | Siddhirganj | 226 | 1:00 | 220 | 8:00
| Baghabari | 231 | 10:00 | 224 | 19:00 | Maniknagar | 224 | 1:00 | 217 | 10:00
| Barapukuria | 236 | 24:00 | 223 | 19:30 | Agargaon | 223 | 4:00 | 214 | 10:00
| Bogra | 225 | 1:00 | 210 | 19:30 | Barisal | 249 | 17:00 | 238 | 15:00
| Rajshahi | 231 | 18:00 | 218 | 19:00 | Bhola 225 MW | 254 | 18:30 | 238 | 19:00
| Khulna South | 234 | 9:00 | 218 | 19:30 | AKSML | 226 | 17:00 | 218 | 10:00
| Rampura | 225 | 23:00 | 220 | 10:00 | BSRM | 229 | 19:00 | 216 | 10:00
| Haripur | 225 | 1:00 | 218 | 10:00 | Bibiyana | 240 | 13:00 | 235 | 21:00
| Hasnabad | 226 | 24:00 | 218 | 9:00 | Bhulta | 228 | 22:00 | 220 | 10:00
| Shyampur | 223 | 20:00 | 220 | 10:00 | Ashuganj (S) | 231 | 1:00 | 228 | 10:00
| Aminbazar | 225 | 1:00 | 215 | 2:00 | Kaliakoir | 223 | 1:00 | 214 | 9:00
| Tongi | 223 | 18:00 | 215 | 9:00 | GPH | 229 | 19:00 | 216 | 10:00
| Comilla (N) | 226 | 14:00 | 220 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:00 | 129 | 10:00 | Madanhat | 137 | 0.77083 | 132 | 0.125
| Munsiganj | 133 | 1:00 | 130 | 9:00 | Hathazari | 135 | 0.79167 | 131 | 0.375
| Sonargaon | 135 | 20:00 | 129 | 9:00 | Khulshi | 134 | 0.91667 | 129 | 0.16667
| Shyampur | 132 | 19:30 | 127 | 10:00 | Halishahar | 136 | 0.54167 | 130 | 0.25
| Bhulta | 127 | 5:00 | 121 | 17:00 | Baraulia | 135 | 0.625 | 128 | 0.45833
| Madanganj | 131 | 18:00 | 128 | 10:00 | Sikalbaha | 139 | 0.75 | 132 | 0.25
| Shitalakhya | 138 | 22:00 | 126 | 10:00 | Dohazari | 133 | 0.54167 | 128 | 0.375
| Rahim steal | 134 | 19:00 | 129 | 10:00 | Cox'sbazar | 128 | 0.66667 | 118 | 0.8125
| Matuail | 134 | 19:00 | 129 | 10:00 | Chandraghona | 136 | 0.79167 | 131 | 0.45833
| Ghorasal | 136 | 23:00 | 132 | 15:00 | Kaptai | 135 | 0.54167 | 132 | 0.29167
| Narsinghdi | 130 | 7:00 | 124 | 19:30 | A. Khaer Stl. | 132 | 0.5 | 128 | 0.041667
| Haripur (SBU) | 133 | 2:00 | 129 | 10:00 | Bakulia | 137 | 0.79167 | 130 | 0.16667
| Sreenagar |  |  |  |  | Julda | 138 | 0.77083 | 132 | 0.20833
| Ullon | 133 | 1:00 | 129 | 9:00 | TK Chemical | 137 | 0.79167 | 131 | 0.16667
| Hasnabad | 135 | 13:00 | 129 | 10:00 | Modern Steel
| Magbazar | 133 | 2:00 | 129 | 10:00 | Shahmirpur | 139 | 0.79167 | 131 | 0.33333
| Maniknagar | 135 | 21:00 | 130 | 10:00 | Khagrachhari | 133 | 0.54167 | 131 | 0.083333
| Bangabhaban | 135 | 21:00 | 130 | 10:00 | Matarbari | 132 | 0.29167 | 120 | 0.041667
| Narinda | 135 | 21:00 | 130 | 10:00 | Baroiar Hat | 134 | 0.54167 | 128 | 0.125
| Dhanmondi | 133 | 1:00 | 129 | 9:00 | Rangamati | 135 | 0.79167 | 131 | 0.083333
| Lalbag | 135 | 23:00 | 126 | 10:00 | Goalpara S/S | 139 | 9:00 | 131 | 19:00
| Madartek | 133 | 1:00 | 128 | 10:00 | Khulna Central S/S | 139 | 18:00 | 131 | 19:00
| Dhaka University | 133 | 1:00 | 129 | 9:00 | Noapara | 136 | 9:00 | 127 | 0.79167
| Aftabnagar | 133 | 1:00 | 128 | 10:00 | Jessore | 129 | 9:00 | 118 | 0.79167
| Fatullah | 133 | 21:00 | 127 | 10:00 | Benapol | 130 | 9:00 | 118 | 0.79167
| Nawabganj | 128 | 1:00 | 124 | 10:00 | Jhenida | 127 | 9:00 | 110 | 0.54167
| Mirpur | 133 | 19:00 | 126 | 10:00 | Bottail | 132 | 0.375 | 122 | 0.8125
| Kalyanpur | 134 | 13:00 | 127 | 10:00 | G.K Project | 139 | 9:00 | 133 | 0.58333
| Gulshan | 133 | 1:00 | 128 | 10:00 | Faridpur | 135 | 0.125 | 127 | 0.79167
| Uttara | 135 | 20:00 | 127 | 10:00 | Madaripur | 139 | 0.041667 | 129 | 0.79167
| Uttara New | 134 | 20:00 | 125 | 10:00 | Shariyatpur S/S | 140 | 0.20833 | 129 | 0.8125
| Kamrangirchar | 135 | 22:00 | 127 | 10:00 | Gopalganj | 143 | 0.16667 | 130 | 0.8125
| Savar | 136 | 20:00 | 127 | 10:00 | Bagerhat | 135 | 8:00 | 126 | 0.29167
| Bhasantec | 129 | 1:00 | 124 | 10:00 | Mongla | 135 | 0.375 | 126 | 0.041667
| Agargaon | 130 | 1:00 | 125 | 10:00 | Satkhira | 139 | 9:00 | 127 | 0.79167
| Satmosjid | 130 | 1:00 | 125 | 10:00 | Gallamari | 139 | 9:00 | 131 | 0.79167
| Tongi | 134 | 13:00 | 130 | 9:00 | Magura | 126 | 9:00 | 110 | 19:00
| Kabirpur | 135 | 1:00 | 129 | 18:30 | Narail | 125 | 0.375 | 108 | 19:00
| Basundhara | 133 | 19:00 | 127 | 10:00 | Chuadanga | 122 | 9:00 | 102 | 0.77083
| Manikganj | 136 | 14:00 | 132 | 2:00 | Borguna | 139 | 0.29167 | 132 | 0.83333
| Joydevpur | 139 | 19:30 | 126 | 9:00 | Barisal(N) | 141 | 4:00 | 133 | 0.625
| New Tongi | 134 | 13:00 | 128 | 9:00 | Barisal (S) | 139 | 18:00 | 131 | 0.625
| Kodda | 137 | 21:00 | 125 | 9:00 | Patuakhali(S) | 137 | 18:00 | 130 | 13:00
| Dhamrai | 134 | 1:00 | 129 | 7:00 | Bhandaria | 137 | 0.41667 | 129 | 0.70833
| Rajendrapur | 137 | 20:00 | 123 | 10:00 | Ishurdi | 136 | 0.75 | 130: | 0.79167
| Valuka | 122 | 10:00 | 110 | 18:30 | Ruppur Paromanobik | 135 | 0.75 | 130 | 0.79167
| Tangail | 130 | 1:00 | 123 | 22:00 | Natore | 135 | 18:00 | 128 | 19:00
| Mymensing | 127 | 10:00 | 115 | 18:30 | Bogra | 134 | 18:00 | 124 | 19:30
| Kishorganj | 126 | 4:00 | 118 | 19:00 | Noagaon | 128 | 18:00 | 116 | 19:00
| Netrokona | 124 | 6:00 | 110 | 19:00 | Rajshahi | 135 | 18:00 | 128 | 19:00
| Jamalpur | 138 | 10:00 | 118 | 6:00 | Rajshahi New | 135 | 18:00 | 127 | 19:00
| Sherpur | 138 | 1:00 | 118 | 6:00 | C.Nawabganj | 134 | 18:00 | 125 | 19:00
| Srimongal | 136 | 1:00 | 133 | 20:00 | Amnura | 133 | 18:00 | 124 | 7:00
| Shahjibazar | 134 | 4:00 | 129 | 19:30 | Pabna | 133 | 18:00 | 127 | 19:00
| Fenchuganj | 136 | 7:00 | 134 | 18:30 | Shahjadpur | 139 | 18:00 | 131 | 19:30
| Khulawara | 136 | 7:00 | 133 | 18:30 | Serajganj | 131 | 4:00 | 125 | 19:00
| Sylhet | 134 | 3:00 | 132 | 19:00 | Niyamatpur | 125 | 18:00 | 110 | 19:30
| Chatak | 134 | 7:00 | 129 | 18:30 | Joypurhat | 126 | 18:00 | 114 | 19:30
| Sunamganj | 134 | 8:30 | 129 | 18:00 | Sherpur(Bogura) | 134 | 1:00 | 124 | 19:00
| Biani Bazar | 134 | 6:00 | 129 | 19:00 | Mohastangor | 132 | 18:00 | 122 | 19:00
| Comilla(s) | 130 | 6:00 | 122 | 18:30 | Bangura | 135 | 18:00 | 130 | 20:00
| Comilla(n) | 137 | 18:30 | 133 | 5:00 | Rangpur | 133 | 1:00 | 116 | 19:00
| Chandpur | 142 | 12:00 | 131 | 5:00 | Lalmonirhat | 134 | 1:00 | 116 | 19:00
| Feni | 136 | 20:00 | 128 | 6:00 | Saidpur | 130 | 1:00 | 110 | 19:30
| Chowmuhani | 136 | 6:00 | 131 | 18:00 | Purbasadipur | 130 | 5:00 | 108 | 19:30
| Ashuganj | 135 | 1:00 | 131 | 21:00 | Thakurgaon | 128 | 4:00 | 108 | 19:00
| Daudkandi | 133 | 18:30 | 129 | 7:00 | Palashbari | 131 | 3:00 | 118 | 19:00
| B.Baria | 130 | 8:00 | 125 | 21:00 | Barapukuria | 135 | 3:00 | 123 | 19:30
| Ramganj | 137 | 12:00 | 128 | 6:00 | Panchagar | 127 | 2:00 | 103 | 19:00
| Chaddagram | 137 | 20:00 | 131 | 7:00 | Joldhaka | 131 | 1:00 | 109 | 19:00
| PHP | 140 | 18:00 | 126 | 3:00 | Kurigram | 131 | 2:00 | 111 | 19:00
| Kochua | 137 | 16:00 | 133 | 7:00 | Mithapukur | 134 | 0.083333 | 118 | 0.8125

## L-Curve
Date | 2021-04-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 200 | 8207 | 3248 | 11455 |  |  |  | QF-LDC-11
0:30 | 160 | 7674.5 | 3138.5 | 10813 | Date: | 2021-04-07
1:00 | 120 | 7142 | 3029 | 10171
1:30 | 86 | 6978 | 2974 | 9952
2:00 | 52 | 6814 | 2919 | 9733
2:30 | 38 | 6662 | 2866.5 | 9528.5 | [5 empty] | Gen. at Eve. Peak | 12651 | 12651 MW (21:00 )
3:00 | 24 | 6510 | 2814 | 9324 | [6 empty] | 21:00
3:30 | 14 | 6464 | 2805.5 | 9269.5 | [5 empty] | Gen. at Day Peak | 10450 | 10450 MW (12:00 )
4:00 | 4 | 6418 | 2797 | 9215 | [6 empty] | 12:00
4:30 | 11 | 6366 | 2750 | 9116 | [5 empty] | Highest Generation | 12651
5:00 | 18 | 6314 | 2703 | 9017 | [6 empty] | 21:00
5:30 | 23 | 6229.5 | 2673.5 | 8903
6:00 | 28 | 6145 | 2644 | 8789
6:30 | 67 | 6182.5 | 2727.5 | 8910
7:00 | 106 | 6220 | 2811 | 9031
7:30 | 66 | 6237.5 | 2889 | 9126.5
8:00 | 26 | 6255 | 2967 | 9222
8:30 | 73 | 6418.5 | 2958.5 | 9377
9:00 | 120 | 6582 | 2950 | 9532
9:30 | 125 | 6756 | 2971 | 9727
10:00 | 130 | 6930 | 2992 | 9922
10:30 | 86 | 7070 | 2960 | 10030
11:00 | 42 | 7210 | 2928 | 10138
11:30 | 46 | 7346.5 | 2947.5 | 10294
12:00 | 50 | 7483 | 2967 | 10450
12:30 | 170 | 7694 | 2959.5 | 10653.5
13:00 | 290 | 7905 | 2952 | 10857
13:30 | 235 | 7828 | 2959.5 | 10787.5
14:00 | 180 | 7751 | 2967 | 10718
14:30 | 153 | 7860 | 3016 | 10876
15:00 | 126 | 7969 | 3065 | 11034
15:30 | 87 | 7943 | 3091.5 | 11034.5
16:00 | 48 | 7917 | 3118 | 11035
16:30 | 48 | 7636.5 | 3090 | 10726.5
17:00 | 48 | 7356 | 3062 | 10418
17:30 | 105 | 7241.5 | 3113.5 | 10355
18:00 | 162 | 7127 | 3165 | 10292
18:30 | 271 | 7885 | 3344.5 | 11229.5
19:00 | 380 | 8643 | 3524 | 12167
19:30 | 380 | 8936 | 3707 | 12643
20:00 | 410 | 8951 | 3698 | 12649 |  |  |  | Executive Engineer
20:30 | 420 | 8943.5 | 3706.5 | 12650 |  |  |  | Network Operation Division
21:00 | 430 | 8936 | 3715 | 12651
21:30 | 405 | 8896.5 | 3676 | 12572.5
22:00 | 380 | 8857 | 3637 | 12494 |  |  |  |  | Page 6 of 7
22:30 | 345 | 8738 | 3547 | 12285
23:00 | 310 | 8619 | 3457 | 12076
23:30 | 255 | 8413 | 3352.5 | 11765.5
24:00 | 200 | 8207 | 3248 | 11455
12651 MW (21:00 )
10450 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-07 |  | Energy | 254654456
[11 empty] | 2021-04-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4583 | 829 | 1775 | 3652 | 709 | 106 | 126 | 0 | 154 | 0
0:30 | 4523.5 | 829 | 1789 | 2882 | 689.5 | 88 | 106.5 | 0 | 145 | 0 | Date: | 2021-04-07
1:00 | 4464 | 829 | 1803 | 2112 | 670 | 70 | 87 | 0 | 136 | 0
1:30 | 4452 | 829.5 | 1814 | 1930.5 | 660 | 70 | 62 | 0 | 134 | 0 | [7 empty] | Total Energy | 254.6545 | Total Energy Gen 254.654 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.654 MKWHr
2:00 | 4440 | 830 | 1825 | 1749 | 650 | 70 | 37 | 0 | 132 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4445 | 829.5 | 1819.5 | 1563 | 650 | 70 | 20.5 | 0 | 131 | 0 | [7 empty] | Energy Requirement | 254.6545
3:00 | 4450 | 829 | 1814 | 1377 | 650 | 70 | 4 | 0 | 130 | 0
3:30 | 4439 | 829.5 | 1820.5 | 1343.5 | 635 | 70 | 4 | 0 | 128 | 0 | [6 empty] | Shortage
4:00 | 4428 | 830 | 1827 | 1310 | 620 | 70 | 4 | 0 | 126 | 0
4:30 | 4435.5 | 830 | 1828 | 1206 | 619.5 | 70 | 4 | 0 | 123 | 0
5:00 | 4443 | 830 | 1829 | 1102 | 619 | 70 | 4 | 0 | 120 | 0
5:30 | 4487.5 | 830 | 1741.5 | 1034 | 619 | 70 | 4 | 0 | 117 | 0
6:00 | 4532 | 830 | 1654 | 966 | 619 | 70 | 4 | 0 | 114 | 0
6:30 | 4535.5 | 830 | 1684 | 1053 | 619 | 70 | 4 | 0 | 109 | 5.5 |  |  |  |  | Coal
7:00 | 4539 | 830 | 1714 | 1140 | 619 | 70 | 4 | 0 | 104 | 11
7:30 | 4460 | 830 | 1686 | 1305 | 619.5 | 70 | 28 | 0 | 106 | 22 |  |  |  | Oil |  |  |  | ,
8:00 | 4381 | 830 | 1658 | 1470 | 620 | 70 | 52 | 0 | 108 | 33
8:30 | 4245 | 830 | 1704 | 1653.5 | 610 | 70 | 103 | 0 | 115 | 46.5
9:00 | 4109 | 830 | 1750 | 1837 | 600 | 70 | 154 | 0 | 122 | 60
9:30 | 4135.5 | 830 | 1775 | 1966.5 | 600 | 70 | 154 | 0 | 121 | 75
10:00 | 4162 | 830 | 1800 | 2096 | 600 | 70 | 154 | 0 | 120 | 90
10:30 | 4155.5 | 830 | 1765 | 2234.5 | 600 | 70 | 154 | 0 | 125 | 96
11:00 | 4149 | 830 | 1730 | 2373 | 600 | 70 | 154 | 0 | 130 | 102
11:30 | 4104.5 | 830 | 1736.5 | 2562 | 600 | 70 | 155 | 0 | 129 | 107
12:00 | 4060 | 830 | 1743 | 2751 | 600 | 70 | 156 | 0 | 128 | 112
12:30 | 4045 | 830 | 1743.5 | 2971 | 600 | 70 | 154.5 | 0 | 131 | 108.5
13:00 | 4030 | 830 | 1744 | 3191 | 600 | 70 | 153 | 0 | 134 | 105
13:30 | 4030 | 830 | 1744 | 3191 | 600 | 70 | 153 | 0 | 134 | 105
14:00 | 4030 | 830 | 1744 | 3191 | 600 | 70 | 153 | 0 | 134 | 105
14:30 | 4033.5 | 829.5 | 1738 | 3270 | 625 | 70 | 165 | 0 | 129 | 85.5
15:00 | 4037 | 829 | 1732 | 3349 | 650 | 70 | 177 | 0 | 124 | 66
15:30 | 4045.5 | 829.5 | 1698.5 | 3365.5 | 655 | 70 | 188 | 0 | 131 | 51.5
16:00 | 4054 | 830 | 1665 | 3382 | 660 | 70 | 199 | 0 | 138 | 37
16:30 | 4102 | 829.5 | 1649 | 3063.5 | 645 | 70 | 203 | 0 | 138 | 26.5
17:00 | 4150 | 829 | 1633 | 2745 | 630 | 70 | 207 | 0 | 138 | 16
17:30 | 4066.5 | 829.5 | 1605.5 | 2767.5 | 615 | 70 | 256 | 0 | 136 | 9
18:00 | 3983 | 830 | 1578 | 2790 | 600 | 70 | 305 | 0 | 134 | 2
18:30 | 4248.5 | 829.5 | 1663 | 3250 | 610 | 70 | 411.5 | 0 | 146 | 1
19:00 | 4514 | 829 | 1748 | 3710 | 620 | 70 | 518 | 0 | 158 | 0
19:30 | 4628 | 830 | 1745 | 3956 | 730 | 70 | 522 | 0 | 162 | 0
20:00 | 4593 | 829 | 1762 | 3983 | 730 | 70 | 522 | 0 | 160 | 0
20:30 | 4612 | 829.5 | 1760 | 3994.5 | 740 | 70 | 484 | 0 | 160 | 0
21:00 | 4631 | 830 | 1758 | 4006 | 750 | 70 | 446 | 0 | 160 | 0
21:30 | 4597.5 | 830 | 1758.5 | 3970.5 | 740 | 86 | 430 | 0 | 160 | 0
22:00 | 4564 | 830 | 1759 | 3935 | 730 | 102 | 414 | 0 | 160 | 0
22:30 | 4595.5 | 830 | 1757 | 3793.5 | 720 | 104 | 327 | 0 | 158 | 0
23:00 | 4627 | 830 | 1755 | 3652 | 710 | 106 | 240 | 0 | 156 | 0
23:30 | 4605 | 829.5 | 1765 | 3652 | 709.5 | 106 | 183 | 0 | 155 | 0 | Max Temp. in Dhaka |  | 36.2° C
24:00 | 4583 | 829 | 1775 | 3652 | 709 | 106 | 126 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 254.654 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.654 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [23 empty] | 32 | 36 | 36 | 86225
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 603532
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 |  |  | 12 | 15 | 17 | 18 | 18 | 16 | 12 |  | 2 | [9 empty] | 110835
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 201 | 202 | 203 | 203 | 205 | 217 | 203 | 203 | 203 | 195 | 195 | 201 | 202 | 203 | 202 | 203 | 203 |  | 203 | 202 | 203 | 202 | 202 | 205 | 208 | 4808156
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 70 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3061632
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 17 | [17 empty] | 85 | 85 | 85 | 85 | 85 | 68 | 41 | 544091
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 0 |  |  |  | 95592
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 170 | 145 | 145 | 120 | 120 | 99 | 100 | 150 | 150 | 150 | 150 | 175 | 175 | 115 | 182 | 110 | 115 | 73 |  | 182 | 182 | 177 | 177 | 177 | 140 | 140 | 3663000
17 | Siddhirganj 335 MW CCPP | [16 empty] | 12 | 12 |  | 217 | 219 | 220 | 222 | 223 | 222 | 223 | 1295528
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 5 | 35 | 144 | 150 | 159 | 227 | 240 | 243 |  | 259 | 284 | 282 | 282 | 284 | 284 | 95 | 2860362
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4000500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7150127
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1947542
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 541008
33 | Ashuganj 225 MW CCPP | 206 | 202 | 206 | 198 | 179 | 198 | 154 | 161 | 171 | 174 | 175 | 171 | 181 | 181 | 184 | 209 | 208 | 210 |  | 212 | 212 | 212 | 212 | 210 | 214 | 215 | 4681000
34 | Ashuganj 450 MW CCPP(South) | 295 | 295 | 295 | 295 | 295 | 325 | 335 | 300 | 300 | 320 | 300 | 300 | 300 | 295 | 275 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 280 | 285 | 7135000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 305 | 330 | 340 | 300 | 300 | 320 | 295 | 260 | 260 | 260 | 270 | 260 | 275 | 275 |  | 275 | 275 | 275 | 275 | 275 | 275 | 275 | 7288000
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 54 | 53 | 54 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 40 | 52 | 52 | 51 | 53 | 51 | 53 | 984480
36 | Chandpur 150 MW CCPP | 86 | 86 | 89 | 88 | 89 | 90 | 90 | 89 | 90 | 89 | 90 | 90 | 88 | 89 | 89 | 87 | 87 | 89 |  | 90 | 90 | 90 | 89 | 82 | 82 | 81 | 2093360
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 264 | 264 | 260 | 259 | 259 | 260 | 264 | 261 | 0 | [10 empty] | 3 | 54 | 32 | 40 | 10 | 61 | 0 | 2420740
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7070050
41 | Haripur 360MW CCPP(HPL) | 190 | 211 | 231 | 231 | 236 | 225 | 213 | 160 | 183 | 187 | 186 | 188 | 188 | 184 | 178 | 173 | 160 | 158 |  | 153 | 148 | 148 | 146 | 135 | 130 | 140 | 4382000
42 | RPCL 210MW CCPP | 160 | 159 | 161 | 161 | 161 | 161 | 159 | 139 | 137 | 137 | 133 | 116 | 111 | 113 | 112 | 122 | 131 | 127 |  | 120 | 119 | 116 | 114 | 113 | 121 | 129 | 3128200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 5 | 16 | 21 | 39 | 44 | 49 | 44 | 41 | 24 | 17 | 6 | 1 | [8 empty] | 301570
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 42 | 43 | 42 | 41 | 42 | 41 | 41 |  | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 1016000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1026600
46 | Shajibazar 330 MW CCPP | 163 | 163 | 164 | 163 | 163 | 161 | 164 | 162 | 164 | 164 | 165 | 164 | 164 | 165 | 164 | 295 | 307 | 282 |  | 308 | 336 | 332 | 332 | 330 | 334 | 333 | 5103000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 35 | 35 | 35 | 34 | 34 | 33 | 33 | 32 | 32 | 31 | 32 | 31 | 31 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791424
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 40 | 40 | 50 | 75 | 78 | 78 | 78 | 77 | 77 | 76 | 75 | 76 | 77 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1777920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 217 | 217 | 217 | 217 | 217 | 217 | 216 | 217 | 217 | 217 | 217 | 208 | 190 | 210 | 210 | 210 | 182 |  | 204 | 204 | 204 | 204 | 204 | 204 | 196 | 5047100
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 417000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 8 | 8 | 8 | 9 | 7 |  | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 194760
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 163000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 22 | 22 | 22 | 50 | 50 | 50 | 50 | 53 | 22 | 47 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1139400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  |  | 8 | 8 | 16 | 16 | 16 | 16 | 360768
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 280 | 280 | 295 | 290 | 290 | 325 | 320 | 310 | 315 | 300 | 310 | 310 | 305 | 320 | 290 | 295 | 290 |  | 310 | 300 | 310 | 300 | 305 | 300 | 310 | 7408500
| Bibiyana South 400 MW | 370 | 370 | 370 | 370 | 400 | 400 | 400 | 385 | 384 | 400 | 385 | 400 | 370 | 379 | 392 | 340 | 340 | 330 |  | 370 | 382 | 378 | 400 | 378 | 400 | 400 | 9171500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1106978
59 | Tangail Palli Power Gen 22 MW | 18 | 18 | 18 | 18 | 20 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 23 | 23 |  | 24 | 24 | 24 | 24 | 24 | 24 | 20 | 543600
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 456336
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 463896
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 14 | 14 | 14 | 14 | 14 | 17 | 336816
63 | Impoprt (Tripura) | 136 | 132 | 130 | 126 | 120 | 114 | 104 | 108 | 122 | 120 | 130 | 128 | 134 | 134 | 124 | 138 | 138 | 134 |  | 158 | 162 | 160 | 160 | 160 | 156 | 154 | 3250560
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 39 | 39 | 39 | 33 | 8 | 3 | 6 | 6 | 9 | 9 | 5 | 3 | 3 | 8 | 8 |  | 14 | 15 | 24 | 29 | 37 | 39 | 40 | 489120
65 | Feni 22MW PP (Doreen) | 20 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 17 | 17 | 17 | 19 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 456408
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 232200
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 739000
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 11 | 11 | 11 | 401770
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 0 | 0 | 0 | 80 | 8 | 20 | 20 | 20 | 20 | 20 | 24 |  | 15 | 26 | 26 | 26 | 26 | 26 | 28 | 482760
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 628800
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598100
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 98 | 97 | 99 | 97 | 95 | 96 | 96 | 96 | 56 | 26 |  | 102 | 102 | 102 | 103 | 103 | 104 | 104 | 2262363
| Feni Lanka Power | [11 empty] | 17 | 17 | 17 | 52 | 52 | 17 | 17 |  | 114 | 114 | 114 | 114 | 114 | 17 |  | 663480
| Chowmuhani 113 MW | 75 | 17 | [6 empty] | 27 | 75 | 75 | 93 | 110 | 112 | 110 | 111 | 75 | 75 |  | 111 | 112 | 111 | 111 | 110 | 105 | 112 | 1787520
| Manikgonj 162MW PP(MPGL) | 17 | [7 empty] | 7 | 17 | 36 | 94 | 162 | 162 | 162 | 162 | 108 | 108 |  | 147 | 162 | 162 | 162 | 162 | 162 | 162 | 2047680
77 | Siddhirganj 100 PP(Dutch Bangla) | [8 empty] | 4 | 28 | 45 | 80 | 95 | 95 | 100 | 100 | 60 | 60 |  | 85 | 100 | 100 | 100 | 100 | 100 | 50 | 1287360
78 | Gazipur 52 MW PP | [8 empty] | 22 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 |  |  | 685488
79 | Kodda 150MW PP | 32 | 16 | [5 empty] | 48 | 150 | 150 | 150 | 150 | 150 | 147 | 147 | 147 | 147 | 147 |  | 148 | 149 | 150 | 150 | 133 | 115 | 82 | 2372160
80 | Jamalpur 95 MW PP(Powerpac) | 49 | 49 | 49 | 16 | 8 | 8 | 8 | 8 | 16 | 24 | 16 | 16 | 16 | 16 | 16 | 24 | 24 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 566400
81 | Jangalia 52 MW PP (Lakdanavi) | [10 empty] | 1 | 18 | 50 | 52 | 52 | 48 | 25 | 25 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 514877
| Gazipur 100 MW PP | [17 empty] | 1 |  | 79 | 105 | 105 | 105 | 105 | 105 | 90 | 618000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 29520
| Jodiac Power | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 51 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1181575
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 5 | 50 | 10 | 30 | 23 | 10 | 10 |  | 45 | 60 | 60 | 61 | 61 |  |  | 415624
86 | ` | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 235 | 235 | 235 | 265 | 265 | 265 | 235 | 230 | 230 | 130 | 130 |  | 230 | 230 | 260 | 260 | 260 | 230 | 230 | 5499927
87 | Meghnaghat 100 MW(IEL) | [8 empty] | 3 | 7 | 24 | 63 | 92 | 91 | 94 | 100 | 55 | 50 |  | 78 | 100 | 100 | 100 | 100 | 100 | 100 | 1181760
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 45 | 17 | 17 | 17 | 17 | 17 | 60 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2055360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 100 | 100 | 100 | 90 | 90 | 30 | 30 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 1243320
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [8 empty] | 2 | 7 | 24 | 32 | 70 | 102 | 102 | 64 | 64 | 64 |  | 85 | 93 | 95 | 102 | 102 | 102 | 102 | 1154448
95 | Patenga 50MW PP (Baraka) | [7 empty] | 3 | 18 | 18 | 19 | 21 | 42 | 47 | 50 | 50 | 24 | 24 |  | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 624480
96 | Chattogram 108 MW PP (ECPV) | [11 empty] | 2 | 38 | 51 | 55 | 40 | 17 | 12 |  | 72 | 98 | 98 | 92 | 60 | 45 | 15 | 624000
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 30 | 15 | 15 | 15 | 15 | 15 | 15 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1073093
100 | Manikganj 55 MW PP (Northern) | 55 | 17 | [5 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 925518
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 130 | 163 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3677072
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1188360
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 183 | 192 | 140 | 140 | 140 | 140 | 175 | 185 | 185 | 185 | 184 | 183 | 183 | 183 | 182 | 182 | 181 | 191 |  | 191 | 191 | 191 | 191 | 192 | 192 | 183 | 4281600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 138 | 96 | 80 | 80 | 67 | 65 | 67 | 124 | 114 | 11 | 108 | 141 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 2911680
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 60 | 30 | 30 | 30 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2101440
116 | Chandpur 200MW (Desh energy) | 180 | 179 | 179 | 173 | 120 | 68 | 68 | 68 | 96 | 155 | 178 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 171 | 180 | 175 | 180 | 180 | 180 | 173 | 3869280
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 366 | 366 | 366 | 392 | 402 | 363 | 365 | 377 | 367 | 367 | 367 | 367 | 373 | 333 | 330 | 307 |  | 365 | 367 | 365 | 364 | 366 | 375 | 382 | 8844000
| Jamalpur 115 MW PP (United) | 75 | 8 |  |  |  |  | 17 | 103 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2128800
| Anwara 300 MW PP (United) | [11 empty] | 16 | 33 | 33 | 66 | 66 | 16 | 16 |  | 48 | 32 | 32 | 32 | 32 | 32 | 16 | 411491
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 60 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2290560
| Anlima Energy Ltd. | 32 | [7 empty] | 2 | 17 | 35 | 57 | 60 | 76 | 75 | 79 | 80 | 80 |  | 94 | 95 | 98 | 98 | 97 | 99 | 97 | 1225691
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 870840
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 13 | 21 | 28 | 32 | 33 | 31 | 27 | 21 | 14 | 5 | 1 | [8 empty] | 234521
120 | Eastern Zone Total | 7142 | 6814 | 6510 | 6418 | 6314 | 6145 | 6220 | 6255 | 6582 | 6930 | 7210 | 7483 | 7905 | 7751 | 7969 | 7917 | 7356 | 7127 | 0 | 8643 | 8936 | 8951 | 8936 | 8857 | 8619 | 8207 | 179592211
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 83 | 66 | 66 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2278080
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 6 | 3 | 3 | 5 | 3 | 3 | 11 |  | 13 | 13 | 13 | 4 | 3 | 3 | 3 | 109440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 35 |  |  |  |  | 17 | 35 | 35 | 35 | 35 | 70 | 70 | 80 | 105 | 105 | 53 | 53 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 938880
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | [26 empty] | 0
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 16 |  | 75 | 80 | 80 | 96 | 96 | 80 | 16 | 501216
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 95 | 95 | 95 | 95 | 71 | 54 | 55 | 55 | 89 | 93 | 94 | 95 | 93 | 95 | 95 | 96 | 97 |  | 98 | 96 | 96 | 96 | 96 | 97 | 95 | 2142739
| Bhola 225 MW CCPP | 64 | 67 | 69 | 68 | 69 | 68 | 68 | 66 | 67 | 67 | 67 | 66 | 61 | 65 | 65 | 55 | 65 | 65 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1515000
140 | Bhola 33 MW PP (Venture) | 25 | 23 | 23 | 22 | 21 | 18 | 15 | 15 | 15 | 15 | 17 | 18 | 20 | 20 | 16 | 13 | 20 | 25 |  | 29 | 29 | 27 | 30 | 26 | 30 | 28 | 503084
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 38 | 100 | 100 | 100 | 60 | 60 |  | 428160
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 16 | 205875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 829 | 830 | 829 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 829 | 829 | 830 | 829 | 830 |  | 829 | 830 | 829 | 830 | 830 | 830 | 829 | 20053091
147 | Bheramara 410 MW CCPP | 185 | 185 | 185 | 195 | 195 | 205 | 205 | 190 | 180 | 170 | 160 | 160 | 150 | 160 | 170 | 180 | 195 | 200 |  | 200 | 200 | 200 | 200 | 200 | 190 | 190 | 4545216
148 | Payra 1320 MW | 520 | 500 | 500 | 470 | 470 | 470 | 470 | 470 | 450 | 450 | 450 | 450 | 450 | 460 | 500 | 510 | 480 | 450 |  | 470 | 580 | 580 | 600 | 580 | 560 | 560 | 12874400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3669700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 5 |  | 43 | 43 | 43 | 43 | 43 |  |  | 181689
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 126 | 127 | 130 | 130 | 130 | 130 | 130 | 130 | 128 | 123 | 124 | 124 | 124 | 124 | 124 | 130 | 140 | 152 |  | 156 | 155 | 155 | 158 | 155 | 155 | 155 | 3496709
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 123 | 124 | 127 | 131 | 131 | 131 | 134 | 137 | 130 | 130 | 130 | 130 | 130 | 140 | 135 | 155 | 165 | 180 |  | 190 | 195 | 190 | 190 | 193 | 193 | 190 | 3890345
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 362 | 362 | 362 | 362 | 364 | 340 | 403 | 419 | 401 | 403 | 342 | 341 | 341 | 340 | 345 | 343 | 344 | 320 |  | 351 | 351 | 350 | 350 | 351 | 351 | 352 | 8673100
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 8 | 27 |  | 27 | 27 | 27 |  |  |  |  | 92822
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 19 | 20 | 20 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 490560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 124452
165 | Amnura 50 MW PP(Sinha) | [20 empty] | 0 | [5 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 6 |  | 31 | 31 | 31 | 31 | 17 | 4 |  | 109853
168 | Santahar 50 MW Peaking PP | [17 empty] | 25 |  | 31 | 34 | 33 | 33 | 33 |  |  | 166082
169 | Natore 52 MW PP (Rajlanka) | 16 | [7 empty] | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 766080
170 | Chapainawabganj 100 MW Peaking PP | [14 empty] | 25 | 49 | 49 | 84 |  | 90 | 90 | 90 | 100 | 100 | 50 |  | 637504
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 50 | 50 | 60 | 92 | 94 | 94 | 94 | 94 | 94 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2398944
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | 70 | 35 | 35 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2146560
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 92 | 34 |  |  |  |  | 58 | 102 | 113 | 107 | 107 | 107 | 107 | 113 | 113 | 113 | 106 | 111 |  | 113 | 113 | 113 | 113 | 113 | 113 | 106 | 2083200
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 2 | 3 | 6 | 6 | 6 | 5 | 3 | 2 | 0 | [8 empty] | 39464
178
178