## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-10 | Saturday
|  |  | Date (day): | 2021-04-10 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14128.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15072 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-09 | 2021-04-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 103 | 104 | 104
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 338 | 345 | 350 | 360 | 0 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 400 | 400 | 50 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 75 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 270 | 0 | 0 | 305 |  | Dust in the gas line
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 155 | 180 | 180
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 214 | 223 | 0 | 0 |  | 335 | Dust in the gas line
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 72 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 133 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 51 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 195 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 52 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 108 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 1914 | 3031 | 3392 | 3622 | 875 | 1210
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 72 | 72 | 70 | 70 | 160 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 82 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 12 | 20 | 15 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 100 | 100
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 35 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 53 | 60 | 60 | 60 |  | 56 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 766 | 1014 | 1618 | 1651 | 520 | 171
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 100 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 206 | 215 | 225 | 225 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 270 | 360 | 360 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 295 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 50 | 50
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Filter change.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 150 | 196 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 156 | 136 | 168
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 17 | 17 |  | 8 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 0 | 0 | 36 | 36
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1332 | 1547 | 1883 | 2065 | 584 | 171
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 133 | 147 | 160 | 160 | 42 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 24 | 32 | 49 | 49 |  | 46 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 16 | 183 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 105 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 53 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 243 | 508 | 614.6 | 563 | 42 | 51
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 35 | 43 | 44 | 44 |  | 26 | Engine problem
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 309 | 334 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 33 | 33 | 33 |  | 33 | GT-9 Under maint.
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 75 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 20/04/2021
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 120 | 100 | 120 |  | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 20 | 20
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 235 | 295 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 366 | 342 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 9 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 360 | 340 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1603 | 1842 | 2037 | 2060 | 0 | 448
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 643 | 832 | 654 | 848
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 49 | 90 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 295 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 32 | 32 |  | 8 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 92 | 105 | 105
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1092 | 1442 | 1520 | 2000 | 0 | 107
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 33 | 25 | 26 |  | 7 | Engine problem
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 67 | 70 | 70 |  | 124 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 39 | 96 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 570 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 73 | 0 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 618 | 862 | 1072 | 1073 | 0 | 131
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 65 | 65
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 40 | 40
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 144 | 144 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 199 | 180 | 200 | 20 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 187 | 163 | 200 | 200 | 20 |  | Gas shortage
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 376 | 364 | 400 | 400
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 34
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 99 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 54 | 94 | 94 | 94 |  | 19 | Engine problem
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 856 | 1141 | 1711 | 1765 | 240 | 19
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 5 | 0 | 0 |  | 20 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 50 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 205 | 268 | 281 | 273 | 124 | 200
|  | Total |  |  |  |  | 21967 | 21219 | 8629 | 11655 | 14128.6 | 15072 | 2385 | 2508
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8179.5961 | 11048 | 13392.7733 | 14287.0404
| A. |  | 2021-04-09 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 11655 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7301 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11655 | MW
| 3 | Day peak Generation : |  |  | 8629 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11048 | MW
| 4 | Evening peak Generation : |  |  | 11655 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 222.2813 | MKWHr | By Solar | 0.61765 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 139.6044 | MKWHr |  | By Oil: | 42.973 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.7746 | MKWHr |  | By Hydro: | 2.0585 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2385 | MW | Dhaka | 3717 | 3717 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2508 | MW | Chittagong | 1148 | 1148 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4893 | MW | Khulna | 1505 | 1505 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1112.71 | MMCFD |  |  | Rajshahi | 1087 | 1087 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146638206.854 | ii) Oil : | Taka | 296079281.88 | Comilla | 1205 | 1205 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 73045941 | Total | Taka | 515763429.734 | Mymensingh | 878 | 878 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.8965 | MKWHr. | Sylhet | 445 | 445 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -128 | MW (E to W) at | 21:00 | hrs | Barisal | 347 | 347 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -312 | MW at | 19:00 | hrs | Rangpur | 716 | 716 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.7° C |  |  | Total | 11048 | 11048 |  | 0
| B. |  | 2021-04-10 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 36.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15072 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
| 4 | Reserve(Generation end) |  |  |  | 2272 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 244.1185 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8974 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.1571 | MKWHr. | ii) HVDC Flow at Peak Time |  | 832 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.096 | MKWHr. | iii) Maximum HVDC Flow : |  | 833 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.58 |  | (b) Today: | 82.1 |  | (c) Rule Curve: |  | 86.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 261 |  | 0 | 320 | 230 | 30 | 0 | 55 | 220 | 0 | 120 | 40 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 29 | 33 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 34 | 90 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 260 | 265 | 181 | 8 | 82 | 26 | 53 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 148 | 143 | 32 | 17 | 0 | 43 | 43 | 53 | 0 | 110 | 335 | 34 | 78 | 0 | 0 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 95 | 0 | 0 | 45 | 0 | 149 | 0 | 100 | 169 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 35 | 0 | 0 | 37 | 0 |  | 832 | 0 | 190 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 16 | 68 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 96 | 0 | 130 | 0 | 302 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 0 | 0 |  | 6721 | 2736 | 9457 | 3905 | 832 | 1754 | 1934 | 710 | 105 | 69 | 148 | 0 | 0 | 82.68
2:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 280 |  | 0 | 320 | 230 | 0 | 0 | 55 | 221 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 0 | 25 | 29 | 0 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 34 | 90 | 0 | 0 | 20 | 32 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 81 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 144 | 110 | 8 | 0 | 0 | 43 | 43 | 53 | 0 | 110 | 305 | 35 | 75 | 0 | 0 | 18 | 0 | 9 | 275 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 100 | 171 | 0 | 312 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 8 | 100 | 350 | 104 | 0 | 0 | 0 | 0 | 30 | 0 |  | 832 | 0 | 220 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 67 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 302 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 6004 | 2655 | 8659 | 3823 | 832 | 1711 | 1327 | 680 | 105 | 37 | 144 | 0 | 0 | 82.66
3:00 | 0 | 0 | 0 | 0 | 280 | 12 | 0 | 0 | 291 |  | 0 | 320 | 230 | 0 | 0 | 15 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 7 | 0 | 0 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 202 | 0 | 130 | 0 |  | 0 | 0 | 0 | 90 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 260 | 265 | 180 | 8 | 81 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 140 | 113 | 0 | 0 | 0 | 43 | 43 | 11 | 0 | 110 | 310 | 35 | 10 | 0 | 0 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76 | 0 | 100 | 126 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 340 | 53 | 0 | 0 | 0 | 0 | 17 | 0 |  | 832 | 0 | 240 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 85 | 0 | 130 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 |  | 5304 | 2463 | 7767 | 3624 | 832 | 1500 | 956 | 610 | 105 | 0 | 140 | 0 | 0 | 82.64
4:00 | 0 | 0 | 0 | 0 | 250 | 12 | 0 | 0 | 291 |  | 0 | 320 | 230 | 0 | 0 | 15 | 150 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 7 | 0 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 195 | 0 | 130 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 39 | 80 | 0 | 0 | 265 | 270 | 186 | 8 | 81 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 13 | 134 | 113 | 0 | 0 | 0 | 35 | 43 | 11 | 0 | 130 | 307 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 100 | 125 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 100 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 833 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 86 | 0 | 130 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 |  | 5151 | 2402 | 7553 | 3630 | 833 | 1535 | 746 | 570 | 105 | 0 | 134 | 0 | 0 | 82.62
5:00 | 0 | 0 | 0 | 0 | 250 | 12 | 0 | 0 | 291 |  | 0 | 320 | 230 | 0 | 0 | 15 | 150 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 18 | 0 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 195 | 0 | 130 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 280 | 295 | 181 | 8 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 33 | 15 | 126 | 112 | 0 | 0 | 0 | 35 | 43 | 11 | 0 | 110 | 308 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 100 | 127 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 0 | 0 | 100 | 340 | 0 | 0 | 0 | 36 | 0 | 0 | 0 |  | 832 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 86 | 0 | 130 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 0 | 0 | 0 |  | 5161 | 2450 | 7611 | 3656 | 832 | 1564 | 758 | 570 | 105 | 0 | 126 | 0 | 0 | 82.6
6:00 | 0 | 0 | 0 | 0 | 250 | 12 | 0 | 0 | 251 |  | 0 | 320 | 230 | 0 | 0 | 45 | 150 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 18 | 13 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 194 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 310 | 295 | 180 | 8 | 79 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 116 | 113 | 0 | 0 | 0 | 35 | 43 | 11 | 0 | 110 | 309 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 100 | 150 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 0 | 100 | 300 | 0 | 1 | 0 | 45 | 0 | 0 | 0 |  | 833 | 0 | 240 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 53 | 0 | 130 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5103 | 2383 | 7486 | 3649 | 833 | 1413 | 819 | 550 | 105 | 0 | 116 | 1 | 0 | 82.58
7:00 | 0 | 0 | 0 | 0 | 230 | 12 | 0 | 0 | 250 |  | 0 | 320 | 230 | 0 | 0 | 55 | 150 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 18 | 25 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 196 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 30 | 100 | 0 | 0 | 270 | 270 | 180 | 8 | 80 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 18 | 102 | 113 | 3 | 0 | 0 | 35 | 43 | 11 | 0 | 110 | 308 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 86 | 150 | 0 | 331 | 0 | 0 | 0 | 1 | 0 | 36 | 0 | 0 | 0 | 100 | 320 | 0 | 9 | 0 | 17 | 0 | 0 | 5 |  | 833 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 36 | 0 | 130 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 380 | 0 | 0 | 0 |  | 4988 | 2313 | 7301 | 3597 | 833 | 1397 | 718 | 530 | 105 | 0 | 102 | 19 | 0 | 82.56
8:00 | 0 | 0 | 0 | 0 | 230 | 12 | 0 | 0 | 253 |  | 0 | 320 | 230 | 0 | 0 | 15 | 150 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 27 | 25 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 0 | 201 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 28 | 100 | 0 | 0 | 270 | 270 | 181 | 8 | 79 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 33 | 18 | 100 | 111 | 8 | 0 | 0 | 35 | 43 | 11 | 0 | 110 | 308 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 100 | 150 | 0 | 332 | 0 | 0 | 0 | 1 | 0 | 36 | 0 | 0 | 0 | 100 | 320 | 0 | 22 | 0 | 17 | 0 | 0 | 9 |  | 833 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 34 | 0 | 147 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 380 | 0 | 0 | 0 |  | 4978 | 2381 | 7359 | 3674 | 833 | 1393 | 689 | 530 | 105 | 0 | 100 | 35 | 0 | 82.54
9:00 | 0 | 0 | 0 | 0 | 230 | 12 | 0 | 0 | 272 |  | 0 | 320 | 230 | 0 | 0 | 15 | 150 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 25 | 25 | 0 | 0 | 35 | 70 | 0 | 0 | 16 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 28 | 100 | 0 | 0 | 275 | 270 | 181 | 8 | 82 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 102 | 133 | 32 | 17 | 0 | 38 | 43 | 11 | 0 | 110 | 308 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 12 | 100 | 150 | 0 | 342 | 0 | 0 | 0 | 2 | 0 | 36 | 0 | 0 | 0 | 100 | 320 | 0 | 34 | 0 | 17 | 0 | 0 | 0 |  | 832 | 0 | 240 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 34 | 0 | 156 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 380 | 0 | 0 | 0 |  | 5133 | 2434 | 7567 | 3729 | 832 | 1483 | 736 | 530 | 105 | 0 | 102 | 50 | 0 | 82.52
10:00 | 0 | 0 | 0 | 0 | 230 | 12 | 0 | 0 | 341 |  | 0 | 320 | 230 | 0 | 0 | 15 | 218 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 36 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 100 | 0 | 0 | 285 | 280 | 189 | 8 | 86 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 106 | 157 | 32 | 17 | 2 | 35 | 43 | 11 | 0 | 110 | 310 | 20 | 10 | 0 | 0 | 18 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 16 | 100 | 150 | 0 | 365 | 0 | 0 | 0 | 4 | 0 | 36 | 0 | 0 | 0 | 90 | 340 | 0 | 21 | 0 | 17 | 0 | 0 | 0 |  | 643 | 0 | 375 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 35 | 0 | 161 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 380 | 0 | 0 | 0 |  | 5462 | 2390 | 7852 | 4116 | 643 | 1562 | 744 | 530 | 106 | 0 | 106 | 45 | 0 | 82.5
11:00 | 0 | 0 | 0 | 0 | 300 | 65 | 0 | 0 | 339 |  | 0 | 320 | 270 | 0 | 0 | 15 | 218 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 37 | 70 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 12 | 100 | 0 | 0 | 285 | 275 | 190 | 8 | 0 | 26 | 5 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 106 | 157 | 24 | 17 | 2 | 35 | 43 | 11 | 0 | 110 | 309 | 20 | 78 | 0 | 0 | 18 | 0 | 0 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 18 | 100 | 150 | 0 | 365 | 0 | 0 | 0 | 4 | 0 | 36 | 0 | 0 | 0 | 90 | 346 | 0 | 24 | 0 | 43 | 0 | 0 | 0 |  | 643 | 0 | 400 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 35 | 0 | 172 | 0 | 372 | 0 | 0 | 16 | 0 | 45 | 0 | 2 | 0 | 420 | 75 | 0 | 0 |  | 5600 | 2633 | 8233 | 4203 | 643 | 1654 | 900 | 570 | 107 | 0 | 106 | 50 | 0 | 82.48
12:00 | 0 | 0 | 0 | 0 | 300 | 95 | 0 | 0 | 338 |  | 0 | 320 | 270 | 0 | 0 | 15 | 214 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 37 | 35 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 100 | 0 | 0 | 315 | 310 | 206 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 110 | 133 | 24 | 17 | 0 | 35 | 43 | 11 | 0 | 110 | 309 | 20 | 78 | 0 | 0 | 18 | 0 | 0 | 235 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 19 | 100 | 150 | 0 | 366 | 0 | 0 | 0 | 5 | 0 | 36 | 0 | 0 | 0 | 90 | 360 | 0 | 53 | 0 | 53 | 0 | 0 | 31 |  | 643 | 0 | 400 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 39 | 0 | 187 | 0 | 376 | 0 | 0 | 54 | 0 | 50 | 0 | 5 | 35 | 420 | 73 | 0 | 0 |  | 5858 | 2771 | 8629 | 4335 | 643 | 1765 | 1021 | 570 | 72 | 0 | 110 | 113 | 0 | 82.46
13:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 0 | 337 |  | 0 | 320 | 270 | 0 | 0 | 28 | 214 | 0 | 180 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 30 | 10 | 25 | 22 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 4 | 0 | 0 | 14 | 0 | 4 | 20 | 23 | 100 | 0 | 0 | 305 | 275 | 186 | 8 | 0 | 26 | 45 | 0 | 0 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 132 | 133 | 24 | 14 | 2 | 35 | 43 | 11 | 0 | 110 | 309 | 20 | 78 | 0 | 0 | 18 | 0 | 7 | 320 | 16 | 2 | 0 | 0 | 0 | 0 | 77 | 0 | 0 | 17 | 100 | 150 | 0 | 366 | 0 | 0 | 0 | 4 | 32 | 36 | 0 | 0 | 0 | 100 | 360 | 73 | 45 | 0 | 60 | 0 | 14 | 26 |  | 643 | 0 | 365 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 93 | 0 | 201 | 0 | 392 | 0 | 0 | 92 | 0 | 98 | 0 | 5 | 100 | 420 | 68 | 0 | 0 |  | 6242 | 3043 | 9285 | 4258 | 643 | 1954 | 1559 | 570 | 70 | 0 | 132 | 99 | 9285 | 82.44
14:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 0 | 337 |  | 0 | 320 | 270 | 0 | 0 | 42 | 214 | 0 | 130 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 13 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 204 | 0 | 120 | 0 |  | 10 | 0 | 0 | 20 | 0 | 47 | 20 | 16 | 135 | 0 | 0 | 305 | 270 | 210 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 18 | 11 | 33 | 17 | 128 | 128 | 24 | 14 | 2 | 35 | 43 | 11 | 0 | 110 | 312 | 20 | 77 | 0 | 0 | 18 | 0 | 7 | 280 | 16 | 2 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 15 | 70 | 150 | 0 | 366 | 0 | 0 | 0 | 4 | 16 | 36 | 0 | 0 | 0 | 100 | 360 | 104 | 43 | 0 | 60 | 0 | 18 | 27 |  | 643 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 204 | 0 | 73 | 0 | 177 | 0 | 404 | 0 | 0 | 94 | 0 | 70 | 0 | 4 | 113 | 420 | 67 | 0 | 0 |  | 6418 | 2962 | 9380 | 4224 | 643 | 1888 | 1746 | 570 | 70 | 16 | 128 | 95 | 0 | 82.42
15:00 | 0 | 0 | 0 | 0 | 300 | 101 | 0 | 0 | 320 |  | 0 | 337 | 270 | 0 | 0 | 42 | 209 | 0 | 180 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 15 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 204 | 0 | 120 | 0 |  | 23 | 0 | 0 | 50 | 0 | 50 | 20 | 16 | 100 | 0 | 0 | 345 | 305 | 193 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 33 | 17 | 124 | 131 | 24 | 14 | 1 | 35 | 43 | 48 | 0 | 130 | 310 | 31 | 78 | 0 | 0 | 18 | 0 | 7 | 320 | 16 | 2 | 0 | 0 | 0 | 0 | 193 | 0 | 18 | 12 | 100 | 139 | 0 | 366 | 0 | 0 | 0 | 3 | 16 | 36 | 0 | 0 | 25 | 100 | 360 | 87 | 29 | 0 | 60 | 0 | 18 | 18 |  | 643 | 0 | 310 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 206 | 0 | 74 | 0 | 182 | 0 | 404 | 17 | 0 | 94 | 0 | 70 | 0 | 3 | 113 | 430 | 58 | 0 | 0 |  | 6666 | 2993 | 9659 | 4281 | 643 | 1977 | 1902 | 580 | 70 | 16 | 124 | 66 | 0 | 82.4
16:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 0 | 337 |  | 0 | 320 | 270 | 0 | 0 | 40 | 211 | 0 | 180 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 15 | 25 | 25 | 0 | 0 | 30 | 35 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 50 | 0 | 50 | 20 | 16 | 100 | 0 | 0 | 300 | 260 | 210 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 33 | 17 | 115 | 153 | 24 | 14 | 1 | 35 | 43 | 50 | 0 | 110 | 311 | 31 | 75 | 0 | 0 | 18 | 0 | 9 | 320 | 16 | 2 | 0 | 0 | 0 | 0 | 193 | 0 | 46 | 7 | 90 | 136 | 0 | 366 | 0 | 0 | 0 | 2 | 16 | 36 | 0 | 0 | 65 | 90 | 360 | 87 | 25 | 0 | 60 | 0 | 18 | 10 |  | 643 | 0 | 285 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 74 | 0 | 185 | 0 | 380 | 17 | 0 | 94 | 0 | 70 | 0 | 2 | 113 | 440 | 58 | 0 | 0 |  | 6609 | 2949 | 9558 | 4207 | 643 | 1930 | 1945 | 590 | 65 | 16 | 115 | 47 | 0 | 82.38
17:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 297 |  | 0 | 320 | 270 | 0 | 0 | 40 | 210 | 0 | 65 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 8 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 50 | 0 | 50 | 20 | 16 | 100 | 0 | 0 | 300 | 270 | 212 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 20 | 11 | 33 | 17 | 118 | 154 | 24 | 14 | 0 | 35 | 43 | 50 | 0 | 110 | 308 | 31 | 78 | 0 | 0 | 18 | 0 | 9 | 285 | 16 | 2 | 0 | 0 | 0 | 0 | 192 | 0 | 48 | 2 | 90 | 152 | 0 | 366 | 0 | 0 | 0 | 1 | 16 | 36 | 0 | 0 | 65 | 100 | 360 | 87 | 15 | 0 | 60 | 0 | 18 | 2 |  | 643 | 0 | 270 | 0 | 66 | 0 | 0 | 0 | 0 | 2 | 0 | 66 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 196 | 0 | 74 | 0 | 185 | 0 | 382 | 17 | 0 | 50 | 0 | 50 | 0 | 1 | 113 | 440 | 58 | 0 | 0 |  | 6446 | 2870 | 9316 | 4087 | 643 | 1861 | 1908 | 590 | 70 | 18 | 118 | 21 | 0 | 82.36
18:00 | 0 | 0 | 0 | 0 | 280 | 99 | 0 | 0 | 257 |  | 0 | 320 | 270 | 1 | 0 | 40 | 170 | 0 | 70 | 24 | 5 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 13 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 24 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 20 | 0 | 50 | 20 | 20 | 100 | 0 | 0 | 285 | 285 | 192 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 2 | 20 | 11 | 33 | 17 | 110 | 148 | 24 | 14 | 0 | 35 | 43 | 50 | 0 | 110 | 310 | 32 | 78 | 0 | 0 | 18 | 0 | 9 | 280 | 16 | 2 | 0 | 7 | 0 | 0 | 191 | 0 | 46 | 0 | 90 | 180 | 0 | 329 | 4 | 7 | 0 | 0 | 16 | 35 | 0 | 0 | 65 | 100 | 360 | 53 | 0 | 2 | 60 | 0 | 18 | 1 |  | 642 | 0 | 270 | 0 | 66 | 0 | 0 | 0 | 0 | 9 | 0 | 66 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 24 | 30 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 54 | 0 | 183 | 0 | 346 | 17 | 0 | 50 | 0 | 50 | 0 | 0 | 50 | 440 | 0 | 0 | 0 |  | 6230 | 2688 | 8918 | 3942 | 642 | 1710 | 1795 | 590 | 70 | 58 | 110 | 1 | 0 | 82.34
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #REF!
19:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 341 |  | 0 | 320 | 270 | 35 | 0 | 40 | 219 | 0 | 185 | 50 | 40 | 100 | 7 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 13 | 25 | 25 | 8 | 0 | 36 | 35 | 0 | 0 | 25 | 205 | 0 | 120 | 0 |  | 24 | 0 | 83 | 100 | 12 | 50 | 20 | 20 | 100 | 0 | 0 | 280 | 300 | 212 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 27 | 22 | 11 | 33 | 19 | 150 | 148 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 130 | 309 | 32 | 78 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 136 | 0 | 0 | 191 | 0 | 83 | 0 | 100 | 196 | 0 | 342 | 37 | 71 | 0 | 0 | 16 | 35 | 0 | 0 | 65 | 100 | 370 | 92 | 0 | 109 | 60 | 0 | 28 | 0 |  | 643 | 0 | 285 | 0 | 70 | 0 | 0 | 0 | 0 | 6 | 33 | 67 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 24 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 8 | 0 | 0 | 153 | 0 | 96 | 10 | 175 | 0 | 396 | 17 | 0 | 85 | 0 | 112 | 0 | 0 | 90 | 500 | 0 | 0 | 0 |  | 7504 | 3174 | 10678 | 4202 | 643 | 1933 | 2708 | 650 | 71 | 321 | 150 | 0 | 0 | 82.28
19:30 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 347 |  | 0 | 320 | 270 | 100 | 0 | 40 | 223 | 0 | 175 | 100 | 85 | 100 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 8 | 0 | 30 | 35 | 0 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 83 | 100 | 12 | 50 | 20 | 20 | 100 | 0 | 0 | 270 | 300 | 213 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 150 | 147 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 130 | 306 | 32 | 78 | 0 | 0 | 18 | 0 | 9 | 263 | 16 | 11 | 0 | 175 | 0 | 0 | 180 | 0 | 90 | 0 | 100 | 196 | 0 | 366 | 115 | 105 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 162 | 60 | 0 | 37 | 0 |  | 688 | 0 | 285 | 0 | 73 | 0 | 0 | 0 | 0 | 6 | 33 | 67 | 34 | 80 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 96 | 100 | 170 | 0 | 360 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7911 | 3529 | 11440 | 4228 | 688 | 1867 | 3401 | 720 | 65 | 321 | 150 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 0 | 345 |  | 0 | 320 | 270 | 79 | 0 | 40 | 222 | 0 | 155 | 100 | 72 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 35 | 35 | 0 | 0 | 25 | 202 | 0 | 120 | 0 |  | 24 | 0 | 83 | 100 | 5 | 50 | 20 | 20 | 100 | 0 | 0 | 270 | 295 | 214 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 147 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 333 | 20 | 78 | 0 | 0 | 18 | 0 | 9 | 275 | 16 | 11 | 0 | 192 | 0 | 0 | 173 | 0 | 146 | 0 | 100 | 196 | 0 | 366 | 115 | 52 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 108 | 60 | 0 | 0 | 0 |  | 832 | 0 | 290 | 0 | 76 | 0 | 0 | 0 | 0 | 2 | 33 | 67 | 34 | 80 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 96 | 90 | 168 | 0 | 387 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7759 | 3692 | 11451 | 4220 | 832 | 1881 | 3257 | 720 | 70 | 317 | 154 | 0 | 0 | 82.3
21:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 345 |  | 0 | 320 | 270 | 75 | 0 | 40 | 223 | 0 | 155 | 100 | 72 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 37 | 35 | 0 | 0 | 25 | 203 | 0 | 130 | 0 |  | 24 | 0 | 83 | 100 | 0 | 50 | 20 | 20 | 100 | 0 | 0 | 270 | 295 | 215 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 147 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 334 | 33 | 78 | 0 | 120 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 195 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 196 | 0 | 342 | 105 | 52 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 108 | 60 | 0 | 0 | 0 |  | 832 | 0 | 295 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 33 | 67 | 33 | 96 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 0 | 0 | 199 | 0 | 96 | 100 | 163 | 0 | 364 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7942 | 3713 | 11655 | 4345 | 832 | 1883 | 3294 | 720 | 72 | 353 | 156 | 0 | 0 | 82.28
22:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 346 |  | 0 | 320 | 270 | 40 | 0 | 40 | 223 | 0 | 150 | 60 | 32 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 0 | 25 | 0 | 0 | 38 | 35 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 83 | 100 | 0 | 50 | 20 | 40 | 100 | 0 | 0 | 270 | 295 | 215 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 160 | 152 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 334 | 33 | 78 | 0 | 150 | 18 | 0 | 9 | 280 | 0 | 11 | 0 | 95 | 0 | 0 | 192 | 0 | 118 | 0 | 100 | 199 | 0 | 343 | 105 | 17 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 35 | 60 | 0 | 0 | 0 |  | 833 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 66 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 0 | 0 | 200 | 0 | 96 | 100 | 165 | 0 | 370 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7559 | 3754 | 11313 | 4351 | 833 | 1893 | 2955 | 720 | 73 | 328 | 160 | 0 | 0 | 82.26
23:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 343 |  | 0 | 320 | 270 | 32 | 0 | 40 | 223 | 0 | 155 | 60 | 32 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 0 | 25 | 0 | 0 | 37 | 35 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 68 | 92 | 0 | 50 | 20 | 41 | 100 | 0 | 0 | 270 | 295 | 216 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 158 | 159 | 32 | 17 | 0 | 44 | 43 | 50 | 0 | 110 | 331 | 33 | 78 | 0 | 150 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 193 | 0 | 85 | 0 | 100 | 194 | 0 | 343 | 105 | 17 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 354 | 104 | 0 | 35 | 57 | 0 | 0 | 0 |  | 833 | 0 | 325 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 66 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 0 | 0 | 204 | 0 | 97 | 100 | 170 | 0 | 372 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7494 | 3655 | 11149 | 4416 | 833 | 1893 | 2869 | 720 | 72 | 188 | 158 | 0 | 0 | 82.24
24:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 347 |  | 0 | 320 | 270 | 22 | 0 | 55 | 224 | 0 | 155 | 60 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 33 | 35 | 0 | 0 | 25 | 202 | 0 | 130 | 0 |  | 24 | 0 | 68 | 92 | 0 | 50 | 20 | 41 | 100 | 0 | 0 | 270 | 295 | 218 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 152 | 159 | 32 | 17 | 0 | 44 | 43 | 50 | 0 | 163 | 312 | 33 | 78 | 0 | 140 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 170 | 0 | 58 | 0 | 100 | 197 | 0 | 344 | 85 | 17 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 17 | 57 | 0 | 0 | 0 |  | 832 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 58 | 32 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 206 | 0 | 96 | 50 | 172 | 0 | 380 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 7336 | 3617 | 10953 | 4410 | 832 | 1956 | 2714 | 721 | 68 | 100 | 152 | 0 | 0 | 82.22
KWH | 0 | 0 | 0 | 0 | 6739500 | 1642409 | 0 | 0 | 7418000 |  | 0 | 7068500 | 6116829 | 343680 | 0 | 862845 | 4831675 | 0 | 3060000 | 779520 | 339408 | 742080 | 14219 | 0 | 0 | 0 | 1073520 | 744442 | 694550 | 258408 | 600000 | 467820 | 489800 | 607100 | 12000 | 0 | 814516 | 1244000 | 0 | 0 | 440672 | 4853511 | 0 | 3047590 | 0 |  | 287760 | 0 | 534103 | 1128840 | 18240 | 571200 | 467136 | 686400 | 2461614 | 0 | 0 | 7180000 | 6895000 | 4734000 | 217454 | 844020 | 432864 | 607200 | 0 | 0 | 0 | 0 | 264629 | 468900 | 211500 | 818600 | 450330 | 3096000 | 3162720 | 494400 | 218592 | 9550 | 897000 | 1033440 | 742200 | 0 | 2999618 | 7144000 | 643584 | 1344960 | 0 | 472820 | 421000 | 0 | 108180 | 6997500 | 199200 | 82512 | 0 | 870654 | 0 | 0 | 2277600 | 0 | 1245460 | 124065 | 2315520 | 3870240 | 0 | 8257000 | 555600 | 308400 | 0 | 31080 | 213273 | 936150 | 0 | 0 | 1153320 | 2363520 | 8324500 | 1449600 | 300790 | 612000 | 973527 | 0 | 220680 | 117559 |  | 18157091 | 0 | 7125408 | 0 | 1344960 | 0 | 0 | 0 | 8640 | 17408 | 214500 | 1573000 | 589768 | 689184 | 0 | 0 | 0 | 0 | 0 | 434256 | 0 | 0 | 0 | 462720 | 145294 | 324000 | 0 | 140652 | 0 | 0 | 3684900 | 0 | 20000 | 0 | 0 | 4323309 | 0 | 1756523 | 506880 | 4197136 | 0 | 8511700 | 794880 | 0 | 1138080 | 0 | 1148160 | 0 | 34603 | 1219584 | 12089700 | 454773 | 0 | 0 |  | 151174198 | 71107109 | 222281307 | 98135241 | 18157091 | 41469185 | 41071246 | 15774600 | 2058516 | 1901781 | 3096000 | 617647 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7480845 | 2167979.88 | 0 | 0 | 7640540 |  | 0 | 7704665 | 6789680.19 | 2608531.2 | 0 | 7299668.7 | 5024942 | 0 | 5293800 | 5869785.6 | 3095400.96 | 7302067.2 | 131099.18 | 0 | 0 | 0 | 7836696 | 5754536.66 | 6848263 | 193806 | 450000 | 0 | 0 | 0 | 116040 | 0 | 219919.32 | 335880 | 0 | 0 | 4093842.88 | 5290326.99 | 0 | 5180903 | 0 |  | 0 | 0 | 5180799.1 | 10780422 | 158688 | 4523904 | 588591.36 | 2038608 | 3643188.72 | 0 | 0 | 5313200 | 6895000 | 4355280 | 280515.66 | 970623 | 489136.32 | 850080 | 0 | 0 | 0 | 0 | 2527206.95 | 595503 | 158625 | 1432550 | 337747.5 | 23220000 | 3352483.2 | 4489152 | 277611.84 | 152227 | 1471080 | 1653504 | 1321116 | 0 | 3419564.52 | 7429760 | 1267860.48 | 2568873.6 | 0 | 817978.6 | 921990 | 0 | 220687.2 | 7067475 | 149400 | 62709.12 | 0 | 6582144.24 | 0 | 0 | 11843520 | 0 | 12255326.4 | 1450319.85 | 18871488 | 41992104 | 0 | 7679010 | 5067072 | 2914380 | 0 | 0 | 1612343.88 | 8153866.5 | 0 | 0 | 9883952.4 | 15741043.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104584844.16 | 0 | 7481678.4 | 0 | 10571385.6 | 0 | 0 | 0 | 90633.6 | 182435.84 | 2235090 | 1777490 | 914140.4 | 6726435.84 | 0 | 0 | 0 | 0 | 0 | 3843165.6 | 0 | 0 | 0 | 4483756.8 | 1409351.8 | 622080 | 0 | 106473.564 | 0 | 0 | 19972158 | 0 | 570600 | 0 | 0 | 5706767.88 | 0 | 2634784.5 | 8622028.8 | 4910649.12 | 0 | 8426583 | 8298547.2 | 0 | 10800379.2 | 0 | 8909721.6 | 0 | 382363.15 | 9012725.76 | 53073783 | 0 | 0 | 0 |  | 359758930.4 | 286350052.814 | 646108983.214 | 98760514.094 | 104584844.16 | 47877692.76 | 277500228.74 | 73045941 | 555799.32 | 18579053.14 | 23220000 | 1984910 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 95 | 0 | 0 | 338 |  | 0 | 320 | 270 | 0 | 0 | 15 | 214 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 22 | 25 | 25 | 0 | 0 | 37 | 35 | 0 | 0 | 25 | 204 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 12 | 100 | 0 | 0 | 315 | 310 | 206 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 0 | 19 | 8 | 33 | 17 | 110 | 133 | 24 | 17 | 0 | 35 | 43 | 11 | 0 | 110 | 309 | 20 | 78 | 0 | 0 | 18 | 0 | 0 | 235 | 16 | 2 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 19 | 100 | 150 | 0 | 366 | 0 | 0 | 0 | 5 | 0 | 36 | 0 | 0 | 0 | 90 | 360 | 0 | 53 | 0 | 53 | 0 | 0 | 31 |  | 643 | 0 | 400 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 39 | 0 | 187 | 0 | 376 | 0 | 0 | 54 | 0 | 50 | 0 | 5 | 35 | 420 | 73 | 0 | 0 |  | 8629 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 345 | 0 | 0 | 320 | 270 | 75 | 0 | 40 | 223 | 0 | 155 | 100 | 72 | 133 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 25 | 25 | 0 | 0 | 37 | 35 | 0 | 0 | 25 | 203 | 0 | 130 | 0 | 0 | 24 | 0 | 83 | 100 | 0 | 50 | 20 | 20 | 100 | 0 | 0 | 270 | 295 | 215 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 147 | 32 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 334 | 33 | 78 | 0 | 120 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 195 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 196 | 0 | 342 | 105 | 52 | 0 | 0 | 16 | 35 | 0 | 0 | 113 | 100 | 340 | 104 | 0 | 108 | 60 | 0 | 0 | 0 |  | 832 | 0 | 295 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 33 | 67 | 33 | 96 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 5 | 0 | 0 | 199 | 0 | 96 | 100 | 163 | 0 | 364 | 92 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 0 |  | 11655 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 360 | 0 | 0 | 400 | 0 | 100 | 0 | 55 | 0 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 35 | 35 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 85 | 100 | 100 | 50 | 22 | 20 | 80 | 0 | 0 | 360 | 300 | 225 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 17 | 168 | 160 | 49 | 17 | 0 | 44 | 43 | 51 | 0 | 163 | 330 | 33 | 78 | 0 | 120 | 20 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 60 | 0 | 36 |  |  | 848 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 70 | 26 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 144 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 350 | 0 | 0 | 400 | 0 | 100 | 0 | 55 | 0 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 35 | 35 | 0 | 0 | 25 | 225 | 0 | 130 | 0 | 0 | 22 |  | 82 | 100 | 100 | 50 | 22 | 15 | 80 | 0 | 0 | 360 | 300 | 225 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 17 | 136 | 160 | 49 | 17 | 1.6 | 44 | 43 | 51 | 0 | 163 | 330 | 33 | 75 | 0 | 100 | 20 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 200 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 60 | 0 | 36 | 30 |  | 654 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 70 | 25 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 0 | 0 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 144 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 310 | 0 | 0 | 300 | 0 | 30 | 0 | 55 | 0 | 0 | 35 | 24 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 24 | 33 |  | 0 | 0 | 28 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 24 | 0 | 0 | 20 | 98 | 25 | 20 | 2 | 80 | 0 | 0 | 270 | 285 | 201 | 8 | 0 | 26 | 30 | 0 | 0 | 0 | 0 | 42 | 19 | 11 | 33 | 17 | 120 | 158 | 16 | 17 | 1 | 43 | 43 | 14 | 0 | 110 | 307 | 20 | 78 | 0 | 100 | 18 | 0 | 9 | 270 | 16 | 2 | 0 | 81 | 0 | 0 | 120 | 0 | 146 | 6 | 100 | 170 | 0 | 343 | 8 | 0 | 0 | 2 | 0 | 35 | 0 | 0 | 55 | 100 | 340 | 104 | 15 | 17 | 58 | 0 | 17 | 6 | 0 | 834 | 0 | 330 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 133 | 0 | 54 | 0 | 130 | 0 | 345 | 17 | 0 | 70 | 0 | 35 | 0 | 2 | 35 | 390 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7301 | 7:00
| Highest Generation |  | 11655 | 21:00
| Day Peak Generation |  | 8629 | 12:00
| Evening Peak Generation |  | 11655 | 21:00
| HVDC Max Flow |  | 833 | 4:00
| HVDC EvPeak Flow |  | 832 | 21:00
| Load factor L.F |  | 79.47%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-10
Till now the maximum generation is : - |  |  | 13018 MW | 21:00 | Hrs on | 2021-04-03
The Summary of Yesterday's |  | 2021-04-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8629 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8974 | MW
Evening Peak Generation : |  | 11655 | MW Hour : | 21:00 | Available Max Generation : |  | 15072 | MW
E.P. Demand (at gen end) : |  | 11655 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12800 | MW
Maximum Generation : |  | 11655 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2272 | MW
Total Gen. (MKWH) : |  | 222.2813 | System Load Factor : | 79.47% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -312 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-10
Actual : | 82.1 | Ft.(MSL) , | Rule curve : | 86.2 | Ft.( MSL )
Gas Consumed : | Total = | 1112.71 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146638206.854
: |  | Coal : | 73045941 | Oil : | 296079281.88 | Total : | 515763429.734
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4510.7329 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1537.9791 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1378.7053 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1246.0347 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1125.8812 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 908.5566 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 502.7695 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 233.7899 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 700.749 |  |  | 0 | 0%
Total | 0 |  | 12145.1982 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Baghabari-100 MW
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ramganj 132/33 kV T-2 transformer was under shutdown from 08:07 to 09:41 for C/M.
b) Madunaghat 132/33 kV T-2 transformer was under shutdown from 08:43 to 14:25 for project work.
c) Barapukuria 132/33 kV T-4 transformer was under shutdown from 11:02 to 14:58 for sky wire work.
d) Barapukuria 132/33 kV T-3 transformer was under shutdown from 11:08 to 14:50 for 33 kV bus |  |  |  |  | About 17 MW power interruption occurred under Barapukuria S/S area
maintenance by NESCO. |  |  |  |  | from 11:08 to 14:50.
e) Faridpur 132/33 kV T-3 transformer was under shutdown from 09:52 to 10:10 for 33 kV auxiliary |  |  |  |  | About 45 MW power interruption occurred under Faridpur S/S area
transformer maintenance by WZPDCL. |  |  |  |  | from 09:52 to 10:10.
f) Madaripur 132/33 kV T-3 transformer was under shutdown from 08:18 to 13:12 for C/M.
g) Chandpur CCPP 150 MW was under shut down since 10:35 due to Filter changing.
h) HVDC Bheramara-Bahrampur 400 kV Ckt-2 was shut down from 10:21 to 19:12 for D/W.
i) Kamrangirchar-Aurahati 132 kV Ckt was switched on at 20:37.
j) Keraniganj 132/33 kV T1 transformer was shut down from 16:18 to 17:25 for 33 kV bus section maintenance.
k) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 16:44 to 18:14 for removing kite.
l) After maintenance Sylhet 225 MW was synchronized at 20:56.
m) Tongi-Kabirpur 132 kV Ckt-1 tripped at 21:45 showing dist Z1 and was switched on at 21:55.
n) Tangail-Kaliakoir 132 kV Ckt-2 was under shut down since 07:28(10-04-2021) for D/W.
o) Meghnaghat-Shyampur 230 kV Ckt-2 was under shut down from 07:13 to 09:04(10-04-2021) for red
hot maintenance
p) Summit Meghna was under shut down since 04:44(10-04-2021) due to dust in the gas line.
q) Siddhirganj 335 MW was under shut down since 05:10(10-04-2021) due to dust in the gas line.
r) Sirajganj #01 GT was synchronized at 05:52.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 6739500 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 1642409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under S/D due to dust in the gas line.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7418000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 7068500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 75 | 343680 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6116829
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 862845 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 14219 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 258408
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 155 | 3060000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 779520
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 223 | 4831675 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 339408 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1073520
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 742080 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 744442
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 694550
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 51 | 1067820 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 489800
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 607100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 12000 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 870654 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1245460
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 308400 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1449600
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 612000 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 117559
| Dhaka area Total |  |  |  | 5829 | 3031 | 49509978
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 440672
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 124065
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 571200
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 72 | 2058516 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4853511 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3047590 | Machine problem
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 83 | 534103 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1128840
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2315520
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 467136
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 686400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 18240 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31080
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 213273 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 936150 | Low demand
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2363520
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 60 | 973527 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1014 | 20763343
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2461614 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4734000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7180000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 6895000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 432864 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 607200
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 844020 | Under maint.
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 196 | 3870240
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 468900
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 211500
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 156 | 3096000
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818600
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 264629
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 450330
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1153320
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 220680 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 1547 | 33926351
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 147 | 3162720 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 218592 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 32 | 494400 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9550
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 183 | 2277600 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 105 | 555600
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 300790
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 287760
| Mymensingh Area Total |  |  |  | 709 | 508 | 7307012
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 897000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1033440 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2999618 | frequency control.
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 334 | 7144000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 742200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 82512
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 643584 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1344960 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 472820 | Machine problem
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 421000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 199200 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 6997500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 342 | 8257000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 108180
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 340 | 8324500
| Sylhet Area Total |  |  |  | 2377 | 1842 | 39667514
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 832 | 18157091
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 90 | 1344960 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 8640 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 17408 | Low demand
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 295 | 7125408 | Gas shortage.
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 214500 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 506880
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 794880 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1442 | 28169767
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 689184 | High voltage.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 589768
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1573000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1756523
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 570 | 12089700
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 454773 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 862 | 17152948
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4323309 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 163 | 4197136 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 364 | 8511700
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 145294 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 324000
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 140652 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 462720
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 434256
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1138080 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1219584
| Rajshahi Area Total |  |  |  | 2173 | 1141 | 20896731
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3684900 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 5 | 20000 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1148160
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34603
| Rangpur Area Total |  |  |  | 605 | 268 | 4887663
| Total |  |  |  | 21219 | 11655 | 222281307
| Eastern Grid Total |  |  |  | 14331 | 7942 | 151174198
| Western Grid Total |  |  |  | 6888 | 3713 | 71107109
| National Grid Total |  |  |  | 21219 | 11655 | 222281307
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-09
(a) ENTIRE EASTERN GRID : |  | 7393 | MW | (b) ENTIRE WESTERN GRID : |  | 3655 | MW
i) Dhaka area |  | 3717 | MW | i) Khulna area |  | 1505 | MW
ii) Chittagong area |  | 1148 | MW | ii) Rajshahi area |  | 1087 | MW
iii) Comilla area |  | 1205 | MW | iii) Barisal area |  | 347 | MW
iv) Mymensingh area |  | 878 | MW | iv) Rangpur area |  | 716 | MW
v) Sylhet area |  | 445 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11048 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 0:00 | Jamalpur | 135 | 20:00 | Jhenida | 118 | 21:00
Munsiganj | 128 | 19:30 | Sherpur | 116 | 21:00 | Bottail | 111 | 19:00
Sonargaon | 93 | 1:00 | Srimongal | 47 | 18:00 | G.K Project | 54 | 19:30
Shyampur | 206 | 9:00 | Shahjibazar | 113 | 21:00 | Faridpur | 184 | 19:30
Bhulta | 206 | 1:00 | Fenchuganj | 31 | 21:00 | Madaripur | 105 | 22:00
Madanganj | 53 | 0:00 | Kulawara | 39 | 20:00 | Sariatpur | 66 | 21:00
Shitalakhya | 94 | 1:00 | Sylhet | 107 | 20:00 | Gopalganj | 86 | 19:30
Rahim steel | 8 | 1:00 | Chatak | 26 | 19:00 | Bagerhat | 101 | 20:00
Matuail | 54 | 0:00 | Sunamganj | 35 | 21:00 | Mongla | 42 | 1:00
Ghorasal | 79 | 1:00 | Biani Bazar | 52 | 18:30 | Satkhira | 104 | 23:00
Narsingdi | 163 | 21:00 | Comilla (S) | 160 | 22:00 | Gallamari | 42 | 13:00
Haripur (SBU) | 114 | 1:00 | Comilla(N) | 137 | 22:00 | Magura | 52 | 19:00
Sreenagar |  |  | Chandpur | 75 | 21:00 | Norail | 40 | 20:00
Ullon | 78 | 19:30 | Feni | 125 | 21:00 | Chuadanga | 87 | 19:30
Hasnabad | 98 | 21:00 | Chowmuhani | 174 | 21:00 | Borguna | 16 | 21:00
Magbazar | 52 | 13:00 | Ashuganj | 51 | 0:00 | Barisal(N) | 45 | 21:00
Maniknagar | 76 | 23:00 | Daudkandi | 136 | 21:00 | Barisal (S) | 104 | 22:00
Bangabhaban | 7 | 15:00 | B.Baria | 165 | 20:00 | Patuakhali | 101 | 21:00
Narinda | 68 | 23:00 | Ramganj | 86 | 19:00 | Bhandaria | 48 | 21:00
Dhanmondi | 135 | 13:00 | Chaddagram | 40 | 19:30 | Borhan Uddin | 38 | 22:00
Lalbag | 61 | 11:00 | PHP | 5 | 9:00 | Ishurdi | 47 | 15:00
Madartek | 77 | 22:00 | Kochua | 65 | 21:00 | Ruppur Paromanobik | 3 | 1:00
Dhaka University | 23 | 11:00 | Madunaghat | 63 | 20:00 | Natore | 96 | 15:00
Aftabnagar | 9 | 19:00 | Hathazari | 79 | 21:00 | Bogra | 139 | 21:00
Fatullah | 54 | 1:00 | Khulshi | 186 | 12:00 | Noagaon | 116 | 21:00
Nawabganj | 48 | 19:30 | Halishahar | 125 | 15:00 | Rajshahi | 130 | 21:00
Mirpur | 95 | 19:00 | Baraulia | 149 | 2:00 | Rajshahi New | 17 | 19:30
Kalyanpur | 105 | 19:00 | Sikalbaha | 31 | 2:00 | C.Nawabganj | 83 | 21:00
Gulshan | 92 | 19:30 | Dohazari | 82 | 19:00 | Amnura | 62 | 20:00
Uttara | 74 | 19:30 | Cox'sbazar | 100 | 19:30 | Pabna | 88 | 1:00
Uttara New | 23 | 19:30 | Chandraghona | 28 | 18:30 | Shahjadpur | 81 | 19:00
Kamrangirchar | 67 | 19:30 | Kaptai | 6 | 19:00 | Serajganj | 85 | 19:30
Savar | 130 | 15:00 | A. Khaer Stl. | 10 | 10:00 | Niyamatpur | 70 | 21:00
Bhasantec | 130 | 19:30 | Bakulia | 94 | 1:00 | Joypurhat | 53 | 21:00
Agargaon | 59 | 19:30 | Julda | 22 | 1:00 | Sherpur(Bogura) | 47 | 18:30
Satmosjid | 78 | 19:30 | TK chemical | 26.5 | 21:00 | Mohastangor | 58 | 19:00
Tongi | 115 | 11:00 | Modern Steel | 0 | #N/A | Bangura | 28 | 14:00
Kabirpur | 190 | 1:00 | Shahmirpur | 23.1 | 1:00 | Rangpur | 114 | 19:00
Basundhara | 132 | 19:30 | Khagrachhari | 24 | 8:00 | Lalmonirhat | 42 | 19:00
Manikganj | 82 | 19:30 | Matarbari | 37.5 | 19:30 | Saidpur | 102 | 19:30
Joydevpur | 137 | 1:00 | Baroiar Hat | 42 | 14:00 | Purbasadipur | 91 | 20:00
New Tongi | 82 | 1:00 | Rangamati | 12 | 18:30 | Thakurgaon | 76 | 19:00
Kodda | 212 | 0 | Abul Khair 230 | 14 | 8:00 | Palashbari | 104 | 20:00
Dhamrai | 92 | 19:30 | BSRM | 119 | 23:00 | Barapukuria | 42 | 21:00
Rajendrapur | 92 | 1:00 | GPH Ispat | 81 | 6:00 | Panchagar | 45 | 19:00
Valuka | 118 | 20:00 | Goalpara | 23 | 1:00 | Joldhaka | 50 | 19:00
Tangail | 224 | 19:30 | Central s/s | 96 | 19:30 | Kurigram | 57 | 19:00
Mymensing | 168 | 19:00 | Noapara | 47 | 0.91667 | Mithapukur | 34 | 19:30
Kishorganj | 136 | 21:00 | Jessore | 127 | 21:00
Netrokona | 102 | 19:30 | Benapol | 66 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 20:00 | 399 | 12:00 | Kaliakoir | 391 | 0.125 | 379 | 0.5
| Bheramara | 398 | 6:00 | 391 | 20:00 | Bhulta | 380 | 0.8125 | 369 | 0.5
| Ashuganj(N) | 387 | 7:00 | 377 | 12:00 | Gopalganj | 405 | 0.625 | 390 | 0.875
| Payra | 409 | 19:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 225 | 8:00 | 219 | 16:00
| Ishurdi | 234 | 10:00 | 227 | 19:00 | Megnaghat | 230 | 5:00 | 222 | 10:00
| Ashuganj | 235 | 7:00 | 229 | 16:00 | Fenchuganj | 241 | 19:00 | 234 | 19:00
| Serajganj | 232 | 18:30 | 227 | 22:00 | Siddhirganj | 229 | 19:00 | 221 | 12:00
| Baghabari | 232 | 1:00 | 228 | 18:30 | Maniknagar | 228 | 19:00 | 220 | 12:00
| Barapukuria | 238 | 1:00 | 229 | 19:00 | Agargaon | 226 | 24:00 | 215 | 12:00
| Bogra | 230 | 1:00 | 219 | 19:00 | Barisal | 248 | 8:00 | 237 | 18:30
| Rajshahi | 231 | 1:00 | 219 | 22:00 | Bhola 225 MW | 250 | 24:00 | 240 | 21:00
| Khulna South | 229 | 18:00 | 209 | 3:00 | AKSML | 227 | 8:00 | 218 | 12:00
| Rampura | 230 | 24:00 | 220 | 12:00 | BSRM | 227 | 8:00 | 219 | 15:00
| Haripur | 225 | 7:00 | 219 | 12:00 | Bibiyana | 240 | 5:00 | 233 | 24:00
| Hasnabad | 225 | 1:00 | 220 | 12:00 | Bhulta | 231 | 19:30 | 221 | 12:00
| Shyampur | 225 | 19:00 | 220 | 12:00 | Ashuganj (S) | 232 | 3:00 | 228 | 12:00
| Aminbazar | 227 | 1:00 | 215 | 2:00 | Kaliakoir | 225 | 3:00 | 215 | 14:00
| Tongi | 224 | 18:00 | 215 | 10:00 | GPH | 226 | 8:00 | 217 | 15:00
| Comilla (N) | 225 | 7:00 | 219 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 19:30 | 129 | 12:00 | Madanhat | 135 | 0.29167 | 131 | 0.5
| Munsiganj | 135 | 18:30 | 128 | 10:00 | Hathazari | 134 | 0.33333 | 130 | 0.58333
| Sonargaon | 135 | 19:00 | 127 | 12:00 | Khulshi | 133 | 0.375 | 128 | 0.5
| Shyampur | 134 | 19:00 | 128 | 12:00 | Halishahar | 135 | 0.77083 | 130 | 0.5
| Bhulta | 130 | 3:00 | 122 | 11:00 | Baraulia | 135 | 0.083333 | 128 | 0.5
| Madanganj | 132 | 1:00 | 127 | 11:00 | Sikalbaha | 136 | 0.8125 | 131 | 0.5
| Shitalakhya | 141 | 19:30 | 129 | 12:00 | Dohazari | 134 | 0.33333 | 127 | 0.5
| Rahim steal | 134 | 18:30 | 129 | 12:00 | Cox'sbazar | 126 | 0.33333 | 117 | 0.041667
| Matuail | 136 | 19:30 | 129 | 12:00 | Chandraghona | 135 | 0.33333 | 131 | 0.5
| Ghorasal | 137 | 18:00 | 134 | 13:00 | Kaptai | 135 | 0.29167 | 131 | 0.41667
| Narsinghdi | 133 | 5:00 | 124 | 22:00 | A. Khaer Stl. | 132 | 0.083333 | 129 | 0.45833
| Haripur (SBU) | 134 | 19:00 | 129 | 12:00 | Bakulia | 135 | 0.33333 | 131 | 0.5
| Sreenagar |  |  |  |  | Julda | 136 | 0.75 | 131 | 0.45833
| Ullon | 135 | 19:30 | 130 | 12:00 | TK Chemical | 134 | 0.20833 | 130 | 0.5
| Hasnabad | 137 | 19:30 | 128 | 12:00 | Modern Steel
| Magbazar | 135 | 6:00 | 130 | 12:00 | Shahmirpur | 136 | 0.75 | 131 | 0.5
| Maniknagar | 136 | 19:30 | 133 | 10:00 | Khagrachhari | 134 | 0.33333 | 129 | 0.54167
| Bangabhaban | 136 | 19:30 | 133 | 10:00 | Matarbari | 128 | 0.29167 | 120 | 0.041667
| Narinda | 136 | 19:30 | 133 | 10:00 | Baroiar Hat | 133 | 0.77083 | 127 | 0.5
| Dhanmondi | 135 | 19:30 | 130 | 12:00 | Rangamati | 135 | 0.33333 | 129 | 0.5
| Lalbag | 138 | 19:30 | 128 | 12:00 | Goalpara S/S | 137 | 18:00 | 126 | 5:00
| Madartek | 135 | 3:00 | 130 | 12:00 | Khulna Central S/S | 137 | 18:00 | 124 | 7:00
| Dhaka University | 135 | 6:00 | 130 | 12:00 | Noapara | 133 | 18:00 | 120 | 0.16667
| Aftabnagar | 135 | 7:00 | 130 | 12:00 | Jessore | 128 | 18:00 | 114 | 0.875
| Fatullah | 135 | 19:00 | 128 | 12:00 | Benapol | 130 | 13:00 | 113 | 0.79167
| Nawabganj | 130 | 19:30 | 124 | 12:00 | Jhenida | 125 | 18:00 | 108 | 0.875
| Mirpur | 136 | 19:30 | 125 | 12:00 | Bottail | 132 | 0.41667 | 121 | 0.77083
| Kalyanpur | 135 | 19:30 | 127 | 12:00 | G.K Project | 138 | 10:00 | 133 | 0.875
| Gulshan | 134 | 19:30 | 130 | 12:00 | Faridpur | 137 | 0.41667 | 129 | 0.875
| Uttara | 135 | 19:30 | 124 | 12:00 | Madaripur | 139 | 0.33333 | 133 | 0.45833
| Uttara New | 134 | 19:30 | 125 | 12:00 | Shariyatpur S/S | 140 | 0.125 | 132 | 0.875
| Kamrangirchar | 133 | 19:30 | 123 | 12:00 | Gopalganj | 141 | 0.25 | 135 | 0.77083
| Savar | 138 | 19:30 | 124 | 12:00 | Bagerhat | 134 | 18:00 | 121 | 0.79167
| Bhasantec | 130 | 19:30 | 124 | 12:00 | Mongla | 131 | 0.75 | 122 | 0.79167
| Agargaon | 132 | 19:30 | 126 | 12:00 | Satkhira | 135 | 18:00 | 123 | 0.875
| Satmosjid | 132 | 19:30 | 125 | 12:00 | Gallamari | 137 | 18:00 | 125 | 0.16667
| Tongi | 137 | 21:00 | 127 | 14:00 | Magura | 121 | 9:00 | 105 | 18:30
| Kabirpur | 138 | 22:00 | 133 | 12:00 | Narail | 123 | 0.41667 | 104 | 21:00
| Basundhara | 134 | 21:00 | 125 | 14:00 | Chuadanga | 120 | 18:00 | 96 | 0.875
| Manikganj | 141 | 21:00 | 126 | 15:00 | Borguna | 138 | 0.16667 | 131 | 0.625
| Joydevpur | 137 | 3:00 | 129 | 15:00 | Barisal(N) | 139 | 1:00 | 133 | 0.625
| New Tongi | 135 | 19:00 | 125 | 15:00 | Barisal (S) | 137 | 1:00 | 130 | 0.77083
| Kodda | 135 | 21:00 | 122 | 7:00 | Patuakhali(S) | 134 | 3:00 | 128 | 15:00
| Dhamrai | 138 | 3:00 | 131 | 13:00 | Bhandaria | 138 | 0.20833 | 130 | 0.58333
| Rajendrapur | 136 | 22:00 | 124 | 5:00 | Ishurdi | 136 | 0.41667 | 132 | 0.79167
| Valuka | 138 | 2:00 | 115 | 12:00 | Ruppur Paromanobik | 137 | 0.125 | 131 | 0.875
| Tangail | 139 | 2:00 | 121 | 12:00 | Natore | 136 | 1:00 | 132 | 9:00
| Mymensing | 138 | 1:00 | 118 | 12:00 | Bogra | 138 | 1:00 | 131 | 12:00
| Kishorganj | 137 | 1:00 | 123 | 12:00 | Noagaon | 136 | 1:00 | 124 | 21:00
| Netrokona | 139 | 2:00 | 116 | 12:00 | Rajshahi | 134 | 16:00 | 130 | 21:00
| Jamalpur | 141 | 1:00 | 113 | 12:00 | Rajshahi New | 136 | 18:00 | 129 | 21:00
| Sherpur | 142 | 1:00 | 112 | 12:00 | C.Nawabganj | 132 | 1:00 | 125 | 23:00
| Srimongal | 138 | 1:00 | 131 | 20:00 | Amnura | 131 | 18:00 | 124 | 23:00
| Shahjibazar | 139 | 2:00 | 129 | 21:00 | Pabna | 135 | 6:00 | 130 | 19:00
| Fenchuganj | 138 | 5:00 | 132 | 21:00 | Shahjadpur | 140 | 2:00 | 135 | 19:00
| Khulawara | 137 | 2:00 | 131 | 19:30 | Serajganj | 135 | 1:00 | 130 | 19:00
| Sylhet | 135 | 2:00 | 129 | 14:00 | Niyamatpur | 138 | 1:00 | 121 | 21:00
| Chatak | 134 | 2:00 | 123 | 20:00 | Joypurhat | 138 | 1:00 | 125 | 19:00
| Sunamganj | 135 | 2:00 | 123 | 20:00 | Sherpur(Bogura) | 137 | 1:00 | 131 | 21:00
| Biani Bazar | 135 | 6:00 | 125 | 18:00 | Mohastangor | 137 | 1:00 | 128 | 19:30
| Comilla(s) | 127 | 5:00 | 120 | 19:00 | Bangura | 136 | 1:00 | 132 | 19:00
| Comilla(n) | 135 | 7:00 | 130 | 15:00 | Rangpur | 134 | 2:00 | 123 | 19:00
| Chandpur | 138 | 18:00 | 128 | 15:00 | Lalmonirhat | 135 | 1:00 | 120 | 19:00
| Feni | 132 | 8:00 | 124 | 15:00 | Saidpur | 135 | 1:00 | 119 | 19:00
| Chowmuhani | 132 | 9:00 | 125 | 15:00 | Purbasadipur | 132 | 1:00 | 117 | 19:00
| Ashuganj | 140 | 2:00 | 133 | 21:00 | Thakurgaon | 130 | 1:00 | 117 | 19:00
| Daudkandi | 131 | 5:00 | 126 | 12:00 | Palashbari | 135 | 1:00 | 125 | 19:00
| B.Baria | 134 | 6:00 | 127 | 20:00 | Barapukuria | 138 | 1:00 | 129 | 19:00
| Ramganj | 134 | 8:00 | 122 | 14:00 | Panchagar | 129 | 1:00 | 115 | 19:00
| Chaddagram | 134 | 7:00 | 128 | 2:00 | Joldhaka | 134 | 1:00 | 116 | 19:00
| PHP | 133 | 8:00 | 125 | 12:00 | Kurigram | 133 | 1:00 | 120 | 19:00
| Kochua | 139 | 18:00 | 128 | 15:00 | Mithapukur | 135 | 0.041667 | 124 | 0.79167

## L-Curve
Date | 2021-04-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 158 | 7336 | 3617 | 10953 |  |  |  | QF-LDC-11
0:30 | 209 | 7028.5 | 3176.5 | 10205 | Date: | 2021-04-09
1:00 | 260 | 6721 | 2736 | 9457
1:30 | 252 | 6362.5 | 2695.5 | 9058
2:00 | 244 | 6004 | 2655 | 8659
2:30 | 182 | 5654 | 2559 | 8213 | [5 empty] | Gen. at Eve. Peak | 11655 | 11655 MW (21:00 )
3:00 | 120 | 5304 | 2463 | 7767 | [6 empty] | 21:00
3:30 | 123 | 5227.5 | 2432.5 | 7660 | [5 empty] | Gen. at Day Peak | 8629 | 8629 MW (12:00 )
4:00 | 126 | 5151 | 2402 | 7553 | [6 empty] | 12:00
4:30 | 144 | 5156 | 2426 | 7582 | [5 empty] | Highest Generation | 11655
5:00 | 162 | 5161 | 2450 | 7611 | [6 empty] | 21:00
5:30 | 158 | 5132 | 2416.5 | 7548.5
6:00 | 154 | 5103 | 2383 | 7486
6:30 | 115 | 5045.5 | 2348 | 7393.5
7:00 | 76 | 4988 | 2313 | 7301
7:30 | 74 | 4983 | 2347 | 7330
8:00 | 72 | 4978 | 2381 | 7359
8:30 | 91 | 5055.5 | 2407.5 | 7463
9:00 | 110 | 5133 | 2434 | 7567
9:30 | 114 | 5297.5 | 2412 | 7709.5
10:00 | 118 | 5462 | 2390 | 7852
10:30 | 183 | 5531 | 2511.5 | 8042.5
11:00 | 248 | 5600 | 2633 | 8233
11:30 | 202 | 5729 | 2702 | 8431
12:00 | 156 | 5858 | 2771 | 8629
12:30 | 96 | 6050 | 2907 | 8957
13:00 | 36 | 6242 | 3043 | 9285
13:30 | 44 | 6330 | 3002.5 | 9332.5
14:00 | 52 | 6418 | 2962 | 9380
14:30 | 54 | 6542 | 2977.5 | 9519.5
15:00 | 56 | 6666 | 2993 | 9659
15:30 | 48 | 6637.5 | 2971 | 9608.5
16:00 | 40 | 6609 | 2949 | 9558
16:30 | 25 | 6527.5 | 2909.5 | 9437
17:00 | 10 | 6446 | 2870 | 9316
17:30 | 26 | 6338 | 2779 | 9117
18:00 | 42 | 6230 | 2688 | 8918
18:30 | 177 | 6867 | 2931 | 9798
19:00 | 312 | 7504 | 3174 | 10678
19:30 | 194 | 7911 | 3529 | 11440
20:00 | 50 | 7759 | 3692 | 11451 |  |  |  | Executive Engineer
20:30 | 89 | 7850.5 | 3702.5 | 11553 |  |  |  | Network Operation Division
21:00 | 128 | 7942 | 3713 | 11655
21:30 | 88 | 7750.5 | 3733.5 | 11484
22:00 | 48 | 7559 | 3754 | 11313 |  |  |  |  | Page 6 of 7
22:30 | 68 | 7526.5 | 3704.5 | 11231
23:00 | 88 | 7494 | 3655 | 11149
23:30 | 123 | 7415 | 3636 | 11051
24:00 | 158 | 7336 | 3617 | 10953
11655 MW (21:00 )
8629 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-09 |  | Energy | 222281307
[11 empty] | 2021-04-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4410 | 832 | 1956 | 2869 | 721 | 68 | 100 | 0 | 152 | 0
0:30 | 4157.5 | 832 | 1855 | 2401.5 | 715.5 | 86.5 | 84.5 | 0 | 150 | 0 | Date: | 2021-04-09
1:00 | 3905 | 832 | 1754 | 1934 | 710 | 105 | 69 | 0 | 148 | 0
1:30 | 3864 | 832 | 1732.5 | 1630.5 | 695 | 105 | 53 | 0 | 146 | 0 | [7 empty] | Total Energy | 222.2813 | Total Energy Gen 222.281 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.281 MKWHr
2:00 | 3823 | 832 | 1711 | 1327 | 680 | 105 | 37 | 0 | 144 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3723.5 | 832 | 1605.5 | 1141.5 | 645 | 105 | 18.5 | 0 | 142 | 0 | [7 empty] | Energy Requirement | 222.2813
3:00 | 3624 | 832 | 1500 | 956 | 610 | 105 | 0 | 0 | 140 | 0
3:30 | 3627 | 832.5 | 1517.5 | 851 | 590 | 105 | 0 | 0 | 137 | 0 | [6 empty] | Shortage
4:00 | 3630 | 833 | 1535 | 746 | 570 | 105 | 0 | 0 | 134 | 0
4:30 | 3643 | 832.5 | 1549.5 | 752 | 570 | 105 | 0 | 0 | 130 | 0
5:00 | 3656 | 832 | 1564 | 758 | 570 | 105 | 0 | 0 | 126 | 0
5:30 | 3652.5 | 832.5 | 1488.5 | 788.5 | 560 | 105 | 0 | 0 | 121 | 0.5
6:00 | 3649 | 833 | 1413 | 819 | 550 | 105 | 0 | 0 | 116 | 1
6:30 | 3623 | 833 | 1405 | 768.5 | 540 | 105 | 0 | 0 | 109 | 10 |  |  |  |  | Coal
7:00 | 3597 | 833 | 1397 | 718 | 530 | 105 | 0 | 0 | 102 | 19
7:30 | 3635.5 | 833 | 1395 | 703.5 | 530 | 105 | 0 | 0 | 101 | 27 |  |  |  | Oil |  |  |  | ,
8:00 | 3674 | 833 | 1393 | 689 | 530 | 105 | 0 | 0 | 100 | 35
8:30 | 3701.5 | 832.5 | 1438 | 712.5 | 530 | 105 | 0 | 0 | 101 | 42.5
9:00 | 3729 | 832 | 1483 | 736 | 530 | 105 | 0 | 0 | 102 | 50
9:30 | 3922.5 | 737.5 | 1522.5 | 740 | 530 | 105.5 | 0 | 0 | 104 | 47.5
10:00 | 4116 | 643 | 1562 | 744 | 530 | 106 | 0 | 0 | 106 | 45
10:30 | 4159.5 | 643 | 1608 | 822 | 550 | 106.5 | 0 | 0 | 106 | 47.5
11:00 | 4203 | 643 | 1654 | 900 | 570 | 107 | 0 | 0 | 106 | 50
11:30 | 4269 | 643 | 1709.5 | 960.5 | 570 | 89.5 | 0 | 0 | 108 | 81.5
12:00 | 4335 | 643 | 1765 | 1021 | 570 | 72 | 0 | 0 | 110 | 113
12:30 | 4296.5 | 643 | 1859.5 | 1290 | 570 | 71 | 0 | 0 | 121 | 106
13:00 | 4258 | 643 | 1954 | 1559 | 570 | 70 | 0 | 0 | 132 | 99
13:30 | 4258 | 643 | 1954 | 1559 | 570 | 70 | 0 | 0 | 132 | 99
14:00 | 4258 | 643 | 1954 | 1559 | 570 | 70 | 0 | 0 | 132 | 99
14:30 | 4269.5 | 643 | 1965.5 | 1730.5 | 575 | 70 | 8 | 0 | 128 | 82.5
15:00 | 4281 | 643 | 1977 | 1902 | 580 | 70 | 16 | 0 | 124 | 66
15:30 | 4244 | 643 | 1953.5 | 1923.5 | 585 | 67.5 | 16 | 0 | 119.5 | 56.5
16:00 | 4207 | 643 | 1930 | 1945 | 590 | 65 | 16 | 0 | 115 | 47
16:30 | 4147 | 643 | 1895.5 | 1926.5 | 590 | 67.5 | 17 | 0 | 116.5 | 34
17:00 | 4087 | 643 | 1861 | 1908 | 590 | 70 | 18 | 0 | 118 | 21
17:30 | 4014.5 | 642.5 | 1785.5 | 1851.5 | 590 | 70 | 38 | 0 | 114 | 11
18:00 | 3942 | 642 | 1710 | 1795 | 590 | 70 | 58 | 0 | 110 | 1
18:30 | 4072 | 642.5 | 1821.5 | 2251.5 | 620 | 70.5 | 189.5 | 0 | 130 | 0.5
19:00 | 4202 | 643 | 1933 | 2708 | 650 | 71 | 321 | 0 | 150 | 0
19:30 | 4228 | 688 | 1867 | 3401 | 720 | 65 | 321 | 0 | 150 | 0
20:00 | 4220 | 832 | 1881 | 3257 | 720 | 70 | 317 | 0 | 154 | 0
20:30 | 4282.5 | 832 | 1882 | 3275.5 | 720 | 71 | 335 | 0 | 155 | 0
21:00 | 4345 | 832 | 1883 | 3294 | 720 | 72 | 353 | 0 | 156 | 0
21:30 | 4348 | 832.5 | 1888 | 3124.5 | 720 | 72.5 | 340.5 | 0 | 158 | 0
22:00 | 4351 | 833 | 1893 | 2955 | 720 | 73 | 328 | 0 | 160 | 0
22:30 | 4383.5 | 833 | 1893 | 2912 | 720 | 72.5 | 258 | 0 | 159 | 0
23:00 | 4416 | 833 | 1893 | 2869 | 720 | 72 | 188 | 0 | 158 | 0
23:30 | 4413 | 832.5 | 1924.5 | 2869 | 720.5 | 70 | 144 | 0 | 155 | 0 | Max Temp. in Dhaka |  | 34.7° C
24:00 | 4410 | 832 | 1956 | 2869 | 721 | 68 | 100 | 0 | 152 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 222.281 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 222.281 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 37 | 37 | 35 | 35 | 35 | 30 | 35 | 35 |  | 36 | 30 | 35 | 37 | 38 | 37 | 33 | 814516
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 1244000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [6 empty] | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 440672
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 3 | 1 | 12 | 16 | 18 | 19 | 17 | 15 | 12 | 7 | 2 | 0 | [8 empty] | 124065
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 203 | 202 | 195 | 195 | 194 | 196 | 201 | 203 | 203 | 203 | 204 | 204 | 204 | 204 | 203 | 203 | 204 |  | 205 | 203 | 202 | 203 | 202 | 202 | 202 | 4853511
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 130 | 130 | 130 | 130 | 3047590
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 0 | [16 empty] | 83 | 83 | 83 | 83 | 83 | 68 | 68 | 534103
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 115 | 70 | 70 | 92 | 52 | 35 | 35 | 35 | 120 | 155 | 180 | 180 | 130 | 180 | 180 | 65 | 70 |  | 185 | 175 | 155 | 155 | 150 | 155 | 155 | 3060000
17 | Siddhirganj 335 MW CCPP | 220 | 221 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 218 | 218 | 214 | 214 | 214 | 209 | 211 | 210 | 170 |  | 219 | 223 | 222 | 223 | 223 | 223 | 224 | 4831675
18 | Kodda 300 MW PP Unit-2 (Summit) | 95 | 0 | [15 empty] | 7 |  | 136 | 175 | 192 | 195 | 95 | 45 | 45 | 870654
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 280 | 250 | 250 | 250 | 230 | 230 | 230 | 230 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6739500
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2461614
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 432864
33 | Ashuganj 225 MW CCPP | 181 | 180 | 180 | 186 | 181 | 180 | 180 | 181 | 181 | 189 | 190 | 206 | 186 | 210 | 193 | 210 | 212 | 192 |  | 212 | 213 | 214 | 215 | 215 | 216 | 218 | 4734000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 270 | 295 | 295 | 270 | 270 | 270 | 280 | 275 | 310 | 275 | 270 | 305 | 260 | 270 | 285 |  | 300 | 300 | 295 | 295 | 295 | 295 | 295 | 6895000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 265 | 280 | 310 | 270 | 270 | 275 | 285 | 285 | 315 | 305 | 305 | 345 | 300 | 300 | 285 |  | 280 | 270 | 270 | 270 | 270 | 270 | 270 | 7180000
35 | Ashuganj 55 MW PP (Precision) | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 45 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 607200
36 | Chandpur 150 MW CCPP | 82 | 81 | 81 | 81 | 80 | 79 | 80 | 79 | 82 | 86 | [16 empty] | 844020
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 337 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7068500
41 | Haripur 360MW CCPP(HPL) | 261 | 280 | 291 | 291 | 291 | 251 | 250 | 253 | 272 | 341 | 339 | 338 | 337 | 337 | 320 | 337 | 297 | 257 |  | 341 | 347 | 345 | 345 | 346 | 343 | 347 | 7418000
42 | RPCL 210MW CCPP | 143 | 110 | 113 | 113 | 112 | 113 | 113 | 111 | 133 | 157 | 157 | 133 | 133 | 128 | 131 | 153 | 154 | 148 |  | 148 | 147 | 147 | 147 | 152 | 159 | 159 | 3162720
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 9 | 22 | 34 | 21 | 24 | 53 | 45 | 43 | 29 | 25 | 15 | 0 | [8 empty] | 300790
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 | 38 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 897000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1033440
46 | Shajibazar 330 MW CCPP | 335 | 305 | 310 | 307 | 308 | 309 | 308 | 308 | 308 | 310 | 309 | 309 | 309 | 312 | 310 | 311 | 308 | 310 |  | 309 | 306 | 333 | 334 | 334 | 331 | 312 | 7144000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 35 | 35 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 31 | 31 | 31 | 32 |  | 32 | 32 | 20 | 33 | 33 | 33 | 33 | 643584
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 75 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 78 | 78 | 78 | 77 | 78 | 75 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1344960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | [22 empty] | 120 | 150 | 150 | 140 | 472820
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 421000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 0 | [9 empty] | 7 | 7 | 7 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 108180
54 | Hobiganj 11MW PP Cofidence-E | 5 | 0 | [9 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 82512
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 48 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 742200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 0 | [8 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 0 | 16 | 16 | 199200
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 275 | 280 | 295 | 310 | 270 | 280 | 280 | 290 | 305 | 185 | 235 | 320 | 280 | 320 | 320 | 285 | 280 |  | 300 | 263 | 275 | 295 | 280 | 280 | 280 | 6997500
| Bibiyana South 400 MW | 340 | 350 | 340 | 370 | 340 | 300 | 320 | 320 | 320 | 340 | 346 | 360 | 360 | 360 | 360 | 360 | 360 | 360 |  | 370 | 340 | 340 | 340 | 340 | 354 | 340 | 8324500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 35 | 0 | [9 empty] | 30 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 55 | 55 | 694550
59 | Tangail Palli Power Gen 22 MW | 24 | 0 | [10 empty] | 4 | 10 | 23 | 23 | 23 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 287760
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 467136
61 | Narshingdi 22 MW PP (Doreen) | [12 empty] | 10 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 258408
62 | Tangail 22 MW PP (Doreen) | 17 | 0 | [6 empty] | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 14 | 14 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 218592
63 | Impoprt (Tripura) | 148 | 144 | 140 | 134 | 126 | 116 | 102 | 100 | 102 | 106 | 106 | 110 | 132 | 128 | 124 | 115 | 118 | 110 |  | 150 | 150 | 154 | 156 | 160 | 158 | 152 | 3096000
64 | Malancha, Ctg. EPZ (United) | 39 | 32 | 39 | 39 | 40 | 30 | 30 | 28 | 28 | 12 | 12 | 12 | 23 | 16 | 16 | 16 | 16 | 20 |  | 20 | 20 | 20 | 20 | 40 | 41 | 41 | 686400
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 20 | 20 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 468900
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 0 | 11 | 8 |  | 8 | 8 | 8 | 8 | 11 | 11 |  |  | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 211500
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818600
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 13 | 15 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 450330
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 7 | 7 | 18 | 18 | 18 | 27 | 20 | 22 | 22 | 22 | 22 | 13 | 15 | 15 | 8 | 13 |  | 13 | 26 | 26 | 26 | 26 | 26 | 26 | 467820
71 | Maona 33 MW PP(Summit) | 33 | 0 | 0 | 0 | 0 | 13 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 0 | 0 | 25 | 489800
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 607100
73 | Ghorashal 108MW PP (Regent) | 100 | 103 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 65 | 95 | 101 | 101 | 101 | 99 | 100 | 99 |  | 100 | 100 | 97 | 103 | 100 | 100 | 100 | 1642409
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 113 | 8 | 0 | [11 empty] | 25 | 65 | 65 | 65 |  | 65 | 113 | 113 | 113 | 113 | 113 | 113 | 1153320
| Manikgonj 162MW PP(MPGL) | 35 | 0 | [15 empty] | 2 |  | 109 | 162 | 108 | 108 | 35 | 35 | 17 | 612000
77 | Siddhirganj 100 PP(Dutch Bangla) | 40 | 0 | [10 empty] | 13 | 50 | 50 | 50 | 50 | 24 |  | 50 | 100 | 100 | 100 | 60 | 60 | 60 | 779520
78 | Gazipur 52 MW PP | [19 empty] | 8 | 8 | [5 empty] | 12000
79 | Kodda 150MW PP | 32 | 0 | [11 empty] | 16 | 16 | 16 | 16 | 16 |  | 100 | 100 | 100 | 133 | 115 | 115 | 32 | 742080
80 | Jamalpur 95 MW PP(Powerpac) | 32 | 8 | 0 |  |  |  | 3 | 8 | 32 | 32 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 494400
81 | Jangalia 52 MW PP (Lakdanavi) | [17 empty] | 2 |  | 27 | 52 | 52 | 52 | 52 | 52 | 52 | 264629
| Gazipur 100 MW PP | [17 empty] | 7 |  | 71 | 105 | 52 | 52 | 17 | 17 | 17 | 308400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 2 | 4 | 4 | 5 | 4 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 31080
| Jodiac Power | 50 | 54 | 54 | 54 | 38 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 936150
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 7 | 10 | [5 empty] | 14219
86 | Meghnaghat CCPP ( Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6116829
87 | Meghnaghat 100 MW(IEL) | 30 | 0 | [15 empty] | 1 |  | 35 | 100 | 79 | 75 | 40 | 32 | 22 | 343680
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 53 | 0 | [8 empty] | 73 | 104 | 87 | 87 | 87 | 53 |  | 92 | 104 | 104 | 104 | 104 | 104 | 104 | 1449600
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 90 | 90 | 90 | 50 | 50 | 10 | [6 empty] | 14 | 20 | 50 | 50 | 50 | 20 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1128840
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 | [15 empty] | 5 |  | 40 | 85 | 72 | 72 | 32 | 32 | 7 | 339408
95 | Patenga 50MW PP (Baraka) | [12 empty] | 4 | 47 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 571200
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 12 | 12 | 5 |  |  |  |  | 18240
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC) | [26 empty] | 0
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 15 | 15 | 15 | 45 | 55 | 15 | 15 | 15 | 15 | 15 | 28 | 42 | 42 | 40 | 40 | 40 |  | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 862845
100 | Manikganj 55 MW PP (Northern) | 55 | 0 | [10 empty] | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 744442
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 130 | 110 | 110 | 110 |  | 130 | 130 | 110 | 110 | 110 | 110 | 163 | 2999618
102 | Sarishabari 3 MW Solar Plant | [9 empty] | 2 | 2 | 0 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 9550
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 0 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1073520
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 45 | 0 |  |  |  |  | 8 |  | 7 | 16 | 16 | 16 | 77 | 193 | 193 | 193 | 192 | 191 |  | 191 | 180 | 173 | 183 | 192 | 193 | 170 | 2277600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 136 | 76 | 2 | 30 | 37 | [8 empty] | 18 | 46 | 48 | 46 |  | 83 | 90 | 146 | 149 | 118 | 85 | 58 | 1245460
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 86 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 100 | 90 | 90 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2315520
116 | Chandpur 200MW (Desh energy) | 169 | 171 | 126 | 125 | 127 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 139 | 136 | 152 | 180 |  | 196 | 196 | 196 | 196 | 199 | 194 | 197 | 3870240
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 311 | 312 | 317 | 317 | 315 | 319 | 331 | 332 | 342 | 365 | 365 | 366 | 366 | 366 | 366 | 366 | 366 | 329 |  | 342 | 366 | 366 | 342 | 343 | 343 | 344 | 8257000
| Jamalpur 115 MW PP (United) | [17 empty] | 4 |  | 37 | 115 | 115 | 105 | 105 | 105 | 85 | 555600
| Anwara 300 MW PP (United) | [12 empty] | 32 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 213273
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 90 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2363520
| Anlima Energy Ltd. |  |  |  | 0 | 36 | 45 | 17 | 17 | 17 | 17 | 43 | 53 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 57 | 57 | 973527
| Bhairob 54.5 MW | 37 | 30 | 17 | 0 | [8 empty] | 14 | 18 | 18 | 18 | 18 | 18 |  | 28 | 37 | [5 empty] | 220680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 9 |  |  |  | 31 | 26 | 27 | 18 | 10 | 2 | 1 | [8 empty] | 117559
120 | Eastern Zone Total | 6721 | 6004 | 5304 | 5151 | 5161 | 5103 | 4988 | 4978 | 5133 | 5462 | 5600 | 5858 | 6242 | 6418 | 6666 | 6609 | 6446 | 6230 |  | 7504 | 7911 | 7759 | 7942 | 7559 | 7494 | 7336 | 151174198
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 83 | 83 | 41 | 16 | 32 | 49 | 16 | 16 | 16 | 16 | 16 | 49 | 83 | 66 | 66 | 66 | 66 | 66 |  | 70 | 73 | 76 | 90 | 99 | 99 | 99 | 1344960
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 3 | 3 | 0 | [23 empty] | 8640
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 93 | 53 | 0 | [11 empty] | 17 | 17 | 17 | 17 |  | 17 | 92 | 92 | 92 | 92 | 92 | 92 | 794880
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | [10 empty] | 75 | 73 | 68 | 67 | 58 | 58 | 58 | 0 | [8 empty] | 454773
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 16 | 0 | [14 empty] | 16 |  | 64 | 80 | 80 | 96 | 110 | 110 | 110 | 689184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 95 | 85 | 86 | 86 | 53 | 36 | 34 | 34 | 35 | 35 | 39 | 93 | 73 | 74 | 74 | 74 | 54 |  | 96 | 96 | 96 | 96 | 96 | 97 | 96 | 1756523
| Bhola 225 MW CCPP | 68 | 67 | 66 | 69 | 69 | 65 | 67 | 67 | 67 | 64 | 67 | 64 | 60 | 65 | 64 | 65 | 66 | 66 |  | 67 | 67 | 67 | 67 | 66 | 66 | 58 | 1573000
140 | Bhola 33 MW PP (Venture) | 25 | 26 | 24 | 24 | 23 | 20 | 18 | 17 | 16 | 20 | 21 | 22 | 23 | 26 | 25 | 23 | 23 | 27 |  | 33 | 34 | 34 | 33 | 34 | 33 | 32 | 589768
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 10 | 100 | 90 | 100 | 100 | 100 | 50 | 506880
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 0 | [17 empty] | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 214500
143 | Gopalganj 100 MW Peaking PP | [16 empty] | 2 | 9 |  | 6 | 6 | 2 |  |  |  |  | 17408
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 832 | 832 | 832 | 833 | 832 | 833 | 833 | 833 | 832 | 643 | 643 | 643 | 643 | 643 | 643 | 643 | 643 | 642 |  | 643 | 688 | 832 | 832 | 833 | 833 | 832 | 18157091
147 | Bheramara 410 MW CCPP | 190 | 220 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 375 | 400 | 400 | 365 | 330 | 310 | 285 | 270 | 270 |  | 285 | 285 | 290 | 295 | 310 | 325 | 340 | 7125408
148 | Payra 1320 MW | 560 | 530 | 460 | 420 | 420 | 400 | 380 | 380 | 380 | 380 | 420 | 420 | 420 | 420 | 430 | 440 | 440 | 440 |  | 500 | 570 | 570 | 570 | 570 | 570 | 570 | 12089700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 3684900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 185 | 166 | 163 | 173 | 175 | 178 | 204 | 206 | 200 | 196 | 162 |  | 153 | 197 | 197 | 199 | 200 | 204 | 206 | 4323309
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 147 | 156 | 161 | 172 | 187 | 201 | 177 | 182 | 185 | 185 | 183 |  | 175 | 170 | 168 | 163 | 165 | 170 | 172 | 4197136
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 302 | 302 | 302 | 301 | 335 | 310 | 304 | 302 | 364 | 370 | 372 | 376 | 392 | 404 | 404 | 380 | 382 | 346 |  | 396 | 360 | 387 | 364 | 370 | 372 | 380 | 8511700
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 10 | 18 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 324000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 140652
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 30 |  | 34 | 33 | 33 | 33 | 33 |  |  | 145294
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 43 | 24 | 52 | 52 | 52 | 24 |  | 24 | 43 | 43 | 43 | 43 | 43 | 43 | 462720
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 3 |  | 90 | 99 | 99 | 99 | 92 |  |  | 434256
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 16 | 54 | 92 | 94 | 94 | 94 | 50 | 50 |  | 85 | 94 | 94 | 94 | 94 | 94 | 94 | 1138080
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 35 | 100 | 113 | 113 | 113 | 113 | 50 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1219584
173 | Rangpur 20 MW GTPP | [17 empty] | 0 |  | 0 |  | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | [19 empty] | 8 |  |  | 5 | 5 | 5 |  | 20000
176 | Rangpur 113 MW PP (Confidence) | [10 empty] | 45 | 50 | 98 | 70 | 70 | 70 | 50 | 50 |  | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 1148160
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 5 | 5 | 4 | 3 | 2 | 1 | 0 | [8 empty] | 34603
178
178