## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-14 | Wednesday
|  |  | Date (day): | 2021-04-14 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14754.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15498 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-13 | 2021-04-14 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 103 | 103 | 103
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 180 | 160 | 280 | 280 | 80 |  | Dust in the gas line
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 260 | 260 | 260 | 190 |  | Dust in the gas line
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 93 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 240 | 235 | 235 | 70 |  | Dust in the gas line
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 50 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 46 | 82 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 180 | 180 | 180
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 96 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 211 | 221 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 132 | 133 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 28 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 38 | 50 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 232 | 268 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 256 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 101 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 3088 | 3581 | 3636 | 3856 | 911 | 990
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 70 | 70 | 70 | 70 | 160 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 40 | 230 | 230 | 230
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 50 | 100
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 82 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 98 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 31 | 25 | 35
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 57 | 84 | 100 | 100
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 249 | 125 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 57 | 57 | 60 | 60 |  | 56 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1025 | 1257 | 1633 | 1671 | 520 | 171
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 188 | 208 | 225 | 225
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 300 | 360 | 360 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 300 | 300 | 300 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 47 | 50 | 50 | 50
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 51 | 50 | 50 |  | 113 | ST Under S/D.
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 154 | 154 | 170 | 170 |  | 30 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 146 | 170 | 157 | 188
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 37 | 37 | 36 | 36 |  | 18 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1646 | 1969 | 1982 | 2163 | 469 | 166
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 99 | 100 | 150 | 150 | 52 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 17 | 17 |  | 5 | Engine problem
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 41 | 57 | 56 | 56 |  | 39 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 160 | 180 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 49 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 504 | 493 | 611.6 | 560 | 52 | 44
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Engine problem
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 110 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 310 | 326 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 27 | 50 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 33 | 33 |  | 33 | GT-9 Under maint.
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 69 | 78 | 75 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 20/04/2021
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 163 | 200 | 220
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 320 | 300 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 345 | 368 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 8 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 331 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1850 | 1896 | 2133 | 2156 | 0 | 225
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 769 | 843 | 858 | 858
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 19 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 315 | 250 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 33 | 32 | 33 |  | 8 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 91 | 92 | 92 | 92 |  | 13 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1294 | 1436 | 1711 | 1998 | 0 | 120
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 67 | 70 | 70 |  | 124 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 58 | 96 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 500 | 610 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 4 | 4 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 644 | 975 | 1080 | 1080 | 0 | 124
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 10 | 43 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 5 | 42 | 35 | 35
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 31
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 80 | 120 | 120 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 212 | 174 | 180 | 200
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 140 | 176 | 200 | 200
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 372 | 394 | 400 | 400
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 33
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 96 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 1035 | 1363 | 1617 | 1671 | 271 | 9
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 71 | 75 | 70 | 70
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 261 | 338 | 351 | 343 | 124 | 115
|  | Total |  |  |  |  | 21967 | 21219 | 11347 | 13308 | 14754.6 | 15498 | 2347 | 1964
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10843.0868 | 12717 | 14099.3574 | 14809.7435
| A. |  | 2021-04-13 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13308 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10030 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13308 | MW
| 3 | Day peak Generation : |  |  | 11347 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12717 | MW
| 4 | Evening peak Generation : |  |  | 13308 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 272.1288 | MKWHr | By Solar | 0.76253 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 141.4173 | MKWHr |  | By Oil: | 85.5753 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.8061 | MKWHr |  | By Hydro: | 1.676 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2347 | MW | Dhaka | 4246 | 4246 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1964 | MW | Chittagong | 1338 | 1338 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4311 | MW | Khulna | 1639 | 1639 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1165.48 | MMCFD |  |  | Rajshahi | 1428 | 1428 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 152731068.286 | ii) Oil : | Taka | 651703522.44 | Comilla | 1301 | 1301 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 93652596.16 | Total | Taka | 898087186.886 | Mymensingh | 1056 | 1056 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.22 | MKWHr. | Sylhet | 493 | 493 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -390 | MW (E to W) at | 21:00 | hrs | Barisal | 383 | 383 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -440 | MW at | 22:00 | hrs | Rangpur | 833 | 833 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.9° C |  |  | Total | 12717 | 12717 |  | 0
| B. |  | 2021-04-14 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 40.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15498 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 2298 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 269.9204 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9531 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.3338 | MKWHr. | ii) HVDC Flow at Peak Time |  | 843 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5578 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 21:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.92 |  | (b) Today: | 80.64 |  | (c) Rule Curve: |  | 85.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-13
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 258 |  | 0 | 240 | 230 | 93 | 0 | 55 | 221 | 0 | 185 | 84 | 102 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 150 | 0 | 130 | 0 |  | 24 | 0 | 83 | 0 | 91 | 50 | 20 | 38 | 110 | 0 | 0 | 310 | 280 | 204 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 160 | 140 | 57 | 17 | 0 | 42 | 43 | 52 | 0 | 130 | 328 | 32 | 78 | 0 | 163 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 283 | 0 | 0 | 174 | 0 | 149 | 0 | 100 | 172 | 0 | 340 | 109 | 105 | 0 | 0 | 143 | 54 | 0 | 23 | 113 | 100 | 320 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 723 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 8 | 0 | 32 | 68 | 34 | 99 | 0 | 0 | 0 | 50 | 7 | 100 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 135 | 0 | 190 | 0 | 95 | 100 | 201 | 0 | 418 | 92 | 0 | 113 | 0 | 105 | 0 | 0 | 113 | 590 | 0 | 0 | 0 |  | 8346 | 3917 | 12263 | 4470 | 723 | 1836 | 3808 | 815 | 70 | 381 | 160 | 0 | 0 | 81.02
2:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 264 |  | 0 | 250 | 230 | 91 | 0 | 55 | 226 | 0 | 150 | 70 | 102 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 151 | 0 | 130 | 0 |  | 24 | 0 | 34 | 0 | 63 | 50 | 20 | 38 | 110 | 0 | 0 | 310 | 280 | 213 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 156 | 139 | 57 | 17 | 0 | 43 | 43 | 52 | 0 | 130 | 326 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 290 | 16 | 7 | 0 | 283 | 0 | 0 | 174 | 0 | 149 | 0 | 100 | 172 | 0 | 340 | 115 | 105 | 0 | 0 | 126 | 54 | 0 | 0 | 113 | 100 | 320 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 722 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 66 | 33 | 96 | 0 | 0 | 0 | 0 | 7 | 94 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 77 | 0 | 150 | 0 | 0 | 135 | 0 | 190 | 0 | 97 | 60 | 201 | 0 | 418 | 92 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 590 | 0 | 0 | 0 |  | 8035 | 3816 | 11851 | 4416 | 722 | 1843 | 3588 | 817 | 70 | 239 | 156 | 0 | 0 | 81
3:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 275 |  | 0 | 250 | 230 | 91 | 0 | 55 | 223 | 0 | 185 | 70 | 102 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 151 | 0 | 130 | 0 |  | 24 | 0 | 17 | 0 | 0 | 30 | 20 | 38 | 110 | 0 | 0 | 315 | 285 | 209 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 154 | 139 | 57 | 17 | 0 | 43 | 43 | 52 | 0 | 130 | 326 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 205 | 0 | 0 | 174 | 0 | 149 | 0 | 100 | 172 | 0 | 339 | 115 | 0 | 0 | 0 | 52 | 54 | 0 | 0 | 113 | 100 | 350 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 723 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 67 | 32 | 48 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 77 | 0 | 150 | 0 | 0 | 135 | 0 | 188 | 0 | 97 | 30 | 201 | 0 | 419 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 590 | 0 | 0 | 0 |  | 7725 | 3643 | 11368 | 4480 | 723 | 1863 | 3169 | 817 | 70 | 92 | 154 | 0 | 0 | 80.98
4:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 280 |  | 0 | 250 | 230 | 93 | 0 | 55 | 227 | 0 | 185 | 70 | 102 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 152 | 0 | 130 | 0 |  | 24 | 0 | 17 | 0 | 0 | 25 | 20 | 38 | 110 | 0 | 0 | 310 | 280 | 199 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 152 | 129 | 57 | 17 | 0 | 43 | 43 | 52 | 0 | 130 | 328 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 145 | 0 | 0 | 175 | 0 | 149 | 0 | 100 | 172 | 0 | 341 | 85 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 320 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 723 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 16 | 68 | 29 | 32 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 78 | 0 | 150 | 0 | 0 | 135 | 0 | 187 | 0 | 97 | 0 | 201 | 0 | 391 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 590 | 0 | 0 | 0 |  | 7549 | 3550 | 11099 | 4445 | 723 | 1837 | 2979 | 818 | 70 | 75 | 152 | 0 | 0 | 80.96
5:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 282 |  | 0 | 250 | 230 | 93 | 0 | 55 | 225 | 0 | 180 | 70 | 58 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 152 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 38 | 110 | 0 | 0 | 310 | 280 | 194 | 8 | 0 | 26 | 51 | 0 | 0 | 0 | 0 | 25 | 22 | 5 | 33 | 20 | 148 | 141 | 57 | 17 | 0 | 44 | 43 | 52 | 0 | 130 | 326 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 45 | 0 | 0 | 166 | 0 | 149 | 0 | 100 | 172 | 0 | 340 | 65 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 343 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 723 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 27 | 16 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 79 | 0 | 150 | 0 | 0 | 135 | 0 | 198 | 0 | 96 | 0 | 156 | 0 | 407 | 92 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 590 | 0 | 0 | 0 |  | 7325 | 3499 | 10824 | 4416 | 723 | 1858 | 2748 | 819 | 70 | 42 | 148 | 0 | 0 | 80.94
6:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 272 |  | 0 | 250 | 230 | 75 | 0 | 55 | 180 | 0 | 120 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 100 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 38 | 110 | 0 | 0 | 310 | 280 | 191 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 8 | 22 | 5 | 33 | 20 | 134 | 143 | 41 | 17 | 0 | 44 | 43 | 52 | 0 | 110 | 328 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 275 | 16 | 5 | 0 | 45 | 0 | 0 | 165 | 0 | 149 | 1 | 100 | 172 | 0 | 340 | 45 | 0 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 322 | 104 | 1 | 90 | 57 | 0 | 32 | 0 |  | 765 | 0 | 260 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 27 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 77 | 0 | 150 | 0 | 0 | 100 | 0 | 188 | 0 | 97 | 0 | 168 | 0 | 334 | 92 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 560 | 0 | 0 | 0 |  | 6870 | 3385 | 10255 | 4219 | 765 | 1726 | 2542 | 787 | 70 | 10 | 134 | 2 | 0 | 80.92
7:00 | 0 | 0 | 0 | 0 | 300 | 104 | 0 | 0 | 245 |  | 0 | 260 | 230 | 33 | 0 | 47 | 180 | 0 | 120 | 70 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 78 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 30 | 110 | 0 | 0 | 310 | 295 | 184 | 8 | 0 | 26 | 52 | 0 | 0 | 0 | 0 | 8 | 22 | 2 | 33 | 21 | 124 | 134 | 37 | 17 | 0 | 43 | 43 | 52 | 0 | 110 | 325 | 33 | 78 | 0 | 163 | 18 | 0 | 9 | 275 | 16 | 5 | 0 | 45 | 0 | 0 | 165 | 0 | 149 | 4 | 100 | 172 | 0 | 340 | 45 | 0 | 0 | 1 | 16 | 54 | 0 | 0 | 110 | 100 | 336 | 104 | 7 | 90 | 57 | 0 | 0 | 5 |  | 765 | 0 | 280 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 69 | 26 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 77 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 73 | 0 | 187 | 0 | 368 | 92 | 0 | 113 | 0 | 107 | 0 | 1 | 113 | 480 | 37 | 0 | 0 |  | 6748 | 3282 | 10030 | 4134 | 765 | 1749 | 2453 | 707 | 70 | 10 | 124 | 18 | 0 | 80.9
8:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 228 |  | 0 | 260 | 250 | 47 | 0 | 55 | 224 | 0 | 95 | 76 | 50 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 30 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 25 | 41 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 25 | 20 | 4 | 90 | 0 | 0 | 310 | 285 | 202 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 8 | 22 | 2 | 33 | 21 | 120 | 132 | 40 | 17 | 1 | 43 | 43 | 52 | 0 | 110 | 328 | 33 | 75 | 0 | 163 | 18 | 0 | 0 | 290 | 8 | 5 | 0 | 45 | 0 | 0 | 163 | 0 | 149 | 9 | 100 | 170 | 0 | 401 | 65 | 17 | 0 | 1 | 32 | 54 | 0 | 0 | 110 | 100 | 320 | 104 | 20 | 124 | 57 | 0 | 0 | 11 |  | 808 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 221 | 0 | 52 | 0 | 140 | 0 | 329 | 92 | 0 | 113 | 0 | 104 | 0 | 2 | 113 | 490 | 4 | 0 | 0 |  | 6918 | 3230 | 10148 | 4144 | 808 | 1607 | 2602 | 711 | 70 | 42 | 120 | 44 | 0 | 80.88
9:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 218 |  | 0 | 260 | 230 | 81 | 0 | 55 | 219 | 0 | 95 | 92 | 102 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 28 | 25 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 42 | 0 | 130 | 0 |  | 24 | 0 | 0 | 10 | 0 | 38 | 20 | 2 | 90 | 0 | 0 | 335 | 305 | 190 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 34 | 22 | 2 | 33 | 20 | 126 | 117 | 40 | 17 | 2 | 42 | 43 | 52 | 0 | 110 | 310 | 31 | 75 | 0 | 163 | 18 | 0 | 0 | 290 | 8 | 5 | 0 | 129 | 0 | 0 | 163 | 0 | 149 | 14 | 100 | 155 | 0 | 362 | 75 | 35 | 0 | 3 | 100 | 54 | 0 | 0 | 110 | 100 | 350 | 104 | 33 | 162 | 57 | 0 | 0 | 18 |  | 807 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 66 | 17 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 221 | 0 | 51 | 0 | 140 | 0 | 369 | 92 | 0 | 113 | 0 | 50 | 0 | 4 | 113 | 500 | 5 | 0 | 0 |  | 7192 | 3223 | 10415 | 4146 | 807 | 1629 | 2802 | 720 | 70 | 41 | 126 | 74 | 0 | 80.86
10:00 | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 0 | 200 |  | 0 | 260 | 230 | 91 | 0 | 55 | 214 | 0 | 155 | 100 | 102 | 32 | 2 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 29 | 28 | 25 | 3 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 24 | 0 | 0 | 88 | 6 | 44 | 17 | 2 | 80 | 0 | 0 | 305 | 320 | 185 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 2 | 33 | 20 | 124 | 100 | 32 | 17 | 2 | 43 | 43 | 11 | 0 | 110 | 308 | 31 | 75 | 0 | 163 | 18 | 0 | 8 | 320 | 8 | 5 | 0 | 172 | 0 | 0 | 160 | 0 | 141 | 18 | 100 | 155 | 0 | 364 | 115 | 78 | 0 | 3 | 151 | 54 | 0 | 34 | 110 | 100 | 350 | 104 | 44 | 162 | 57 | 0 | 16 | 25 |  | 841 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 32 | 66 | 18 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 217 | 0 | 51 | 0 | 140 | 0 | 370 | 92 | 0 | 113 | 0 | 35 | 0 | 5 | 113 | 480 | 4 | 0 | 0 |  | 7514 | 3253 | 10767 | 4149 | 841 | 1606 | 3138 | 701 | 70 | 41 | 124 | 97 | 0 | 80.84
11:00 | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 191 |  | 0 | 260 | 290 | 93 | 0 | 42 | 214 | 0 | 150 | 100 | 102 | 64 | 42 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 28 | 28 | 25 | 18 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 24 | 0 | 0 | 80 | 35 | 44 | 17 | 2 | 80 | 0 | 0 | 310 | 320 | 187 | 8 | 0 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 21 | 2 | 33 | 20 | 136 | 100 | 41 | 17 | 2 | 42 | 43 | 11 | 0 | 110 | 312 | 30 | 73 | 0 | 164 | 18 | 0 | 0 | 310 | 8 | 5 | 0 | 229 | 0 | 0 | 160 | 0 | 131 | 10 | 90 | 154 | 0 | 334 | 115 | 90 | 0 | 4 | 216 | 54 | 0 | 34 | 110 | 90 | 350 | 104 | 49 | 162 | 57 | 0 | 37 | 28 |  | 842 | 0 | 290 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 32 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 34 | 0 | 20 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 214 | 0 | 52 | 0 | 140 | 0 | 371 | 92 | 0 | 94 | 0 | 35 | 0 | 6 | 113 | 490 | 5 | 0 | 0 |  | 7764 | 3234 | 10998 | 4118 | 842 | 1582 | 3368 | 710 | 70 | 73 | 136 | 99 | 0 | 80.83
12:00 | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 0 | 180 |  | 0 | 260 | 295 | 93 | 0 | 50 | 211 | 0 | 180 | 100 | 102 | 132 | 46 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 28 | 25 | 38 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 21 | 0 | 0 | 90 | 57 | 45 | 17 | 2 | 80 | 0 | 0 | 305 | 320 | 188 | 0 | 0 | 26 | 47 | 0 | 0 | 0 | 0 | 43 | 21 | 2 | 33 | 20 | 146 | 99 | 41 | 17 | 2 | 42 | 43 | 27 | 0 | 110 | 310 | 31 | 69 | 0 | 164 | 18 | 0 | 8 | 320 | 8 | 5 | 0 | 232 | 0 | 0 | 160 | 0 | 131 | 19 | 100 | 154 | 0 | 345 | 115 | 90 | 0 | 5 | 249 | 54 | 0 | 114 | 110 | 90 | 350 | 104 | 49 | 144 | 57 | 0 | 37 | 31 |  | 769 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 32 | 64 | 18 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 212 | 0 | 58 | 0 | 140 | 0 | 372 | 91 | 0 | 113 | 0 | 34 | 0 | 6 | 113 | 500 | 4 | 0 | 0 |  | 8113 | 3234 | 11347 | 4172 | 769 | 1591 | 3615 | 721 | 70 | 151 | 146 | 112 | 0 | 80.82
13:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 180 |  | 0 | 260 | 230 | 97 | 0 | 55 | 210 | 0 | 175 | 100 | 102 | 132 | 48 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 28 | 25 | 51 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 19 | 0 | 51 | 90 | 77 | 45 | 20 | 2 | 80 | 0 | 0 | 280 | 295 | 210 | 0 | 0 | 26 | 47 | 0 | 0 | 0 | 8 | 43 | 21 | 2 | 33 | 20 | 144 | 99 | 41 | 17 | 2 | 41 | 43 | 52 | 0 | 110 | 328 | 31 | 72 | 0 | 164 | 18 | 0 | 8 | 310 | 8 | 5 | 0 | 239 | 0 | 0 | 157 | 0 | 130 | 19 | 100 | 155 | 0 | 368 | 115 | 92 | 0 | 4 | 252 | 54 | 0 | 114 | 110 | 100 | 320 | 104 | 45 | 144 | 57 | 0 | 21 | 29 |  | 838 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 5 | 0 | 32 | 64 | 20 | 0 | 0 | 0 | 0 | 50 | 6 | 52 | 0 | 0 | 27 | 43 | 0 | 19 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 213 | 0 | 63 | 0 | 140 | 0 | 335 | 91 | 0 | 94 | 0 | 34 | 0 | 6 | 113 | 510 | 3 | 0 | 0 |  | 8165 | 3385 | 11550 | 4152 | 838 | 1583 | 3596 | 731 | 70 | 331 | 144 | 105 | 0 | 80.81
14:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 176 |  | 0 | 260 | 290 | 98 | 0 | 55 | 160 | 0 | 150 | 100 | 102 | 129 | 47 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 28 | 25 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 18 | 0 | 45 | 90 | 86 | 50 | 20 | 2 | 80 | 0 | 0 | 280 | 295 | 207 | 8 | 50 | 26 | 45 | 0 | 0 | 0 | 50 | 52 | 21 | 2 | 33 | 20 | 158 | 98 | 41 | 17 | 2 | 41 | 43 | 51 | 0 | 110 | 325 | 31 | 71 | 0 | 163 | 18 | 0 | 8 | 280 | 8 | 5 | 0 | 250 | 0 | 0 | 157 | 0 | 131 | 17 | 100 | 154 | 0 | 370 | 115 | 105 | 0 | 4 | 249 | 54 | 0 | 114 | 110 | 100 | 320 | 104 | 38 | 144 | 57 | 0 | 37 | 26 |  | 841 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 7 | 0 | 32 | 63 | 20 | 0 | 0 | 0 | 0 | 50 | 7 | 54 | 0 | 0 | 30 | 43 | 0 | 19 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 216 | 0 | 72 | 0 | 140 | 0 | 337 | 91 | 0 | 94 | 0 | 34 | 0 | 6 | 113 | 520 | 3 | 0 | 0 |  | 8254 | 3423 | 11677 | 4125 | 841 | 1564 | 3714 | 740 | 70 | 372 | 158 | 93 | 0 | 80.8
15:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 170 |  | 0 | 260 | 290 | 98 | 0 | 55 | 208 | 0 | 175 | 100 | 102 | 130 | 49 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 28 | 25 | 50 | 0 | 0 | 70 | 0 | 0 | 0 | 45 | 0 | 130 | 0 |  | 23 | 0 | 48 | 90 | 90 | 50 | 17 | 2 | 80 | 0 | 0 | 335 | 320 | 202 | 8 | 52 | 26 | 44 | 0 | 0 | 0 | 42 | 52 | 21 | 2 | 33 | 20 | 160 | 97 | 41 | 17 | 1 | 40 | 43 | 50 | 0 | 110 | 321 | 30 | 72 | 0 | 163 | 18 | 0 | 8 | 300 | 8 | 5 | 0 | 250 | 0 | 0 | 155 | 0 | 132 | 13 | 100 | 154 | 0 | 398 | 115 | 105 | 0 | 3 | 250 | 54 | 0 | 114 | 110 | 100 | 350 | 104 | 31 | 144 | 58 | 0 | 36 | 20 |  | 841 | 0 | 335 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 32 | 63 | 17 | 0 | 0 | 0 | 0 | 50 | 13 | 54 | 0 | 0 | 30 | 43 | 0 | 18 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 203 | 0 | 92 | 0 | 185 | 0 | 382 | 91 | 0 | 113 | 0 | 34 | 0 | 4 | 113 | 550 | 4 | 0 | 0 |  | 8460 | 3582 | 12042 | 4375 | 841 | 1639 | 3744 | 771 | 70 | 370 | 160 | 72 | 0 | 80.79
16:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 0 | 170 |  | 0 | 260 | 250 | 100 | 0 | 55 | 210 | 0 | 148 | 100 | 102 | 130 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 25 | 28 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 71 | 0 | 130 | 0 |  | 22 | 0 | 81 | 79 | 78 | 50 | 17 | 2 | 80 | 0 | 0 | 280 | 300 | 206 | 8 | 52 | 26 | 40 | 0 | 0 | 0 | 42 | 52 | 20 | 5 | 33 | 20 | 164 | 97 | 41 | 17 | 1 | 40 | 42 | 50 | 0 | 110 | 324 | 30 | 71 | 0 | 163 | 18 | 0 | 8 | 300 | 8 | 5 | 0 | 255 | 0 | 0 | 155 | 0 | 138 | 8 | 100 | 154 | 0 | 370 | 115 | 105 | 0 | 1 | 250 | 54 | 0 | 62 | 110 | 100 | 320 | 104 | 5 | 132 | 58 | 0 | 37 | 12 |  | 841 | 0 | 350 | 0 | 84 | 0 | 0 | 0 | 15 | 0 | 8 | 65 | 24 | 16 | 0 | 0 | 0 | 50 | 39 | 54 | 0 | 0 | 29 | 43 | 20 | 18 | 0 | 0 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 204 | 0 | 93 | 0 | 200 | 0 | 362 | 89 | 0 | 113 | 0 | 97 | 0 | 3 | 113 | 570 | 4 | 0 | 0 |  | 8190 | 3725 | 11915 | 4276 | 841 | 1622 | 3661 | 791 | 70 | 460 | 164 | 30 | 0 | 80.78
17:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 170 |  | 0 | 260 | 240 | 70 | 0 | 55 | 214 | 0 | 145 | 85 | 64 | 130 | 40 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 25 | 28 | 25 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 96 | 0 | 130 | 0 |  | 22 | 0 | 82 | 30 | 64 | 50 | 17 | 16 | 80 | 0 | 0 | 280 | 300 | 207 | 8 | 50 | 26 | 43 | 0 | 0 | 0 | 50 | 25 | 21 | 5 | 33 | 20 | 142 | 100 | 41 | 17 | 0 | 41 | 42 | 53 | 0 | 110 | 325 | 31 | 72 | 0 | 163 | 18 | 0 | 8 | 295 | 8 | 5 | 0 | 265 | 0 | 0 | 164 | 0 | 132 | 3 | 50 | 154 | 0 | 368 | 115 | 70 | 0 | 1 | 160 | 54 | 0 | 52 | 65 | 100 | 320 | 104 | 11 | 139 | 58 | 0 | 36 | 5 |  | 842 | 0 | 335 | 0 | 86 | 0 | 0 | 0 | 15 | 0 | 8 | 65 | 21 | 16 | 0 | 0 | 0 | 50 | 39 | 54 | 0 | 0 | 29 | 25 | 27 | 19 | 0 | 0 | 70 | 0 | 150 | 0 | 0 | 48 | 0 | 209 | 0 | 62 | 0 | 200 | 0 | 357 | 53 | 0 | 70 | 0 | 113 | 0 | 2 | 70 | 530 | 4 | 0 | 0 |  | 7764 | 3569 | 11333 | 4344 | 842 | 1601 | 3086 | 750 | 70 | 476 | 142 | 22 | 0 | 80.77
18:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 165 |  | 0 | 260 | 220 | 65 | 0 | 55 | 180 | 0 | 65 | 70 | 64 | 130 | 40 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 26 | 28 | 33 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 161 | 0 | 100 | 0 |  | 24 | 0 | 83 | 30 | 64 | 50 | 20 | 12 | 80 | 0 | 0 | 280 | 300 | 180 | 8 | 52 | 26 | 47 | 0 | 0 | 0 | 50 | 25 | 22 | 5 | 33 | 20 | 112 | 117 | 49 | 17 | 0 | 41 | 43 | 33 | 0 | 110 | 328 | 32 | 50 | 0 | 163 | 18 | 0 | 8 | 270 | 8 | 8 | 0 | 265 | 0 | 0 | 175 | 0 | 147 | 0 | 50 | 154 | 0 | 368 | 115 | 70 | 0 | 0 | 105 | 54 | 0 | 52 | 65 | 100 | 321 | 104 | 2 | 154 | 58 | 0 | 36 | 1 |  | 841 | 0 | 315 | 0 | 70 | 0 | 0 | 0 | 15 | 9 | 8 | 57 | 18 | 36 | 0 | 0 | 0 | 50 | 39 | 54 | 0 | 0 | 29 | 25 | 26 | 21 | 0 | 5 | 77 | 0 | 150 | 0 | 0 | 100 | 0 | 165 | 0 | 63 | 0 | 150 | 0 | 318 | 53 | 0 | 70 | 0 | 70 | 0 | 0 | 35 | 520 | 0 | 0 | 0 |  | 7557 | 3389 | 10946 | 4214 | 841 | 1486 | 2988 | 747 | 70 | 485 | 112 | 3 | 0 | 80.76
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 165 |  | 0 | 260 | 240 | 79 | 0 | 55 | 216 | 0 | 150 | 80 | 102 | 130 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 20 | 33 | 25 | 26 | 0 | 0 | 70 | 0 | 0 | 15 | 227 | 0 | 130 | 0 |  | 24 | 0 | 83 | 96 | 81 | 50 | 20 | 20 | 100 | 0 | 0 | 300 | 300 | 210 | 8 | 52 | 26 | 48 | 0 | 0 | 0 | 50 | 29 | 22 | 5 | 33 | 20 | 164 | 110 | 49 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 325 | 32 | 78 | 0 | 163 | 18 | 0 | 8 | 290 | 8 | 11 | 100 | 268 | 110 | 50 | 177 | 52 | 149 | 0 | 100 | 154 | 0 | 369 | 115 | 80 | 0 | 0 | 105 | 54 | 0 | 114 | 110 | 100 | 320 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 842 | 0 | 295 | 0 | 85 | 0 | 0 | 0 | 15 | 9 | 33 | 67 | 34 | 88 | 0 | 0 | 0 | 43 | 37 | 94 | 0 | 0 | 30 | 35 | 26 | 21 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 120 | 0 | 167 | 0 | 92 | 38 | 167 | 0 | 359 | 92 | 20 | 93 | 0 | 113 | 0 | 0 | 90 | 560 | 0 | 0 | 1 |  | 8689 | 3897 | 12586 | 4516 | 842 | 1646 | 4045 | 786 | 70 | 517 | 164 | 0 | 0 | 80.73
19:30 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 161 |  | 0 | 260 | 240 | 100 | 0 | 55 | 219 | 0 | 150 | 100 | 102 | 130 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 50 | 0 | 0 | 70 | 0 | 0 | 25 | 229 | 0 | 130 | 0 |  | 24 | 0 | 83 | 98 | 85 | 50 | 20 | 22 | 100 | 0 | 0 | 300 | 300 | 210 | 8 | 51 | 26 | 48 | 0 | 0 | 0 | 50 | 52 | 22 | 5 | 33 | 20 | 164 | 106 | 49 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 325 | 32 | 78 | 0 | 163 | 18 | 0 | 8 | 305 | 8 | 11 | 100 | 268 | 110 | 50 | 178 | 52 | 149 | 0 | 100 | 154 | 0 | 369 | 115 | 105 | 0 | 0 | 105 | 54 | 0 | 114 | 113 | 100 | 338 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 841 | 0 | 270 | 0 | 92 | 0 | 0 | 0 | 21 | 9 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 34 | 96 | 0 | 0 | 30 | 43 | 26 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 130 | 0 | 190 | 0 | 94 | 100 | 198 | 0 | 394 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 600 | 0 | 0 | 35 |  | 8877 | 4172 | 13049 | 4582 | 841 | 1696 | 4349 | 825 | 70 | 522 | 164 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 160 |  | 0 | 260 | 245 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 102 | 133 | 82 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 50 | 0 | 0 | 70 | 0 | 0 | 25 | 229 | 0 | 130 | 0 |  | 24 | 0 | 83 | 98 | 84 | 50 | 20 | 28 | 100 | 0 | 0 | 300 | 300 | 210 | 8 | 51 | 26 | 49 | 0 | 0 | 0 | 50 | 47 | 22 | 11 | 33 | 20 | 160 | 100 | 57 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 326 | 32 | 77 | 0 | 163 | 18 | 0 | 8 | 300 | 16 | 11 | 100 | 268 | 110 | 50 | 177 | 52 | 149 | 0 | 100 | 154 | 0 | 368 | 115 | 105 | 0 | 0 | 105 | 54 | 0 | 114 | 113 | 100 | 327 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 842 | 0 | 270 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 43 | 94 | 0 | 0 | 31 | 43 | 26 | 21 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 100 | 0 | 191 | 0 | 94 | 100 | 194 | 0 | 395 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 600 | 21 | 0 | 35 |  | 8907 | 4169 | 13076 | 4580 | 842 | 1718 | 4359 | 825 | 70 | 522 | 160 | 0 | 0 | 80.74
21:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 160 |  | 0 | 260 | 240 | 100 | 0 | 55 | 221 | 0 | 180 | 96 | 102 | 133 | 82 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 0 | 70 | 0 | 0 | 25 | 230 | 0 | 130 | 0 |  | 24 | 0 | 83 | 98 | 84 | 50 | 20 | 31 | 100 | 0 | 0 | 300 | 300 | 208 | 8 | 51 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 170 | 100 | 57 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 326 | 32 | 78 | 0 | 163 | 18 | 0 | 8 | 300 | 16 | 11 | 150 | 268 | 256 | 50 | 180 | 101 | 149 | 0 | 100 | 154 | 0 | 368 | 115 | 105 | 0 | 0 | 125 | 54 | 0 | 114 | 113 | 100 | 331 | 104 | 0 | 162 | 57 | 0 | 37 | 0 |  | 843 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 42 | 96 | 0 | 0 | 31 | 43 | 26 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 174 | 0 | 96 | 100 | 176 | 0 | 394 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 610 | 4 | 0 | 54 |  | 9196 | 4112 | 13308 | 4517 | 843 | 1707 | 4643 | 835 | 70 | 523 | 170 | 0 | 0 | 80.73
22:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 160 |  | 0 | 260 | 240 | 100 | 0 | 55 | 221 | 0 | 180 | 100 | 102 | 133 | 83 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 230 | 0 | 130 | 0 |  | 24 | 0 | 83 | 98 | 85 | 50 | 20 | 34 | 100 | 0 | 0 | 305 | 300 | 172 | 8 | 52 | 26 | 30 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 172 | 101 | 57 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 326 | 32 | 78 | 0 | 164 | 18 | 0 | 8 | 300 | 16 | 11 | 150 | 270 | 257 | 50 | 181 | 101 | 149 | 0 | 100 | 154 | 0 | 366 | 115 | 105 | 0 | 0 | 125 | 54 | 0 | 114 | 113 | 100 | 351 | 104 | 0 | 162 | 57 | 0 | 36 | 0 |  | 843 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 35 | 99 | 0 | 0 | 30 | 43 | 26 | 21 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 80 | 0 | 159 | 0 | 95 | 100 | 159 | 0 | 394 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 4 | 0 | 54 |  | 9176 | 4062 | 13238 | 4445 | 843 | 1689 | 4653 | 848 | 70 | 518 | 172 | 0 | 0 | 80.72
23:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 161 |  | 0 | 260 | 245 | 100 | 0 | 55 | 223 | 0 | 180 | 100 | 102 | 133 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 229 | 0 | 130 | 0 |  | 24 | 0 | 83 | 90 | 85 | 50 | 20 | 38 | 100 | 0 | 0 | 300 | 295 | 182 | 8 | 50 | 26 | 30 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 158 | 104 | 57 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 333 | 32 | 78 | 0 | 164 | 18 | 0 | 8 | 305 | 16 | 11 | 150 | 275 | 210 | 50 | 181 | 101 | 149 | 0 | 100 | 154 | 0 | 367 | 115 | 105 | 0 | 0 | 125 | 54 | 0 | 114 | 113 | 100 | 350 | 104 | 0 | 162 | 57 | 0 | 37 | 0 |  | 843 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 18 | 0 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 33 | 99 | 0 | 0 | 30 | 43 | 26 | 21 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 80 | 0 | 149 | 0 | 95 | 100 | 153 | 0 | 372 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 4 | 0 | 35 |  | 9146 | 3977 | 13123 | 4420 | 843 | 1677 | 4592 | 848 | 70 | 515 | 158 | 0 | 0 | 80.71
24:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 167 |  | 0 | 260 | 235 | 94 | 0 | 55 | 223 | 0 | 175 | 100 | 102 | 133 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 0 | 70 | 0 | 0 | 25 | 229 | 0 | 130 | 0 |  | 24 | 0 | 83 | 90 | 83 | 50 | 20 | 38 | 80 | 0 | 0 | 260 | 265 | 201 | 8 | 48 | 26 | 30 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 156 | 120 | 57 | 17 | 0 | 43 | 43 | 50 | 0 | 110 | 332 | 32 | 78 | 0 | 163 | 18 | 0 | 9 | 295 | 16 | 11 | 150 | 273 | 205 | 50 | 173 | 102 | 149 | 0 | 100 | 170 | 0 | 367 | 115 | 105 | 0 | 0 | 125 | 54 | 0 | 114 | 113 | 100 | 320 | 104 | 0 | 162 | 56 | 0 | 37 | 0 |  | 843 | 0 | 175 | 0 | 99 | 0 | 0 | 0 | 18 | 0 | 33 | 68 | 34 | 96 | 0 | 0 | 0 | 43 | 34 | 100 | 0 | 0 | 30 | 43 | 27 | 21 | 0 | 11 | 76 | 0 | 149 | 0 | 0 | 80 | 0 | 145 | 0 | 95 | 100 | 152 | 0 | 350 | 93 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 36 | 0 | 35 |  | 9032 | 3947 | 12979 | 4298 | 843 | 1684 | 4563 | 847 | 70 | 518 | 156 | 0 | 0 | 80.7
KWH | 0 | 0 | 0 | 0 | 7149391 | 2416045 | 0 | 0 | 4976000 |  | 0 | 5979300 | 5900044 | 2105280 | 0 | 1315132 | 519382 | 0 | 3986000 | 2172480 | 2132352 | 2264640 | 984747 | 0 | 0 | 0 | 1283040 | 1125164 | 1268047 | 344340 | 600000 | 617940 | 743900 | 692400 | 654720 | 0 | 0 | 1676000 | 0 | 0 | 366682 | 2929083 | 0 | 3067034 | 0 |  | 566160 | 0 | 1031555 | 1205520 | 1225920 | 1053600 | 442272 | 506400 | 2313324 | 0 | 0 | 7674700 | 7233000 | 4755000 | 200727 | 487260 | 594288 | 1131840 | 0 | 0 | 0 | 516912 | 1035701 | 497772 | 159660 | 817400 | 514160 | 3557760 | 2701520 | 1147200 | 360000 | 14750 | 997000 | 1031880 | 1113000 | 0 | 2977036 | 7432000 | 774912 | 1785600 | 0 | 3918390 | 410000 | 0 | 170280 | 7360500 | 273936 | 165100 | 744192 | 5045779 | 1043927 | 288662 | 3976800 | 473305 | 3482928 | 122445 | 2318400 | 388848 | 0 | 8679000 | 2516400 | 1749600 | 0 | 31318 | 3138873 | 1299734 | 0 | 1476300 | 2730840 | 2420160 | 8063600 | 261690 | 336810 | 3680640 | 1377491 | 0 | 737280 | 213419 |  | 19333818 | 0 | 6920928 | 0 | 2106240 | 0 | 0 | 0 | 198720 | 16256 | 526875 | 1579000 | 632574 | 102048 | 0 | 0 | 0 | 612000 | 422426 | 1067768 | 0 | 0 | 329200 | 990720 | 229588 | 475200 | 0 | 167598 | 1786472 | 0 | 3664200 | 0 | 0 | 1599000 | 0 | 4826382 | 0 | 1936835 | 792960 | 4521764 | 0 | 9070781 | 2129280 | 25655 | 2604864 | 0 | 2077440 | 0 | 43792 | 2614560 | 14355400 | 124827 | 0 | 222000 |  | 184021619 | 88107171 | 272128790 | 100560316 | 19333818 | 40856945 | 78886280 | 19806072 | 1676000 | 6689065 | 3557760 | 762534 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7935824.01 | 3189179.4 | 0 | 0 | 5125280 |  | 0 | 6517437 | 6549048.84 | 15979075.2 | 0 | 11126016.72 | 540157.28 | 0 | 6895780 | 16358774.4 | 19447050.24 | 22284057.6 | 9079367.34 | 0 | 0 | 0 | 9366192 | 8697517.72 | 12502943.42 | 258255 | 450000 | 0 | 0 | 0 | 6331142.4 | 0 | 0 | 452520 | 0 | 0 | 3406475.78 | 3192700.47 | 0 | 5213957.8 | 0 |  | 0 | 0 | 10006083.5 | 11512716 | 10665504 | 8344512 | 557262.72 | 1504008 | 3423719.52 | 0 | 0 | 5679278 | 7233000 | 4374600 | 258937.83 | 560349 | 671545.44 | 1584576 | 0 | 0 | 0 | 5220811.2 | 9890944.55 | 632170.44 | 119745 | 1430450 | 385620 | 26683200 | 2863611.2 | 10416576 | 457200 | 235115 | 1635080 | 1651008 | 1981140 | 0 | 3393821.04 | 7729280 | 1526576.64 | 3410496 | 0 | 6778814.7 | 897900 | 0 | 347371.2 | 7434105 | 205452 | 125476 | 12658705.92 | 38146089.24 | 17725880.46 | 4826428.64 | 20679360 | 7913659.6 | 34272011.52 | 1431382.05 | 18894960 | 4219000.8 | 0 | 8071470 | 22949568 | 16533720 | 0 | 0 | 23729879.88 | 11320683.14 | 0 | 14733474 | 23403298.8 | 16118265.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 111362791.68 | 0 | 7266974.4 | 0 | 16555046.4 | 0 | 0 | 0 | 2084572.8 | 170362.88 | 5490037.5 | 1784270 | 980489.7 | 995988.48 | 0 | 0 | 0 | 6022080 | 4291848.16 | 9449746.8 | 0 | 0 | 3189948 | 9600076.8 | 2227003.6 | 912384 | 0 | 126871.686 | 10772426.16 | 0 | 19859964 | 0 | 0 | 1870830 | 0 | 6370824.24 | 0 | 2905252.5 | 13488249.6 | 5290463.88 | 0 | 8980073.19 | 22229683.2 | 436391.55 | 24720159.36 | 0 | 16120934.4 | 0 | 483901.6 | 19321598.4 | 63020206 | 0 | 0 | 0 |  | 640354646.25 | 398381450.966 | 1038736097.216 | 104206517.426 | 111362791.68 | 48524550.86 | 586757007.9 | 93652596.16 | 452520 | 64946514.54 | 26683200 | 2150398.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 0 | 180 |  | 0 | 260 | 295 | 93 | 0 | 50 | 211 | 0 | 180 | 100 | 102 | 132 | 46 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 28 | 25 | 38 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 130 | 0 |  | 21 | 0 | 0 | 90 | 57 | 45 | 17 | 2 | 80 | 0 | 0 | 305 | 320 | 188 | 0 | 0 | 26 | 47 | 0 | 0 | 0 | 0 | 43 | 21 | 2 | 33 | 20 | 146 | 99 | 41 | 17 | 2 | 42 | 43 | 27 | 0 | 110 | 310 | 31 | 69 | 0 | 164 | 18 | 0 | 8 | 320 | 8 | 5 | 0 | 232 | 0 | 0 | 160 | 0 | 131 | 19 | 100 | 154 | 0 | 345 | 115 | 90 | 0 | 5 | 249 | 54 | 0 | 114 | 110 | 90 | 350 | 104 | 49 | 144 | 57 | 0 | 37 | 31 |  | 769 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 32 | 64 | 18 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 212 | 0 | 58 | 0 | 140 | 0 | 372 | 91 | 0 | 113 | 0 | 34 | 0 | 6 | 113 | 500 | 4 | 0 | 0 |  | 11347 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 160 | 0 | 0 | 260 | 240 | 100 | 0 | 55 | 221 | 0 | 180 | 96 | 102 | 133 | 82 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 0 | 70 | 0 | 0 | 25 | 230 | 0 | 130 | 0 | 0 | 24 | 0 | 83 | 98 | 84 | 50 | 20 | 31 | 100 | 0 | 0 | 300 | 300 | 208 | 8 | 51 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 170 | 100 | 57 | 17 | 0 | 42 | 43 | 50 | 0 | 110 | 326 | 32 | 78 | 0 | 163 | 18 | 0 | 8 | 300 | 16 | 11 | 150 | 268 | 256 | 50 | 180 | 101 | 149 | 0 | 100 | 154 | 0 | 368 | 115 | 105 | 0 | 0 | 125 | 54 | 0 | 114 | 113 | 100 | 331 | 104 | 0 | 162 | 57 | 0 | 37 | 0 |  | 843 | 0 | 250 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 33 | 67 | 34 | 110 | 0 | 0 | 0 | 43 | 42 | 96 | 0 | 0 | 31 | 43 | 26 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 174 | 0 | 96 | 100 | 176 | 0 | 394 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 610 | 4 | 0 | 54 |  | 13308 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 280 | 0 | 0 | 260 | 235 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 230 | 0 | 130 | 0 | 0 | 22 |  | 85 | 100 | 100 | 50 | 22 | 35 | 135 | 0 | 0 | 360 | 300 | 225 | 8 | 50 | 26 | 50 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 188 | 150 | 56 | 17 | 0 | 42 | 43 | 51 | 0 | 163 | 330 | 33 | 78 | 0 | 220 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 170 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 60 | 0 | 36 |  |  | 858 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 70 | 33 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 31 | 43 | 33 | 22 | 0 | 11 | 70 | 0 | 150 | 10 | 0 | 120 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 92 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 0 | 280 | 0 | 0 | 260 | 235 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 25 | 52 | 0 | 0 | 70 | 0 | 0 | 25 | 230 | 0 | 130 | 0 | 0 | 22 |  | 82 | 100 | 100 | 50 | 22 | 25 | 135 | 0 | 0 | 360 | 300 | 225 | 8 | 50 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 150 | 56 | 17 | 1.6 | 42 | 43 | 51 | 0 | 163 | 330 | 33 | 75 | 0 | 200 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 170 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 60 | 0 | 36 | 30 |  | 858 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 70 | 33 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 0 | 30 | 43 | 0 | 22 | 0 | 11 | 70 | 0 | 150 | 10 | 0 | 120 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 92 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 0 | 280 | 0 | 0 | 260 | 235 | 0 | 0 | 12 | 223 | 0 | 75 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 50 | 22 | 25 | 26 | 33 |  | 0 | 0 | 0 | 70 | 0 | 0 | 8 | 230 | 0 | 130 | 0 | 0 | 6 | 0 | 0 | 10 | 0 | 0 | 20 | 41 | 80 | 0 | 0 | 260 | 265 | 193 | 8 | 50 | 26 | 52 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 19 | 120 | 153 | 40 | 19 | 1 | 42 | 43 | 44 | 0 | 110 | 332 | 32 | 75 | 0 | 163 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 149 | 9 | 100 | 172 | 0 | 367 | 0 | 34 | 0 | 2 | 0 | 54 | 0 | 0 | 46 | 100 | 335 | 54 | 19 | 17 | 57 | 0 | 0 | 11 | 0 | 843 | 0 | 190 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 76 | 0 | 149 | 0 | 0 | 80 | 0 | 165 | 0 | 84 | 0 | 176 | 0 | 340 | 0 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 440 | 48 | 0 | 0 | 0
199
| Minimum Generation |  | 10030 | 7:00
| Highest Generation |  | 13308 | 21:00
| Day Peak Generation |  | 11347 | 12:00
| Evening Peak Generation |  | 13308 | 21:00
| HVDC Max Flow |  | 843 | 21:00
| HVDC EvPeak Flow |  | 843 | 21:00
| Load factor L.F |  | 85.2%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-14
Till now the maximum generation is : - |  |  | 13377 MW | 21:00 | Hrs on | M90
The Summary of Yesterday's |  | 2021-04-13 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11347 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9531 | MW
Evening Peak Generation : |  | 13308 | MW Hour : | 21:00 | Available Max Generation : |  | 15498 | MW
E.P. Demand (at gen end) : |  | 13308 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 13308 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2298 | MW
Total Gen. (MKWH) : |  | 272.1288 | System Load Factor : | 85.2% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -440 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-14
Actual : | 80.64 | Ft.(MSL) , | Rule curve : | 85.8 | Ft.( MSL )
Gas Consumed : | Total = | 1165.48 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 152731068.286
: |  | Coal : | 93652596.16 | Oil : | 651703522.44 | Total : | 898087186.886
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4686.5377 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1599.0371 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1433.6384 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1295.752 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1170.7655 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 944.7798 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 521.3836 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 243.073 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 728.6941 |  |  | 0 | 0%
Total | 0 |  | 12623.6611 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Baghabari-71,100 MW
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
7) Ghorasal-3,4,5
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Cumilla(N)-Shahjibazar 230 kV Ckt-1 was under shut down from 10:22 to 12:30 for C/M.
b) Daudkandi 132/33 kV T-1 transformer was under shut down from 09:31 to 14:25 for C/M.
c) Faridpur 132/33 kV T-2 transformer was under shut down from 09:50 to 12:48 for C/M.
d) Feni-PHP 132 kV Ckt is under shutdown since 08:10 for D/W.
e) Gopalganj 132/33 kV T-1 transformer was under shut down from 08:31 to 18:36 for C/M.
f) Khulna(S)-Khulna(C) 132 kV Ckt-1 was under shut down from 08:39 to 10:10 for D/W.
g) Rangpur S/S-Rangpur Confidence 132 kV Ckt-1 was under shut down from 08:46 to 11:57 for C/M.
h) Mirpur 132/33 kV T-3 transformer was under shut down from 08:16 to 22:05 for C/M.
i) Sherpur 132/33 kV T-3 transformer was under shut down from 09:55 to 11:40 for C/M.
j) Rangpur S/S-Rangpur Confidence 132 kV Ckt-2 was under shut down from 12:40 to 15:17 for C/M.
k) Baghabari-Bhangura 132 kV Ckt-1 was under shut down from 10:10 to 18:01 for R/H.
l) Mohasthangarh 132/33 kV T-1 & T-2 transformers were under shut down from 09:46 to 12:10 for 33 kV |  |  |  |  | About 45 MW power interruption occurred under Mohasthangarh S/S
Bus maintenance. |  |  |  |  | area from 09:46 to 12:10.
m) Natore-Rajshahi 132 kV Ckt-1 tripped at 10:31 from both ends showing E/F at Natore end & Dist. at Rajshahi
end and was switched on at 10:56.
n) Chandpur CCPP GT was synchronized at 13:59.
o) Sikalbaha 225 MW ST was synchronized at 15:44.
p) Chattak-Sylhet 132 kV Ckt-2 was switched on at 15:20.
q) Aminbazar-Kaliakoir 230 kV Ckt-2 was under shut down from 15:41 to 21:23 for C/M.
r) Baghabari-Bhangura 132 kV Ckt-2 was charged at 19:01 from Baghabari end for the first time.
s) Sirajganj unit-1 was synchronized at 16:18.
t) Rajshahi(Old)-Rajshahi(New) 132 kV Ckt-1 was shut down at 07:12(14/04/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-13 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7149391 | Machine problem
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2416045
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under S/D due to dust in the gas line.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 160 | 4976000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 5979300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 2105280
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 5900044 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1315132
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 82 | 984747 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 344340
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3986000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 96 | 2172480
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 519382 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2132352
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1283040
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 2264640
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1125164
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1268047
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Engine problem
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1217940 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 743900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 692400 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 50 | 654720
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 268 | 5045779 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 256 | 1043927 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 288662 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 101 | 473305
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3482928
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1749600
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 261690
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3680640
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 213419
| Dhaka area Total |  |  |  | 5829 | 3581 | 65470294
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 366682
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122445
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 1053600
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 70 | 1676000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 230 | 2929083
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3067034
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 0 | Reserve.
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 83 | 1031555 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 98 | 1205520
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2318400
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 442272
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 31 | 506400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 84 | 1225920 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 31318
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 125 | 3138873 | Transformer O/L
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299734
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2420160
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 57 | 1377491 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1257 | 24212487
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2313324
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 4755000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 300 | 7674700 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7233000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 594288 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1131840
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 516912
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 51 | 487260 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 154 | 388848 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 497772
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 159660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 170 | 3557760
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817400
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1035701
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 514160
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 744192
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1476300
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2730840
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 37 | 737280 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 1969 | 37566964
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 100 | 2701520 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 360000 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 57 | 1147200 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 180 | 3976800 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2516400
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 336810
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 566160
| Mymensingh Area Total |  |  |  | 709 | 493 | 11619640
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 997000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1031880 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 110 | 2977036 | Gas shortage
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 326 | 7432000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1113000
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 165100
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 774912 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1785600
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 163 | 3918390 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 410000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 273936 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7360500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 368 | 8679000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 170280
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 331 | 8063600
| Sylhet Area Total |  |  |  | 2377 | 1896 | 45152234
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 843 | 19333818
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2106240 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 19 | 198720 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 16256 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 250 | 6920928 | Gas shortage.
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 526875 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 792960
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 2129280 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1436 | 32025077
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 102048
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 632574
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1579000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 1936835
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 610 | 14355400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 4 | 124827 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 222000 | Low demand
| Barisal Area Total |  |  |  | 1826 | 975 | 18952684
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 612000
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 42 | 422426 | Engine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 329200 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 80 | 1599000 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 174 | 4826382 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 176 | 4521764 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 394 | 9070781 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 229588 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 475200
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 167598
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 990720
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1067768
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 25655 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2604864
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2614560
| Rajshahi Area Total |  |  |  | 2173 | 1363 | 29557506
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1786472
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3664200 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2077440
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43792
| Rangpur Area Total |  |  |  | 605 | 338 | 7571904
| Total |  |  |  | 21219 | 13308 | 272128790
| Eastern Grid Total |  |  |  | 14331 | 9196 | 184021619
| Western Grid Total |  |  |  | 6888 | 4112 | 88107171
| National Grid Total |  |  |  | 21219 | 13308 | 272128790
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-13
(a) ENTIRE EASTERN GRID : |  | 8434 | MW | (b) ENTIRE WESTERN GRID : |  | 4283 | MW
i) Dhaka area |  | 4246 | MW | i) Khulna area |  | 1639 | MW
ii) Chittagong area |  | 1338 | MW | ii) Rajshahi area |  | 1428 | MW
iii) Comilla area |  | 1301 | MW | iii) Barisal area |  | 383 | MW
iv) Mymensingh area |  | 1056 | MW | iv) Rangpur area |  | 833 | MW
v) Sylhet area |  | 493 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12717 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 1:00 | Jamalpur | 153 | 21:00 | Jhenida | 123 | 20:00
Munsiganj | 142 | 22:00 | Sherpur | 130 | 20:00 | Bottail | 128 | 21:00
Sonargaon | 87 | 11:00 | Srimongal | 52 | 21:00 | G.K Project | 66 | 22:00
Shyampur | 214 | 12:00 | Shahjibazar | 128 | 21:00 | Faridpur | 201 | 20:00
Bhulta | 207 | 22:00 | Fenchuganj | 44 | 20:00 | Madaripur | 108 | 21:00
Madanganj | 63 | 12:00 | Kulawara | 39 | 22:00 | Sariatpur | 74 | 21:00
Shitalakhya | 129 | 16:00 | Sylhet | 123 | 18:30 | Gopalganj | 97 | 22:00
Rahim steel | 26 | 10:00 | Chatak | 19 | 15:00 | Bagerhat | 109 | 20:00
Matuail | 66 | 10:00 | Sunamganj | 42 | 21:00 | Mongla | 40 | 10:00
Ghorasal | 80 | 15:00 | Biani Bazar | 56 | 21:00 | Satkhira | 110 | 21:00
Narsingdi | 175 | 23:00 | Comilla (S) | 172 | 18:00 | Gallamari | 35 | 1:00
Haripur (SBU) | 122 | 2:00 | Comilla(N) | 151 | 21:00 | Magura | 56 | 21:00
Sreenagar |  |  | Chandpur | 81 | 21:00 | Norail | 35 | 19:30
Ullon | 91 | 23:00 | Feni | 141 | 21:00 | Chuadanga | 84 | 19:00
Hasnabad | 97 | 22:00 | Chowmuhani | 192 | 22:00 | Borguna | 20 | 21:00
Magbazar | 76 | 14:00 | Ashuganj | 47 | 9:00 | Barisal(N) | 48 | 21:00
Maniknagar | 106 | 13:00 | Daudkandi | 164 | 21:00 | Barisal (S) | 116 | 21:00
Bangabhaban | 24 | 10:00 | B.Baria | 178 | 20:00 | Patuakhali | 121 | 22:00
Narinda | 84 | 13:00 | Ramganj | 96 | 21:00 | Bhandaria | 56 | 21:00
Dhanmondi | 199 | 13:00 | Chaddagram | 45 | 19:30 | Borhan Uddin | 45 | 21:00
Lalbag | 88 | 13:00 | PHP | 2 | 1:00 | Ishurdi | 65 | 21:00
Madartek | 84 | 21:00 | Kochua | 69 | 21:00 | Ruppur Paromanobik | 3 | 1:00
Dhaka University | 42 | 13:00 | Madunaghat | 71 | 19:00 | Natore | 143 | 21:00
Aftabnagar | 10 | 13:00 | Hathazari | 96 | 21:00 | Bogra | 166 | 1:00
Fatullah | 65 | 10:00 | Khulshi | 228 | 15:00 | Noagaon | 132 | 19:30
Nawabganj | 56 | 21:00 | Halishahar | 139 | 13:00 | Rajshahi | 163 | 22:00
Mirpur | 114 | 15:00 | Baraulia | 159 | 15:00 | Rajshahi New | 20 | 21:00
Kalyanpur | 11 | 15:00 | Sikalbaha | 35 | 10:00 | C.Nawabganj | 83 | 21:00
Gulshan | 142 | 14:00 | Dohazari | 88 | 19:30 | Amnura | 64 | 21:00
Uttara | 108 | 15:00 | Cox'sbazar | 109 | 22:00 | Pabna | 114 | 21:00
Uttara New | 29 | 15:00 | Chandraghona | 32 | 19:00 | Shahjadpur | 101 | 15:00
Kamrangirchar | 87 | 13:00 | Kaptai | 4.4 | 19:00 | Serajganj | 96 | 20:00
Savar | 175 | 16:00 | A. Khaer Stl. | 10 | 12:00 | Niyamatpur | 86 | 19:30
Bhasantec | 156 | 15:00 | Bakulia | 111 | 12:00 | Joypurhat | 63 | 21:00
Agargaon | 77 | 13:00 | Julda | 26 | 16:00 | Sherpur(Bogura) | 60 | 20:00
Satmosjid | 95 | 15:00 | TK chemical | 29 | 22:00 | Mohastangor | 64 | 19:30
Tongi | 94 | 21:00 | Modern Steel | 0 | #N/A | Bangura | 31 | 21:00
Kabirpur | 260 | 15:00 | Shahmirpur | 26.7 | 1:00 | Rangpur | 137 | 23:00
Basundhara | 167 | 15:00 | Khagrachhari | 24 | 13:00 | Lalmonirhat | 48 | 21:00
Manikganj | 76 | 22:00 | Matarbari | 40 | 20:00 | Saidpur | 122 | 19:30
Joydevpur | 168 | 19:00 | Baroiar Hat | 60 | 14:00 | Purbasadipur | 108 | 21:00
New Tongi | 110 | 15:00 | Rangamati | 12 | 19:00 | Thakurgaon | 81 | 19:00
Kodda | 277 | 15:00 | Abul Khair 230 | 15 | 14:00 | Palashbari | 124 | 19:00
Dhamrai | 120 | 19:00 | BSRM | 129 | 19:30 | Barapukuria | 58 | 21:00
Rajendrapur | 100 | 22:00 | GPH Ispat | 88 | 4:00 | Panchagar | 45 | 19:00
Valuka | 114 | 16:00 | Goalpara | 27 | 1:00 | Joldhaka | 55 | 21:00
Tangail | 204 | 12:00 | Central s/s | 99 | 21:00 | Kurigram | 62 | 21:00
Mymensing | 226 | 20:00 | Noapara | 70 | 0.8125 | Mithapukur | 36 | 19:00
Kishorganj | 154 | 19:00 | Jessore | 127 | 21:00
Netrokona | 120 | 19:00 | Benapol | 66 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-13 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 404 | 24:00 | 397 | 17:00 | Kaliakoir | 386 | 0.75 | 377 | 0.5
| Bheramara | 400 | 13:00 | 390 | 19:00 | Bhulta | 378 | 0.083333 | 367 | 0.45833
| Ashuganj(N) | 384 | 1:00 | 375 | 11:00 | Gopalganj | 407 | 0.625 | 387 | 0.58333
| Payra | 407 | 21:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 228 | 24:00 | 219 | 9:00
| Ishurdi | 234 | 1:00 | 223 | 19:00 | Megnaghat | 228 | 4:00 | 220 | 13:00
| Ashuganj | 232 | 1:00 | 226 | 12:00 | Fenchuganj | 239 | 24:00 | 235 | 17:00
| Serajganj | 230 | 2:00 | 222 | 12:00 | Siddhirganj | 227 | 5:00 | 220 | 11:00
| Baghabari | 232 | 1:00 | 226 | 11:00 | Maniknagar | 225 | 5:00 | 217 | 16:00
| Barapukuria | 236 | 3:00 | 225 | 13:00 | Agargaon | 224 | 2:00 | 215 | 11:00
| Bogra | 227 | 5:00 | 211 | 21:00 | Barisal | 248 | 13:00 | 238 | 14:00
| Rajshahi | 231 | 1:00 | 216 | 12:00 | Bhola 225 MW | 251 | 2:00 | 241 | 15:00
| Khulna South | 228 | 18:00 | 208 | 21:00 | AKSML | 226 | 13:00 | 218 | 3:00
| Rampura | 226 | 5:00 | 219 | 11:00 | BSRM | 229 | 24:00 | 220 | 9:00
| Haripur | 225 | 21:00 | 218 | 11:00 | Bibiyana | 240 | 18:00 | 234 | 11:00
| Hasnabad | 226 | 1:00 | 215 | 9:00 | Bhulta | 227 | 20:00 | 220 | 10:00
| Shyampur | 223 | 21:00 | 220 | 16:00 | Ashuganj (S) | 232 | 2:00 | 226 | 17:00
| Aminbazar | 224 | 1:00 | 218 | 2:00 | Kaliakoir | 225 | 19:30 | 220 | 7:00
| Tongi | 225 | 20:00 | 213 | 8:00 | GPH | 227 | 13:00 | 219 | 3:00
| Comilla (N) | 229 | 24:00 | 221 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 21:00 | 130 | 11:00 | Madanhat | 137 | 0.58333 | 132 | 0.29167
| Munsiganj | 133 | 7:00 | 129 | 11:00 | Hathazari | 135 | 0.54167 | 131 | 0.041667
| Sonargaon | 136 | 24:00 | 130 | 11:00 | Khulshi | 133 | 0.54167 | 128 | 0.16667
| Shyampur | 137 | 22:00 | 131 | 10:00 | Halishahar | 135 | 0.54167 | 132 | 0.25
| Bhulta | 128 | 21:00 | 122 | 12:00 | Baraulia | 135 | 0.083333 | 129 | 0.375
| Madanganj | 132 | 24:00 | 126 | 11:00 | Sikalbaha | 139 | 0.83333 | 131 | 0.041667
| Shitalakhya | 140 | 21:00 | 130 | 17:00 | Dohazari | 133 | 0.625 | 127 | 0.16667
| Rahim steal | 134 | 19:30 | 130 | 10:00 | Cox'sbazar | 125 | 0.54167 | 114 | 0.875
| Matuail | 135 | 21:00 | 130 | 11:00 | Chandraghona | 135 | 0.54167 | 130 | 0.16667
| Ghorasal | 137 | 18:00 | 135 | 1:00 | Kaptai | 134 | 0.041667 | 132 | 0.29167
| Narsinghdi | 132 | 6:00 | 125 | 1:00 | A. Khaer Stl. | 133 | 0.875 | 130 | 0.16667
| Haripur (SBU) | 135 | 21:00 | 130 | 12:00 | Bakulia | 136 | 0.54167 | 131 | 0.29167
| Sreenagar |  |  |  |  | Julda | 138 | 0.54167 | 132 | 0.16667
| Ullon | 133 | 5:00 | 126 | 12:00 | TK Chemical | 136 | 0.54167 | 132 | 0.375
| Hasnabad | 137 | 20:00 | 129 | 17:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 132 | 4:00 | 125 | 11:00 | Shahmirpur | 137 | 0.54167 | 133 | 0.083333
| Maniknagar | 135 | 24:00 | 129 | 10:00 | Khagrachhari | 133 | 0.54167 | 129 | 0.16667
| Bangabhaban | 135 | 24:00 | 129 | 10:00 | Matarbari | 127 | 0.54167 | 117 | 0.875
| Narinda | 135 | 24:00 | 129 | 10:00 | Baroiar Hat | 135 | 0.54167 | 127 | 0.083333
| Dhanmondi | 133 | 5:00 | 126 | 12:00 | Rangamati | 134 | 0.54167 | 130 | 0.16667
| Lalbag | 137 | 21:00 | 127 | 10:00 | Goalpara S/S | 137 | 6:00 | 123 | 21:00
| Madartek | 133 | 2:00 | 126 | 11:00 | Khulna Central S/S | 136 | 2:00 | 121 | 22:00
| Dhaka University | 133 | 1:00 | 126 | 11:00 | Noapara | 131 | 6:00 | 118 | 0.875
| Aftabnagar | 133 | 4:00 | 126 | 15:00 | Jessore | 126 | 18:30 | 108 | 0.91667
| Fatullah | 137 | 21:00 | 131 | 10:00 | Benapol | 125 | 6:00 | 106 | 0.875
| Nawabganj | 128 | 19:00 | 123 | 11:00 | Jhenida | 121 | 6:00 | 102 | 0.83333
| Mirpur | 137 | 20:00 | 130 | 17:00 | Bottail | 128 | 0.25 | 117 | 0.91667
| Kalyanpur | 136 | 5:00 | 131 | 11:00 | G.K Project | 137 | 18:00 | 130 | 0.5
| Gulshan | 133 | 5:00 | 126 | 11:00 | Faridpur | 134 | 0.75 | 126 | 0.79167
| Uttara | 132 | 21:00 | 127 | 17:00 | Madaripur | 140 | 0.16667 | 134 | 0.5
| Uttara New | 135 | 5:00 | 130 | 17:00 | Shariyatpur S/S | 140 | 0.75 | 132 | 0.58333
| Kamrangirchar | 136 | 20:00 | 124 | 17:00 | Gopalganj | 145 | 0.75 | 134 | 0.58333
| Savar | 137 | 4:00 | 131 | 16:00 | Bagerhat | 133 | 5:00 | 117 | 0.83333
| Bhasantec | 133 | 5:00 | 126 | 15:00 | Mongla | 133 | 0.25 | 115 | 0.91667
| Agargaon | 134 | 4:00 | 128 | 17:00 | Satkhira | 134 | 6:00 | 116 | 0.91667
| Satmosjid | 133 | 5:00 | 127 | 17:00 | Gallamari | 137 | 18:00 | 123 | 0.875
| Tongi | 136 | 21:00 | 129 | 17:00 | Magura | 120 | 20:00 | 98 | 22:00
| Kabirpur | 135 | 2:00 | 128 | 10:00 | Narail | 118 | 0.83333 | 98 | 22:00
| Basundhara | 135 | 1:00 | 128 | 8:00 | Chuadanga | 115 | 8:00 | 91 | 0.91667
| Manikganj | 138 | 1:00 | 131 | 7:00 | Borguna | 137 | 0.8125 | 128 | 0.625
| Joydevpur | 138 | 0:00 | 129 | 7:00 | Barisal(N) | 140 | 18:00 | 133 | 0.58333
| New Tongi | 135 | 19:30 | 130 | 5:00 | Barisal (S) | 139 | 18:00 | 130 | 0.54167
| Kodda | 137 | 1:00 | 125 | 9:00 | Patuakhali(S) | 139 | 18:00 | 128 | 13:00
| Dhamrai | 134 | 4:00 | 127 | 9:00 | Bhandaria | 138 | 0.75 | 125 | 0.66667
| Rajendrapur | 135 | 14:00 | 127 | 10:00 | Ishurdi | 136 | 0.083333 | 129 | 0.375
| Valuka | 122 | 5:00 | 109 | 21:00 | Ruppur Paromanobik | 134 | 0.041667 | 129 | 0.875
| Tangail | 130 | 3:00 | 122 | 22:00 | Natore | 135 | 4:00 | 126 | 21:00
| Mymensing | 129 | 5:00 | 112 | 21:00 | Bogra | 136 | 5:00 | 124 | 21:00
| Kishorganj | 128 | 6:00 | 115 | 22:00 | Noagaon | 128 | 5:00 | 116 | 21:00
| Netrokona | 125 | 6:00 | 109 | 22:00 | Rajshahi | 134 | 17:00 | 126 | 12:00
| Jamalpur | 136 | 2:00 | 123 | 21:00 | Rajshahi New | 135 | 1:00 | 126 | 12:00
| Sherpur | 136 | 10:00 | 120 | 21:00 | C.Nawabganj | 133 | 18:00 | 122 | 11:00
| Srimongal | 136 | 9:00 | 130 | 22:00 | Amnura | 133 | 18:00 | 122 | 12:00
| Shahjibazar | 135 | 7:00 | 129 | 20:00 | Pabna | 133 | 2:00 | 126 | 10:00
| Fenchuganj | 137 | 6:00 | 133 | 1:00 | Shahjadpur | 134 | 4:00 | 130 | 9:00
| Khulawara | 135 | 2:00 | 132 | 24:00 | Serajganj | 132 | 1:00 | 125 | 9:00
| Sylhet | 133 | 5:00 | 131 | 1:00 | Niyamatpur | 125 | 3:00 | 110 | 21:00
| Chatak | 132 | 6:00 | 129 | 14:00 | Joypurhat | 125 | 3:00 | 110 | 21:00
| Sunamganj | 133 | 7:00 | 127 | 19:00 | Sherpur(Bogura) | 134 | 4:00 | 124 | 21:00
| Biani Bazar | 132 | 6:00 | 128 | 21:00 | Mohastangor | 132 | 3:00 | 121 | 21:00
| Comilla(s) | 128 | 18:00 | 119 | 18:30 | Bangura | 133 | 1:00 | 130 | 7:00
| Comilla(n) | 137 | 4:00 | 135 | 1:00 | Rangpur | 131 | 5:00 | 113 | 13:00
| Chandpur | 142 | 7:00 | 137 | 18:30 | Lalmonirhat | 131 | 4:00 | 112 | 19:00
| Feni | 137 | 15:00 | 128 | 1:00 | Saidpur | 131 | 5:00 | 110 | 19:30
| Chowmuhani | 132 | 6:00 | 126 | 3:00 | Purbasadipur | 131 | 5:00 | 104 | 19:30
| Ashuganj | 136 | 8:00 | 132 | 21:00 | Thakurgaon | 129 | 1:00 | 101 | 19:30
| Daudkandi | 138 | 21:00 | 128 | 1:00 | Palashbari | 131 | 4:00 | 115 | 19:00
| B.Baria | 131 | 5:00 | 125 | 21:00 | Barapukuria | 136 | 3:00 | 125 | 13:00
| Ramganj | 137 | 7:00 | 130 | 1:00 | Panchagar | 130 | 4:00 | 98 | 19:30
| Chaddagram | 138 | 14:00 | 129 | 2:00 | Joldhaka | 130 | 4:00 | 109 | 21:00
| PHP | 135 | 13:00 | 126 | 3:00 | Kurigram | 131 | 5:00 | 107 | 19:30
| Kochua | 138 | 8:00 | 130 | 1:00 | Mithapukur | 133 | 0.16667 | 116 | 0.79167

## L-Curve
Date | 2021-04-13
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 330 | 9032 | 3947 | 12979 |  |  |  | QF-LDC-11
0:30 | 176 | 8689 | 3932 | 12621 | Date: | 2021-04-13
1:00 | 22 | 8346 | 3917 | 12263
1:30 | 23 | 8190.5 | 3866.5 | 12057
2:00 | 24 | 8035 | 3816 | 11851
2:30 | 52 | 7880 | 3729.5 | 11609.5 | [5 empty] | Gen. at Eve. Peak | 13308 | 13308 MW (21:00 )
3:00 | 80 | 7725 | 3643 | 11368 | [6 empty] | 21:00
3:30 | 100 | 7637 | 3596.5 | 11233.5 | [5 empty] | Gen. at Day Peak | 11347 | 11347 MW (12:00 )
4:00 | 120 | 7549 | 3550 | 11099 | [6 empty] | 12:00
4:30 | 152 | 7437 | 3524.5 | 10961.5 | [5 empty] | Highest Generation | 13308
5:00 | 184 | 7325 | 3499 | 10824 | [6 empty] | 21:00
5:30 | 164 | 7097.5 | 3442 | 10539.5
6:00 | 144 | 6870 | 3385 | 10255
6:30 | 106 | 6809 | 3333.5 | 10142.5
7:00 | 68 | 6748 | 3282 | 10030
7:30 | 83 | 6833 | 3256 | 10089
8:00 | 98 | 6918 | 3230 | 10148
8:30 | 125 | 7055 | 3226.5 | 10281.5
9:00 | 152 | 7192 | 3223 | 10415
9:30 | 157 | 7353 | 3238 | 10591
10:00 | 162 | 7514 | 3253 | 10767
10:30 | 134 | 7639 | 3243.5 | 10882.5
11:00 | 106 | 7764 | 3234 | 10998
11:30 | 84 | 7938.5 | 3234 | 11172.5
12:00 | 62 | 8113 | 3234 | 11347
12:30 | 65 | 8139 | 3309.5 | 11448.5
13:00 | 68 | 8165 | 3385 | 11550
13:30 | 49 | 8209.5 | 3404 | 11613.5
14:00 | 30 | 8254 | 3423 | 11677
14:30 | 25 | 8357 | 3502.5 | 11859.5
15:00 | 20 | 8460 | 3582 | 12042
15:30 | 110 | 8325 | 3653.5 | 11978.5
16:00 | 200 | 8190 | 3725 | 11915
16:30 | 249 | 7977 | 3647 | 11624
17:00 | 298 | 7764 | 3569 | 11333
17:30 | 214 | 7660.5 | 3479 | 11139.5
18:00 | 130 | 7557 | 3389 | 10946
18:30 | 123 | 8123 | 3643 | 11766
19:00 | 116 | 8689 | 3897 | 12586
19:30 | 210 | 8877 | 4172 | 13049
20:00 | 210 | 8907 | 4169 | 13076 |  |  |  | Executive Engineer
20:30 | 300 | 9051.5 | 4140.5 | 13192 |  |  |  | Network Operation Division
21:00 | 390 | 9196 | 4112 | 13308
21:30 | 415 | 9186 | 4087 | 13273
22:00 | 440 | 9176 | 4062 | 13238 |  |  |  |  | Page 6 of 7
22:30 | 300 | 9161 | 4019.5 | 13180.5
23:00 | 160 | 9146 | 3977 | 13123
23:30 | 245 | 9089 | 3962 | 13051
24:00 | 330 | 9032 | 3947 | 12979
13308 MW (21:00 )
11347 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-13 |  | Energy | 272128790
[11 empty] | 2021-04-13 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4298 | 843 | 1684 | 4592 | 847 | 70 | 518 | 0 | 156 | 0
0:30 | 4384 | 783 | 1760 | 4200 | 831 | 70 | 449.5 | 0 | 158 | 0 | Date: | 2021-04-13
1:00 | 4470 | 723 | 1836 | 3808 | 815 | 70 | 381 | 0 | 160 | 0
1:30 | 4443 | 722.5 | 1839.5 | 3698 | 816 | 70 | 310 | 0 | 158 | 0 | [7 empty] | Total Energy | 272.1288 | Total Energy Gen 272.129 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.129 MKWHr
2:00 | 4416 | 722 | 1843 | 3588 | 817 | 70 | 239 | 0 | 156 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4448 | 722.5 | 1853 | 3378.5 | 817 | 70 | 165.5 | 0 | 155 | 0 | [7 empty] | Energy Requirement | 272.1288
3:00 | 4480 | 723 | 1863 | 3169 | 817 | 70 | 92 | 0 | 154 | 0
3:30 | 4462.5 | 723 | 1850 | 3074 | 817.5 | 70 | 83.5 | 0 | 153 | 0 | [6 empty] | Shortage
4:00 | 4445 | 723 | 1837 | 2979 | 818 | 70 | 75 | 0 | 152 | 0
4:30 | 4430.5 | 723 | 1847.5 | 2863.5 | 818.5 | 70 | 58.5 | 0 | 150 | 0
5:00 | 4416 | 723 | 1858 | 2748 | 819 | 70 | 42 | 0 | 148 | 0
5:30 | 4317.5 | 744 | 1792 | 2645 | 803 | 70 | 26 | 0 | 141 | 1
6:00 | 4219 | 765 | 1726 | 2542 | 787 | 70 | 10 | 0 | 134 | 2
6:30 | 4176.5 | 765 | 1737.5 | 2497.5 | 747 | 70 | 10 | 0 | 129 | 10 |  |  |  |  | Coal
7:00 | 4134 | 765 | 1749 | 2453 | 707 | 70 | 10 | 0 | 124 | 18
7:30 | 4139 | 786.5 | 1678 | 2527.5 | 709 | 70 | 26 | 0 | 122 | 31 |  |  |  | Oil |  |  |  | ,
8:00 | 4144 | 808 | 1607 | 2602 | 711 | 70 | 42 | 0 | 120 | 44
8:30 | 4145 | 807.5 | 1618 | 2702 | 715.5 | 70 | 41.5 | 0 | 123 | 59
9:00 | 4146 | 807 | 1629 | 2802 | 720 | 70 | 41 | 0 | 126 | 74
9:30 | 4147.5 | 824 | 1617.5 | 2970 | 710.5 | 70 | 41 | 0 | 125 | 85.5
10:00 | 4149 | 841 | 1606 | 3138 | 701 | 70 | 41 | 0 | 124 | 97
10:30 | 4133.5 | 841.5 | 1594 | 3253 | 705.5 | 70 | 57 | 0 | 130 | 98
11:00 | 4118 | 842 | 1582 | 3368 | 710 | 70 | 73 | 0 | 136 | 99
11:30 | 4145 | 805.5 | 1586.5 | 3491.5 | 715.5 | 70 | 112 | 0 | 141 | 105.5
12:00 | 4172 | 769 | 1591 | 3615 | 721 | 70 | 151 | 0 | 146 | 112
12:30 | 4162 | 803.5 | 1587 | 3605.5 | 726 | 70 | 241 | 0 | 145 | 108.5
13:00 | 4152 | 838 | 1583 | 3596 | 731 | 70 | 331 | 0 | 144 | 105
13:30 | 4152 | 838 | 1583 | 3596 | 731 | 70 | 331 | 0 | 144 | 105
14:00 | 4152 | 838 | 1583 | 3596 | 731 | 70 | 331 | 0 | 144 | 105
14:30 | 4263.5 | 839.5 | 1611 | 3670 | 751 | 70 | 350.5 | 0 | 152 | 88.5
15:00 | 4375 | 841 | 1639 | 3744 | 771 | 70 | 370 | 0 | 160 | 72
15:30 | 4325.5 | 841 | 1630.5 | 3702.5 | 781 | 70 | 415 | 0 | 162 | 51
16:00 | 4276 | 841 | 1622 | 3661 | 791 | 70 | 460 | 0 | 164 | 30
16:30 | 4310 | 841.5 | 1611.5 | 3373.5 | 770.5 | 70 | 468 | 0 | 153 | 26
17:00 | 4344 | 842 | 1601 | 3086 | 750 | 70 | 476 | 0 | 142 | 22
17:30 | 4279 | 841.5 | 1543.5 | 3037 | 748.5 | 70 | 480.5 | 0 | 127 | 12.5
18:00 | 4214 | 841 | 1486 | 2988 | 747 | 70 | 485 | 0 | 112 | 3
18:30 | 4365 | 841.5 | 1566 | 3516.5 | 766.5 | 70 | 501 | 0 | 138 | 1.5
19:00 | 4516 | 842 | 1646 | 4045 | 786 | 70 | 517 | 0 | 164 | 0
19:30 | 4582 | 841 | 1696 | 4349 | 825 | 70 | 522 | 0 | 164 | 0
20:00 | 4580 | 842 | 1718 | 4359 | 825 | 70 | 522 | 0 | 160 | 0
20:30 | 4548.5 | 842.5 | 1712.5 | 4501 | 830 | 70 | 522.5 | 0 | 165 | 0
21:00 | 4517 | 843 | 1707 | 4643 | 835 | 70 | 523 | 0 | 170 | 0
21:30 | 4481 | 843 | 1698 | 4648 | 841.5 | 70 | 520.5 | 0 | 171 | 0
22:00 | 4445 | 843 | 1689 | 4653 | 848 | 70 | 518 | 0 | 172 | 0
22:30 | 4432.5 | 843 | 1683 | 4622.5 | 848 | 70 | 516.5 | 0 | 165 | 0
23:00 | 4420 | 843 | 1677 | 4592 | 848 | 70 | 515 | 0 | 158 | 0
23:30 | 4359 | 843 | 1680.5 | 4592 | 847.5 | 70 | 516.5 | 0 | 157 | 0 | Max Temp. in Dhaka |  | 36.9° C
24:00 | 4298 | 843 | 1684 | 4592 | 847 | 70 | 518 | 0 | 156 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 272.129 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 272.129 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-13
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1676000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | [11 empty] | 15 | 25 | 25 | 25 | 25 | 25 | 25 | 366682
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 9 | 14 | 18 | 10 | 19 | 19 | 17 | 13 | 8 | 3 | [9 empty] | 122445
6 | Sikalbaha 225MW CCPP (Gas) | 150 | 151 | 151 | 152 | 152 | 100 | 78 | 41 | 42 | 40 | 40 | 40 | 40 | 40 | 45 | 71 | 96 | 161 |  | 227 | 229 | 229 | 230 | 230 | 229 | 229 | 2929083
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 100 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3067034
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 83 | 34 | 17 | 17 | 0 | [7 empty] | 51 | 45 | 48 | 81 | 82 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1031555
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [26 empty] | 0
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 100 | 100 | 100 | 150 | 150 | 150 | 150 | 744192
14 | Titas 50 MW Peaking PP | [12 empty] | 8 | 50 | 42 | 42 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 516912
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 185 | 150 | 185 | 185 | 180 | 120 | 120 | 95 | 95 | 155 | 150 | 180 | 175 | 150 | 175 | 148 | 145 | 65 |  | 150 | 150 | 180 | 180 | 180 | 180 | 175 | 3986000
17 | Siddhirganj 335 MW CCPP | 221 | 226 | 223 | 227 | 225 | 180 | 180 | 224 | 219 | 214 | 214 | 211 | 210 | 160 | 208 | 210 | 214 | 180 |  | 216 | 219 | 220 | 221 | 221 | 223 | 223 | 519382
18 | Kodda 300 MW PP Unit-2 (Summit) | 283 | 283 | 205 | 145 | 45 | 45 | 45 | 45 | 129 | 172 | 229 | 232 | 239 | 250 | 250 | 255 | 265 | 265 |  | 268 | 268 | 268 | 268 | 270 | 275 | 273 | 5045779
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7149391
26
28 | Ashuganj TPP Unit- 3 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 90 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 2313324
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 594288
33 | Ashuganj 225 MW CCPP | 204 | 213 | 209 | 199 | 194 | 191 | 184 | 202 | 190 | 185 | 187 | 188 | 210 | 207 | 202 | 206 | 207 | 180 |  | 210 | 210 | 210 | 208 | 172 | 182 | 201 | 4755000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 285 | 280 | 280 | 280 | 295 | 285 | 305 | 320 | 320 | 320 | 295 | 295 | 320 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 295 | 265 | 7233000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 315 | 310 | 310 | 310 | 310 | 310 | 335 | 305 | 310 | 305 | 280 | 280 | 335 | 280 | 280 | 280 |  | 300 | 300 | 300 | 300 | 305 | 300 | 260 | 7674700
35 | Ashuganj 55 MW PP (Precision) | 50 | 50 | 50 | 50 | 51 | 50 | 52 | 50 | 50 | 50 | 50 | 47 | 47 | 45 | 44 | 40 | 43 | 47 |  | 48 | 48 | 49 | 50 | 30 | 30 | 30 | 1131840
36 | Chandpur 150 MW CCPP | [13 empty] | 50 | 52 | 52 | 50 | 52 |  | 52 | 51 | 51 | 51 | 52 | 50 | 48 | 487260
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 250 | 250 | 250 | 250 | 250 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 5979300
41 | Haripur 360MW CCPP(HPL) | 258 | 264 | 275 | 280 | 282 | 272 | 245 | 228 | 218 | 200 | 191 | 180 | 180 | 176 | 170 | 170 | 170 | 165 |  | 165 | 161 | 160 | 160 | 160 | 161 | 167 | 4976000
42 | RPCL 210MW CCPP | 140 | 139 | 139 | 129 | 141 | 143 | 134 | 132 | 117 | 100 | 100 | 99 | 99 | 98 | 97 | 97 | 100 | 117 |  | 110 | 106 | 100 | 100 | 101 | 104 | 120 | 2701520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 20 | 33 | 44 | 49 | 49 | 45 | 38 | 31 | 5 | 11 | 2 | [8 empty] | 336810
44 | Fenchugonj CCPP Phase-1 | 42 | 43 | 43 | 43 | 44 | 44 | 43 | 43 | 42 | 43 | 42 | 42 | 41 | 41 | 40 | 40 | 41 | 41 |  | 43 | 42 | 42 | 42 | 42 | 42 | 43 | 997000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1031880
46 | Shajibazar 330 MW CCPP | 328 | 326 | 326 | 328 | 326 | 328 | 325 | 328 | 310 | 308 | 312 | 310 | 328 | 325 | 321 | 324 | 325 | 328 |  | 325 | 325 | 326 | 326 | 326 | 333 | 332 | 7432000
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 31 | 30 | 31 | 31 | 31 | 30 | 30 | 31 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 774912
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 73 | 69 | 72 | 71 | 72 | 71 | 72 | 50 |  | 78 | 78 | 77 | 78 | 78 | 78 | 78 | 1785600
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 164 | 164 | 163 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 164 | 164 | 163 | 3918390
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 410000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 170280
54 | Hobiganj 11MW PP Cofidence-E | 11 | 7 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 165100
55 | Fenchugonj 51 MW PP (Barakatullah) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 11 | 11 | 27 | 52 | 51 | 50 | 50 | 53 | 33 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1113000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 273936
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 290 | 300 | 300 | 305 | 275 | 275 | 290 | 290 | 320 | 310 | 320 | 310 | 280 | 300 | 300 | 295 | 270 |  | 290 | 305 | 300 | 300 | 300 | 305 | 295 | 7360500
| Bibiyana South 400 MW | 320 | 320 | 350 | 320 | 343 | 322 | 336 | 320 | 350 | 350 | 350 | 350 | 320 | 320 | 350 | 320 | 320 | 321 |  | 320 | 338 | 327 | 331 | 351 | 350 | 320 | 8063600
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1268047
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 19 | 18 | 23 | 22 | 22 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 566160
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 20 | 20 | 17 | 17 | 17 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 442272
61 | Narshingdi 22 MW PP (Doreen) | 22 | 0 |  | 16 | 0 |  |  |  | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 344340
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 360000
63 | Impoprt (Tripura) | 160 | 156 | 154 | 152 | 148 | 134 | 124 | 120 | 126 | 124 | 136 | 146 | 144 | 158 | 160 | 164 | 142 | 112 |  | 164 | 164 | 160 | 170 | 172 | 158 | 156 | 3557760
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 38 | 38 | 30 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 16 | 12 |  | 20 | 22 | 28 | 31 | 34 | 38 | 38 | 506400
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 497772
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 5 | 5 | 5 |  | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 159660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817400
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 514160
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 26 |  | 20 | 22 | 22 | 27 | 22 | 29 | 29 | 617940
71 | Maona 33 MW PP(Summit) | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 743900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 692400
73 | Ghorashal 108MW PP (Regent) | 104 | 104 | 103 | 103 | 103 | 104 | 104 | 103 | 100 | 97 | 100 | 97 | 102 | 102 | 102 | 102 | 103 | 103 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 2416045
| Feni Lanka Power | 23 | [8 empty] | 34 | 34 | 114 | 114 | 114 | 114 | 62 | 52 | 52 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1476300
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 65 | 65 |  | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 2730840
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 90 | 90 | 124 | 162 | 162 | 162 | 144 | 144 | 144 | 144 | 132 | 139 | 154 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3680640
77 | Siddhirganj 100 PP(Dutch Bangla) | 84 | 70 | 70 | 70 | 70 | 70 | 70 | 76 | 92 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 85 | 70 |  | 80 | 100 | 100 | 96 | 100 | 100 | 100 | 2172480
78 | Gazipur 52 MW PP | 51 | 0 | [7 empty] | 3 | 18 | 38 | 51 | 50 | 50 | 16 | 16 | 16 |  | 26 | 50 | 50 | 50 | 51 | 51 | 51 | 654720
79 | Kodda 150MW PP | 133 | 100 | 64 | 48 | 32 |  |  | 32 | 32 | 32 | 64 | 132 | 132 | 129 | 130 | 130 | 130 | 130 |  | 130 | 130 | 133 | 133 | 133 | 133 | 133 | 2264640
80 | Jamalpur 95 MW PP(Powerpac) | 57 | 57 | 57 | 57 | 57 | 41 | 37 | 40 | 40 | 32 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 49 |  | 49 | 49 | 57 | 57 | 57 | 57 | 57 | 1147200
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 8 | 34 | 52 | 52 | 43 | 43 | 52 | 52 | 52 | 25 | 25 |  | 29 | 52 | 47 | 52 | 52 | 52 | 52 | 1035701
| Gazipur 100 MW PP | 105 | 105 | 0 |  |  |  |  | 17 | 35 | 78 | 90 | 90 | 92 | 105 | 105 | 105 | 70 | 70 |  | 80 | 105 | 105 | 105 | 105 | 105 | 105 | 1749600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 3 | 4 | 5 | 4 | 4 | 3 | 1 | 1 | [9 empty] | 31318
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299734
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 50 | 0 | [7 empty] | 2 | 42 | 46 | 48 | 47 | 49 | 60 | 40 | 40 |  | 70 | 85 | 82 | 82 | 83 | 85 | 86 | 984747
86 | Meghnaghat CCPP ( Summit) | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 250 | 230 | 230 | 290 | 295 | 230 | 290 | 290 | 250 | 240 | 220 |  | 240 | 240 | 245 | 240 | 240 | 245 | 235 | 5900044
87 | Meghnaghat 100 MW(IEL) | 93 | 91 | 91 | 93 | 93 | 75 | 33 | 47 | 81 | 91 | 93 | 93 | 97 | 98 | 98 | 100 | 70 | 65 |  | 79 | 100 | 100 | 100 | 100 | 100 | 94 | 2105280
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 261690
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [8 empty] | 10 | 88 | 80 | 90 | 90 | 90 | 90 | 79 | 30 | 30 |  | 96 | 98 | 98 | 98 | 98 | 90 | 90 | 1205520
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 58 | 32 | 32 | 50 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 64 | 64 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2132352
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 30 | 25 | 25 | 25 | 25 | 25 | 38 | 44 | 44 | 45 | 45 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1053600
96 | Chattogram 108 MW PP (ECPV) | 91 | 63 | 0 | [6 empty] | 6 | 35 | 57 | 77 | 86 | 90 | 78 | 64 | 64 |  | 81 | 85 | 84 | 84 | 85 | 85 | 83 | 1225920
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 47 | 55 | 55 | 55 | 42 | 50 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1315132
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  |  |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1125164
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2977036
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1283040
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 110 | 110 | 110 | 256 | 257 | 210 | 205 | 1043927
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 288662
106 | Mymensingh 200 MW PP (United) | 174 | 174 | 174 | 175 | 166 | 165 | 165 | 163 | 163 | 160 | 160 | 160 | 157 | 157 | 155 | 155 | 164 | 175 |  | 177 | 178 | 177 | 180 | 181 | 181 | 173 | 3976800
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 52 | 52 | 52 | 101 | 101 | 101 | 102 | 473305
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 141 | 131 | 131 | 130 | 131 | 132 | 138 | 132 | 147 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3482928
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2318400
116 | Chandpur 200MW (Desh energy) | 172 | 172 | 172 | 172 | 172 | 172 | 172 | 170 | 155 | 155 | 154 | 154 | 155 | 154 | 154 | 154 | 154 | 154 |  | 154 | 154 | 154 | 154 | 154 | 154 | 170 | 388848
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 340 | 340 | 339 | 341 | 340 | 340 | 340 | 401 | 362 | 364 | 334 | 345 | 368 | 370 | 398 | 370 | 368 | 368 |  | 369 | 369 | 368 | 368 | 366 | 367 | 367 | 8679000
| Jamalpur 115 MW PP (United) | 109 | 115 | 115 | 85 | 65 | 45 | 45 | 65 | 75 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2516400
| Anwara 300 MW PP (United) | 143 | 126 | 52 | 16 | 16 | 16 | 16 | 32 | 100 | 151 | 216 | 249 | 252 | 249 | 250 | 250 | 160 | 105 |  | 105 | 105 | 105 | 125 | 125 | 125 | 125 | 3138873
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2420160
| Anlima Energy Ltd. | 56 | 56 | 56 | 56 | 56 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 58 | 58 | 58 |  | 56 | 56 | 56 | 57 | 57 | 57 | 56 | 1377491
| Bhairob 54.5 MW | 37 | 37 | 37 | 37 | 37 | 32 |  |  |  | 16 | 37 | 37 | 21 | 37 | 36 | 37 | 36 | 36 |  | 37 | 37 | 37 | 37 | 36 | 37 | 37 | 737280
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 11 | 18 | 25 | 28 | 31 | 29 | 26 | 20 | 12 | 5 | 1 | [8 empty] | 213419
120 | Eastern Zone Total | 8346 | 8035 | 7725 | 7549 | 7325 | 6870 | 6748 | 6918 | 7192 | 7514 | 7764 | 8113 | 8165 | 8254 | 8460 | 8190 | 7764 | 7557 |  | 8689 | 8877 | 8907 | 9196 | 9176 | 9146 | 9032 | 184021619
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 84 | 86 | 70 |  | 85 | 92 | 99 | 99 | 99 | 99 | 99 | 2106240
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 8 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 | 7 | 3 | 15 | 15 | 15 |  | 15 | 21 | 19 | 19 | 19 | 18 | 18 | 198720
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 91 | 91 | 91 | 89 | 53 | 53 |  | 92 | 92 | 92 | 92 | 92 | 92 | 93 | 2129280
130
131
132 | United Payra Power Ltd. | [19 empty] | 1 | 35 | 35 | 54 | 54 | 35 | 35 | 222000
133 | Bhola Nutan Biddut BD LTD (GAS) | [6 empty] | 37 | 4 | 5 | 4 | 5 | 4 | 3 | 3 | 4 | 4 | 4 |  |  |  |  | 21 | 4 | 4 | 4 | 36 | 124827
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 99 | 96 | 48 | 32 | 16 | 0 | [9 empty] | 16 | 16 | 36 |  | 88 | 110 | 110 | 110 | 110 | 110 | 96 | 102048
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 97 | 97 | 97 | 96 | 97 | 73 | 52 | 51 | 51 | 52 | 58 | 63 | 72 | 92 | 93 | 62 | 63 |  | 92 | 94 | 94 | 96 | 95 | 95 | 95 | 1936835
| Bhola 225 MW CCPP | 68 | 66 | 67 | 68 | 68 | 68 | 69 | 65 | 66 | 66 | 65 | 64 | 64 | 63 | 63 | 65 | 65 | 57 |  | 67 | 67 | 67 | 67 | 67 | 67 | 68 | 1579000
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 29 | 27 | 27 | 26 | 20 | 17 | 18 | 19 | 18 | 20 | 20 | 17 | 24 | 21 | 18 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 632574
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 60 | 30 | 0 | [15 empty] | 38 | 100 | 100 | 100 | 100 | 100 | 100 | 792960
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 16 | 0 |  |  |  |  | 32 | 32 | 32 | 32 | 32 | 32 | 8 | 8 | 8 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 526875
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 9 |  | 9 | 9 | [5 empty] | 16256
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 723 | 722 | 723 | 723 | 723 | 765 | 765 | 808 | 807 | 841 | 842 | 769 | 838 | 841 | 841 | 841 | 842 | 841 |  | 842 | 841 | 842 | 843 | 843 | 843 | 843 | 19333818
147 | Bheramara 410 MW CCPP | 250 | 250 | 250 | 250 | 250 | 260 | 280 | 290 | 290 | 290 | 290 | 315 | 315 | 320 | 335 | 350 | 335 | 315 |  | 295 | 270 | 270 | 250 | 225 | 200 | 175 | 6920928
148 | Payra 1320 MW | 590 | 590 | 590 | 590 | 590 | 560 | 480 | 490 | 500 | 480 | 490 | 500 | 510 | 520 | 550 | 570 | 530 | 520 |  | 560 | 600 | 600 | 610 | 622 | 622 | 622 | 14355400
149
150 | Barapukuria TPP Unit-1 | 75 | 77 | 77 | 78 | 79 | 77 | 77 | 71 | 70 | 71 | 70 | 71 | 71 | 70 | 71 | 71 | 70 | 77 |  | 76 | 75 | 75 | 75 | 76 | 76 | 76 | 1786472
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 3664200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 0 | [9 empty] | 10 | 50 | 50 | 50 | 50 | 50 | 50 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 612000
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 135 | 135 | 135 | 135 | 135 | 100 | [10 empty] | 48 | 100 |  | 120 | 130 | 100 | 80 | 80 | 80 | 80 | 1599000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 190 | 190 | 188 | 187 | 198 | 188 | 178 | 221 | 221 | 217 | 214 | 212 | 213 | 216 | 203 | 204 | 209 | 165 |  | 167 | 190 | 191 | 174 | 159 | 149 | 145 | 4826382
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 201 | 201 | 201 | 201 | 156 | 168 | 187 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 185 | 200 | 200 | 150 |  | 167 | 198 | 194 | 176 | 159 | 153 | 152 | 4521764
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 418 | 418 | 419 | 391 | 407 | 334 | 368 | 329 | 369 | 370 | 371 | 372 | 335 | 337 | 382 | 362 | 357 | 318 |  | 359 | 394 | 395 | 394 | 394 | 372 | 350 | 9070781
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 6 | 7 | 13 | 39 | 39 | 39 |  | 37 | 34 | 43 | 42 | 35 | 33 | 34 | 422426
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 19 | 19 | 19 | 18 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 475200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 5 |  | 5 | 5 | 8 | 11 | 11 | 11 | 11 | 167598
165 | Amnura 50 MW PP(Sinha)
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [12 empty] | 27 | 30 | 30 | 29 | 29 | 29 |  | 30 | 30 | 31 | 31 | 30 | 30 | 30 | 329200
168 | Santahar 50 MW Peaking PP | [15 empty] | 20 | 27 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 27 | 229588
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 43 | 43 | 43 | 43 | 43 | 25 | 25 |  | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 990720
170 | Chapainawabganj 100 MW Peaking PP | 100 | 94 | 0 | [9 empty] | 52 | 54 | 54 | 54 | 54 | 54 |  | 94 | 96 | 94 | 96 | 99 | 99 | 100 | 1067768
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 20 | [6 empty] | 25655
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 94 | 113 | 94 | 94 | 113 | 113 | 70 | 70 |  | 93 | 113 | 113 | 113 | 113 | 113 | 113 | 2604864
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 35 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2614560
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 105 | 107 | 106 | 106 | 107 | 107 | 107 | 104 | 50 | 35 | 35 | 34 | 34 | 34 | 34 | 97 | 113 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2077440
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 5 | 6 | 6 | 6 | 6 | 4 | 3 | 2 | 0 | [8 empty] | 43792
178
178