## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-21 | Wednesday
|  |  | Date (day): | 2021-04-21 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14745.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15595 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-20 | 2021-04-21 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 104 | 104 | 104
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 262 | 278 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 300 | 300 | 150 |  | Dust in the gas line
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 35 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 285 | 285 | 285
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 80 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 95 | 180 | 120 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 90 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 207 | 204 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 38 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 149 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 54 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 43 | 53 | 58 | 58 |  | 22 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 50 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 282 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 52 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 75 | 101 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 60 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2356 | 3301 | 3625 | 3895 | 721 | 1092
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 25 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 218 | 203 | 230 | 230
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 30 | 50 | 100
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 83 | 83 | 83 |  | 19 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 90 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 35 | 10 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 90 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 51 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 109 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 884 | 1214 | 1622 | 1657 | 555 | 143
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 135 | 100 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 209 | 225 | 225
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 340 | 325 | 340 | 340 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 310 | 310 | 310 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 | 19 |  | Gas shortage
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 52 | 50 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 89 | 89 | 90 | 90 | 73 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 178 | 180 | 180 | 200 |  | 50
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 144 | 156 | 184
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 20 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 37 | 36 | 37 | 37 |  | 17 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1600 | 1949 | 1987 | 2225 | 542 | 222
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 162 | 160 | 165
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 50 | 74 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 189 | 182 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 13 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 18 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 465 | 570 | 642.6 | 596 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 40 | 43 | 43 |  | 27 | Engine problem
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 328 | 334 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 48 | 50 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 20 | 33 | 33 |  | 33 | GT-8 Under maint.
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 78 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 20/04/2021
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 148 | 162 | 135 | 150 |  |  | ST under maint.
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 8 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 386 | 375 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 9 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1934 | 2001 | 2072 | 2087 | 0 | 224
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 717 | 717 | 851 | 851
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 4 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 385 | 380 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 33 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 92 | 93 | 93 |  | 12 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1242 | 1441 | 1705 | 1992 | 0 | 118
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 70 | 70 |  | 124 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 82 | 82 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 420 | 540 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 107 | 110 | 109 | 110 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 695 | 941 | 1189 | 1190 | 0 | 124
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 35 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 24 | 50 | 50
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 31 |  | 19 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 100 | 128 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 180 | 182 | 180 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 190 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 404 | 413 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 32
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 43 | 43 |  | 9 | Engine problem
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 97 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 1150 | 1479 | 1547 | 1605 | 431 | 28
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 78 | 71 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 225 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 111 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 421 | 332 | 356 | 348 | 124 | 115
|  | Total |  |  |  |  | 21967 | 21219 | 10747 | 13228 | 14745.6 | 15595 | 2373 | 2087
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10305.8433 | 12685 | 14140.3036 | 14954.8363
| A. |  | 2021-04-20 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13296 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9565 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13228 | MW
| 3 | Day peak Generation : |  |  | 10747 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12685 | MW
| 4 | Evening peak Generation : |  |  | 13228 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 273.2645 | MKWHr | By Solar | 0.81196 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 152.7933 | MKWHr |  | By Oil: | 79.6446 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 18.6476 | MKWHr |  | By Hydro: | 0.848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2373 | MW | Dhaka | 4292 | 4292 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2087 | MW | Chittagong | 1308 | 1308 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4460 | MW | Khulna | 1608 | 1608 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1279.9 | MMCFD |  |  | Rajshahi | 1488 | 1488 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161984375.682 | ii) Oil : | Taka | 570824078.82 | Comilla | 1283 | 1283 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 89265298.35 | Total | Taka | 822073752.852 | Mymensingh | 1101 | 1101 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.051 | MKWHr. | Sylhet | 501 | 501 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -60 | MW (E to W) at | 21:00 | hrs | Barisal | 378 | 378 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -136 | MW at | 18:30 | hrs | Rangpur | 726 | 726 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.9° C |  |  | Total | 12685 | 12685 |  | 0
| B. |  | 2021-04-21 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 38.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15595 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11300 | MW
| 4 | Reserve(Generation end) |  |  |  | 2095 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 277.4572 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10015 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2953 | MKWHr. | ii) HVDC Flow at Peak Time |  | 717 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.2237 | MKWHr. | iii) Maximum HVDC Flow : |  | 717 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.92 |  | (b) Today: | 78.75 |  | (c) Rule Curve: |  | 84.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-20
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 319 |  | 0 | 280 | 240 | 100 | 0 | 40 | 224 | 0 | 115 | 100 | 64 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 54 | 22 | 25 | 29 | 28 | 33 | 16 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 23 | 0 | 68 | 92 | 51 | 50 | 21 | 38 | 80 | 0 | 0 | 310 | 260 | 214 | 8 | 87 | 23 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 160 | 65 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 332 | 30 | 78 | 0 | 136 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 200 | 0 | 0 | 194 | 0 | 136 | 0 | 50 | 178 | 0 | 367 | 75 | 90 | 0 | 0 | 70 | 54 | 0 | 17 | 113 | 100 | 370 | 104 | 0 | 162 | 115 | 0 | 37 | 0 |  | 714 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 30 | 52 | 32 | 22 | 0 | 10 | 75 | 0 | 150 | 0 | 0 | 120 | 0 | 183 | 0 | 81 | 0 | 185 | 0 | 355 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 540 | 107 | 0 | 0 |  | 8017 | 3760 | 11777 | 4540 | 714 | 1947 | 3412 | 765 | 35 | 220 | 144 | 0 | 0 | 79.02
2:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 340 |  | 0 | 280 | 255 | 70 | 0 | 40 | 180 | 0 | 120 | 100 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 54 | 22 | 25 | 29 | 28 | 33 | 8 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 23 | 0 | 68 | 92 | 51 | 50 | 21 | 38 | 80 | 0 | 0 | 310 | 260 | 214 | 8 | 88 | 23 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 142 | 162 | 57 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 332 | 30 | 78 | 0 | 136 | 18 | 0 | 9 | 285 | 8 | 11 | 0 | 95 | 0 | 0 | 194 | 0 | 143 | 0 | 50 | 169 | 0 | 366 | 55 | 90 | 0 | 0 | 71 | 54 | 0 | 17 | 113 | 100 | 370 | 104 | 0 | 108 | 116 | 0 | 36 | 0 |  | 714 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 30 | 52 | 32 | 22 | 0 | 10 | 76 | 0 | 150 | 0 | 0 | 100 | 0 | 161 | 0 | 82 | 0 | 185 | 0 | 373 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 520 | 108 | 0 | 0 |  | 7753 | 3716 | 11469 | 4453 | 714 | 1990 | 3169 | 746 | 35 | 220 | 142 | 0 | 0 | 79
3:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 348 |  | 0 | 280 | 260 | 50 | 0 | 55 | 180 | 0 | 180 | 100 | 32 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 29 | 28 | 33 | 8 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 68 | 92 | 51 | 50 | 21 | 39 | 80 | 0 | 0 | 310 | 260 | 212 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 163 | 49 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 332 | 30 | 78 | 0 | 136 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 95 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 160 | 0 | 364 | 55 | 84 | 0 | 0 | 52 | 54 | 0 | 17 | 113 | 100 | 377 | 104 | 0 | 108 | 116 | 0 | 36 | 0 |  | 715 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 16 | 65 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 30 | 52 | 32 | 22 | 0 | 10 | 77 | 0 | 150 | 0 | 0 | 100 | 0 | 160 | 0 | 81 | 0 | 188 | 0 | 414 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 520 | 108 | 0 | 0 |  | 7816 | 3765 | 11581 | 4525 | 715 | 2054 | 3141 | 747 | 35 | 220 | 144 | 0 | 0 | 78.98
4:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 349 |  | 0 | 280 | 270 | 55 | 0 | 55 | 180 | 0 | 150 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 26 | 28 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 30 | 50 | 21 | 40 | 80 | 0 | 0 | 320 | 275 | 213 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 163 | 41 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 332 | 30 | 78 | 0 | 136 | 18 | 0 | 7 | 290 | 8 | 11 | 0 | 85 | 0 | 0 | 200 | 0 | 149 | 0 | 50 | 160 | 0 | 368 | 35 | 52 | 0 | 0 | 16 | 54 | 0 | 0 | 113 | 100 | 400 | 104 | 0 | 35 | 116 | 0 | 36 | 0 |  | 715 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 10 | 76 | 0 | 150 | 0 | 0 | 100 | 0 | 185 | 0 | 80 | 0 | 186 | 0 | 414 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 500 | 108 | 0 | 0 |  | 7492 | 3623 | 11115 | 4578 | 715 | 2043 | 2874 | 726 | 35 | 0 | 144 | 0 | 0 | 78.96
5:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 351 |  | 0 | 280 | 250 | 12 | 0 | 55 | 180 | 0 | 150 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 26 | 28 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 202 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 0 | 25 | 21 | 40 | 80 | 0 | 0 | 310 | 260 | 214 | 8 | 90 | 23 | 20 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 136 | 168 | 33 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 334 | 30 | 78 | 0 | 136 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 149 | 0 | 50 | 160 | 0 | 368 | 0 | 52 | 0 | 0 | 0 | 54 | 0 | 0 | 65 | 100 | 370 | 104 | 0 | 17 | 72 | 0 | 36 | 0 |  | 714 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 77 | 0 | 150 | 0 | 0 | 100 | 0 | 185 | 0 | 81 | 0 | 187 | 0 | 396 | 35 | 0 | 113 | 0 | 90 | 0 | 0 | 70 | 500 | 108 | 0 | 0 |  | 6872 | 3392 | 10264 | 4517 | 714 | 2027 | 2108 | 727 | 35 | 0 | 136 | 0 | 0 | 78.94
6:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 308 |  | 0 | 280 | 265 | 0 | 0 | 30 | 180 | 0 | 118 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 26 | 28 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 5 | 0 | 0 | 50 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 310 | 260 | 214 | 8 | 90 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 124 | 171 | 33 | 19 | 0 | 40 | 43 | 50 | 0 | 110 | 330 | 30 | 78 | 0 | 136 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 140 | 1 | 50 | 160 | 0 | 365 | 0 | 52 | 0 | 0 | 0 | 54 | 0 | 0 | 36 | 100 | 347 | 53 | 1 | 17 | 72 | 0 | 36 | 1 |  | 714 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 77 | 0 | 150 | 0 | 0 | 80 | 0 | 164 | 0 | 82 | 0 | 180 | 0 | 365 | 17 | 0 | 70 | 0 | 71 | 0 | 0 | 70 | 460 | 108 | 0 | 0 |  | 6439 | 3195 | 9634 | 4416 | 714 | 1905 | 1750 | 687 | 35 | 0 | 124 | 3 | 0 | 78.92
7:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 308 |  | 0 | 280 | 275 | 0 | 0 | 30 | 180 | 0 | 118 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 29 | 28 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 6 | 0 | 0 | 50 | 0 | 0 | 21 | 15 | 80 | 0 | 0 | 315 | 275 | 214 | 8 | 90 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 33 | 20 | 124 | 173 | 33 | 19 | 0 | 42 | 43 | 50 | 0 | 110 | 331 | 30 | 75 | 0 | 136 | 18 | 0 | 9 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 149 | 5 | 50 | 160 | 0 | 371 | 0 | 52 | 0 | 1 | 0 | 54 | 0 | 0 | 36 | 100 | 350 | 53 | 5 | 17 | 72 | 0 | 36 | 7 |  | 715 | 0 | 370 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 77 | 0 | 150 | 0 | 0 | 80 | 0 | 154 | 0 | 81 | 0 | 169 | 0 | 365 | 17 | 0 | 70 | 0 | 34 | 0 | 1 | 70 | 420 | 108 | 0 | 0 |  | 6476 | 3089 | 9565 | 4433 | 715 | 1875 | 1717 | 647 | 35 | 0 | 124 | 19 | 0 | 78.91
8:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 308 |  | 0 | 280 | 275 | 0 | 0 | 30 | 218 | 0 | 118 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 22 | 25 | 28 | 28 | 33 | 4 | 0 | 0 | 35 | 0 | 0 | 17 | 216 | 0 | 130 | 0 |  | 5 | 0 | 0 | 50 | 0 | 7 | 21 | 3 | 80 | 0 | 0 | 335 | 285 | 211 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 33 | 20 | 112 | 170 | 33 | 19 | 1 | 42 | 43 | 50 | 0 | 110 | 330 | 30 | 75 | 0 | 136 | 18 | 0 | 9 | 310 | 8 | 11 | 0 | 30 | 0 | 0 | 120 | 0 | 149 | 8 | 50 | 160 | 0 | 380 | 0 | 70 | 0 | 3 | 0 | 54 | 0 | 0 | 36 | 100 | 351 | 53 | 25 | 17 | 72 | 0 | 37 | 15 |  | 714 | 0 | 380 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 10 | 76 | 0 | 150 | 0 | 0 | 80 | 0 | 172 | 0 | 80 | 0 | 187 | 0 | 364 | 17 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 400 | 109 | 0 | 0 |  | 6607 | 3113 | 9720 | 4561 | 714 | 1872 | 1746 | 626 | 35 | 0 | 112 | 54 | 0 | 78.9
9:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 347 |  | 0 | 280 | 275 | 4 | 0 | 30 | 217 | 0 | 118 | 7 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 22 | 25 | 28 | 28 | 33 | 8 | 0 | 0 | 35 | 0 | 0 | 17 | 205 | 0 | 130 | 0 |  | 8 | 0 | 0 | 50 | 0 | 24 | 21 | 2 | 80 | 0 | 0 | 325 | 280 | 195 | 8 | 88 | 23 | 20 | 0 | 0 | 0 | 0 | 0 | 22 | 2 | 33 | 20 | 110 | 159 | 33 | 19 | 2 | 40 | 43 | 50 | 0 | 130 | 330 | 30 | 72 | 0 | 135 | 18 | 0 | 7 | 310 | 8 | 11 | 0 | 30 | 0 | 0 | 127 | 0 | 149 | 13 | 50 | 160 | 0 | 375 | 0 | 85 | 0 | 4 | 0 | 54 | 0 | 0 | 47 | 100 | 350 | 68 | 19 | 17 | 80 | 0 | 37 | 23 |  | 715 | 0 | 380 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 10 | 76 | 0 | 150 | 0 | 0 | 80 | 0 | 181 | 0 | 82 | 0 | 202 | 0 | 366 | 17 | 0 | 84 | 0 | 91 | 0 | 4 | 90 | 400 | 106 | 0 | 0 |  | 6745 | 3229 | 9974 | 4521 | 715 | 1923 | 1979 | 626 | 35 | 0 | 110 | 65 | 0 | 78.89
10:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 314 |  | 0 | 280 | 275 | 32 | 0 | 40 | 211 | 0 | 120 | 7 | 48 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 33 | 13 | 0 | 0 | 35 | 0 | 0 | 17 | 217 | 0 | 130 | 0 |  | 18 | 0 | 0 | 80 | 0 | 25 | 21 | 2 | 80 | 0 | 0 | 340 | 295 | 182 | 8 | 89 | 20 | 20 | 0 | 0 | 0 | 0 | 7 | 22 | 0 | 33 | 20 | 102 | 158 | 33 | 19 | 2 | 39 | 43 | 50 | 0 | 130 | 330 | 30 | 75 | 0 | 149 | 18 | 0 | 7 | 310 | 8 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 149 | 11 | 50 | 160 | 0 | 403 | 0 | 67 | 0 | 5 | 0 | 54 | 0 | 0 | 81 | 100 | 350 | 104 | 23 | 18 | 114 | 0 | 36 | 29 |  | 714 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 77 | 0 | 150 | 0 | 0 | 80 | 0 | 185 | 0 | 83 | 0 | 199 | 0 | 367 | 17 | 0 | 94 | 0 | 113 | 0 | 6 | 95 | 400 | 108 | 0 | 0 |  | 7017 | 3283 | 10300 | 4589 | 714 | 1895 | 2262 | 627 | 35 | 0 | 102 | 76 | 0 | 78.88
11:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 0 | 270 |  | 0 | 280 | 275 | 32 | 0 | 35 | 210 | 0 | 71 | 55 | 48 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 18 | 33 | 33 | 34 | 0 | 0 | 35 | 0 | 0 | 17 | 216 | 0 | 130 | 0 |  | 18 | 0 | 0 | 80 | 0 | 25 | 21 | 2 | 80 | 0 | 0 | 310 | 270 | 208 | 8 | 88 | 20 | 20 | 0 | 0 | 0 | 0 | 8 | 20 | 0 | 33 | 20 | 116 | 146 | 33 | 19 | 2 | 39 | 43 | 50 | 0 | 110 | 327 | 30 | 78 | 0 | 149 | 18 | 0 | 7 | 300 | 8 | 11 | 0 | 30 | 0 | 0 | 189 | 0 | 149 | 17 | 50 | 170 | 0 | 371 | 8 | 67 | 0 | 3 | 0 | 54 | 0 | 0 | 109 | 100 | 350 | 104 | 51 | 54 | 116 | 0 | 37 | 33 |  | 717 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 78 | 0 | 217 | 0 | 0 | 80 | 0 | 169 | 0 | 83 | 0 | 193 | 0 | 368 | 53 | 0 | 94 | 0 | 113 | 0 | 6 | 95 | 400 | 108 | 0 | 0 |  | 7052 | 3384 | 10436 | 4407 | 717 | 1823 | 2531 | 695 | 35 | 0 | 116 | 112 | 0 | 78.87
12:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 0 | 262 |  | 0 | 280 | 275 | 35 | 0 | 30 | 207 | 0 | 95 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 38 | 35 | 35 | 22 | 25 | 18 | 33 | 33 | 41 | 0 | 0 | 35 | 0 | 0 | 17 | 218 | 0 | 130 | 0 |  | 18 | 0 | 0 | 92 | 0 | 25 | 21 | 2 | 80 | 0 | 0 | 340 | 295 | 205 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 8 | 20 | 11 | 33 | 20 | 120 | 148 | 50 | 19 | 2 | 39 | 43 | 48 | 0 | 130 | 328 | 30 | 78 | 0 | 148 | 18 | 0 | 7 | 310 | 8 | 11 | 0 | 30 | 0 | 0 | 189 | 0 | 149 | 19 | 50 | 178 | 0 | 386 | 13 | 75 | 0 | 5 | 0 | 54 | 0 | 0 | 113 | 100 | 350 | 104 | 26 | 60 | 116 | 0 | 37 | 34 |  | 717 | 0 | 385 | 0 | 83 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 78 | 0 | 225 | 0 | 0 | 100 | 0 | 180 | 0 | 82 | 0 | 196 | 0 | 404 | 53 | 0 | 94 | 0 | 112 | 0 | 6 | 95 | 420 | 107 | 0 | 0 |  | 7239 | 3508 | 10747 | 4573 | 717 | 1877 | 2606 | 723 | 35 | 4 | 120 | 92 | 0 | 78.86
13:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 0 | 263 |  | 0 | 280 | 245 | 80 | 0 | 35 | 175 | 0 | 85 | 100 | 75 | 48 | 23 | 0 | 0 | 0 | 54 | 35 | 35 | 22 | 25 | 18 | 33 | 33 | 41 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 9 | 92 | 18 | 30 | 21 | 9 | 80 | 0 | 0 | 310 | 265 | 209 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 32 | 19 | 11 | 33 | 20 | 124 | 149 | 74 | 19 | 2 | 39 | 43 | 47 | 0 | 163 | 330 | 30 | 76 | 0 | 148 | 18 | 0 | 9 | 305 | 8 | 11 | 0 | 86 | 0 | 0 | 179 | 0 | 149 | 19 | 50 | 178 | 0 | 367 | 64 | 85 | 0 | 1 | 5 | 46 | 0 | 17 | 113 | 90 | 350 | 104 | 53 | 141 | 116 | 0 | 37 | 33 |  | 716 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 5 | 32 | 66 | 21 | 0 | 0 | 0 | 0 | 15 | 4 | 0 | 0 | 8 | 0 | 52 | 0 | 16 | 0 | 11 | 77 | 0 | 243 | 0 | 0 | 132 | 0 | 184 | 0 | 82 | 0 | 191 | 0 | 394 | 55 | 0 | 94 | 0 | 110 | 0 | 7 | 95 | 440 | 104 | 0 | 0 |  | 7574 | 3608 | 11182 | 4445 | 716 | 1897 | 3009 | 760 | 35 | 81 | 124 | 115 | 0 | 78.85
14:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 0 | 256 |  | 0 | 280 | 245 | 91 | 0 | 55 | 150 | 0 | 113 | 100 | 102 | 48 | 50 | 0 | 0 | 0 | 54 | 50 | 35 | 22 | 25 | 24 | 33 | 33 | 41 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 49 | 92 | 51 | 45 | 21 | 2 | 80 | 0 | 0 | 310 | 265 | 205 | 8 | 87 | 26 | 47 | 0 | 0 | 0 | 6 | 52 | 19 | 11 | 33 | 20 | 132 | 148 | 65 | 0 | 2 | 39 | 43 | 47 | 0 | 130 | 330 | 30 | 75 | 0 | 149 | 18 | 0 | 9 | 290 | 8 | 11 | 0 | 280 | 0 | 0 | 188 | 0 | 149 | 17 | 50 | 178 | 0 | 367 | 88 | 85 | 0 | 5 | 16 | 54 | 0 | 17 | 112 | 100 | 370 | 104 | 39 | 162 | 116 | 0 | 37 | 28 |  | 716 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 0 | 5 | 32 | 66 | 24 | 0 | 0 | 0 | 0 | 50 | 10 | 0 | 0 | 8 | 0 | 52 | 0 | 16 | 0 | 11 | 76 | 0 | 290 | 0 | 0 | 116 | 0 | 167 | 0 | 82 | 0 | 188 | 0 | 361 | 90 | 0 | 104 | 0 | 107 | 0 | 6 | 95 | 450 | 106 | 0 | 0 |  | 8019 | 3671 | 11690 | 4421 | 716 | 1835 | 3470 | 816 | 35 | 168 | 132 | 97 | 0 | 78.84
15:00 | 0 | 0 | 0 | 190 | 0 | 96 | 0 | 0 | 270 |  | 0 | 280 | 245 | 91 | 0 | 55 | 150 | 0 | 155 | 100 | 102 | 48 | 50 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 12 | 0 | 49 | 92 | 51 | 50 | 21 | 3 | 80 | 0 | 0 | 310 | 265 | 204 | 8 | 87 | 26 | 46 | 0 | 0 | 0 | 50 | 52 | 19 | 11 | 33 | 20 | 148 | 147 | 65 | 0 | 1 | 39 | 42 | 47 | 0 | 130 | 328 | 20 | 75 | 0 | 149 | 18 | 0 | 8 | 290 | 8 | 11 | 0 | 297 | 0 | 0 | 188 | 0 | 140 | 13 | 50 | 178 | 0 | 368 | 108 | 85 | 0 | 3 | 16 | 54 | 0 | 17 | 113 | 100 | 370 | 104 | 35 | 162 | 116 | 0 | 11 | 7 |  | 716 | 0 | 360 | 0 | 66 | 0 | 0 | 0 | 0 | 5 | 32 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 14 | 0 | 0 | 8 | 0 | 52 | 0 | 15 | 0 | 11 | 74 | 0 | 300 | 0 | 0 | 113 | 0 | 159 | 0 | 83 | 0 | 187 | 0 | 400 | 90 | 0 | 101 | 0 | 112 | 0 | 5 | 95 | 470 | 107 | 0 | 0 |  | 8112 | 3714 | 11826 | 4437 | 716 | 1882 | 3484 | 844 | 35 | 216 | 148 | 64 | 0 | 78.83
16:00 | 0 | 0 | 0 | 190 | 0 | 96 | 0 | 0 | 260 |  | 0 | 280 | 245 | 80 | 0 | 55 | 150 | 0 | 150 | 100 | 64 | 48 | 14 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 18 | 0 | 49 | 50 | 23 | 50 | 21 | 3 | 80 | 0 | 0 | 310 | 295 | 204 | 8 | 86 | 23 | 47 | 0 | 0 | 0 | 49 | 52 | 20 | 11 | 33 | 20 | 134 | 148 | 74 | 19 | 1 | 39 | 42 | 45 | 0 | 130 | 330 | 20 | 75 | 0 | 149 | 18 | 0 | 8 | 290 | 0 | 11 | 0 | 210 | 0 | 0 | 188 | 0 | 130 | 8 | 50 | 178 | 0 | 368 | 55 | 70 | 0 | 2 | 16 | 54 | 0 | 17 | 111 | 100 | 370 | 104 | 22 | 108 | 116 | 0 | 36 | 14 |  | 716 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 32 | 66 | 21 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 8 | 0 | 16 | 0 | 15 | 0 | 11 | 72 | 0 | 241 | 0 | 0 | 119 | 0 | 159 | 0 | 84 | 0 | 187 | 0 | 396 | 91 | 0 | 113 | 0 | 104 | 0 | 4 | 95 | 450 | 106 | 0 | 0 |  | 7774 | 3621 | 11395 | 4480 | 716 | 1864 | 3134 | 763 | 35 | 218 | 134 | 51 | 0 | 78.82
17:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 0 | 260 |  | 0 | 280 | 245 | 55 | 0 | 55 | 150 | 0 | 150 | 50 | 64 | 48 | 10 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 0 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 49 | 50 | 24 | 50 | 21 | 15 | 80 | 0 | 0 | 310 | 295 | 206 | 8 | 88 | 26 | 48 | 0 | 0 | 0 | 49 | 52 | 20 | 11 | 33 | 20 | 120 | 148 | 74 | 19 | 0 | 39 | 42 | 48 | 0 | 130 | 331 | 20 | 75 | 0 | 149 | 18 | 0 | 8 | 285 | 0 | 11 | 0 | 208 | 0 | 0 | 188 | 0 | 149 | 3 | 90 | 178 | 0 | 367 | 55 | 102 | 0 | 1 | 16 | 54 | 0 | 17 | 110 | 100 | 370 | 104 | 9 | 108 | 112 | 0 | 37 | 6 |  | 716 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 32 | 65 | 21 | 0 | 0 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 16 | 0 | 16 | 0 | 11 | 74 | 0 | 156 | 0 | 0 | 105 | 0 | 160 | 0 | 82 | 0 | 188 | 0 | 392 | 70 | 0 | 70 | 0 | 107 | 0 | 1 | 70 | 450 | 106 | 0 | 0 |  | 7714 | 3439 | 11153 | 4449 | 716 | 1876 | 3039 | 680 | 35 | 218 | 120 | 20 | 0 | 78.82
18:00 | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 0 | 257 |  | 0 | 280 | 245 | 55 | 0 | 55 | 150 | 0 | 120 | 50 | 64 | 48 | 10 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 20 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 49 | 50 | 14 | 50 | 21 | 18 | 80 | 0 | 0 | 310 | 295 | 206 | 8 | 87 | 26 | 49 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 130 | 150 | 74 | 19 | 0 | 39 | 43 | 48 | 0 | 110 | 331 | 20 | 76 | 0 | 149 | 18 | 0 | 8 | 290 | 8 | 11 | 0 | 210 | 0 | 0 | 180 | 0 | 149 | 0 | 90 | 178 | 0 | 367 | 55 | 102 | 0 | 0 | 16 | 54 | 0 | 17 | 113 | 100 | 377 | 104 | 1 | 108 | 109 | 0 | 18 | 0 |  | 716 | 0 | 360 | 0 | 89 | 0 | 0 | 0 | 3 | 0 | 32 | 65 | 21 | 6 | 0 | 0 | 0 | 50 | 43 | 0 | 0 | 0 | 5 | 16 | 15 | 18 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 105 | 0 | 159 | 0 | 83 | 0 | 165 | 0 | 334 | 70 | 0 | 70 | 0 | 107 | 0 | 0 | 70 | 450 | 106 | 0 | 0 |  | 7668 | 3392 | 11060 | 4434 | 716 | 1808 | 3000 | 673 | 35 | 263 | 130 | 1 | 0 | 78.81
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 302 |  | 0 | 280 | 260 | 88 | 0 | 55 | 204 | 0 | 155 | 70 | 85 | 149 | 77 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 20 | 33 | 17 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 83 | 100 | 60 | 50 | 21 | 25 | 110 | 0 | 0 | 315 | 300 | 207 | 8 | 88 | 26 | 49 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 154 | 151 | 74 | 19 | 0 | 40 | 43 | 48 | 0 | 163 | 332 | 20 | 77 | 0 | 162 | 18 | 0 | 9 | 280 | 8 | 11 | 20 | 245 | 0 | 25 | 180 | 30 | 149 | 0 | 90 | 178 | 0 | 367 | 115 | 102 | 2 | 0 | 16 | 54 | 0 | 99 | 113 | 100 | 400 | 104 | 0 | 153 | 109 | 0 | 37 | 0 |  | 716 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 33 | 65 | 33 | 70 | 0 | 0 | 0 | 50 | 39 | 97 | 0 | 0 | 30 | 52 | 34 | 19 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 117 | 0 | 162 | 0 | 84 | 25 | 164 | 0 | 396 | 92 | 0 | 105 | 0 | 107 | 0 | 0 | 95 | 470 | 106 | 0 | 2 |  | 8674 | 3875 | 12549 | 4607 | 716 | 1983 | 3815 | 694 | 35 | 545 | 154 | 0 | 0 | 78.8
19:30 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 304 |  | 0 | 280 | 260 | 100 | 0 | 55 | 204 | 0 | 170 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 20 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 83 | 100 | 86 | 50 | 21 | 29 | 135 | 0 | 0 | 310 | 295 | 209 | 8 | 84 | 26 | 51 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 152 | 153 | 74 | 19 | 0 | 40 | 43 | 48 | 0 | 163 | 333 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 285 | 8 | 11 | 50 | 245 | 0 | 25 | 180 | 50 | 149 | 0 | 90 | 178 | 0 | 367 | 115 | 102 | 17 | 0 | 16 | 54 | 10 | 99 | 113 | 100 | 370 | 104 | 0 | 162 | 109 | 0 | 37 | 0 |  | 716 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 18 | 0 | 33 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 41 | 97 | 0 | 8 | 30 | 52 | 34 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 134 | 0 | 178 | 0 | 83 | 100 | 186 | 0 | 378 | 92 | 0 | 113 | 0 | 107 | 0 | 0 | 95 | 530 | 106 | 0 | 17 |  | 8895 | 4120 | 13015 | 4674 | 716 | 1980 | 4153 | 753 | 35 | 552 | 152 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 290 |  | 0 | 280 | 265 | 100 | 0 | 55 | 204 | 0 | 180 | 100 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 50 | 54 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 83 | 100 | 89 | 50 | 21 | 31 | 135 | 0 | 0 | 310 | 295 | 209 | 8 | 87 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 158 | 153 | 74 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 334 | 20 | 78 | 0 | 162 | 18 | 0 | 8 | 280 | 8 | 11 | 20 | 270 | 0 | 0 | 182 | 50 | 149 | 0 | 90 | 178 | 0 | 367 | 115 | 102 | 16 | 0 | 16 | 54 | 21 | 114 | 113 | 100 | 370 | 104 | 0 | 162 | 109 | 0 | 37 | 0 |  | 716 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 34 | 110 | 0 | 0 | 0 | 50 | 40 | 97 | 0 | 8 | 31 | 52 | 33 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 131 | 0 | 178 | 0 | 82 | 100 | 186 | 0 | 382 | 92 | 0 | 113 | 0 | 107 | 0 | 0 | 95 | 520 | 107 | 0 | 17 |  | 8912 | 4107 | 13019 | 4687 | 716 | 1970 | 4158 | 742 | 35 | 553 | 158 | 0 | 0 | 78.8
21:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 278 |  | 0 | 280 | 285 | 100 | 0 | 55 | 204 | 0 | 180 | 90 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 54 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 83 | 100 | 90 | 50 | 21 | 35 | 135 | 0 | 0 | 325 | 310 | 209 | 8 | 89 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 144 | 162 | 74 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 334 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 290 | 8 | 11 | 20 | 282 | 0 | 0 | 182 | 52 | 149 | 0 | 90 | 180 | 0 | 375 | 115 | 101 | 30 | 0 | 16 | 54 | 51 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 109 | 0 | 36 | 0 |  | 717 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 34 | 110 | 0 | 0 | 0 | 50 | 40 | 97 | 0 | 24 | 30 | 52 | 33 | 21 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 128 | 0 | 182 | 0 | 82 | 100 | 190 | 0 | 413 | 92 | 0 | 113 | 0 | 111 | 0 | 0 | 95 | 540 | 110 | 0 | 0 |  | 9035 | 4193 | 13228 | 4797 | 717 | 2007 | 4215 | 761 | 35 | 552 | 144 | 0 | 0 | 78.8
22:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 262 |  | 0 | 280 | 280 | 100 | 0 | 55 | 204 | 0 | 185 | 92 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 18 | 0 | 83 | 100 | 90 | 50 | 21 | 36 | 135 | 0 | 0 | 330 | 310 | 210 | 8 | 89 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 144 | 162 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 330 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 305 | 8 | 11 | 20 | 282 | 0 | 0 | 182 | 52 | 149 | 0 | 90 | 198 | 0 | 376 | 115 | 101 | 45 | 0 | 16 | 54 | 51 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 109 | 0 | 36 | 0 |  | 716 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 97 | 0 | 43 | 30 | 52 | 33 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 130 | 0 | 183 | 0 | 82 | 100 | 191 | 0 | 416 | 92 | 0 | 113 | 0 | 112 | 0 | 0 | 95 | 540 | 110 | 0 | 0 |  | 9077 | 4219 | 13296 | 4809 | 716 | 2012 | 4266 | 762 | 35 | 552 | 144 | 0 | 0 | 78.79
23:00 | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 263 |  | 0 | 280 | 270 | 100 | 0 | 55 | 204 | 0 | 185 | 91 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 209 | 0 | 130 | 0 |  | 18 | 0 | 83 | 92 | 83 | 50 | 21 | 39 | 135 | 0 | 0 | 325 | 310 | 211 | 8 | 89 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 188 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 333 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 282 | 0 | 0 | 182 | 0 | 149 | 0 | 90 | 194 | 0 | 376 | 115 | 100 | 70 | 0 | 0 | 54 | 17 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 109 | 0 | 37 | 0 |  | 716 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 34 | 64 | 0 | 0 | 0 | 50 | 25 | 97 | 0 | 0 | 30 | 52 | 33 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 141 | 0 | 184 | 0 | 81 | 100 | 192 | 0 | 418 | 92 | 0 | 113 | 0 | 112 | 0 | 0 | 95 | 540 | 110 | 0 | 0 |  | 8937 | 4138 | 13075 | 4866 | 716 | 2012 | 4050 | 765 | 35 | 487 | 144 | 0 | 0 | 78.79
24:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 283 |  | 0 | 280 | 245 | 100 | 0 | 55 | 204 | 0 | 185 | 93 | 102 | 150 | 88 | 0 | 0 | 0 | 54 | 35 | 54 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 19 | 0 | 83 | 92 | 71 | 50 | 21 | 39 | 135 | 0 | 0 | 310 | 290 | 212 | 8 | 89 | 26 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 154 | 186 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 332 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 282 | 0 | 0 | 182 | 0 | 149 | 0 | 90 | 197 | 0 | 366 | 115 | 100 | 80 | 0 | 0 | 54 | 17 | 114 | 113 | 100 | 370 | 104 | 0 | 156 | 90 | 0 | 36 | 0 |  | 716 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 34 | 64 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 136 | 0 | 188 | 0 | 81 | 100 | 197 | 0 | 395 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 95 | 540 | 109 | 0 | 0 |  | 8840 | 4088 | 12928 | 4782 | 716 | 2023 | 3991 | 765 | 35 | 462 | 154 | 0 | 0 | 78.78
KWH | 0 | 0 | 0 | 4554900 | 0 | 2411863 | 0 | 0 | 7032000 |  | 0 | 6644750 | 6334953 | 1476480 | 0 | 1155274 | 465437 | 0 | 3507000 | 1766400 | 1459872 | 1256640 | 770550 | 0 | 0 | 0 | 1272960 | 1015289 | 1070410 | 484416 | 600000 | 580860 | 788000 | 802800 | 668640 | 0 | 0 | 848000 | 0 | 0 | 415915 | 4856118 | 0 | 3122828 | 0 |  | 422400 | 0 | 972185 | 1913040 | 849600 | 939360 | 502992 | 525120 | 2204578 | 0 | 0 | 7947400 | 6879000 | 5030000 | 217454 | 2096990 | 518256 | 826080 | 0 | 0 | 0 | 433064 | 879806 | 496620 | 227160 | 817200 | 500390 | 3223680 | 3721680 | 1354560 | 403128 | 15400 | 953000 | 1015680 | 1195200 | 0 | 3496418 | 7576000 | 626784 | 1830720 | 0 | 3535440 | 412000 | 0 | 198360 | 7339000 | 180936 | 264000 | 104640 | 3768653 | 0 | 21972 | 4140000 | 186592 | 3553780 | 130410 | 1501440 | 4207680 | 0 | 8935000 | 1482000 | 1994400 | 231672 | 36600 | 416509 | 1292347 | 200720 | 793440 | 2481360 | 2413440 | 8808500 | 2410560 | 346080 | 2557440 | 2545473 | 0 | 842400 | 235986 |  | 17295272 | 0 | 9049536 | 0 | 2151360 | 0 | 0 | 0 | 125760 | 14336 | 443625 | 1561000 | 620516 | 821664 | 0 | 0 | 0 | 537152 | 267810 | 804240 | 0 | 112685 | 266200 | 919680 | 323670 | 453600 | 0 | 239976 | 1806545 | 0 | 4310100 | 0 | 0 | 2770500 | 0 | 4375018 | 0 | 1976980 | 553920 | 4732773 | 0 | 9210454 | 1658400 | 0 | 2445216 | 0 | 2413440 | 0 | 47484 | 2188704 | 12531000 | 2670927 | 0 | 22800 |  | 183542130 | 89722343 | 273264473 | 106143896 | 17295272 | 46649442 | 74643521 | 18647645 | 848000 | 5001057 | 3223680 | 811960 | 0
Fuel Cost | 0 | 0 | 0 | 6695703 | 0 | 3183659.16 | 0 | 0 | 7242960 |  | 0 | 7242777.5 | 7031797.83 | 11206483.2 | 0 | 9773618.04 | 484054.48 | 0 | 6067110 | 13300992 | 13314032.64 | 12365337.6 | 7104471 | 0 | 0 | 0 | 9292608 | 7848183.97 | 10554242.6 | 363312 | 450000 | 0 | 0 | 0 | 6465748.8 | 0 | 0 | 228960 | 0 | 0 | 3863850.35 | 5293168.62 | 0 | 5308807.6 | 0 |  | 0 | 0 | 9430194.5 | 18269532 | 7391520 | 7439731.2 | 633769.92 | 1559606.4 | 3262775.44 | 0 | 0 | 5881076 | 6879000 | 4627600 | 280515.66 | 2411538.5 | 585629.28 | 1156512 | 0 | 0 | 0 | 4373946.4 | 8402147.3 | 630707.4 | 170370 | 1430100 | 375292.5 | 24177600 | 3944980.8 | 12299404.8 | 511972.56 | 245476 | 1562920 | 1625088 | 2127456 | 0 | 3985916.52 | 7879040 | 1234764.48 | 3496675.2 | 0 | 6116311.2 | 902280 | 0 | 404654.4 | 7412390 | 135702 | 200640 | 1779926.4 | 28491016.68 | 0 | 367371.84 | 21528000 | 3119818.24 | 34969195.2 | 1524492.9 | 12236736 | 45653328 | 0 | 8309550 | 13515840 | 18847080 | 2017863.12 | 0 | 3148808.04 | 11256342.37 | 1764328.8 | 7918531.2 | 21265255.2 | 16073510.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99620766.72 | 0 | 9502012.8 | 0 | 16909689.6 | 0 | 0 | 0 | 1319222.4 | 150241.28 | 4622572.5 | 1763930 | 961799.8 | 8019440.64 | 0 | 0 | 0 | 5285575.68 | 2720949.6 | 7117524 | 0 | 1523501.2 | 2579478 | 8911699.2 | 3139599 | 870912 | 0 | 181661.832 | 10893466.35 | 0 | 23360742 | 0 | 0 | 3241485 | 0 | 5775023.76 | 0 | 2965470 | 9422179.2 | 5537344.41 | 0 | 9118349.46 | 17313696 | 0 | 23205099.84 | 0 | 18728294.4 | 0 | 524698.2 | 16174522.56 | 55011090 | 0 | 0 | 0 |  | 571923709.24 | 376472037.432 | 948395746.672 | 109974721.582 | 99620766.72 | 52009654.1 | 522342010.36 | 89265298.35 | 228960 | 48482068.46 | 24177600 | 2294667.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 0 | 262 |  | 0 | 280 | 275 | 35 | 0 | 30 | 207 | 0 | 95 | 100 | 50 | 0 | 0 | 0 | 0 | 0 | 38 | 35 | 35 | 22 | 25 | 18 | 33 | 33 | 41 | 0 | 0 | 35 | 0 | 0 | 17 | 218 | 0 | 130 | 0 |  | 18 | 0 | 0 | 92 | 0 | 25 | 21 | 2 | 80 | 0 | 0 | 340 | 295 | 205 | 8 | 89 | 23 | 20 | 0 | 0 | 0 | 0 | 8 | 20 | 11 | 33 | 20 | 120 | 148 | 50 | 19 | 2 | 39 | 43 | 48 | 0 | 130 | 328 | 30 | 78 | 0 | 148 | 18 | 0 | 7 | 310 | 8 | 11 | 0 | 30 | 0 | 0 | 189 | 0 | 149 | 19 | 50 | 178 | 0 | 386 | 13 | 75 | 0 | 5 | 0 | 54 | 0 | 0 | 113 | 100 | 350 | 104 | 26 | 60 | 116 | 0 | 37 | 34 |  | 717 | 0 | 385 | 0 | 83 | 0 | 0 | 0 | 0 | 4 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 78 | 0 | 225 | 0 | 0 | 100 | 0 | 180 | 0 | 82 | 0 | 196 | 0 | 404 | 53 | 0 | 94 | 0 | 112 | 0 | 6 | 95 | 420 | 107 | 0 | 0 |  | 10747 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 278 | 0 | 0 | 280 | 285 | 100 | 0 | 55 | 204 | 0 | 180 | 90 | 102 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 54 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 | 0 | 18 | 0 | 83 | 100 | 90 | 50 | 21 | 35 | 135 | 0 | 0 | 325 | 310 | 209 | 8 | 89 | 26 | 52 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 144 | 162 | 74 | 19 | 0 | 40 | 43 | 50 | 0 | 163 | 334 | 20 | 78 | 0 | 162 | 18 | 0 | 9 | 290 | 8 | 11 | 20 | 282 | 0 | 0 | 182 | 52 | 149 | 0 | 90 | 180 | 0 | 375 | 115 | 101 | 30 | 0 | 16 | 54 | 51 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 109 | 0 | 36 | 0 |  | 717 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 33 | 65 | 34 | 110 | 0 | 0 | 0 | 50 | 40 | 97 | 0 | 24 | 30 | 52 | 33 | 21 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 128 | 0 | 182 | 0 | 82 | 100 | 190 | 0 | 413 | 92 | 0 | 113 | 0 | 111 | 0 | 0 | 95 | 540 | 110 | 0 | 0 |  | 13228 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 300 | 285 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 230 | 0 | 130 | 0 | 0 | 22 |  | 83 | 100 | 90 | 50 | 22 | 20 | 135 | 0 | 0 | 340 | 310 | 225 | 8 | 90 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 184 | 165 | 74 | 20 | 0 | 43 | 43 | 51 | 0 | 163 | 330 | 33 | 78 | 0 | 150 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 37 |  |  | 851 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 70 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 0 | 50 | 31 | 43 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 93 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 110 |  | 150
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 300 | 285 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 100 | 149 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 33 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 230 | 0 | 130 | 0 | 0 | 22 |  | 83 | 100 | 90 | 50 | 22 | 10 | 100 | 0 | 0 | 340 | 310 | 225 | 8 | 90 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 160 | 74 | 20 | 1.6 | 43 | 43 | 51 | 0 | 163 | 330 | 33 | 78 | 0 | 135 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 180 | 0 | 400 | 115 | 105 | 50 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 37 | 30 |  | 851 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 70 | 33 | 110 | 0 | 0 | 0 | 50 | 35 | 100 | 0 | 50 | 30 | 43 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 0 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 93 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 109 |  | 150
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 0 | 337 | 0 | 0 | 280 | 255 | 7 | 0 | 55 | 203 | 0 | 120 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 18 | 33 |  | 2 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 | 0 | 18 | 0 | 0 | 52 | 0 | 0 | 21 | 3 | 100 | 0 | 0 | 275 | 295 | 183 | 8 | 88 | 23 | 53 | 0 | 0 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 122 | 200 | 74 | 19 | 1 | 40 | 43 | 53 | 0 | 130 | 333 | 20 | 78 | 0 | 135 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 8 | 90 | 180 | 0 | 366 | 85 | 80 | 58 | 2 | 0 | 54 | 0 | 0 | 112 | 90 | 400 | 53 | 25 | 54 | 0 | 0 | 37 | 14 | 0 | 717 | 0 | 370 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 100 | 0 | 149 | 0 | 51 | 0 | 174 | 0 | 410 | 17 | 0 | 0 | 0 | 49 | 0 | 1 | 0 | 450 | 110 | 0 | 0 | 0
199
| Minimum Generation |  | 9565 | 7:00
| Highest Generation |  | 13296 | 22:00
| Day Peak Generation |  | 10747 | 12:00
| Evening Peak Generation |  | 13228 | 21:00
| HVDC Max Flow |  | 717 | 11:00
| HVDC EvPeak Flow |  | 717 | 21:00
| Load factor L.F |  | 85.63%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-21
Till now the maximum generation is : - |  |  | 13380 | 21:00 | Hrs on | 2021-04-15
The Summary of Yesterday's |  | 2021-04-20 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10747 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10015 | MW
Evening Peak Generation : |  | 13228 | MW Hour : | 21:00 | Available Max Generation : |  | 15595 | MW
E.P. Demand (at gen end) : |  | 13228 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13296 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2095 | MW
Total Gen. (MKWH) : |  | 273.2645 | System Load Factor : | 85.63% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -136 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-21
Actual : | 78.75 | Ft.(MSL) , | Rule curve : | 84.2 | Ft.( MSL )
Gas Consumed : | Total = | 1279.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161984375.682
: |  | Coal : | 89265298.35 | Oil : | 570824078.82 | Total : | 822073752.852
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4808.22 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1641.298 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1471.6599 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1330.1635 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1201.8319 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 969.8515 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 534.2672 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 249.4983 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 748.0361 |  |  | 0 | 0%
Total | 0 |  | 12954.8263 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
7) Baghabari 100 & 71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 09:23 to 13:52 for C/M.
b) Rampura-Moghbazar 132 kV Ckt-1 was under shut down from 11:46 to 16:24 for D/W.
c) Aminbazar-Mirpur 132 kV Ckt-1 was under shut down from 10:06 to 14:56 for D/W.
d) Barapukuria 132/33 kV T3 transformer was under shut down from 09:10 to 13:09 for C/M.
e) Barapukuria 132/33 kV T4 transformer tripped at 13:54 due to mechanical fault and was switched on
at 14:05
f) Keraniganj 230/132 kV T-01 transformer was under shut down from 13:09 to 14:02 for C/M.
g) Payra unit-2 was synchronized at 15:25.
h) Barapukuria 132/33 kV T4 transformer tripped at 19:58 due to mechanical fault and was switched on |  |  |  |  | About 47 MW power interruption occurred under Barapukuria S/S area
at 21:38 |  |  |  |  | from 19:58 to 21:38.
i) Mymensing RPCL GT-2 was synchronized at 20:30.
j) Payra unit-1 was shut down at 22:06.
k) Naogaon 132/33 kV T1 transformer was under shut down from 07:05(21/04/2021) to 10:34(21/04/2021) |  |  |  |  | About 40 MW power interruption occurred under Naogaon S/S area
for C/M. |  |  |  |  | from 07:05(21/04/2021) to 10:34(21/04/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-20 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4554900
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 2411863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 278 | 7032000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6644750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1476480
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6334953 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1155274
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 100 | 770550
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 484416
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 180 | 3507000
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 90 | 1766400 | Engine problem
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 204 | 465437 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1459872
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1272960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 1256640
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 1015289 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 54 | 1070410
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1180860 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 788000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 802800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 50 | 668640
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 282 | 3768653 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 21972 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 52 | 186592 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3553780
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 101 | 1994400
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2410560
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2557440
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 235986
| Dhaka area Total |  |  |  | 5829 | 3301 | 60848877
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 415915 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 130410
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 939360
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 848000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4856118 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3122828
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 30 | 231672 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 83 | 972185 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1913040
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1501440 | Engine problem
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 502992
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 525120
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 849600 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 36600
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 416509 | Low demand
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1292347
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 51 | 200720 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2413440
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 109 | 2545473
| Chattogram area Total |  |  |  | 2382 | 1214 | 23713769
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 135 | 2204578 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 5030000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7947400 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 6879000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 518256 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 826080
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 433064
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2096990 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 4207680 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 496620
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 227160
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 3223680
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 879806
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 500390 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 20 | 104640 | Low demand
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 793440
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2481360
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 842400 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 1949 | 40727198
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 162 | 3721680 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 403128 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 1354560 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15400
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 4140000 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1482000
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 346080
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 18 | 422400
| Mymensingh Area Total |  |  |  | 709 | 570 | 11885248
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 953000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1015680 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3496418
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 334 | 7576000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1195200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 20 | 626784 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1830720
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 162 | 3535440 | Gas shortage
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 412000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 8 | 180936 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7339000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 375 | 8935000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 198360
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8808500 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2001 | 46367038
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 717 | 17295272
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2151360 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 125760 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 14336 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 380 | 9049536 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 33 | 443625 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 553920
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 1658400 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1441 | 31292209
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 821664
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 620516
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1561000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 82 | 1976980 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 540 | 12531000
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 110 | 2670927 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 22800 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 941 | 20204887
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 537152
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 267810
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 24 | 112685 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 266200
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 128 | 2770500 | ST under S/D.
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4375018 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4732773 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 413 | 9210454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 323670 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 453600
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 239976
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 919680
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 97 | 804240
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2445216
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 2188704 | Engine problem
| Rajshahi Area Total |  |  |  | 2173 | 1479 | 29647678
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 71 | 1806545
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 4310100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 111 | 2413440
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47484
| Rangpur Area Total |  |  |  | 605 | 332 | 8577569
| Total |  |  |  | 21219 | 13228 | 273264473
| Eastern Grid Total |  |  |  | 14331 | 9035 | 183542130
| Western Grid Total |  |  |  | 6888 | 4193 | 89722343
| National Grid Total |  |  |  | 21219 | 13228 | 273264473
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-20
(a) ENTIRE EASTERN GRID : |  | 8485 | MW | (b) ENTIRE WESTERN GRID : |  | 4200 | MW
i) Dhaka area |  | 4292 | MW | i) Khulna area |  | 1608 | MW
ii) Chittagong area |  | 1308 | MW | ii) Rajshahi area |  | 1488 | MW
iii) Comilla area |  | 1283 | MW | iii) Barisal area |  | 378 | MW
iv) Mymensingh area |  | 1101 | MW | iv) Rangpur area |  | 726 | MW
v) Sylhet area |  | 501 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12685 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 13:00 | Jamalpur | 170 | 22:00 | Jhenida | 118 | 22:00
Munsiganj | 140 | 22:00 | Sherpur | 136 | 20:00 | Bottail | 128 | 20:00
Sonargaon | 85 | 0:00 | Srimongal | 49 | 18:30 | G.K Project | 62 | 22:00
Shyampur | 198 | 10:00 | Shahjibazar | 126 | 22:00 | Faridpur | 206 | 22:00
Bhulta | 197 | 0:00 | Fenchuganj | 43 | 21:00 | Madaripur | 113 | 21:00
Madanganj | 58 | 12:00 | Kulawara | 45 | 19:30 | Sariatpur | 74 | 21:00
Shitalakhya | 123 | 15:00 | Sylhet | 112 | 21:00 | Gopalganj | 100 | 19:30
Rahim steel | 28 | 16:00 | Chatak | 31 | 21:00 | Bagerhat | 105 | 21:00
Matuail | 60 | 9:00 | Sunamganj | 42 | 21:00 | Mongla | 42 | 10:00
Ghorasal | 70 | 23:00 | Biani Bazar | 60 | 21:00 | Satkhira | 114 | 22:00
Narsingdi | 172 | 20:00 | Comilla (S) | 158 | 20:00 | Gallamari | 42 | 19:30
Haripur (SBU) | 118 | 22:00 | Comilla(N) | 147 | 21:00 | Magura | 60 | 21:00
Sreenagar |  |  | Chandpur | 84 | 21:00 | Norail | 44 | 22:00
Ullon | 102 | 22:00 | Feni | 132 | 21:00 | Chuadanga | 88 | 23:00
Hasnabad | 100 | 22:00 | Chowmuhani | 197 | 21:00 | Borguna | 18 | 20:00
Magbazar | 60 | 12:00 | Ashuganj | 29 | 21:00 | Barisal(N) | 48 | 22:00
Maniknagar | 96 | 13:00 | Daudkandi | 162 | 20:00 | Barisal (S) | 108 | 19:00
Bangabhaban | 18 | 10:00 | B.Baria | 169 | 21:00 | Patuakhali | 112 | 20:00
Narinda | 72 | 13:00 | Ramganj | 96 | 21:00 | Bhandaria | 54 | 21:00
Dhanmondi | 136 | 13:00 | Chaddagram | 53 | 21:00 | Borhan Uddin | 44 | 21:00
Lalbag | 77 | 13:00 | PHP | 10 | 0:00 | Ishurdi | 66 | 21:00
Madartek | 81 | 23:00 | Kochua | 68 | 22:00 | Ruppur Paromanobik | 3 | 18:00
Dhaka University | 28 | 13:00 | Madunaghat | 58 | 15:00 | Natore | 145 | 21:00
Aftabnagar | 10 | 14:00 | Hathazari | 92 | 21:00 | Bogra | 172 | 23:00
Fatullah | 60 | 12:00 | Khulshi | 210 | 12:00 | Noagaon | 136 | 23:00
Nawabganj | 54 | 19:30 | Halishahar | 142 | 21:00 | Rajshahi | 148 | 21:00
Mirpur | 109 | 21:00 | Baraulia | 171 | 0:00 | Rajshahi New | 21 | 19:30
Kalyanpur | 117 | 21:00 | Sikalbaha | 37 | 22:00 | C.Nawabganj | 84 | 3:00
Gulshan | 112 | 13:00 | Dohazari | 88 | 19:00 | Amnura | 71 | 22:00
Uttara | 95 | 19:00 | Cox'sbazar | 108 | 22:00 | Pabna | 120 | 21:00
Uttara New | 28 | 21:00 | Chandraghona | 30 | 18:30 | Shahjadpur | 119 | 21:00
Kamrangirchar | 83 | 13:00 | Kaptai | 4.5 | 19:00 | Serajganj | 112 | 21:00
Savar | 174 | 15:00 | A. Khaer Stl. | 9 | 5:00 | Niyamatpur | 96 | 20:00
Bhasantec | 153 | 14:00 | Bakulia | 98 | 19:30 | Joypurhat | 65 | 24:00
Agargaon | 67 | 20:00 | Julda | 25 | 13:00 | Sherpur(Bogura) | 64 | 3:00
Satmosjid | 97 | 19:00 | TK chemical | 28.6 | 19:30 | Mohastangor | 68 | 22:00
Tongi | 121 | 24:00 | Modern Steel |  |  | Bangura | 30 | 21:00
Kabirpur | 249 | 15:00 | Shahmirpur | 28 | 13:00 | Rangpur | 124 | 18:30
Basundhara | 147 | 15:00 | Khagrachhari | 24 | 18:30 | Lalmonirhat | 40 | 18:30
Manikganj | 76 | 21:00 | Matarbari | 39.5 | 21:00 | Saidpur | 102 | 16:00
Joydevpur | 163 | 19:30 | Baroiar Hat | 46 | 19:30 | Purbasadipur | 104 | 19:30
New Tongi | 107 | 14:00 | Rangamati | 12 | 19:00 | Thakurgaon | 79 | 19:30
Kodda | 278 | 14:00 | Abul Khair 230 | 164 | 13:00 | Palashbari | 128 | 19:30
Dhamrai | 120 | 21:00 | BSRM | 160 | 23:00 | Barapukuria | 52 | 18:30
Rajendrapur | 96 | 15:00 | GPH Ispat | 58 | 23:00 | Panchagar | 47 | 19:30
Valuka | 120 | 10:00 | Goalpara | 28 | 23:00 | Joldhaka | 54 | 19:00
Tangail | 246 | 22:00 | Central s/s | 93 | 19:30 | Kurigram | 52 | 19:00
Mymensing | 211 | 22:00 | Noapara | 55 | 0.8125 | Mithapukur | 41 | 21:00
Kishorganj | 142 | 22:00 | Jessore | 139 | 22:00
Netrokona | 112 | 21:00 | Benapol | 66 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-20 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 3:00 | 397 | 12:00 | Kaliakoir | 385 | 0.29167 | 373 | 0.5
| Bheramara | 398 | 18:30 | 391 | 20:00 | Bhulta | 379 | 0.041667 | 366 | 0.5
| Ashuganj(N) | 385 | 3:00 | 374 | 12:00 | Gopalganj | 405 | 0.625 | 381 | 0.95833
| Payra | 411 | 18:30 | 394 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 7:00 | Hathazari | 222 | 18:00 | 214 | 9:00
| Ishurdi | 236 | 6:00 | 224 | 19:30 | Megnaghat | 230 | 1:00 | 220 | 11:00
| Ashuganj | 230 | 1:00 | 225 | 9:00 | Fenchuganj | 239 | 3:00 | 235 | 15:00
| Serajganj | 230 | 2:00 | 225 | 19:00 | Siddhirganj | 227 | 3:00 | 219 | 11:00
| Baghabari | 231 | 3:00 | 225 | 19:00 | Maniknagar | 226 | 3:00 | 217 | 12:00
| Barapukuria | 230 | 3:00 | 222 | 13:00 | Agargaon | 226 | 7:00 | 214 | 10:00
| Bogra | 227 | 5:00 | 213 | 19:30 | Barisal | 245 | 1:00 | 236 | 23:00
| Rajshahi | 230 | 5:00 | 218 | 19:30 | Bhola 225 MW | 249 | 11:00 | 241 | 23:00
| Khulna South | 228 | 5:00 | 211 | 19:30 | AKSML | 224 | 1:00 | 214 | 9:00
| Rampura | 226 | 3:00 | 219 | 11:00 | BSRM | 225 | 18:30 | 215 | 10:00
| Haripur | 224 | 1:00 | 216 | 12:00 | Bibiyana | 239 | 1:00 | 235 | 10:00
| Hasnabad | 230 | 18:00 | 215 | 9:00 | Bhulta | 228 | 20:00 | 220 | 10:00
| Shyampur | 223 | 18:30 | 220 | 12:00 | Ashuganj (S) | 234 | 18:30 | 227 | 11:00
| Aminbazar | 224 | 1:00 | 215 | 2:00 | Kaliakoir | 226 | 18:30 | 215 | 11:00
| Tongi | 224 | 19:00 | 212 | 9:00 | GPH | 223 | 20:00 | 214 | 10:00
| Comilla (N) | 225 | 1:00 | 219 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 19:00 | 129 | 9:00 | Madanhat | 134 | 0.77083 | 128 | 0.41667
| Munsiganj | 134 | 18:30 | 127 | 12:00 | Hathazari | 133 | 0.125 | 127 | 0.45833
| Sonargaon | 134 | 4:00 | 129 | 11:00 | Khulshi | 132 | 0.79167 | 126 | 0.41667
| Shyampur | 136 | 18:30 | 128 | 10:00 | Halishahar | 134 | 0.125 | 127 | 0.41667
| Bhulta | 126 | 2:00 | 121 | 12:00 | Baraulia | 134 | 0.91667 | 125 | 0.41667
| Madanganj | 136 | 4:00 | 127 | 12:00 | Sikalbaha | 135 | 0.16667 | 129 | 0.45833
| Shitalakhya | 140 | 18:30 | 127 | 12:00 | Dohazari | 130 | 0.83333 | 124 | 0.16667
| Rahim steal | 134 | 19:00 | 128 | 11:00 | Cox'sbazar | 121 | 0.45833 | 114 | 0.125
| Matuail | 135 | 19:00 | 129 | 9:00 | Chandraghona | 133 | 0.83333 | 127 | 0.41667
| Ghorasal | 138 | 1:00 | 135 | 10:00 | Kaptai | 133 | 0.041667 | 128 | 0.29167
| Narsinghdi | 132 | 17:00 | 125 | 21:00 | A. Khaer Stl. | 132 | 0.8125 | 126 | 0.41667
| Haripur (SBU) | 135 | 18:30 | 128 | 12:00 | Bakulia | 134 | 0.77083 | 129 | 0.29167
| Sreenagar |  |  |  |  | Julda | 134 | 0.041667 | 128 | 0.33333
| Ullon | 134 | 18:00 | 127 | 12:00 | TK Chemical | 134 | 0.125 | 128 | 0.5
| Hasnabad | 136 | 19:00 | 127 | 12:00 | Modern Steel
| Magbazar | 133 | 2:00 | 128 | 10:00 | Shahmirpur | 135 | 0.8125 | 129 | 0.41667
| Maniknagar | 135 | 1:00 | 129 | 12:00 | Khagrachhari | 132 | 0.77083 | 126 | 0.41667
| Bangabhaban | 135 | 1:00 | 129 | 12:00 | Matarbari | 130 | 0.54167 | 119 | 0.125
| Narinda | 135 | 1:00 | 129 | 12:00 | Baroiar Hat | 132 | 0.77083 | 126 | 0.20833
| Dhanmondi | 134 | 18:00 | 127 | 12:00 | Rangamati | 133 | 0.77083 | 127 | 0.41667
| Lalbag | 138 | 18:30 | 124 | 12:00 | Goalpara S/S | 136 | 5:00 | 124 | 19:30
| Madartek | 134 | 1:00 | 128 | 12:00 | Khulna Central S/S | 134 | 5:00 | 124 | 21:00
| Dhaka University | 135 | 18:30 | 127 | 12:00 | Noapara | 131 | 18:00 | 121 | 0.83333
| Aftabnagar | 134 | 1:00 | 128 | 11:00 | Jessore | 125 | 6:00 | 110 | 0.8125
| Fatullah | 136 | 18:30 | 128 | 9:00 | Benapol | 125 | 8:00 | 110 | 0.8125
| Nawabganj | 129 | 18:00 | 122 | 11:00 | Jhenida | 122 | 7:00 | 103 | 0.8125
| Mirpur | 135 | 18:30 | 126 | 10:00 | Bottail | 129 | 0.29167 | 117 | 0.8125
| Kalyanpur | 136 | 18:30 | 129 | 12:00 | G.K Project | 138 | 5:00 | 132 | 0.79167
| Gulshan | 134 | 3:00 | 128 | 10:00 | Faridpur | 135 | 0.29167 | 124 | 0.95833
| Uttara | 134 | 18:30 | 125 | 11:00 | Madaripur | 139 | 0.25 | 129 | 0.95833
| Uttara New | 133 | 1:00 | 125 | 8:00 | Shariyatpur S/S | 139 | 0.25 | 127 | 0.95833
| Kamrangirchar | 135 | 19:30 | 125 | 10:00 | Gopalganj | 144 | 0.29167 | 130 | 0.95833
| Savar | 135 | 1:00 | 126 | 9:00 | Bagerhat | 132 | 5:00 | 117 | 0.875
| Bhasantec | 133 | 1:00 | 126 | 12:00 | Mongla | 132 | 0.75 | 118 | 0.8125
| Agargaon | 134 | 1:00 | 127 | 12:00 | Satkhira | 134 | 6:00 | 119 | 0.8125
| Satmosjid | 134 | 1:00 | 127 | 12:00r | Gallamari | 135 | 5;00 | 124 | 0.8125
| Tongi | 136 | 1:00 | 127 | 9:00 | Magura | 121 | 9:00 | 101 | 19:30
| Kabirpur | 132 | 1:00 | 127 | 8:00 | Narail | 120 | 0.33333 | 99 | 19:30
| Basundhara | 134 | 1:00 | 124 | 12:00 | Chuadanga | 116 | 6:00 | 91 | 0.8125
| Manikganj | 138 | 18:30 | 128 | 12:00 | Borguna | 138 | 0.25 | 127 | 0.95833
| Joydevpur | 137 | 1:00 | 128 | 12:00 | Barisal(N) | 138 | 6:00 | 132 | 0.95833
| New Tongi | 138 | 18:30 | 126 | 11:00 | Barisal (S) | 137 | 18:30 | 131 | 0.625
| Kodda | 134 | 24:00 | 120 | 10:00 | Patuakhali(S) | 137 | 8:00 | 125 | 23:00
| Dhamrai | 130 | 1:00 | 125 | 12:00 | Bhandaria | 135 | 0.29167 | 125 | 0.95833
| Rajendrapur | 132 | 18:30 | 120 | 11:00 | Ishurdi | 136 | 0.25 | 129 | 0.875
| Valuka | 121 | 1:00 | 112 | 19:30 | Ruppur Paromanobik | 135 | 0.16667 | 129 | 0.8125
| Tangail | 127 | 16:00 | 119 | 21:00 | Natore | 134 | 4:00 | 126 | 19:30
| Mymensing | 126 | 1:00 | 115 | 21:00 | Bogra | 134 | 5:00 | 123 | 21:00
| Kishorganj | 129 | 13:00 | 119 | 21:00 | Noagaon | 127 | 4:00 | 114 | 20:00
| Netrokona | 124 | 4:00 | 111 | 21:00 | Rajshahi | 131 | 3:00 | 125 | 19:30
| Jamalpur | 135 | 1:00 | 124 | 9:00 | Rajshahi New | 131 | 5:00 | 126 | 14:00
| Sherpur | 133 | 1:00 | 120 | 7:00 | C.Nawabganj | 128 | 1:00 | 123 | 12:00
| Srimongal | 137 | 6:00 | 133 | 21:00 | Amnura | 127 | 3:00 | 121 | 14:00
| Shahjibazar | 135 | 13:00 | 130 | 21:00 | Pabna | 133 | 5:00 | 126 | 21:00
| Fenchuganj | 138 | 4:00 | 134 | 21:00 | Shahjadpur | 139 | 5:00 | 133 | 18:30
| Khulawara | 136 | 5:00 | 133 | 18:30 | Serajganj | 132 | 4:00 | 125 | 19:30
| Sylhet | 135 | 6:00 | 131 | 21:00 | Niyamatpur | 124 | 3:00 | 104 | 21:00
| Chatak | 134 | 5:00 | 129 | 21:00 | Joypurhat | 125 | 4:00 | 108 | 21:00
| Sunamganj | 134 | 6:00 | 127 | 21:00 | Sherpur(Bogura) | 134 | 5:00 | 123 | 19:30
| Biani Bazar | 137 | 5:00 | 128 | 21:00 | Mohastangor | 133 | 5:00 | 121 | 19:30
| Comilla(s) | 127 | 4:00 | 123 | 18:30 | Bangura | 133 | 7:00 | 129 | 19:30
| Comilla(n) | 136 | 19:00 | 131 | 6:00 | Rangpur | 128 | 3:00 | 115 | 19:00
| Chandpur | 135 | 7:00 | 131 | 23:00 | Lalmonirhat | 130 | 5:00 | 117 | 19:30
| Feni | 132 | 21:00 | 125 | 6:00 | Saidpur | 127 | 6:00 | 115 | 19:30
| Chowmuhani | 132 | 10:00 | 126 | 6:00 | Purbasadipur | 128 | 5:00 | 108 | 19:30
| Ashuganj | 137 | 7:00 | 134 | 21:00 | Thakurgaon | 127 | 5:00 | 106 | 19:30
| Daudkandi | 134 | 19:30 | 127 | 7:00 | Palashbari | 130 | 6:00 | 116 | 18:30
| B.Baria | 133 | 8:00 | 127 | 21:00 | Barapukuria | 130 | 3:00 | 122 | 16:00
| Ramganj | 133 | 10:00 | 126 | 6:00 | Panchagar | 127 | 5:00 | 104 | 19:30
| Chaddagram | 134 | 19:30 | 128 | 6:00 | Joldhaka | 129 | 5:00 | 109 | 19:00
| PHP | 132 | 18:30 | 126 | 6:00 | Kurigram | 128 | 3:00 | 112 | 19:00
| Kochua | 134 | 19:00 | 131 | 7:00 | Mithapukur | 131 | 0.20833 | 118 | 0.8125

## L-Curve
Date | 2021-04-20
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 38 | 8840 | 4088 | 12928 |  |  |  | QF-LDC-11
0:30 | 31.5 | 8428.5 | 3924 | 12352.5 | Date: | 2021-04-20
1:00 | 25 | 8017 | 3760 | 11777
1:30 | 27.5 | 7885 | 3738 | 11623
2:00 | 30 | 7753 | 3716 | 11469
2:30 | 55 | 7784.5 | 3740.5 | 11525 | [5 empty] | Gen. at Eve. Peak | 13228 | 13228 MW (21:00 )
3:00 | 80 | 7816 | 3765 | 11581 | [6 empty] | 21:00
3:30 | 80 | 7654 | 3694 | 11348 | [5 empty] | Gen. at Day Peak | 10747 | 10747 MW (12:00 )
4:00 | 80 | 7492 | 3623 | 11115 | [6 empty] | 12:00
4:30 | 147.5 | 7182 | 3507.5 | 10689.5 | [5 empty] | Highest Generation | 13296
5:00 | 215 | 6872 | 3392 | 10264 | [6 empty] | 22:00
5:30 | 233.5 | 6655.5 | 3293.5 | 9949
6:00 | 252 | 6439 | 3195 | 9634
6:30 | 232 | 6457.5 | 3142 | 9599.5
7:00 | 212 | 6476 | 3089 | 9565
7:30 | 221 | 6541.5 | 3101 | 9642.5
8:00 | 230 | 6607 | 3113 | 9720
8:30 | 233 | 6676 | 3171 | 9847
9:00 | 236 | 6745 | 3229 | 9974
9:30 | 243 | 6881 | 3256 | 10137
10:00 | 250 | 7017 | 3283 | 10300
10:30 | 245 | 7034.5 | 3333.5 | 10368
11:00 | 240 | 7052 | 3384 | 10436
11:30 | 235 | 7145.5 | 3446 | 10591.5
12:00 | 230 | 7239 | 3508 | 10747
12:30 | 185 | 7406.5 | 3558 | 10964.5
13:00 | 140 | 7574 | 3608 | 11182
13:30 | 115 | 7796.5 | 3639.5 | 11436
14:00 | 90 | 8019 | 3671 | 11690
14:30 | 92 | 8065.5 | 3692.5 | 11758
15:00 | 94 | 8112 | 3714 | 11826
15:30 | 109 | 7943 | 3667.5 | 11610.5
16:00 | 124 | 7774 | 3621 | 11395
16:30 | 67 | 7744 | 3530 | 11274
17:00 | 10 | 7714 | 3439 | 11153
17:30 | 38 | 7691 | 3415.5 | 11106.5
18:00 | 66 | 7668 | 3392 | 11060
18:30 | 69 | 8171 | 3633.5 | 11804.5
19:00 | 72 | 8674 | 3875 | 12549
19:30 | 90 | 8895 | 4120 | 13015
20:00 | 80 | 8912 | 4107 | 13019 |  |  |  | Executive Engineer
20:30 | 70 | 8973.5 | 4150 | 13123.5 |  |  |  | Network Operation Division
21:00 | 60 | 9035 | 4193 | 13228
21:30 | 54 | 9056 | 4206 | 13262
22:00 | 48 | 9077 | 4219 | 13296 |  |  |  |  | Page 6 of 7
22:30 | 28 | 9007 | 4178.5 | 13185.5
23:00 | 8 | 8937 | 4138 | 13075
23:30 | 23 | 8888.5 | 4113 | 13001.5
24:00 | 38 | 8840 | 4088 | 12928
13228 MW (21:00 )
10747 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-20 |  | Energy | 273264473
[11 empty] | 2021-04-20 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4782 | 716 | 2023 | 4050 | 765 | 35 | 462 | 0 | 154 | 0
0:30 | 4661 | 715 | 1985 | 3731 | 765 | 35 | 341 | 0 | 149 | 0 | Date: | 2021-04-20
1:00 | 4540 | 714 | 1947 | 3412 | 765 | 35 | 220 | 0 | 144 | 0
1:30 | 4496.5 | 714 | 1968.5 | 3290.5 | 755.5 | 35 | 220 | 0 | 143 | 0 | [7 empty] | Total Energy | 273.2645 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4453 | 714 | 1990 | 3169 | 746 | 35 | 220 | 0 | 142 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4489 | 714.5 | 2022 | 3155 | 746.5 | 35 | 220 | 0 | 143 | 0 | [7 empty] | Energy Requirement | 273.2645
3:00 | 4525 | 715 | 2054 | 3141 | 747 | 35 | 220 | 0 | 144 | 0
3:30 | 4551.5 | 715 | 2048.5 | 3007.5 | 736.5 | 35 | 110 | 0 | 144 | 0 | [6 empty] | Shortage
4:00 | 4578 | 715 | 2043 | 2874 | 726 | 35 | 0 | 0 | 144 | 0
4:30 | 4547.5 | 714.5 | 2035 | 2491 | 726.5 | 35 | 0 | 0 | 140 | 0
5:00 | 4517 | 714 | 2027 | 2108 | 727 | 35 | 0 | 0 | 136 | 0
5:30 | 4466.5 | 714 | 1966 | 1929 | 707 | 35 | 0 | 0 | 130 | 1.5
6:00 | 4416 | 714 | 1905 | 1750 | 687 | 35 | 0 | 0 | 124 | 3
6:30 | 4424.5 | 714.5 | 1890 | 1733.5 | 667 | 35 | 0 | 0 | 124 | 11 |  |  |  |  | Coal
7:00 | 4433 | 715 | 1875 | 1717 | 647 | 35 | 0 | 0 | 124 | 19
7:30 | 4497 | 714.5 | 1873.5 | 1731.5 | 636.5 | 35 | 0 | 0 | 118 | 36.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4561 | 714 | 1872 | 1746 | 626 | 35 | 0 | 0 | 112 | 54
8:30 | 4541 | 714.5 | 1897.5 | 1862.5 | 626 | 35 | 0 | 0 | 111 | 59.5
9:00 | 4521 | 715 | 1923 | 1979 | 626 | 35 | 0 | 0 | 110 | 65
9:30 | 4555 | 714.5 | 1909 | 2120.5 | 626.5 | 35 | 0 | 0 | 106 | 70.5
10:00 | 4589 | 714 | 1895 | 2262 | 627 | 35 | 0 | 0 | 102 | 76
10:30 | 4498 | 715.5 | 1859 | 2396.5 | 661 | 35 | 0 | 0 | 109 | 94
11:00 | 4407 | 717 | 1823 | 2531 | 695 | 35 | 0 | 0 | 116 | 112
11:30 | 4490 | 717 | 1850 | 2568.5 | 709 | 35 | 2 | 0 | 118 | 102
12:00 | 4573 | 717 | 1877 | 2606 | 723 | 35 | 4 | 0 | 120 | 92
12:30 | 4509 | 716.5 | 1887 | 2807.5 | 741.5 | 35 | 42.5 | 0 | 122 | 103.5
13:00 | 4445 | 716 | 1897 | 3009 | 760 | 35 | 81 | 0 | 124 | 115
13:30 | 4445 | 716 | 1897 | 3009 | 760 | 35 | 81 | 0 | 124 | 115
14:00 | 4445 | 716 | 1897 | 3009 | 760 | 35 | 81 | 0 | 124 | 115
14:30 | 4441 | 716 | 1889.5 | 3246.5 | 802 | 35 | 148.5 | 0 | 136 | 89.5
15:00 | 4437 | 716 | 1882 | 3484 | 844 | 35 | 216 | 0 | 148 | 64
15:30 | 4458.5 | 716 | 1873 | 3309 | 803.5 | 35 | 217 | 0 | 141 | 57.5
16:00 | 4480 | 716 | 1864 | 3134 | 763 | 35 | 218 | 0 | 134 | 51
16:30 | 4464.5 | 716 | 1870 | 3086.5 | 721.5 | 35 | 218 | 0 | 127 | 35.5
17:00 | 4449 | 716 | 1876 | 3039 | 680 | 35 | 218 | 0 | 120 | 20
17:30 | 4441.5 | 716 | 1842 | 3019.5 | 676.5 | 35 | 240.5 | 0 | 125 | 10.5
18:00 | 4434 | 716 | 1808 | 3000 | 673 | 35 | 263 | 0 | 130 | 1
18:30 | 4520.5 | 716 | 1895.5 | 3407.5 | 683.5 | 35 | 404 | 0 | 142 | 0.5
19:00 | 4607 | 716 | 1983 | 3815 | 694 | 35 | 545 | 0 | 154 | 0
19:30 | 4674 | 716 | 1980 | 4153 | 753 | 35 | 552 | 0 | 152 | 0
20:00 | 4687 | 716 | 1970 | 4158 | 742 | 35 | 553 | 0 | 158 | 0
20:30 | 4742 | 716.5 | 1988.5 | 4186.5 | 751.5 | 35 | 552.5 | 0 | 151 | 0
21:00 | 4797 | 717 | 2007 | 4215 | 761 | 35 | 552 | 0 | 144 | 0
21:30 | 4803 | 716.5 | 2009.5 | 4240.5 | 761.5 | 35 | 552 | 0 | 144 | 0
22:00 | 4809 | 716 | 2012 | 4266 | 762 | 35 | 552 | 0 | 144 | 0
22:30 | 4837.5 | 716 | 2012 | 4158 | 763.5 | 35 | 519.5 | 0 | 144 | 0
23:00 | 4866 | 716 | 2012 | 4050 | 765 | 35 | 487 | 0 | 144 | 0
23:30 | 4824 | 716 | 2017.5 | 4050 | 765 | 35 | 474.5 | 0 | 149 | 0 | Max Temp. in Dhaka |  | 36.9° C
24:00 | 4782 | 716 | 2023 | 4050 | 765 | 35 | 462 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-20
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 415915
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 8 | 13 | 11 | 17 | 19 | 19 | 17 | 13 | 8 | 3 | 0 | [8 empty] | 130410
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 202 | 203 | 203 | 216 | 205 | 217 | 216 | 218 | 203 | 203 | 204 | 204 | 203 | 203 |  | 203 | 203 | 203 | 203 | 203 | 209 | 203 | 4856118
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3122828
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | [9 empty] | 9 | 49 | 49 | 49 | 49 | 49 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 972185
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [19 empty] | 2 | 17 | 16 | 30 | 45 | 70 | 80 | 231672
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 20 | 50 | 20 | 20 | 20 |  |  | 104640
14 | Titas 50 MW Peaking PP | [13 empty] | 6 | 50 | 49 | 49 | 50 |  | 50 | 50 | 50 | 50 | 50 |  |  | 433064
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 115 | 120 | 180 | 150 | 150 | 118 | 118 | 118 | 118 | 120 | 71 | 95 | 85 | 113 | 155 | 150 | 150 | 120 |  | 155 | 170 | 180 | 180 | 185 | 185 | 185 | 3507000
17 | Siddhirganj 335 MW CCPP | 224 | 180 | 180 | 180 | 180 | 180 | 180 | 218 | 217 | 211 | 210 | 207 | 175 | 150 | 150 | 150 | 150 | 150 |  | 204 | 204 | 204 | 204 | 204 | 204 | 204 | 465437
18 | Kodda 300 MW PP Unit-2 (Summit) | 200 | 95 | 95 | 85 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 86 | 280 | 297 | 210 | 208 | 210 |  | 245 | 245 | 270 | 282 | 282 | 282 | 282 | 3768653
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4554900
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 110 | 135 | 135 | 135 | 135 | 135 | 135 | 2204578
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 23 | 23 | 26 | 26 | 23 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 518256
33 | Ashuganj 225 MW CCPP | 214 | 214 | 212 | 213 | 214 | 214 | 214 | 211 | 195 | 182 | 208 | 205 | 209 | 205 | 204 | 204 | 206 | 206 |  | 207 | 209 | 209 | 209 | 210 | 211 | 212 | 5030000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 275 | 260 | 260 | 275 | 285 | 280 | 295 | 270 | 295 | 265 | 265 | 265 | 295 | 295 | 295 |  | 300 | 295 | 295 | 310 | 310 | 310 | 290 | 6879000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 320 | 310 | 310 | 315 | 335 | 325 | 340 | 310 | 340 | 310 | 310 | 310 | 310 | 310 | 310 |  | 315 | 310 | 310 | 325 | 330 | 325 | 310 | 7947400
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 47 | 46 | 47 | 48 | 49 |  | 49 | 51 | 52 | 52 | 52 | 51 | 52 | 826080
36 | Chandpur 150 MW CCPP | 87 | 88 | 89 | 89 | 90 | 90 | 90 | 89 | 88 | 89 | 88 | 89 | 89 | 87 | 87 | 86 | 88 | 87 |  | 88 | 84 | 87 | 89 | 89 | 89 | 89 | 2096990
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6644750
41 | Haripur 360MW CCPP(HPL) | 319 | 340 | 348 | 349 | 351 | 308 | 308 | 308 | 347 | 314 | 270 | 262 | 263 | 256 | 270 | 260 | 260 | 257 |  | 302 | 304 | 290 | 278 | 262 | 263 | 283 | 7032000
42 | RPCL 210MW CCPP | 160 | 162 | 163 | 163 | 168 | 171 | 173 | 170 | 159 | 158 | 146 | 148 | 149 | 148 | 147 | 148 | 148 | 150 |  | 151 | 153 | 153 | 162 | 162 | 188 | 186 | 3721680
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 25 | 19 | 23 | 51 | 26 | 53 | 39 | 35 | 22 | 9 | 1 | [8 empty] | 346080
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 42 | 42 | 40 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 953000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1015680
46 | Shajibazar 330 MW CCPP | 332 | 332 | 332 | 332 | 334 | 330 | 331 | 330 | 330 | 330 | 327 | 328 | 330 | 330 | 328 | 330 | 331 | 331 |  | 332 | 333 | 334 | 334 | 330 | 333 | 332 | 7576000
47 | Shahjibazar GTPP Unit- 8 & 9 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 626784
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 72 | 75 | 78 | 78 | 76 | 75 | 75 | 75 | 75 | 76 |  | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 1830720
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 136 | 135 | 149 | 149 | 148 | 148 | 149 | 149 | 149 | 149 | 149 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3535440
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 412000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 7 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 9 | 9 | 8 | 8 | 8 | 8 |  | 9 | 9 | 8 | 9 | 9 | 9 | 9 | 198360
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 47 | 47 | 47 | 45 | 48 | 48 |  | 48 | 48 | 50 | 50 | 53 | 53 | 53 | 1195200
56 | Shahjahanulla 25 MW PP | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 8 |  | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 180936
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 300 | 290 | 290 | 300 | 300 | 310 | 310 | 310 | 300 | 310 | 305 | 290 | 290 | 290 | 285 | 290 |  | 280 | 285 | 280 | 290 | 305 | 300 | 315 | 7339000
| Bibiyana South 400 MW | 370 | 370 | 377 | 400 | 370 | 347 | 350 | 351 | 350 | 350 | 350 | 350 | 350 | 370 | 370 | 370 | 370 | 377 |  | 400 | 370 | 370 | 400 | 400 | 400 | 370 | 8808500
58 | Nababganj 55 MW PP (Southern power ) | 54 | 54 | 55 | 55 | 35 | 17 | 17 | 17 | 25 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 55 | 55 | 54 | 1070410
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 5 | 6 | 5 | 8 | 18 | 18 | 18 | 18 | 18 | 12 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 422400
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 502992
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 484416
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 403128
63 | Impoprt (Tripura) | 144 | 142 | 144 | 144 | 136 | 124 | 124 | 112 | 110 | 102 | 116 | 120 | 124 | 132 | 148 | 134 | 120 | 130 |  | 154 | 152 | 158 | 144 | 144 | 144 | 154 | 3223680
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 39 | 40 | 40 | 38 | 15 | 3 | 2 | 2 | 2 | 2 | 9 | 2 | 3 | 3 | 15 | 18 |  | 25 | 29 | 31 | 35 | 36 | 39 | 39 | 525120
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 19 | 19 | 19 | 20 | 20 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 496620
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 2 | 2 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 227160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 500390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 26 | 26 | 26 | 29 | 28 | 28 | 18 | 18 | 18 | 18 | 24 | 24 | 24 | 0 | 20 |  | 20 | 20 | 27 | 28 | 28 | 28 | 28 | 580860
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 802800
73 | Ghorashal 108MW PP (Regent) | 103 | 103 | 103 | 104 | 104 | 104 | 104 | 104 | 104 | 103 | 100 | 100 | 100 | 102 | 96 | 96 | 102 | 102 |  | 104 | 104 | 104 | 104 | 104 | 104 | 103 | 2411863
| Feni Lanka Power | 17 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 99 | 99 | 114 | 114 | 114 | 114 | 114 | 793440
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 65 | 36 | 36 | 36 | 47 | 81 | 109 | 113 | 113 | 112 | 113 | 111 | 110 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2481360
| Manikgonj 162MW PP(MPGL) | 162 | 108 | 108 | 35 | 17 | 17 | 17 | 17 | 17 | 18 | 54 | 60 | 141 | 162 | 162 | 108 | 108 | 108 |  | 153 | 162 | 162 | 162 | 162 | 162 | 156 | 2557440
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 24 | 7 | 7 | 7 | 7 | 7 | 55 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 70 | 100 | 100 | 90 | 92 | 91 | 93 | 1766400
78 | Gazipur 52 MW PP | 16 | 8 | 8 |  |  |  |  | 4 | 8 | 13 | 34 | 41 | 41 | 41 | 49 | 49 | 25 | 25 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 668640
79 | Kodda 150MW PP | 32 | 32 | 32 | [9 empty] | 48 | 48 | 48 | 48 | 48 | 48 |  | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 1256640
80 | Jamalpur 95 MW PP(Powerpac) | 65 | 57 | 49 | 41 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 50 | 74 | 65 | 65 | 74 | 74 | 74 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1354560
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 8 |  |  |  |  | 7 | 8 | 8 | 32 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 879806
| Gazipur 100 MW PP | 90 | 90 | 84 | 52 | 52 | 52 | 52 | 70 | 85 | 67 | 67 | 75 | 85 | 85 | 85 | 70 | 102 | 102 |  | 102 | 102 | 102 | 101 | 101 | 100 | 100 | 1994400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 3 | 5 | 1 | 5 | 3 | 2 | 1 | [9 empty] | 36600
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 46 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1292347
| Karnaphuli Power Ltd. | [20 empty] | 10 | 21 | 51 | 51 | 17 | 17 | 200720
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 23 | 50 | 50 | 14 | 10 | 10 |  | 77 | 100 | 100 | 100 | 100 | 100 | 88 | 770550
86 | Meghnaghat CCPP ( Summit) | 240 | 255 | 260 | 270 | 250 | 265 | 275 | 275 | 275 | 275 | 275 | 275 | 245 | 245 | 245 | 245 | 245 | 245 |  | 260 | 260 | 265 | 285 | 280 | 270 | 245 | 6334953
87 | Meghnaghat 100 MW(IEL) | 100 | 70 | 50 | 55 | 12 |  |  |  | 4 | 32 | 32 | 35 | 80 | 91 | 91 | 80 | 55 | 55 |  | 88 | 100 | 100 | 100 | 100 | 100 | 100 | 1476480
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 53 | 53 | 53 | 68 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2410560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 50 | 50 | 50 | 50 | 80 | 80 | 92 | 92 | 92 | 92 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1913040
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 64 | 32 | 32 | 7 |  |  |  |  | 32 | 48 | 48 | 50 | 75 | 102 | 102 | 64 | 64 | 64 |  | 85 | 102 | 102 | 102 | 102 | 102 | 102 | 1459872
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 50 | 50 | 25 |  |  | 7 | 24 | 25 | 25 | 25 | 30 | 45 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 939360
96 | Chattogram 108 MW PP (ECPV) | 51 | 51 | 51 | 30 | [8 empty] | 18 | 51 | 51 | 23 | 24 | 14 |  | 60 | 86 | 89 | 90 | 90 | 83 | 71 | 849600
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 40 | 35 | 30 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1155274
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 55 | 55 | 35 | 35 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 35 | 35 | 35 | 35 | 1015289
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 130 | 130 | 110 | 130 | 163 | 130 | 130 | 130 | 130 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3496418
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 15400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1272960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 25 | 25 |  |  |  |  | 0 | 21972
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 200 | 200 | 120 | 120 | 120 | 120 | 127 | 150 | 189 | 189 | 179 | 188 | 188 | 188 | 188 | 180 |  | 180 | 180 | 182 | 182 | 182 | 182 | 182 | 4140000
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 30 | 50 | 50 | 52 | 52 |  | 0 | 186592
114 | Kodda 149 MW PP Unit-1 (Summit) | 136 | 143 | 149 | 149 | 149 | 140 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 140 | 130 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3553780
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1501440
116 | Chandpur 200MW (Desh energy) | 178 | 169 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 170 | 178 | 178 | 178 | 178 | 178 | 178 | 178 |  | 178 | 178 | 178 | 180 | 198 | 194 | 197 | 4207680
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 367 | 366 | 364 | 368 | 368 | 365 | 371 | 380 | 375 | 403 | 371 | 386 | 367 | 367 | 368 | 368 | 367 | 367 |  | 367 | 367 | 367 | 375 | 376 | 376 | 366 | 8935000
| Jamalpur 115 MW PP (United) | 75 | 55 | 55 | 35 | [6 empty] | 8 | 13 | 64 | 88 | 108 | 55 | 55 | 55 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1482000
| Anwara 300 MW PP (United) | 70 | 71 | 52 | 16 | [8 empty] | 5 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  | 0 | 416509
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2413440
| Anlima Energy Ltd. | 115 | 116 | 116 | 116 | 72 | 72 | 72 | 72 | 80 | 114 | 116 | 116 | 116 | 116 | 116 | 116 | 112 | 109 |  | 109 | 109 | 109 | 109 | 109 | 109 | 90 | 2545473
| Bhairob 54.5 MW | 37 | 36 | 36 | 36 | 36 | 36 | 36 | 37 | 37 | 36 | 37 | 37 | 37 | 37 | 11 | 36 | 37 | 18 |  | 37 | 37 | 37 | 36 | 36 | 37 | 36 | 842400
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 15 | 23 | 29 | 33 | 34 | 33 | 28 | 7 | 14 | 6 | 0 | [8 empty] | 235986
120 | Eastern Zone Total | 8017 | 7753 | 7816 | 7492 | 6872 | 6439 | 6476 | 6607 | 6745 | 7017 | 7052 | 7239 | 7574 | 8019 | 8112 | 7774 | 7714 | 7668 | 0 | 8674 | 8895 | 8912 | 9035 | 9077 | 8937 | 8840 | 183542130
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 83 | 83 | 99 | 83 | 66 | 83 | 99 | 89 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2151360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 3 | 3 | 3 |  | 13 | 18 | 20 | 20 | 20 | 20 | 20 | 125760
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 35 | 17 | 17 | 17 | 17 | 17 | 53 | 53 | 55 | 90 | 90 | 91 | 70 | 70 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1658400
130
131
132 | United Payra Power Ltd. | [19 empty] | 2 | 17 | 17 |  |  |  |  | 22800
133 | Bhola Nutan Biddut BD LTD (GAS) | 107 | 108 | 108 | 108 | 108 | 108 | 108 | 109 | 106 | 108 | 108 | 107 | 104 | 106 | 107 | 106 | 106 | 106 |  | 106 | 106 | 107 | 110 | 110 | 110 | 109 | 2670927
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 48 | [13 empty] | 6 |  | 70 | 110 | 110 | 110 | 110 | 64 | 64 | 821664
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 81 | 82 | 81 | 80 | 81 | 82 | 81 | 80 | 82 | 83 | 83 | 82 | 82 | 82 | 83 | 84 | 82 | 83 |  | 84 | 83 | 82 | 82 | 82 | 81 | 81 | 1976980
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 66 | 66 | 65 | 66 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1561000
140 | Bhola 33 MW PP (Venture) | 34 | 31 | 31 | 30 | 27 | 23 | 20 | 20 | 18 | 18 | 19 | 21 | 21 | 24 | 24 | 21 | 21 | 21 |  | 33 | 33 | 34 | 34 | 33 | 34 | 34 | 620516
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 25 | 100 | 100 | 100 | 100 | 100 | 100 | 553920
142 | Noapara 40 MW PP (Khanjahan Ali) | 16 | 16 | 16 | [9 empty] | 32 | 32 | 32 | 32 | 32 | 32 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 443625
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 4 | 5 | 5 | 5 | [11 empty] | 14336
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 714 | 714 | 715 | 715 | 714 | 714 | 715 | 714 | 715 | 714 | 717 | 717 | 716 | 716 | 716 | 716 | 716 | 716 |  | 716 | 716 | 716 | 717 | 716 | 716 | 716 | 17295272
147 | Bheramara 410 MW CCPP | 355 | 355 | 360 | 370 | 355 | 360 | 370 | 380 | 380 | 390 | 360 | 385 | 355 | 360 | 360 | 360 | 360 | 360 |  | 365 | 360 | 355 | 380 | 380 | 385 | 380 | 9049536
148 | Payra 1320 MW | 540 | 520 | 520 | 500 | 500 | 460 | 420 | 400 | 400 | 400 | 400 | 420 | 440 | 450 | 470 | 450 | 450 | 450 |  | 470 | 530 | 520 | 540 | 540 | 540 | 540 | 12531000
149
150 | Barapukuria TPP Unit-1 | 75 | 76 | 77 | 76 | 77 | 77 | 77 | 76 | 76 | 77 | 78 | 78 | 77 | 76 | 74 | 72 | 74 | 73 |  | 74 | 73 | 72 | 71 | 72 | 75 | 75 | 1806545
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 217 | 225 | 243 | 290 | 300 | 241 | 156 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 4310100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 15 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 537152
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 120 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 132 | 116 | 113 | 119 | 105 | 105 |  | 117 | 134 | 131 | 128 | 130 | 141 | 136 | 2770500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 161 | 160 | 185 | 185 | 164 | 154 | 172 | 181 | 185 | 169 | 180 | 184 | 167 | 159 | 159 | 160 | 159 |  | 162 | 178 | 178 | 182 | 183 | 184 | 188 | 4375018
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 188 | 186 | 187 | 180 | 169 | 187 | 202 | 199 | 193 | 196 | 191 | 188 | 187 | 187 | 188 | 165 |  | 164 | 186 | 186 | 190 | 191 | 192 | 197 | 4732773
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 355 | 373 | 414 | 414 | 396 | 365 | 365 | 364 | 366 | 367 | 368 | 404 | 394 | 361 | 400 | 396 | 392 | 334 |  | 396 | 378 | 382 | 413 | 416 | 418 | 395 | 9210454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [12 empty] | 4 | 10 | 14 | 19 | 19 | 43 |  | 39 | 41 | 40 | 40 | 40 | 25 |  | 267810
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 18 | 16 | 16 | 15 | 15 | 16 | 18 |  | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 453600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 239976
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [12 empty] | 8 | 8 | 8 | 8 |  |  |  |  | 8 | 8 | 24 | 43 |  | 0 | 112685
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | [14 empty] | 5 |  | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 266200
168 | Santahar 50 MW Peaking PP | 32 | 32 | 32 | [14 empty] | 15 |  | 34 | 34 | 33 | 33 | 33 | 33 | 32 | 323670
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 52 | 52 | 52 | 52 | 52 | 16 | 16 | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 919680
170 | Chapainawabganj 100 MW Peaking PP | 58 | 58 | 58 | [16 empty] | 97 | 97 | 97 | 97 | 97 | 97 | 97 | 804240
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 70 | 84 | 94 | 94 | 94 | 94 | 104 | 101 | 113 | 70 | 70 |  | 105 | 113 | 113 | 113 | 113 | 113 | 113 | 2445216
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 70 | 70 | 70 | 70 | 90 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 70 | 70 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2188704
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | [13 empty] | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 90 | 71 | 34 | 34 | 91 | 113 | 113 | 112 | 110 | 107 | 112 | 104 | 107 | 107 |  | 107 | 107 | 107 | 111 | 112 | 112 | 113 | 2413440
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 6 | 6 | 6 | 7 | 6 | 5 | 4 | 1 | 0 | [8 empty] | 47484
178
178