## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-23 | Friday
|  |  | Date (day): | 2021-04-23 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14725.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15546 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-22 | 2021-04-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 190 | 190
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 103 | 104 | 104
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 281 | 302 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dust in the gas line
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 270 | 285 | 285 | 20 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 75 | 148 | 94 | 180 | 30 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 70 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 0 | 220 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 72 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 53 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 185 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 143 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 88 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 72 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 157 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 0 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2117 | 2893 | 3571 | 3877 | 791 | 1120
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 45 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 55 | 35 | 35 | 195 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 220 | 220
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 100 | 100
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 66 | 66 | 66 |  | 36 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 90 | 90 |  | 10 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 35 | 11 | 21
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 51 | 84 | 84 |  | 24 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 72 | 35 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 964 | 1117 | 1630 | 1615 | 555 | 176
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 135 | 80 | 100 | 100 | 35 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 108 | 211 | 225 | 225 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 275 | 340 | 340 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 285 | 310 | 310 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 48 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 89 | 95 | 90 | 90 | 73 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 178 | 175 | 180 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 90 | 152 | 157 | 179
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 47 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 75 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 37 | 37 | 37 |  | 17 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1485 | 1643 | 1993 | 2185 | 577 | 172
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 179 | 172 | 210 | 210
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 20 | 20
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 73 | 66 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 140 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 36 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 389 | 536 | 692.6 | 641 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 40 | 40 | 40 | 40 |  | 30 | Engine problem
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 42 | 43 |  | 47 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 332 | 331 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 52 | 52 |  | 14 | Engine problem
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 75 | 75 | 75 |  | 11 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 211 | 216 | 0 | 0 |  | 231 | Under maint.
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 15 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 300 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 375 | 368 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 9 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 388 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1977 | 2062 | 1949 | 1950 | 0 | 442
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 588 | 845 | 858 | 858
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 5 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 355 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 92 | 90 | 92 |  | 13 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1082 | 1523 | 1709 | 1998 | 0 | 119
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 80 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 60 | 65 | 65 |  | 129 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 15 | 82 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 380 | 550 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 107 | 107 | 109 | 110 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 50
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 589 | 930 | 1034 | 1085 | 0 | 129
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 50 | 50 | 50 | 21 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 50 | 50 | 50 | 50 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 35 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 31 |  | 19 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 100 | 119 | 144 | 144 | 66 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 154 | 162 | 180 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 157 | 171 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 372 | 426 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 30
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 50 | 50
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 99 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 98 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 0 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 924 | 1366 | 1791 | 1847 | 187 | 26
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 76 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 0 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 337 | 339 | 356 | 348 | 124 | 115
|  | Total |  |  |  |  | 21967 | 21219 | 9864 | 12409 | 14725.6 | 15546 | 2234 | 2320
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9371.9526 | 11790 | 13991.0407 | 14770.5166
| A. |  | 2021-04-22 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 12409 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8089 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12409 | MW
| 3 | Day peak Generation : |  |  | 9864 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11790 | MW
| 4 | Evening peak Generation : |  |  | 12409 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 244.7738 | MKWHr | By Solar | 0.57065 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 150.3483 | MKWHr |  | By Oil: | 57.0142 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.3289 | MKWHr |  | By Hydro: | 0.99362 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2234 | MW | Dhaka | 4049 | 4049 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2320 | MW | Chittagong | 1297 | 1297 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4554 | MW | Khulna | 1539 | 1539 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1210.5 | MMCFD |  |  | Rajshahi | 1162 | 1162 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 158946446.936 | ii) Oil : | Taka | 416442922.17 | Comilla | 1194 | 1194 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 82862269.54 | Total | Taka | 658251638.646 | Mymensingh | 994 | 994 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.5405 | MKWHr. | Sylhet | 512 | 512 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 190 | MW (E to W) at | 21:00 | hrs | Barisal | 358 | 358 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -180 | MW at | 1:00 | hrs | Rangpur | 685 | 685 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 11790 | 11790 |  | 0
| B. |  | 2021-04-23 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 39.0° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15546 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2646 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 254.4591 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8277 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.5709 | MKWHr. | ii) HVDC Flow at Peak Time |  | 845 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9472 | MKWHr. | iii) Maximum HVDC Flow : |  | 845 | MW at | 15:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.6 |  | (b) Today: | 78.48 |  | (c) Rule Curve: |  | 83.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 81 | 0 | 0 | 355 |  | 0 | 280 | 250 | 0 | 0 | 30 | 180 | 0 | 92 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 10 | 0 | 0 | 0 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 201 | 0 | 130 | 0 |  | 0 | 0 | 66 | 92 | 0 | 12 | 21 | 36 | 100 | 0 | 0 | 260 | 270 | 137 | 8 | 89 | 16 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 10 | 122 | 146 | 19 | 0 | 0 | 41 | 43 | 5 | 0 | 163 | 281 | 33 | 50 | 0 | 136 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 90 | 194 | 0 | 366 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 34 | 113 | 100 | 370 | 17 | 0 | 0 | 35 | 0 | 18 | 0 |  | 464 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 33 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 72 | 20 | 175 | 0 | 339 | 92 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 410 | 110 | 0 | 0 |  | 6051 | 2759 | 8810 | 3934 | 464 | 1847 | 1707 | 635 | 35 | 66 | 122 | 0 | 0 | 78.65
2:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 353 |  | 0 | 280 | 270 | 0 | 0 | 40 | 180 | 0 | 92 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 0 | 0 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 214 | 0 | 130 | 0 |  | 22 | 0 | 66 | 92 | 0 | 12 | 18 | 37 | 100 | 0 | 0 | 290 | 300 | 143 | 8 | 89 | 23 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 122 | 145 | 24 | 0 | 0 | 41 | 43 | 5 | 0 | 163 | 280 | 33 | 50 | 0 | 137 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 193 | 0 | 398 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 400 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 464 | 0 | 395 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 74 | 0 | 195 | 0 | 363 | 92 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 450 | 110 | 0 | 0 |  | 6324 | 2887 | 9211 | 4208 | 464 | 1886 | 1755 | 675 | 35 | 66 | 122 | 0 | 0 | 78.64
3:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 353 |  | 0 | 280 | 270 | 0 | 0 | 40 | 176 | 0 | 92 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 23 | 0 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 215 | 0 | 130 | 0 |  | 24 | 0 | 66 | 92 | 0 | 12 | 21 | 38 | 100 | 0 | 0 | 335 | 335 | 143 | 8 | 89 | 23 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 126 | 145 | 24 | 0 | 0 | 42 | 43 | 53 | 0 | 163 | 334 | 33 | 72 | 0 | 150 | 0 | 0 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 90 | 188 | 0 | 398 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 400 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 464 | 0 | 395 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 32 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 203 | 0 | 73 | 0 | 205 | 0 | 423 | 92 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 480 | 110 | 0 | 0 |  | 6595 | 3005 | 9600 | 4408 | 464 | 2036 | 1760 | 705 | 35 | 66 | 126 | 0 | 0 | 78.63
4:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 353 |  | 0 | 280 | 230 | 0 | 0 | 40 | 175 | 0 | 92 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 22 | 25 | 23 | 0 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 66 | 92 | 0 | 12 | 21 | 39 | 100 | 0 | 0 | 300 | 300 | 145 | 8 | 88 | 23 | 53 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 124 | 173 | 61 | 0 | 0 | 41 | 43 | 50 | 0 | 163 | 333 | 33 | 72 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 90 | 185 | 0 | 366 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 370 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 466 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 65 | 32 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 72 | 0 | 194 | 0 | 398 | 92 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 510 | 110 | 0 | 0 |  | 6537 | 2934 | 9471 | 4234 | 466 | 2031 | 1781 | 734 | 35 | 66 | 124 | 0 | 0 | 78.62
5:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 354 |  | 0 | 280 | 250 | 0 | 0 | 40 | 176 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 202 | 0 | 130 | 0 |  | 24 | 0 | 49 | 92 | 0 | 0 | 21 | 38 | 100 | 0 | 0 | 300 | 300 | 144 | 8 | 90 | 23 | 53 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 116 | 175 | 48 | 0 | 0 | 42 | 43 | 11 | 0 | 163 | 331 | 33 | 10 | 0 | 150 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 50 | 195 | 0 | 366 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 370 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | 466 | 0 | 355 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 51 | 0 | 184 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 110 | 0 | 0 |  | 5969 | 2577 | 8546 | 4184 | 466 | 1881 | 1130 | 685 | 35 | 49 | 116 | 0 | 0 | 78.61
6:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 0 | 354 |  | 0 | 280 | 250 | 0 | 0 | 30 | 47 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 23 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 13 | 0 | 32 | 92 | 0 | 0 | 21 | 30 | 100 | 0 | 0 | 265 | 300 | 144 | 8 | 88 | 23 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 110 | 175 | 48 | 0 | 0 | 42 | 43 | 11 | 0 | 110 | 333 | 33 | 10 | 0 | 150 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 1 | 50 | 196 | 0 | 366 | 0 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 399 | 0 | 3 | 0 | 0 | 0 | 18 | 0 |  | 466 | 0 | 320 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 156 | 0 | 32 | 0 | 166 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 109 | 0 | 0 |  | 5623 | 2466 | 8089 | 3970 | 466 | 1718 | 1079 | 675 | 35 | 32 | 110 | 4 | 0 | 78.6
7:00 | 0 | 0 | 0 | 180 | 0 | 32 | 0 | 0 | 353 |  | 0 | 280 | 260 | 0 | 0 | 30 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 22 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 216 | 0 | 130 | 0 |  | 24 | 0 | 32 | 92 | 0 | 0 | 21 | 13 | 100 | 0 | 0 | 305 | 340 | 144 | 8 | 89 | 23 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 15 | 104 | 176 | 48 | 0 | 1 | 42 | 43 | 11 | 0 | 110 | 333 | 33 | 10 | 0 | 150 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 4 | 50 | 196 | 0 | 416 | 0 | 0 | 105 | 1 | 0 | 54 | 0 | 0 | 36 | 10 | 400 | 0 | 4 | 0 | 0 | 0 | 18 | 10 |  | 466 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 149 | 0 | 0 | 0 | 0 | 130 | 0 | 32 | 0 | 136 | 0 | 419 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 450 | 109 | 0 | 0 |  | 5785 | 2405 | 8190 | 4007 | 466 | 1718 | 1133 | 674 | 35 | 32 | 104 | 21 | 0 | 78.59
8:00 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 0 | 355 |  | 0 | 280 | 260 | 0 | 0 | 35 | 0 | 0 | 37 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 5 | 22 | 25 | 26 | 25 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 203 | 0 | 130 | 0 |  | 24 | 0 | 15 | 92 | 0 | 0 | 21 | 4 | 100 | 0 | 0 | 300 | 300 | 31 | 8 | 87 | 23 | 10 | 0 | 0 | 0 | 0 | 52 | 0 | 0 | 33 | 15 | 98 | 210 | 53 | 0 | 1 | 42 | 43 | 32 | 0 | 163 | 332 | 33 | 72 | 0 | 163 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 9 | 90 | 196 | 0 | 367 | 0 | 3 | 105 | 2 | 0 | 54 | 0 | 0 | 36 | 50 | 370 | 2 | 27 | 0 | 2 | 0 | 18 | 14 |  | 466 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 20 | 0 | 0 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 32 | 0 | 175 | 0 | 375 | 0 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 440 | 109 | 0 | 0 |  | 5886 | 2532 | 8418 | 3907 | 466 | 1850 | 1329 | 663 | 35 | 15 | 98 | 55 | 0 | 78.59
9:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 351 |  | 0 | 280 | 265 | 0 | 0 | 35 | 0 | 0 | 40 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 26 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 15 | 92 | 0 | 0 | 21 | 3 | 100 | 0 | 0 | 300 | 300 | 42 | 8 | 89 | 20 | 48 | 0 | 0 | 0 | 0 | 52 | 9 | 0 | 33 | 15 | 96 | 206 | 73 | 0 | 2 | 40 | 43 | 42 | 0 | 163 | 333 | 32 | 72 | 0 | 163 | 0 | 0 | 6 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 14 | 90 | 196 | 0 | 367 | 7 | 58 | 105 | 3 | 0 | 54 | 0 | 0 | 36 | 50 | 400 | 35 | 39 | 0 | 35 | 0 | 18 | 24 |  | 466 | 0 | 360 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 0 | 74 | 0 | 149 | 0 | 0 | 38 | 0 | 182 | 0 | 32 | 0 | 183 | 0 | 412 | 0 | 0 | 0 | 0 | 38 | 0 | 2 | 0 | 440 | 109 | 0 | 0 |  | 6227 | 2675 | 8902 | 4012 | 466 | 1972 | 1559 | 663 | 35 | 15 | 96 | 84 | 0 | 78.58
10:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 348 |  | 0 | 280 | 260 | 8 | 0 | 39 | 0 | 0 | 115 | 24 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 26 | 33 | 33 | 10 | 0 | 0 | 35 | 0 | 0 | 17 | 210 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 0 | 9 | 21 | 4 | 135 | 0 | 0 | 335 | 320 | 42 | 16 | 89 | 20 | 49 | 0 | 0 | 0 | 0 | 52 | 16 | 8 | 33 | 20 | 98 | 200 | 74 | 0 | 1 | 40 | 42 | 42 | 0 | 163 | 332 | 31 | 72 | 0 | 196 | 0 | 0 | 8 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 17 | 90 | 189 | 0 | 383 | 35 | 70 | 105 | 5 | 0 | 54 | 0 | 0 | 36 | 50 | 397 | 35 | 52 | 30 | 33 | 0 | 18 | 0 |  | 466 | 0 | 385 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 142 | 0 | 198 | 0 | 14 | 0 | 200 | 0 | 372 | 0 | 0 | 0 | 0 | 36 | 0 | 1 | 0 | 440 | 108 | 0 | 0 |  | 6568 | 2810 | 9378 | 4402 | 466 | 1927 | 1710 | 664 | 35 | 0 | 98 | 76 | 0 | 78.58
11:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 351 |  | 0 | 280 | 260 | 37 | 0 | 40 | 0 | 0 | 115 | 40 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 0 | 18 | 21 | 2 | 135 | 0 | 0 | 300 | 300 | 71 | 16 | 88 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 16 | 11 | 33 | 20 | 106 | 192 | 65 | 0 | 2 | 40 | 42 | 44 | 0 | 163 | 335 | 31 | 70 | 0 | 210 | 0 | 0 | 8 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 13 | 90 | 175 | 0 | 367 | 65 | 88 | 105 | 5 | 0 | 39 | 9 | 0 | 71 | 100 | 370 | 63 | 33 | 98 | 61 | 0 | 18 | 0 |  | 466 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 120 | 0 | 174 | 0 | 16 | 0 | 182 | 0 | 322 | 35 | 0 | 22 | 0 | 100 | 0 | 0 | 25 | 420 | 107 | 0 | 0 |  | 6863 | 2788 | 9651 | 4280 | 466 | 1859 | 2208 | 644 | 35 | 0 | 106 | 53 | 0 | 78.57
12:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 281 |  | 0 | 280 | 270 | 50 | 0 | 40 | 0 | 0 | 75 | 70 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 80 | 0 | 18 | 18 | 5 | 135 | 0 | 0 | 310 | 280 | 108 | 0 | 89 | 26 | 49 | 0 | 0 | 0 | 0 | 47 | 16 | 11 | 33 | 20 | 90 | 179 | 73 | 0 | 2 | 40 | 42 | 47 | 0 | 110 | 332 | 31 | 73 | 0 | 211 | 0 | 0 | 8 | 295 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 14 | 90 | 178 | 0 | 375 | 75 | 88 | 105 | 5 | 0 | 54 | 17 | 0 | 75 | 100 | 395 | 72 | 36 | 157 | 72 | 0 | 18 | 0 |  | 588 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 154 | 0 | 15 | 0 | 157 | 0 | 372 | 53 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 380 | 107 | 0 | 0 |  | 6932 | 2932 | 9864 | 4240 | 588 | 1780 | 2465 | 604 | 35 | 5 | 90 | 57 | 0 | 78.57
13:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 302 |  | 0 | 280 | 265 | 50 | 0 | 40 | 0 | 0 | 160 | 100 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 26 | 33 | 25 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 205 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 0 | 18 | 18 | 12 | 135 | 0 | 0 | 310 | 275 | 183 | 0 | 94 | 26 | 50 | 0 | 0 | 0 | 0 | 46 | 18 | 11 | 33 | 20 | 110 | 179 | 73 | 0 | 2 | 39 | 43 | 50 | 0 | 163 | 331 | 31 | 77 | 0 | 211 | 0 | 0 | 8 | 305 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 19 | 90 | 176 | 0 | 370 | 75 | 88 | 85 | 5 | 0 | 54 | 17 | 0 | 75 | 100 | 396 | 72 | 35 | 162 | 72 | 0 | 18 | 0 |  | 589 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 0 | 11 | 0 | 64 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 120 | 0 | 159 | 0 | 14 | 0 | 158 | 0 | 373 | 53 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 380 | 106 | 0 | 0 |  | 7229 | 2941 | 10170 | 4375 | 589 | 1878 | 2507 | 604 | 35 | 11 | 110 | 61 | 0 | 78.56
14:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 291 |  | 0 | 280 | 265 | 55 | 0 | 40 | 0 | 0 | 127 | 100 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 20 | 35 | 0 | 0 | 16 | 205 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 0 | 18 | 18 | 5 | 135 | 0 | 0 | 300 | 260 | 209 | 0 | 93 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 122 | 164 | 73 | 0 | 2 | 39 | 43 | 50 | 0 | 163 | 331 | 31 | 77 | 0 | 211 | 17 | 0 | 8 | 310 | 16 | 2 | 0 | 2 | 0 | 0 | 9 | 0 | 149 | 17 | 90 | 165 | 0 | 367 | 91 | 88 | 85 | 3 | 0 | 54 | 17 | 30 | 100 | 100 | 393 | 72 | 32 | 162 | 72 | 0 | 31 | 10 |  | 729 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 120 | 0 | 181 | 0 | 42 | 0 | 167 | 0 | 371 | 53 | 0 | 47 | 0 | 113 | 0 | 0 | 35 | 400 | 107 | 0 | 0 |  | 7319 | 3203 | 10522 | 4399 | 729 | 1894 | 2629 | 625 | 55 | 5 | 122 | 64 | 0 | 78.56
15:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 283 |  | 0 | 280 | 255 | 75 | 0 | 40 | 0 | 0 | 125 | 100 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 23 | 33 | 33 | 6 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 92 | 15 | 18 | 21 | 5 | 135 | 0 | 0 | 300 | 260 | 181 | 0 | 94 | 26 | 50 | 0 | 0 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 134 | 161 | 73 | 0 | 1 | 39 | 42 | 50 | 0 | 163 | 331 | 31 | 77 | 0 | 211 | 17 | 0 | 8 | 290 | 14 | 2 | 0 | 45 | 0 | 0 | 0 | 0 | 149 | 14 | 90 | 167 | 0 | 368 | 115 | 88 | 105 | 4 | 0 | 54 | 0 | 17 | 113 | 70 | 372 | 70 | 17 | 126 | 36 | 0 | 37 | 8 |  | 845 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 0 | 77 | 0 | 150 | 0 | 0 | 120 | 0 | 182 | 0 | 46 | 0 | 155 | 0 | 371 | 53 | 0 | 35 | 0 | 71 | 0 | 3 | 35 | 400 | 105 | 0 | 0 |  | 7212 | 3252 | 10464 | 4326 | 845 | 1872 | 2558 | 627 | 55 | 0 | 134 | 47 | 0 | 78.55
16:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 272 |  | 0 | 280 | 250 | 50 | 0 | 40 | 12 | 0 | 127 | 50 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 24 | 33 | 33 | 8 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 22 | 0 | 0 | 92 | 18 | 18 | 21 | 7 | 135 | 0 | 0 | 310 | 260 | 180 | 0 | 94 | 26 | 50 | 0 | 0 | 0 | 0 | 43 | 20 | 11 | 33 | 20 | 136 | 147 | 73 | 0 | 1 | 39 | 43 | 53 | 0 | 163 | 333 | 31 | 76 | 0 | 211 | 17 | 0 | 8 | 295 | 14 | 2 | 0 | 60 | 0 | 0 | 0 | 0 | 149 | 8 | 90 | 167 | 0 | 368 | 85 | 70 | 105 | 2 | 0 | 54 | 0 | 0 | 113 | 70 | 376 | 35 | 16 | 72 | 35 | 0 | 37 | 5 |  | 844 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 24 | 0 | 0 | 50 | 40 | 0 | 0 | 32 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 0 | 77 | 0 | 150 | 0 | 0 | 120 | 0 | 181 | 0 | 45 | 0 | 154 | 0 | 335 | 17 | 0 | 35 | 0 | 44 | 0 | 2 | 0 | 420 | 146 | 0 | 0 |  | 6976 | 3264 | 10240 | 4437 | 844 | 1875 | 2180 | 647 | 55 | 32 | 136 | 34 | 0 | 78.55
17:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 0 | 272 |  | 0 | 280 | 255 | 32 | 0 | 50 | 150 | 0 | 100 | 40 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 25 | 33 | 33 | 8 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 0 | 92 | 18 | 18 | 21 | 17 | 135 | 0 | 0 | 310 | 260 | 181 | 0 | 94 | 26 | 20 | 0 | 0 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 120 | 147 | 65 | 0 | 0 | 39 | 43 | 14 | 0 | 110 | 332 | 31 | 30 | 0 | 190 | 17 | 0 | 8 | 300 | 14 | 5 | 0 | 60 | 0 | 0 | 0 | 0 | 149 | 2 | 90 | 175 | 0 | 331 | 85 | 70 | 105 | 1 | 0 | 54 | 0 | 0 | 75 | 70 | 383 | 35 | 4 | 72 | 35 | 0 | 37 | 6 |  | 845 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 50 | 40 | 0 | 0 | 32 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 0 | 77 | 0 | 150 | 0 | 0 | 103 | 0 | 159 | 0 | 45 | 0 | 154 | 0 | 345 | 17 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 430 | 145 | 0 | 0 |  | 6724 | 3189 | 9913 | 4433 | 845 | 1679 | 2078 | 657 | 55 | 32 | 120 | 14 | 0 | 78.54
18:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 0 | 272 |  | 0 | 280 | 250 | 33 | 0 | 55 | 150 | 0 | 98 | 40 | 48 | 64 | 13 | 0 | 0 | 0 | 54 | 17 | 45 | 19 | 25 | 25 | 33 | 33 | 8 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 33 | 92 | 18 | 19 | 21 | 20 | 80 | 0 | 0 | 260 | 260 | 180 | 0 | 93 | 26 | 20 | 0 | 0 | 0 | 0 | 46 | 21 | 11 | 33 | 20 | 132 | 148 | 74 | 17 | 0 | 39 | 43 | 14 | 0 | 110 | 330 | 31 | 30 | 0 | 190 | 17 | 0 | 8 | 290 | 15 | 5 | 0 | 74 | 0 | 0 | 34 | 0 | 149 | 0 | 100 | 175 | 0 | 330 | 115 | 70 | 105 | 0 | 0 | 54 | 0 | 0 | 75 | 100 | 370 | 37 | 1 | 72 | 35 | 0 | 37 | 1 |  | 844 | 0 | 300 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 43 | 0 | 50 | 40 | 0 | 0 | 36 | 0 | 0 | 0 | 8 | 7 | 21 | 0 | 0 | 77 | 0 | 150 | 0 | 0 | 80 | 0 | 151 | 0 | 46 | 0 | 150 | 0 | 336 | 35 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 430 | 107 | 0 | 0 |  | 6854 | 3170 | 10024 | 4217 | 844 | 1637 | 2340 | 657 | 55 | 140 | 132 | 2 | 0 | 78.54
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 99 | 0 | 0 | 323 |  | 0 | 280 | 242 | 77 | 0 | 55 | 220 | 0 | 140 | 60 | 80 | 100 | 40 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 13 | 33 | 33 | 24 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 68 | 100 | 26 | 36 | 21 | 25 | 80 | 0 | 0 | 275 | 260 | 137 | 0 | 94 | 26 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 142 | 154 | 74 | 17 | 0 | 39 | 43 | 53 | 0 | 130 | 331 | 32 | 75 | 0 | 210 | 18 | 0 | 9 | 280 | 15 | 11 | 0 | 200 | 0 | 0 | 158 | 0 | 149 | 0 | 100 | 175 | 0 | 345 | 115 | 82 | 105 | 0 | 0 | 54 | 0 | 17 | 90 | 100 | 370 | 72 | 0 | 120 | 35 | 0 | 37 | 0 |  | 845 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 8 | 60 | 31 | 64 | 0 | 50 | 50 | 0 | 0 | 98 | 0 | 0 | 15 | 42 | 30 | 21 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 86 | 0 | 142 | 0 | 83 | 6 | 139 | 0 | 352 | 92 | 0 | 35 | 0 | 113 | 0 | 0 | 25 | 440 | 105 | 0 | 0 |  | 7861 | 3606 | 11467 | 4437 | 845 | 1886 | 3126 | 665 | 55 | 311 | 142 | 0 | 0 | 78.52
19:30 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 321 |  | 0 | 280 | 220 | 100 | 0 | 55 | 220 | 0 | 100 | 100 | 102 | 149 | 10 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 26 | 33 | 33 | 38 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 50 | 45 | 21 | 25 | 80 | 0 | 0 | 275 | 260 | 178 | 0 | 93 | 26 | 20 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 142 | 172 | 74 | 17 | 0 | 40 | 43 | 53 | 0 | 163 | 332 | 32 | 75 | 0 | 217 | 18 | 0 | 9 | 280 | 15 | 11 | 0 | 235 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 175 | 0 | 367 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 370 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 844 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 32 | 64 | 0 | 50 | 50 | 7 | 0 | 98 | 0 | 0 | 29 | 52 | 33 | 21 | 0 | 5 | 77 | 0 | 150 | 0 | 0 | 113 | 0 | 149 | 0 | 82 | 100 | 153 | 0 | 317 | 92 | 0 | 90 | 0 | 113 | 0 | 0 | 35 | 540 | 104 | 0 | 0 |  | 8237 | 3936 | 12173 | 4547 | 844 | 1885 | 3551 | 767 | 55 | 382 | 142 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 311 |  | 0 | 280 | 270 | 100 | 0 | 55 | 222 | 0 | 100 | 100 | 72 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 50 | 45 | 21 | 32 | 80 | 0 | 0 | 275 | 260 | 182 | 0 | 94 | 26 | 47 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 144 | 172 | 66 | 17 | 0 | 40 | 43 | 53 | 0 | 163 | 333 | 32 | 75 | 0 | 225 | 18 | 0 | 9 | 275 | 15 | 11 | 0 | 218 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 175 | 0 | 368 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 844 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 32 | 64 | 0 | 50 | 50 | 50 | 0 | 100 | 0 | 0 | 31 | 52 | 33 | 21 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 114 | 0 | 153 | 0 | 82 | 99 | 154 | 0 | 343 | 92 | 0 | 85 | 0 | 113 | 0 | 0 | 0 | 550 | 108 | 0 | 0 |  | 8213 | 3997 | 12210 | 4612 | 844 | 1934 | 3465 | 776 | 55 | 380 | 144 | 0 | 0 | 78.53
21:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 302 |  | 0 | 280 | 270 | 100 | 0 | 55 | 220 | 0 | 148 | 100 | 72 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 51 | 45 | 21 | 35 | 80 | 0 | 0 | 275 | 285 | 211 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 172 | 66 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 331 | 32 | 75 | 0 | 216 | 18 | 0 | 9 | 300 | 15 | 11 | 0 | 185 | 0 | 0 | 140 | 0 | 149 | 0 | 100 | 175 | 0 | 368 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 388 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 845 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 34 | 80 | 0 | 50 | 50 | 50 | 0 | 99 | 0 | 0 | 30 | 52 | 33 | 21 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 119 | 0 | 162 | 0 | 82 | 100 | 171 | 0 | 426 | 92 | 0 | 98 | 0 | 113 | 0 | 0 | 0 | 550 | 107 | 0 | 17 |  | 8251 | 4158 | 12409 | 4723 | 845 | 2046 | 3434 | 776 | 55 | 378 | 152 | 0 | 0 | 78.52
22:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 291 |  | 0 | 280 | 230 | 100 | 0 | 55 | 221 | 0 | 152 | 50 | 64 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 50 | 45 | 21 | 35 | 80 | 0 | 0 | 275 | 285 | 213 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 172 | 74 | 17 | 0 | 40 | 43 | 53 | 0 | 163 | 332 | 32 | 75 | 0 | 217 | 18 | 0 | 9 | 305 | 15 | 11 | 0 | 168 | 0 | 0 | 140 | 0 | 149 | 0 | 100 | 175 | 0 | 368 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 845 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 34 | 80 | 0 | 50 | 50 | 50 | 0 | 100 | 0 | 0 | 30 | 52 | 33 | 22 | 0 | 5 | 77 | 0 | 150 | 0 | 0 | 126 | 0 | 188 | 0 | 82 | 100 | 183 | 0 | 426 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 0 | 540 | 107 | 0 | 45 |  | 8070 | 4234 | 12304 | 4752 | 845 | 2041 | 3351 | 767 | 35 | 361 | 152 | 0 | 0 | 78.52
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 291 |  | 0 | 280 | 245 | 100 | 0 | 55 | 221 | 0 | 120 | 50 | 64 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 202 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 45 | 45 | 21 | 39 | 80 | 0 | 0 | 260 | 285 | 212 | 8 | 94 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 173 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 332 | 32 | 75 | 0 | 217 | 18 | 0 | 9 | 295 | 15 | 11 | 0 | 80 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 175 | 0 | 367 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 845 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 59 | 34 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 0 | 0 | 30 | 52 | 0 | 22 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 128 | 0 | 188 | 0 | 96 | 80 | 187 | 0 | 424 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 0 | 530 | 0 | 0 | 27 |  | 7897 | 4093 | 11990 | 4709 | 845 | 1907 | 3276 | 756 | 35 | 310 | 152 | 0 | 0 | 78.51
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 291 |  | 0 | 280 | 245 | 100 | 0 | 55 | 221 | 0 | 120 | 50 | 32 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 28 | 33 | 26 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 205 | 0 | 130 | 0 |  | 24 | 0 | 66 | 80 | 45 | 0 | 21 | 37 | 80 | 0 | 0 | 275 | 295 | 211 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 146 | 183 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 332 | 37 | 75 | 0 | 203 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 149 | 0 | 100 | 175 | 0 | 374 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 72 | 0 | 162 | 17 | 0 | 37 | 0 |  | 845 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 34 | 110 | 0 | 50 | 50 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 133 | 0 | 194 | 0 | 97 | 0 | 193 | 0 | 418 | 92 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 530 | 0 | 0 | 35 |  | 7681 | 3755 | 11436 | 4807 | 845 | 1915 | 2769 | 755 | 35 | 164 | 146 | 0 | 0 | 78.51
KWH | 0 | 0 | 0 | 4378500 | 0 | 2011454 | 0 | 0 | 7688000 |  | 0 | 6665000 | 6103447 | 992640 | 0 | 1067177 | 2655037 | 0 | 2555000 | 1359360 | 874656 | 563040 | 77110 | 0 | 0 | 0 | 1056960 | 243117 | 742266 | 385488 | 575000 | 524520 | 684400 | 792800 | 285600 | 0 | 145620 | 848000 | 0 | 0 | 368242 | 4902884 | 0 | 2980992 | 0 |  | 540960 | 0 | 842663 | 2213400 | 340800 | 456480 | 490080 | 507360 | 2649448 | 0 | 0 | 7358200 | 6986000 | 3567000 | 150545 | 2171640 | 528264 | 927840 | 0 | 0 | 0 | 0 | 1230528 | 297936 | 153540 | 817200 | 471320 | 2947200 | 3984400 | 1483200 | 115164 | 13600 | 959000 | 1007640 | 862200 | 0 | 3641318 | 7508000 | 769248 | 1437120 | 0 | 4494540 | 172000 | 0 | 124920 | 7334000 | 192264 | 92000 | 0 | 1141636 | 0 | 0 | 988800 | 0 | 3111840 | 131760 | 2112960 | 4043700 | 0 | 8905000 | 1471200 | 1334400 | 2566799 | 33361 | 0 | 1275373 | 76945 | 159600 | 2226000 | 1929600 | 9315700 | 1016640 | 305660 | 1956960 | 890727 | 0 | 643680 | 71204 |  | 15570909 | 0 | 8695872 | 0 | 1960320 | 0 | 0 | 0 | 0 | 15744 | 298875 | 1496000 | 635705 | 719808 | 0 | 442000 | 375000 | 183361 | 0 | 638032 | 0 | 0 | 110670 | 794400 | 146491 | 324480 | 0 | 24588 | 1826618 | 0 | 3682200 | 0 | 0 | 1908400 | 0 | 4354309 | 0 | 1282706 | 457920 | 4364782 | 0 | 9072036 | 1268640 | 0 | 752448 | 0 | 1536000 | 0 | 15069 | 244608 | 11820100 | 2582482 | 0 | 98400 |  | 167074873 | 77698973 | 244773846 | 105101156 | 15570909 | 45247166 | 54514222 | 17328918 | 993620 | 2500001 | 2947200 | 570654 | 0
Fuel Cost | 0 | 0 | 0 | 6436395 | 0 | 2655119.28 | 0 | 0 | 7918640 |  | 0 | 7264850 | 6774826.17 | 7534137.6 | 0 | 9028317.42 | 2761238.48 | 0 | 4420150 | 10235980.8 | 7976862.72 | 5540313.6 | 710954.2 | 0 | 0 | 0 | 7715808 | 1879294.41 | 7318742.76 | 289116 | 431250 | 0 | 0 | 0 | 2761752 | 0 | 39317.4 | 228960 | 0 | 0 | 3420968.18 | 5344143.56 | 0 | 5067686.4 | 0 |  | 0 | 0 | 8173831.1 | 21137970 | 2964960 | 3615321.6 | 617500.8 | 1506859.2 | 3921183.04 | 0 | 0 | 5445068 | 6986000 | 3281640 | 194203.05 | 2497386 | 596938.32 | 1298976 | 0 | 0 | 0 | 0 | 11751542.4 | 378378.72 | 115155 | 1430100 | 353490 | 22104000 | 4223464 | 13467456 | 146258.28 | 216784 | 1572760 | 1612224 | 1534716 | 0 | 4151102.52 | 7808320 | 1515418.56 | 2744899.2 | 0 | 7775554.2 | 376680 | 0 | 254836.8 | 7407340 | 144198 | 69920 | 0 | 8630768.16 | 0 | 0 | 5141760 | 0 | 30620505.6 | 1540274.4 | 17220624 | 43874145 | 0 | 8281650 | 13417344 | 12610080 | 22356819.29 | 0 | 0 | 11108498.83 | 676346.55 | 1592808 | 19076820 | 12851136 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 89688435.84 | 0 | 9130665.6 | 0 | 15408115.2 | 0 | 0 | 0 | 0 | 164997.12 | 3114277.5 | 1690480 | 985342.75 | 7025326.08 | 0 | 906100 | 768750 | 1804272.24 | 0 | 5646583.2 | 0 | 0 | 1072392.3 | 7697736 | 1420962.7 | 623001.6 | 0 | 18613.116 | 11014506.54 | 0 | 19957524 | 0 | 0 | 2232828 | 0 | 5747687.88 | 0 | 1924059 | 7789219.2 | 5106794.94 | 0 | 8981315.64 | 13244601.6 | 0 | 7140731.52 | 0 | 11919360 | 0 | 166512.45 | 1807653.12 | 51890239 | 0 | 0 | 0 |  | 476146838.6 | 296089084.136 | 772235922.736 | 109501185.896 | 89688435.84 | 49445261.04 | 392619569.91 | 82862269.54 | 268277.4 | 23823352.26 | 22104000 | 1923570.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 281 |  | 0 | 280 | 270 | 50 | 0 | 40 | 0 | 0 | 75 | 70 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 80 | 0 | 18 | 18 | 5 | 135 | 0 | 0 | 310 | 280 | 108 | 0 | 89 | 26 | 49 | 0 | 0 | 0 | 0 | 47 | 16 | 11 | 33 | 20 | 90 | 179 | 73 | 0 | 2 | 40 | 42 | 47 | 0 | 110 | 332 | 31 | 73 | 0 | 211 | 0 | 0 | 8 | 295 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 14 | 90 | 178 | 0 | 375 | 75 | 88 | 105 | 5 | 0 | 54 | 17 | 0 | 75 | 100 | 395 | 72 | 36 | 157 | 72 | 0 | 18 | 0 |  | 588 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 0 | 5 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 154 | 0 | 15 | 0 | 157 | 0 | 372 | 53 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 380 | 107 | 0 | 0 |  | 9864 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 302 | 0 | 0 | 280 | 270 | 100 | 0 | 55 | 220 | 0 | 148 | 100 | 72 | 100 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 20 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 | 0 | 24 | 0 | 66 | 100 | 51 | 45 | 21 | 35 | 80 | 0 | 0 | 275 | 285 | 211 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 152 | 172 | 66 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 331 | 32 | 75 | 0 | 216 | 18 | 0 | 9 | 300 | 15 | 11 | 0 | 185 | 0 | 0 | 140 | 0 | 149 | 0 | 100 | 175 | 0 | 368 | 115 | 88 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 388 | 72 | 0 | 162 | 35 | 0 | 37 | 0 |  | 845 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 34 | 80 | 0 | 50 | 50 | 50 | 0 | 99 | 0 | 0 | 30 | 52 | 33 | 21 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 119 | 0 | 162 | 0 | 82 | 100 | 171 | 0 | 426 | 92 | 0 | 98 | 0 | 113 | 0 | 0 | 0 | 550 | 107 | 0 | 17 |  | 12409 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 280 | 285 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 220 | 0 | 130 | 0 | 0 | 22 |  | 66 | 100 | 84 | 50 | 22 | 21 | 100 | 0 | 0 | 340 | 310 | 225 | 8 | 90 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 179 | 210 | 74 | 20 | 0 | 40 | 43 | 51 | 0 | 163 | 330 | 52 | 75 | 0 | 0 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 90 | 200 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 37 |  |  | 858 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 65 | 33 | 110 | 0 | 50 | 50 | 50 | 40 | 100 | 0 | 43 | 31 | 50 | 30 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 144 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 92 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 110 |  | 50
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 280 | 285 | 100 | 0 | 55 | 220 | 0 | 94 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 220 | 0 | 130 | 0 | 0 | 22 |  | 66 | 100 | 84 | 50 | 22 | 11 | 100 | 0 | 0 | 340 | 310 | 225 | 8 | 90 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 210 | 74 | 20 | 1.6 | 40 | 42 | 51 | 0 | 163 | 330 | 52 | 75 | 0 | 0 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 90 | 180 | 0 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 37 | 30 |  | 858 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 65 | 33 | 110 | 0 | 50 | 50 | 50 | 35 | 100 | 0 | 43 | 30 | 50 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 144 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 109 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 270 | 0 | 0 | 250 | 255 | 0 | 0 | 55 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 |  | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 0 | 0 | 32 | 90 | 0 | 0 | 21 | 28 | 80 | 0 | 0 | 260 | 260 | 216 | 8 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 98 | 208 | 74 | 20 | 1 | 40 | 43 | 53 | 0 | 110 | 334 | 52 | 30 | 0 | 0 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 10 | 20 | 85 | 0 | 367 | 24 | 17 | 17 | 2 | 0 | 54 | 0 | 0 | 0 | 20 | 384 | 0 | 29 | 0 | 0 | 0 | 36 | 11 | 0 | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8089 | 6:00
| Highest Generation |  | 12409 | 21:00
| Day Peak Generation |  | 9864 | 12:00
| Evening Peak Generation |  | 12409 | 21:00
| HVDC Max Flow |  | 845 | 15:00
| HVDC EvPeak Flow |  | 845 | 21:00
| Load factor L.F |  | 82.19%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-23
Till now the maximum generation is : - |  |  | 13380 | 21:00 | Hrs on | 2021-04-15
The Summary of Yesterday's |  | 2021-04-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9864 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8277 | MW
Evening Peak Generation : |  | 12409 | MW Hour : | 21:00 | Available Max Generation : |  | 15546 | MW
E.P. Demand (at gen end) : |  | 12409 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 12409 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2646 | MW
Total Gen. (MKWH) : |  | 244.7738 | System Load Factor : | 82.19% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -180 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-23
Actual : | 78.48 | Ft.(MSL) , | Rule curve : | 83.6 | Ft.( MSL )
Gas Consumed : | Total = | 1210.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 158946446.936
: |  | Coal : | 82862269.54 | Oil : | 416442922.17 | Total : | 658251638.646
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4555.7726 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1553.6216 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1392.7787 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1258.7718 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1137.3802 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 917.8366 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 507.5383 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 236.1682 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 707.9083 |  |  | 0 | 0%
Total | 0 |  | 12267.7763 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chowmuhoni 132/33 kV T-1 transformer was under shut down from 09:15 to 10:25 for R/H maintenance.
b) After maintenance Ashuganj 225 MW STG was synchronized at 10:51.
c) Hathazari 230/132 kV T-03 transformer was under shut down from 10:06 to 10:32 for C/M.
d) Mirpur-Aminbazar 132 kV Ckt-2 was under shut down from 10:07 to 14:35 for D/W.
e) Ashuganj Modular P.P. 230 kV Ckt was under shut down from 12:54 to 19:41 for D/W.
f) Sikalbaha 132 kV Bus-2 was under shutdown from 09:26 to 12:16 for D/W.
g) Tongi 132 kV Bus-1 was under shutdown from 10:22 to 15:47 for D/W.
h) Dohazari 33 kV Bus of 132/33 kV T-1 transformer was under shutdown from 11:13 to 12:08 for C/M by |  |  |  |  | About 20 MW power interruption occurred under Dohazari S/S area
BPDB. |  |  |  |  | from 11:13 to 12:08.
i) After Maintenance, Sirajganj Unit-1 GT was synchronized at 08:33.
j) Tongi-New Tongi 132 kV Ckt-1 was under shut down from 12:38 to 13:40 for R/H maintenance.
k) Sirajganj 132/33 kV T-1 transformer was under shut down from 12:15 to 16:30 for R/H maintenance.
l) After maintenance Bheramara-Bharampur 400 kV Ckt-1 was switched on at 13:48.
m) Mirpur-Aminbazar 132 kV Ckt-1 was under shut down from 14:40 to 14:48 for D/W.
n) After Maintenance Siddhirganj 335 MW CCPP GT was synchronized at 15:11.
o) After availability of gas Baghabari 100 MW & 71 MW were synchronized at 15:19 & 15:50 respectively.
p) Barapukuria 132/33 kV T-4 transformer & its associated 33 kV Bus was under shutdown from 16:07 to |  |  |  |  | About 26 MW power interruption occurred under Barapukuria S/S area
16:53 due to R/H maintenance by PBS. |  |  |  |  | from 16:07 to 16:53.
q) Bogura 33 kV Bus of 132/33 kV T-1 transformer was under shutdown from 14:30 to 15:53 due to R/H |  |  |  |  | About 60 MW power interruption occurred under Bogura S/S area
maintenance by PBS. |  |  |  |  | from 14:30 to 15:53.
r) After maintenance Chapainawabganj-Amnura 132 kV Ckt was switched on at 14:51.
s) Mithapukur 132/33 kV T-1 transformer tripped at 14:02 showing O/C and was switched on at 14:37.
t) Cumilla(S)-Surjamoninagar 132 kV Ckt-2 tripped at 00:22(23/04/2021) from Surjamoninagar showing
Directory trip command and was switched on at 01:01(23/04/2021) and again tripped at 01:08(23/04/2021).
u) Siddhirganj GT-2 was shutdown at 04:10(23/04/2021) due to problem with exhaust temperature thermocouples.
v) After Maintenance Shahjibazar GT-8 was synchronized at 23:51.
w) Hasnabad-Lalbag 132 kV Ckt was under shut down from 04:34(23/04/2021) to 08:49(23/04/2021) for D/W.
x) Hasnabad-Kamrangirchar 132 kV Ckt was shut down at 04:56(23/04/2021) for D/W.
y) Sylhet 225 MW CCPP ST & GT were shutdown at 06:13(23/04/2021) & 06:18(23/04/2021) respectively
for air filter replacement.
z) Dohazari-Cox's Bazar 132 kV Ckt was under shut down from 06:36(23/04/2021) to 09:31(23/04/2021) |  |  |  |  | About 20 MW power interruption occurred under Matarbari S/S area
for D/W. |  |  |  |  | from 06:36(23/04/2021) to 09:32(23/04/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2011454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Dirty in Gas
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 302 | 7688000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6665000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 992640
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6103447 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1067177
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 77110 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 385488
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 148 | 2555000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1359360
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 220 | 2655037 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 874656 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1056960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 563040 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 243117 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 742266
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1099520 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 684400
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 792800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 285600 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 185 | 1141636 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3111840
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1334400 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 1016640 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1956960
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 71204
| Dhaka area Total |  |  |  | 5829 | 2893 | 50913252
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 368242 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 131760
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 456480 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 55 | 993620 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4902884 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2980992
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2566799
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 66 | 842663 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2213400
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2112960 | Engine problem
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 490080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 35 | 507360
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 51 | 340800 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33361
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1275373
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 76945 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1929600
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 890727 | Low demand
| Chattogram area Total |  |  |  | 2382 | 1117 | 23114046
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2649448 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 3567000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 7358200 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6986000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 528264 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 48 | 927840
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 150545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2171640 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 175 | 4043700
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 297936
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 153540
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 2947200
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1230528
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 471320
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 159600 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2226000
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 37 | 643680 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 1643 | 37329641
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 172 | 3984400 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 115164 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 66 | 1483200 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13600
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 140 | 988800 | Engine problem
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1471200
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 305660
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 540960
| Mymensingh Area Total |  |  |  | 709 | 536 | 8902984
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 959000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1007640 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3641318
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 331 | 7508000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 862200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 92000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 769248 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1437120
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 216 | 4494540
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 172000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 15 | 192264 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7334000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 368 | 8905000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 124920
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 388 | 9315700 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2062 | 46814950
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 845 | 15570909
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1960320 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 15744 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 355 | 8695872 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 298875 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 457920
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 1268640 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1523 | 28268280
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 80 | 719808
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 635705
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1496000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 82 | 1282706 | Gas shortage
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 11820100
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 107 | 2582482 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 98400 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 930 | 18635201
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 375000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 442000 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 183361
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 110670 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 119 | 1908400 | ST under S/D.
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 162 | 4354309 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 171 | 4364782 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 426 | 9072036 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 146491 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 324480
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 24588 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 794400
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 99 | 638032 | Engine problem
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 98 | 752448 | Engine problem
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 244608 | Reserve.
| Rajshahi Area Total |  |  |  | 2173 | 1366 | 23735605
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 76 | 1826618
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1536000
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 15069
| Rangpur Area Total |  |  |  | 605 | 339 | 7059887
| Total |  |  |  | 21219 | 12409 | 244773846
| Eastern Grid Total |  |  |  | 14331 | 8251 | 167074873
| Western Grid Total |  |  |  | 6888 | 4158 | 77698973
| National Grid Total |  |  |  | 21219 | 12409 | 244773846
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-22
(a) ENTIRE EASTERN GRID : |  | 8046 | MW | (b) ENTIRE WESTERN GRID : |  | 3744 | MW
i) Dhaka area |  | 4049 | MW | i) Khulna area |  | 1539 | MW
ii) Chittagong area |  | 1297 | MW | ii) Rajshahi area |  | 1162 | MW
iii) Comilla area |  | 1194 | MW | iii) Barisal area |  | 358 | MW
iv) Mymensingh area |  | 994 | MW | iv) Rangpur area |  | 685 | MW
v) Sylhet area |  | 512 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11790 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 14:00 | Jamalpur | 139 | 21:00 | Jhenida | 106 | 21:00
Munsiganj | 136 | 21:00 | Sherpur | 130 | 19:30 | Bottail | 118 | 21:00
Sonargaon | 83 | 23:00 | Srimongal | 48 | 21:00 | G.K Project | 53 | 21:00
Shyampur | 198 | 12:00 | Shahjibazar | 121 | 22:00 | Faridpur | 193 | 21:00
Bhulta | 185 | 0:00 | Fenchuganj | 50 | 19:00 | Madaripur | 102 | 21:00
Madanganj | 63 | 0:00 | Kulawara | 48 | 21:00 | Sariatpur | 68 | 21:00
Shitalakhya | 122 | 15:00 | Sylhet | 112 | 19:00 | Gopalganj | 92 | 21:00
Rahim steel | 23 | 12:00 | Chatak | 34 | 21:00 | Bagerhat | 104 | 22:00
Matuail | 55 | 11:00 | Sunamganj | 44 | 21:00 | Mongla | 44 | 1:00
Ghorasal | 71 | 23:00 | Biani Bazar | 64 | 19:00 | Satkhira | 110 | 21:00
Narsingdi | 161 | 21:00 | Comilla (S) | 152 | 21:00 | Gallamari | 42 | 21:00
Haripur (SBU) | 108 | 13:00 | Comilla(N) | 141 | 21:00 | Magura | 52 | 20:00
Sreenagar |  |  | Chandpur | 69 | 15:00 | Norail | 40 | 21:00
Ullon | 77 | 21:00 | Feni | 129 | 21:00 | Chuadanga | 85 | 22:00
Hasnabad | 101 | 21:00 | Chowmuhani | 180 | 1:00 | Borguna | 18 | 21:00
Magbazar | 68 | 14:00 | Ashuganj | 34 | 12:00 | Barisal(N) | 44 | 19:00
Maniknagar | 88 | 12:00 | Daudkandi | 156 | 21:00 | Barisal (S) | 112 | 21:00
Bangabhaban | 18 | 10:00 | B.Baria | 136 | 1:00 | Patuakhali | 120 | 22:00
Narinda | 83 | 23:00 | Ramganj | 84 | 1:00 | Bhandaria | 55 | 21:00
Dhanmondi | 141 | 13:00 | Chaddagram | 61 | 13:00 | Borhan Uddin | 40 | 22:00
Lalbag | 73 | 13:00 | PHP | 10 | 17:00 | Ishurdi | 55 | 19:30
Madartek | 75 | 23:00 | Kochua | 62 | 21:00 | Ruppur Paromanobik | 3 | 7:00
Dhaka University | 28 | 13:00 | Madunaghat | 64 | 21:00 | Natore | 118 | 20:00
Aftabnagar | 9 | 12:00 | Hathazari | 94 | 19:30 | Bogra | 148 | 20:00
Fatullah | 61 | 10:00 | Khulshi | 201 | 16:00 | Noagaon | 107 | 20:00
Nawabganj | 52 | 21:00 | Halishahar | 133 | 10:00 | Rajshahi | 135 | 21:00
Mirpur | 102 | 21:00 | Baraulia | 162 | 1:00 | Rajshahi New | 12 | 19:00
Kalyanpur | 108 | 21:00 | Sikalbaha | 33 | 13:00 | C.Nawabganj | 71 | 21:00
Gulshan | 108 | 13:00 | Dohazari | 90 | 1:00 | Amnura | 51 | 21:00
Uttara | 78 | 13:00 | Cox'sbazar | 98 | 21:00 | Pabna | 93 | 20:00
Uttara New | 27 | 15:00 | Chandraghona | 30 | 18:30 | Shahjadpur | 84 | 19:30
Kamrangirchar | 80 | 13:00 | Kaptai | 4.5 | 19:00 | Serajganj | 62 | 21:00
Savar | 154 | 15:00 | A. Khaer Stl. | 9 | 3:00 | Niyamatpur | 64 | 21:00
Bhasantec | 136 | 14:00 | Bakulia | 100 | 12:00 | Joypurhat | 57 | 21:00
Agargaon | 62 | 13:00 | Julda | 25 | 10:00 | Sherpur(Bogura) | 50 | 19:30
Satmosjid | 94 | 23:00 | TK chemical | 29 | 19:30 | Mohastangor | 56 | 21:00
Tongi | 118 | 11:00 | Modern Steel | 0 | #N/A | Bangura | 34 | 20:00
Kabirpur | 223 | 14:00 | Shahmirpur | 26 | 1:00 | Rangpur | 110 | 21:00
Basundhara | 157 | 12:00 | Khagrachhari | 26 | 18:30 | Lalmonirhat | 37 | 19:00
Manikganj | 68 | 0:00 | Matarbari | 40.5 | 20:00 | Saidpur | 97 | 20:00
Joydevpur | 148 | 13:00 | Baroiar Hat | 46 | 21:00 | Purbasadipur | 93 | 20:00
New Tongi | 104 | 12:00 | Rangamati | 12 | 18:30 | Thakurgaon | 74 | 19:30
Kodda | 238 | 19:30 | Abul Khair 230 | 70 | 10:00 | Palashbari | 106 | 19:30
Dhamrai | 104 | 20:00 | BSRM | 157 | 17:00 | Barapukuria | 49 | 12:00
Rajendrapur | 100 | 22:00 | GPH Ispat | 91 | 15:00 | Panchagar | 45 | 19:00
Valuka | 110 | 19:30 | Goalpara | 27 | 1:00 | Joldhaka | 44 | 18:30
Tangail | 194 | 21:00 | Central s/s | 90 | 19:00 | Kurigram | 43 | 19:30
Mymensing | 192 | 22:00 | Noapara | 45 | 0.8125 | Mithapukur | 30 | 3:00
Kishorganj | 124 | 21:00 | Jessore | 120 | 19:30
Netrokona | 125 | 19:30 | Benapol | 58 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 406 | 18:30 | 398 | 16:00 | Kaliakoir | 390 | 0.33333 | 375 | 0.66667
| Bheramara | 401 | 1:00 | 390 | 12:00 | Bhulta | 376 | 0.77083 | 345 | 0.625
| Ashuganj(N) | 384 | 1:00 | 369 | 16:00 | Gopalganj | 403 | 0.625 | 383 | 0.83333
| Payra | 409 | 19:00 | 396 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 10:00 | Hathazari | 219 | 11:00 | 214 | 17:00
| Ishurdi | 233 | 11:00 | 226 | 3:00 | Megnaghat | 222 | 19:30 | 220 | 3:00
| Ashuganj | 230 | 1:00 | 222 | 15:00 | Fenchuganj | 240 | 18:00 | 235 | 16:00
| Serajganj | 230 | 11:00 | 225 | 4:00 | Siddhirganj | 225 | 18:30 | 216 | 10:00
| Baghabari | 230 | 4:00 | 227 | 1:00 | Maniknagar | 224 | 18:30 | 214 | 16:00
| Barapukuria | 233 | 14:00 | 228 | 9:00 | Agargaon | 224 | 24:00 | 211 | 16:00
| Bogra | 226 | 11:00 | 219 | 3:00 | Barisal | 247 | 20:00 | 235 | 19:30
| Rajshahi | 230 | 11:00 | 222 | 16:00 | Bhola 225 MW | 250 | 24:00 | 239 | 19:30
| Khulna South | 227 | 4:00 | 215 | 9:00 | AKSML | 221 | 20:00 | 212 | 7:00
| Rampura | 224 | 1:00 | 218 | 16:00 | BSRM | 223 | 18:30 | 212 | 16:00
| Haripur | 223 | 19:00 | 214 | 16:00 | Bibiyana | 239 | 2:00 | 234 | 17:00
| Hasnabad | 220 | 19:00 | 215 | 3:00 | Bhulta | 227 | 18:30 | 217 | 9:00
| Shyampur | 222 | 19:00 | 220 | 16:00 | Ashuganj (S) | 232 | 18:30 | 223 | 17:00
| Aminbazar | 223 | 1:00 | 214 | 2:00 | Kaliakoir | 225 | 18:00 | 215 | 9:00
| Tongi | 223 | 18:00 | 212 | 9:00 | GPH | 221 | 19:30 | 212 | 16:00
| Comilla (N) | 225 | 18:30 | 217 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 18:30 | 126 | 9:00 | Madanhat | 133 | 0.75 | 128 | 0.20833
| Munsiganj | 134 | 18:30 | 125 | 16:00 | Hathazari | 131 | 0.45833 | 128 | 0.5
| Sonargaon | 134 | 18:30 | 128 | 2:00 | Khulshi | 130 | 0.125 | 125 | 0.29167
| Shyampur | 133 | 19:00 | 126 | 9:00 | Halishahar | 132 | 0.77083 | 127 | 0.20833
| Bhulta | 127 | 18:30 | 121 | 9:00 | Baraulia | 131 | 0.77083 | 127 | 0.58333
| Madanganj | 132 | 2:00 | 122 | 9:00 | Sikalbaha | 133 | 0.875 | 129 | 0.45833
| Shitalakhya | 138 | 18:30 | 123 | 9:00 | Dohazari | 128 | 0.75 | 125 | 0.041667
| Rahim steal | 133 | 19:00 | 126 | 10:00 | Cox'sbazar | 118 | 0.33333 | 110 | 0.875
| Matuail | 135 | 18:30 | 126 | 9:00 | Chandraghona | 132 | 0.83333 | 128 | 0.25
| Ghorasal | 136 | 3:00 | 135 | 1:00 | Kaptai | 132 | 0.041667 | 128 | 0.29167
| Narsinghdi | 134 | 5:00 | 126 | 22:00 | A. Khaer Stl. | 130 | 0.79167 | 126 | 0.16667
| Haripur (SBU) | 134 | 18:30 | 126 | 9:00 | Bakulia | 131 | 0.041667 | 128 | 0.41667
| Sreenagar |  |  |  |  | Julda | 135 | 0.77083 | 129 | 0.25
| Ullon | 132 | 1:00 | 126 | 16:00 | TK Chemical | 132 | 0.875 | 128 | 0.33333
| Hasnabad | 135 | 18:30 | 125 | 10:00 | Modern Steel
| Magbazar | 132 | 1:00 | 125 | 15:00 | Shahmirpur | 134 | 0.77083 | 128 | 0.29167
| Maniknagar | 134 | 18:30 | 128 | 10:00 | Khagrachhari | 131 | 0.77083 | 126 | 0.41667
| Bangabhaban | 134 | 18:30 | 128 | 10:00 | Matarbari | 123 | 0.375 | 115 | 0.58333
| Narinda | 134 | 18:30 | 128 | 10:00 | Baroiar Hat | 130 | 0.45833 | 126 | 0.041667
| Dhanmondi | 132 | 1:00 | 126 | 16:00 | Rangamati | 132 | 0.77083 | 127 | 0.041667
| Lalbag | 137 | 18:30 | 122 | 10:00 | Goalpara S/S | 138 | 4:00 | 130 | 9:00
| Madartek | 133 | 18:30 | 126 | 10:00 | Khulna Central S/S | 135 | 2:00 | 127 | 18:30
| Dhaka University | 133 | 18:30 | 126 | 15:00 | Noapara | 131 | 2:00 | 126 | 0.375
| Aftabnagar | 133 | 3:00 | 126 | 15:00 | Jessore | 127 | 4:00 | 119 | 0.875
| Fatullah | 135 | 18:30 | 126 | 10:00 | Benapol | 129 | 11:00 | 118 | 0.79167
| Nawabganj | 127 | 2:00 | 122 | 13:00 | Jhenida | 126 | 11:00 | 113 | 0.875
| Mirpur | 134 | 19:30 | 124 | 9:00 | Bottail | 130 | 0.25 | 123 | 0.875
| Kalyanpur | 135 | 18:30 | 126 | 9:00 | G.K Project | 137 | 11:00 | 132 | 0.875
| Gulshan | 132 | 3:00 | 126 | 10:00 | Faridpur | 134 | 0.20833 | 125 | 0.8125
| Uttara | 134 | 18:30 | 124 | 9:00 | Madaripur | 139 | 0.20833 | 130 | 0.8125
| Uttara New | 134 | 18:00 | 126 | 8:00 | Shariyatpur S/S | 137 | 0.25 | 128 | 0.83333
| Kamrangirchar | 132 | 18:30 | 121 | 9:00 | Gopalganj | 141 | 0.25 | 133 | 0.875
| Savar | 136 | 18:00 | 123 | 9:00 | Bagerhat | 133 | 4:00 | 125 | 0.875
| Bhasantec | 134 | 18:30 | 125 | 16:00 | Mongla | 133 | 0.16667 | 125 | 0.875
| Agargaon | 132 | 1:00 | 126 | 10:00 | Satkhira | 134 | 4:00 | 126 | 0.875
| Satmosjid | 134 | 18:30 | 127 | 9:00 | Gallamari | 138 | 4:00 | 131 | 0.875
| Tongi | 135 | 20:00 | 130 | 9:00 | Magura | 124 | 6:00 | 110 | 21:00
| Kabirpur | 136 | 18:00 | 124 | 15:00 | Narail | 123 | 0.45833 | 112 | 22:00
| Basundhara | 135 | 19:00 | 126 | 14:00 | Chuadanga | 121 | 11:00 | 102 | 0.875
| Manikganj | 138 | 18:30 | 130 | 9:00 | Borguna | 136 | 0.375 | 128 | 0.83333
| Joydevpur | 137 | 19:30 | 128 | 15:00 | Barisal(N) | 140 | 7:00 | 131 | 0.8125
| New Tongi | 135 | 18:00 | 127 | 9:00 | Barisal (S) | 138 | 18:00 | 130 | 0.83333
| Kodda | 132 | 18:00 | 123 | 8:00 | Patuakhali(S) | 137 | 7:00 | 125 | 20:00
| Dhamrai | 134 | 1:00 | 123 | 14:00 | Bhandaria | 135 | 0.29167 | 125 | 0.8125
| Rajendrapur | 132 | 18:30 | 122 | 10:00 | Ishurdi | 135 | 0.45833 | 130 | 0.875
| Valuka | 132 | 1:00 | 115 | 21:00 | Ruppur Paromanobik | 134 | 0.083333 | 131 | 0.66667
| Tangail | 137 | 1:00 | 123 | 15:00 | Natore | 134 | 11:00 | 129 | 16:00
| Mymensing | 133 | 4:00 | 119 | 21:00 | Bogra | 134 | 15:00 | 128 | 17:00
| Kishorganj | 135 | 1:00 | 122 | 21:00 | Noagaon | 128 | 11:00 | 127 | 3:00
| Netrokona | 132 | 1:00 | 114 | 21:00 | Rajshahi | 131 | 5:00 | 127 | 3:00
| Jamalpur | 138 | 18:30 | 124 | 3:00 | Rajshahi New | 132 | 11:00 | 128 | 14:00
| Sherpur | 134 | 19:00 | 120 | 17:00 | C.Nawabganj | 129 | 18:30 | 125 | 10:00
| Srimongal | 140 | 1:00 | 132 | 23:00 | Amnura | 130 | 5:00 | 124 | 14:00
| Shahjibazar | 138 | 1:00 | 130 | 21:00 | Pabna | 133 | 1:00 | 130 | 9:00
| Fenchuganj | 138 | 1:00 | 133 | 24:00 | Shahjadpur | 137 | 1:00 | 133 | 10:00
| Khulawara | 139 | 1:00 | 132 | 21:00 | Serajganj | 133 | 18:30 | 130 | 7:00
| Sylhet | 134 | 1:00 | 131 | 19:00 | Niyamatpur | 129 | 11:00 | 120 | 21:00
| Chatak | 137 | 1:00 | 128 | 21:00 | Joypurhat | 127 | 11:00 | 122 | 21:00
| Sunamganj | 134 | 1:00 | 127 | 19:00 | Sherpur(Bogura) | 133 | 15:00 | 121 | 2:00
| Biani Bazar | 136 | 2:00 | 127 | 21:00 | Mohastangor | 132 | 11:00 | 127 | 2:00
| Comilla(s) | 128 | 1:00 | 121 | 21:00 | Bangura | 136 | 6:00 | 132 | 10:00
| Comilla(n) | 135 | 18:30 | 130 | 15:00 | Rangpur | 132 | 14:00 | 121 | 10:00
| Chandpur | 137 | 4:00 | 132 | 21:00 | Lalmonirhat | 132 | 13:00 | 120 | 18:30
| Feni | 130 | 8:00 | 125 | 21:00 | Saidpur | 130 | 5:00 | 120 | 18:00
| Chowmuhani | 133 | 5:00 | 126 | 0:00 | Purbasadipur | 129 | 12:00 | 120 | 17:00
| Ashuganj | 138 | 1:00 | 134 | 17:00 | Thakurgaon | 129 | 12:00 | 115 | 11:00
| Daudkandi | 129 | 4:00 | 126 | 21:00 | Palashbari | 130 | 13:00 | 121 | 18:00
| B.Baria | 136 | 1:00 | 127 | 21:00 | Barapukuria | 133 | 14:00 | 128 | 9:00
| Ramganj | 133 | 11:00 | 129 | 20:00 | Panchagar | 128 | 12:00 | 115 | 16:00
| Chaddagram | 131 | 10:00 | 127 | 21:00 | Joldhaka | 130 | 14:00 | 119 | 10:00
| PHP | 130 | 18:30 | 125 | 23:00 | Kurigram | 131 | 14:00 | 118 | 10:00
| Kochua | 135 | 5:00 | 131 | 15:00 | Mithapukur | 132 | 0.58333 | 124 | 0.41667

## L-Curve
Date | 2021-04-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 272 | 7681 | 3755 | 11436 |  |  |  | QF-LDC-11
0:30 | 226 | 6866 | 3257 | 10123 | Date: | 2021-04-22
1:00 | 180 | 6051 | 2759 | 8810
1:30 | 135 | 6187.5 | 2823 | 9010.5
2:00 | 90 | 6324 | 2887 | 9211
2:30 | 99 | 6459.5 | 2946 | 9405.5 | [5 empty] | Gen. at Eve. Peak | 12409 | 12409 MW (21:00 )
3:00 | 108 | 6595 | 3005 | 9600 | [6 empty] | 21:00
3:30 | 73.5 | 6566 | 2969.5 | 9535.5 | [5 empty] | Gen. at Day Peak | 9864 | 9864 MW (12:00 )
4:00 | 39 | 6537 | 2934 | 9471 | [6 empty] | 12:00
4:30 | 50.5 | 6253 | 2755.5 | 9008.5 | [5 empty] | Highest Generation | 12409
5:00 | 62 | 5969 | 2577 | 8546 | [6 empty] | 21:00
5:30 | 87 | 5796 | 2521.5 | 8317.5
6:00 | 112 | 5623 | 2466 | 8089
6:30 | 117 | 5704 | 2435.5 | 8139.5
7:00 | 122 | 5785 | 2405 | 8190
7:30 | 121.5 | 5835.5 | 2468.5 | 8304
8:00 | 121 | 5886 | 2532 | 8418
8:30 | 171.5 | 6056.5 | 2603.5 | 8660
9:00 | 222 | 6227 | 2675 | 8902
9:30 | 229 | 6397.5 | 2742.5 | 9140
10:00 | 236 | 6568 | 2810 | 9378
10:30 | 182 | 6715.5 | 2799 | 9514.5
11:00 | 128 | 6863 | 2788 | 9651
11:30 | 202.5 | 6897.5 | 2860 | 9757.5
12:00 | 277 | 6932 | 2932 | 9864
12:30 | 223.5 | 7080.5 | 2936.5 | 10017
13:00 | 170 | 7229 | 2941 | 10170
13:30 | 280 | 7274 | 3072 | 10346
14:00 | 390 | 7319 | 3203 | 10522
14:30 | 415 | 7265.5 | 3227.5 | 10493
15:00 | 440 | 7212 | 3252 | 10464
15:30 | 435 | 7094 | 3258 | 10352
16:00 | 430 | 6976 | 3264 | 10240
16:30 | 390 | 6850 | 3226.5 | 10076.5
17:00 | 350 | 6724 | 3189 | 9913
17:30 | 245 | 6789 | 3179.5 | 9968.5
18:00 | 140 | 6854 | 3170 | 10024
18:30 | 95 | 7357.5 | 3388 | 10745.5
19:00 | 50 | 7861 | 3606 | 11467
19:30 | 23 | 8237 | 3936 | 12173
20:00 | 112 | 8213 | 3997 | 12210 |  |  |  | Executive Engineer
20:30 | 151 | 8232 | 4077.5 | 12309.5 |  |  |  | Network Operation Division
21:00 | 190 | 8251 | 4158 | 12409
21:30 | 232 | 8160.5 | 4196 | 12356.5
22:00 | 274 | 8070 | 4234 | 12304 |  |  |  |  | Page 6 of 7
22:30 | 302 | 7983.5 | 4163.5 | 12147
23:00 | 330 | 7897 | 4093 | 11990
23:30 | 301 | 7789 | 3924 | 11713
24:00 | 272 | 7681 | 3755 | 11436
12409 MW (21:00 )
9864 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-22 |  | Energy | 244773846
[11 empty] | 2021-04-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4807 | 845 | 1915 | 3276 | 755 | 35 | 164 | 0 | 146 | 0
0:30 | 4370.5 | 654.5 | 1881 | 2491.5 | 695 | 35 | 115 | 0 | 134 | 0 | Date: | 2021-04-22
1:00 | 3934 | 464 | 1847 | 1707 | 635 | 35 | 66 | 0 | 122 | 0
1:30 | 4071 | 464 | 1866.5 | 1731 | 655 | 35 | 66 | 0 | 122 | 0 | [7 empty] | Total Energy | 244.7738 | Total Energy Gen 244.774 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 244.774 MKWHr
2:00 | 4208 | 464 | 1886 | 1755 | 675 | 35 | 66 | 0 | 122 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4308 | 464 | 1961 | 1757.5 | 690 | 35 | 66 | 0 | 124 | 0 | [7 empty] | Energy Requirement | 244.7738
3:00 | 4408 | 464 | 2036 | 1760 | 705 | 35 | 66 | 0 | 126 | 0
3:30 | 4321 | 465 | 2033.5 | 1770.5 | 719.5 | 35 | 66 | 0 | 125 | 0 | [6 empty] | Shortage
4:00 | 4234 | 466 | 2031 | 1781 | 734 | 35 | 66 | 0 | 124 | 0
4:30 | 4209 | 466 | 1956 | 1455.5 | 709.5 | 35 | 57.5 | 0 | 120 | 0
5:00 | 4184 | 466 | 1881 | 1130 | 685 | 35 | 49 | 0 | 116 | 0
5:30 | 4077 | 466 | 1799.5 | 1104.5 | 680 | 35 | 40.5 | 0 | 113 | 2
6:00 | 3970 | 466 | 1718 | 1079 | 675 | 35 | 32 | 0 | 110 | 4
6:30 | 3988.5 | 466 | 1718 | 1106 | 674.5 | 35 | 32 | 0 | 107 | 12.5 |  |  |  |  | Coal
7:00 | 4007 | 466 | 1718 | 1133 | 674 | 35 | 32 | 0 | 104 | 21
7:30 | 3957 | 466 | 1784 | 1231 | 668.5 | 35 | 23.5 | 0 | 101 | 38 |  |  |  | Oil |  |  |  | ,
8:00 | 3907 | 466 | 1850 | 1329 | 663 | 35 | 15 | 0 | 98 | 55
8:30 | 3959.5 | 466 | 1911 | 1444 | 663 | 35 | 15 | 0 | 97 | 69.5
9:00 | 4012 | 466 | 1972 | 1559 | 663 | 35 | 15 | 0 | 96 | 84
9:30 | 4207 | 466 | 1949.5 | 1634.5 | 663.5 | 35 | 7.5 | 0 | 97 | 80
10:00 | 4402 | 466 | 1927 | 1710 | 664 | 35 | 0 | 0 | 98 | 76
10:30 | 4341 | 466 | 1893 | 1959 | 654 | 35 | 0 | 0 | 102 | 64.5
11:00 | 4280 | 466 | 1859 | 2208 | 644 | 35 | 0 | 0 | 106 | 53
11:30 | 4260 | 527 | 1819.5 | 2336.5 | 624 | 35 | 2.5 | 0 | 98 | 55
12:00 | 4240 | 588 | 1780 | 2465 | 604 | 35 | 5 | 0 | 90 | 57
12:30 | 4307.5 | 588.5 | 1829 | 2486 | 604 | 35 | 8 | 0 | 100 | 59
13:00 | 4375 | 589 | 1878 | 2507 | 604 | 35 | 11 | 0 | 110 | 61
13:30 | 4375 | 589 | 1878 | 2507 | 604 | 35 | 11 | 0 | 110 | 61
14:00 | 4375 | 589 | 1878 | 2507 | 604 | 35 | 11 | 0 | 110 | 61
14:30 | 4350.5 | 717 | 1875 | 2532.5 | 615.5 | 45 | 5.5 | 0 | 122 | 54
15:00 | 4326 | 845 | 1872 | 2558 | 627 | 55 | 0 | 0 | 134 | 47
15:30 | 4381.5 | 844.5 | 1873.5 | 2369 | 637 | 55 | 16 | 0 | 135 | 40.5
16:00 | 4437 | 844 | 1875 | 2180 | 647 | 55 | 32 | 0 | 136 | 34
16:30 | 4435 | 844.5 | 1777 | 2129 | 652 | 55 | 32 | 0 | 128 | 24
17:00 | 4433 | 845 | 1679 | 2078 | 657 | 55 | 32 | 0 | 120 | 14
17:30 | 4325 | 844.5 | 1658 | 2209 | 657 | 55 | 86 | 0 | 126 | 8
18:00 | 4217 | 844 | 1637 | 2340 | 657 | 55 | 140 | 0 | 132 | 2
18:30 | 4327 | 844.5 | 1761.5 | 2733 | 661 | 55 | 225.5 | 0 | 137 | 1
19:00 | 4437 | 845 | 1886 | 3126 | 665 | 55 | 311 | 0 | 142 | 0
19:30 | 4547 | 844 | 1885 | 3551 | 767 | 55 | 382 | 0 | 142 | 0
20:00 | 4612 | 844 | 1934 | 3465 | 776 | 55 | 380 | 0 | 144 | 0
20:30 | 4667.5 | 844.5 | 1990 | 3449.5 | 776 | 55 | 379 | 0 | 148 | 0
21:00 | 4723 | 845 | 2046 | 3434 | 776 | 55 | 378 | 0 | 152 | 0
21:30 | 4737.5 | 845 | 2043.5 | 3392.5 | 771.5 | 45 | 369.5 | 0 | 152 | 0
22:00 | 4752 | 845 | 2041 | 3351 | 767 | 35 | 361 | 0 | 152 | 0
22:30 | 4730.5 | 845 | 1974 | 3313.5 | 761.5 | 35 | 335.5 | 0 | 152 | 0
23:00 | 4709 | 845 | 1907 | 3276 | 756 | 35 | 310 | 0 | 152 | 0
23:30 | 4758 | 845 | 1911 | 3276 | 755.5 | 35 | 237 | 0 | 149 | 0 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4807 | 845 | 1915 | 3276 | 755 | 35 | 164 | 0 | 146 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 244.774 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 244.774 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [13 empty] | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 0 |  |  | 145620
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 |  |  |  | 9 | 17 | 17 | 17 | 17 | 17 | 16 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 368242
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 9 | 14 | 17 | 13 | 14 | 19 | 17 | 14 | 8 | 2 | [9 empty] | 131760
6 | Sikalbaha 225MW CCPP (Gas) | 201 | 214 | 215 | 204 | 202 | 203 | 216 | 203 | 204 | 210 | 204 | 204 | 205 | 205 | 203 | 203 | 203 | 203 |  | 203 | 203 | 203 | 203 | 203 | 202 | 205 | 4902884
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 100 | 80 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 2980992
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 66 | 66 | 66 | 66 | 49 | 32 | 32 | 15 | 15 | [8 empty] | 33 |  | 68 | 66 | 66 | 66 | 66 | 66 | 66 | 842663
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 85 | 85 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2566799
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 92 | 92 | 92 | 92 | 40 | 40 | 40 | 37 | 40 | 115 | 115 | 75 | 160 | 127 | 125 | 127 | 100 | 98 |  | 140 | 100 | 100 | 148 | 152 | 120 | 120 | 2555000
17 | Siddhirganj 335 MW CCPP | 180 | 180 | 176 | 175 | 176 | 47 | [9 empty] | 12 | 150 | 150 |  | 220 | 220 | 222 | 220 | 221 | 221 | 221 | 2655037
18 | Kodda 300 MW PP Unit-2 (Summit) | [13 empty] | 2 | 45 | 60 | 60 | 74 |  | 200 | 235 | 218 | 185 | 168 | 80 |  | 1141636
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 0 | [10 empty] | 8 | 8 | 8 | 8 | 150545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2649448
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 16 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 528264
33 | Ashuganj 225 MW CCPP | 137 | 143 | 143 | 145 | 144 | 144 | 144 | 31 | 42 | 42 | 71 | 108 | 183 | 209 | 181 | 180 | 181 | 180 |  | 137 | 178 | 182 | 211 | 213 | 212 | 211 | 3567000
34 | Ashuganj 450 MW CCPP(South) | 270 | 300 | 335 | 300 | 300 | 300 | 340 | 300 | 300 | 320 | 300 | 280 | 275 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 285 | 285 | 285 | 295 | 6986000
| Ashuganj 450 MW CCPP(North) | 260 | 290 | 335 | 300 | 300 | 265 | 305 | 300 | 300 | 335 | 300 | 310 | 310 | 300 | 300 | 310 | 310 | 260 |  | 275 | 275 | 275 | 275 | 275 | 260 | 275 | 7358200
35 | Ashuganj 55 MW PP (Precision) | 10 | 10 | 10 | 53 | 53 | 10 | 10 | 10 | 48 | 49 | 48 | 49 | 50 | 48 | 50 | 50 | 20 | 20 |  | 20 | 20 | 47 | 48 | 48 | 48 | 48 | 927840
36 | Chandpur 150 MW CCPP | 89 | 89 | 89 | 88 | 90 | 88 | 89 | 87 | 89 | 89 | 88 | 89 | 94 | 93 | 94 | 94 | 94 | 93 |  | 94 | 93 | 94 | 95 | 95 | 94 | 95 | 2171640
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6665000
41 | Haripur 360MW CCPP(HPL) | 355 | 353 | 353 | 353 | 354 | 354 | 353 | 355 | 351 | 348 | 351 | 281 | 302 | 291 | 283 | 272 | 272 | 272 |  | 323 | 321 | 311 | 302 | 291 | 291 | 291 | 7688000
42 | RPCL 210MW CCPP | 146 | 145 | 145 | 173 | 175 | 175 | 176 | 210 | 206 | 200 | 192 | 179 | 179 | 164 | 161 | 147 | 147 | 148 |  | 154 | 172 | 172 | 172 | 172 | 173 | 183 | 3984400
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 4 | 27 | 39 | 52 | 33 | 36 | 35 | 32 | 17 | 16 | 4 | 1 | [8 empty] | 305660
44 | Fenchugonj CCPP Phase-1 | 41 | 41 | 42 | 41 | 42 | 42 | 42 | 42 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 |  | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 959000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 43 | 43 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1007640
46 | Shajibazar 330 MW CCPP | 281 | 280 | 334 | 333 | 331 | 333 | 333 | 332 | 333 | 332 | 335 | 332 | 331 | 331 | 331 | 333 | 332 | 330 |  | 331 | 332 | 333 | 331 | 332 | 332 | 332 | 7508000
47 | Shahjibazar GTPP Unit- 8 & 9 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 37 | 769248
48 | Shahjibazar 86MW PP (Shahjibazar) | 50 | 50 | 72 | 72 | 10 | 10 | 10 | 72 | 72 | 72 | 70 | 73 | 77 | 77 | 77 | 76 | 30 | 30 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1437120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 136 | 137 | 150 | 150 | 150 | 150 | 150 | 163 | 163 | 196 | 210 | 211 | 211 | 211 | 211 | 211 | 190 | 190 |  | 210 | 217 | 225 | 216 | 217 | 217 | 203 | 4494540
51 | Sylhet 20 MW GTPP | [13 empty] | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 172000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [8 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 124920
54 | Hobiganj 11MW PP Cofidence-E | [11 empty] | 2 | 2 | 2 | 2 | 2 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 92000
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 53 | 50 | 11 | 11 | 11 | 32 | 42 | 42 | 44 | 47 | 50 | 50 | 50 | 53 | 14 | 14 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 862200
56 | Shahjahanulla 25 MW PP | [10 empty] | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 16 | 192264
57 | Bibiana-II 341 MW CCPP (Summit) | 305 | 300 | 320 | 300 | 275 | 290 | 310 | 300 | 305 | 310 | 290 | 295 | 305 | 310 | 290 | 295 | 300 | 290 |  | 280 | 280 | 275 | 300 | 305 | 295 | 310 | 7334000
| Bibiyana South 400 MW | 370 | 400 | 400 | 370 | 370 | 399 | 400 | 370 | 400 | 397 | 370 | 395 | 396 | 393 | 372 | 376 | 383 | 370 |  | 370 | 370 | 400 | 388 | 370 | 370 | 400 | 9315700
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 |  |  |  | 5 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 45 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 742266
59 | Tangail Palli Power Gen 22 MW | 0 | 22 | 24 | 24 | 24 | 13 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 540960
60 | Barabkunda 22 MW PP (Regent) | 21 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 490080
61 | Narshingdi 22 MW PP (Doreen) | 10 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 385488
62 | Tangail 22 MW PP (Doreen) | [17 empty] | 17 |  | 17 | 17 | 17 | 19 | 17 | 19 | 19 | 115164
63 | Impoprt (Tripura) | 122 | 122 | 126 | 124 | 116 | 110 | 104 | 98 | 96 | 98 | 106 | 90 | 110 | 122 | 134 | 136 | 120 | 132 |  | 142 | 142 | 144 | 152 | 152 | 152 | 146 | 2947200
64 | Malancha, Ctg. EPZ (United) | 36 | 37 | 38 | 39 | 38 | 30 | 13 | 4 | 3 | 4 | 2 | 5 | 12 | 5 | 5 | 7 | 17 | 20 |  | 25 | 25 | 32 | 35 | 35 | 39 | 37 | 507360
65 | Feni 22MW PP (Doreen) | [8 empty] | 9 | 16 | 16 | 16 | 18 | 19 | 19 | 20 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 297936
66 | Feni 11 MW PP (Doreen) | [9 empty] | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 153540
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817200
68 | Cumilla 25 MW PP (Summit) | 10 | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 471320
69 | Summit Ashulia |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 575000
70 | Summit Madhabdi | 0 | 0 | 23 | 23 | 23 | 23 | 22 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 24 | 25 | 25 |  | 13 | 26 | 28 | 28 | 28 | 28 | 28 | 524520
71 | Maona 33 MW PP(Summit) |  |  |  |  | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 684400
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 26 | 792800
73 | Ghorashal 108MW PP (Regent) | 81 | 101 | 101 | 101 | 101 | 32 | 32 | 70 | 100 | 100 | 100 | 97 | 96 | 100 | 101 | 103 | 53 | 53 |  | 99 | 103 | 103 | 103 | 103 | 103 | 103 | 2011454
| Feni Lanka Power | 34 | 17 | 17 | 17 | [9 empty] | 30 | 17 |  |  |  |  | 17 | 17 | [5 empty] | 159600
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 36 | 36 | 36 | 36 | 36 | 36 | 71 | 75 | 75 | 100 | 113 | 113 | 75 | 75 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 2226000
| Manikgonj 162MW PP(MPGL) | [9 empty] | 30 | 98 | 157 | 162 | 162 | 126 | 72 | 72 | 72 |  | 120 | 162 | 162 | 162 | 162 | 162 | 162 | 1956960
77 | Siddhirganj 100 PP(Dutch Bangla) | 16 | 50 | 50 | 50 |  |  |  | 1 | 20 | 24 | 40 | 70 | 100 | 100 | 100 | 50 | 40 | 40 |  | 60 | 100 | 100 | 100 | 50 | 50 | 50 | 1359360
78 | Gazipur 52 MW PP | [9 empty] | 10 | 25 | 25 | 25 | 25 | 6 | 8 | 8 | 8 |  | 24 | 38 | 25 | 25 | 25 | 25 |  | 285600
79 | Kodda 150MW PP | [17 empty] | 64 |  | 100 | 149 | 100 | 100 | 82 | 64 | 48 | 563040
80 | Jamalpur 95 MW PP(Powerpac) | 19 | 24 | 24 | 61 | 48 | 48 | 48 | 53 | 73 | 74 | 65 | 73 | 73 | 73 | 73 | 73 | 65 | 74 |  | 74 | 74 | 66 | 66 | 74 | 74 | 74 | 1483200
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 47 | 46 | 52 | 52 | 43 | 43 | 46 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1230528
| Gazipur 100 MW PP | [7 empty] | 3 | 58 | 70 | 88 | 88 | 88 | 88 | 88 | 70 | 70 | 70 |  | 82 | 88 | 88 | 88 | 88 | 88 | 88 | 1334400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 5 | 5 | 3 | 4 | 2 | 1 | [9 empty] | 33361
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 39 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1275373
| Karnaphuli Power Ltd. | [10 empty] | 9 | 17 | 17 | 17 | [12 empty] | 76945
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 13 |  | 40 | 10 | [5 empty] | 77110
86 | Meghnaghat CCPP ( Summit) | 250 | 270 | 270 | 230 | 250 | 250 | 260 | 260 | 265 | 260 | 260 | 270 | 265 | 265 | 255 | 250 | 255 | 250 |  | 242 | 220 | 270 | 270 | 230 | 245 | 245 | 6103447
87 | Meghnaghat 100 MW(IEL) | [9 empty] | 8 | 37 | 50 | 50 | 55 | 75 | 50 | 32 | 33 |  | 77 | 100 | 100 | 100 | 100 | 100 | 100 | 992640
| Meghnaghat 104 MW PP (OPCL) | 17 | [6 empty] | 2 | 35 | 35 | 63 | 72 | 72 | 72 | 70 | 35 | 35 | 37 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 1016640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 80 | 92 | 92 | 92 | 92 | 92 | 92 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 2213400
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 7 | 24 | 64 | 64 | 64 | 40 | 40 | 40 | 48 |  | 80 | 102 | 72 | 72 | 64 | 64 | 32 | 874656
95 | Patenga 50MW PP (Baraka) | 12 | 12 | 12 | 12 | [5 empty] | 9 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 |  | 36 | 45 | 45 | 45 | 45 | 45 |  | 456480
96 | Chattogram 108 MW PP (ECPV) | [14 empty] | 15 | 18 | 18 | 18 |  | 26 | 50 | 50 | 51 | 50 | 45 | 45 | 340800
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 40 | 40 | 40 | 40 | 30 | 30 | 35 | 35 | 39 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1067177
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 35 | 17 | 17 | 17 |  | 17 | 35 | 35 | 35 | 17 | 17 |  | 243117
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 163 | 163 | 163 | 163 | 110 | 163 | 163 | 163 | 163 | 110 | 110 |  | 130 | 163 | 163 | 163 | 163 | 130 | 130 | 3641318
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13600
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 |  |  |  | 10 | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1056960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [13 empty] | 9 |  |  |  | 34 |  | 158 | 186 | 186 | 140 | 140 | 150 | 120 | 988800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 38 | 50 | 58 | 104 | 105 | 90 | 126 | 143 | 141 | 143 | 143 | 143 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3111840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2112960
116 | Chandpur 200MW (Desh energy) | 194 | 193 | 188 | 185 | 195 | 196 | 196 | 196 | 196 | 189 | 175 | 178 | 176 | 165 | 167 | 167 | 175 | 175 |  | 175 | 175 | 175 | 175 | 175 | 175 | 175 | 4043700
117 | Ashuganj 150MW PP (Midland) | [26 empty] | 0
118 | Bibiyana-III 400 MW CCPP | 366 | 398 | 398 | 366 | 366 | 366 | 416 | 367 | 367 | 383 | 367 | 375 | 370 | 367 | 368 | 368 | 331 | 330 |  | 345 | 367 | 368 | 368 | 368 | 367 | 374 | 8905000
| Jamalpur 115 MW PP (United) | [8 empty] | 7 | 35 | 65 | 75 | 75 | 91 | 115 | 85 | 85 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 1471200
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1929600
| Anlima Energy Ltd. | 35 | 35 | 35 | 35 |  |  |  | 2 | 35 | 33 | 61 | 72 | 72 | 72 | 36 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 890727
| Bhairob 54.5 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 31 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 643680
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 10 | 14 | 24 |  |  |  |  | 10 | 8 | 5 | 6 | 1 | [8 empty] | 71204
120 | Eastern Zone Total | 6051 | 6324 | 6595 | 6537 | 5969 | 5623 | 5785 | 5886 | 6227 | 6568 | 6863 | 6932 | 7229 | 7319 | 7212 | 6976 | 6724 | 6854 |  | 7861 | 8237 | 8213 | 8251 | 8070 | 7897 | 7681 | 167074873
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 51 | 35 | 32 | 32 | 32 | 66 | 66 | 66 | 83 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1960320
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | [6 empty] | 35 | 53 | 53 | 53 | 53 | 17 | 17 | 35 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 1268640
130
131
132 | United Payra Power Ltd. | [22 empty] | 17 | 45 | 27 | 35 | 98400
133 | Bhola Nutan Biddut BD LTD (GAS) | 110 | 110 | 110 | 110 | 110 | 109 | 109 | 109 | 109 | 108 | 107 | 107 | 106 | 107 | 105 | 146 | 145 | 107 |  | 105 | 104 | 108 | 107 | 107 |  |  | 2582482
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | 29 | [13 empty] | 43 |  | 64 | 64 | 64 | 80 | 80 | 110 | 110 | 719808
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 72 | 74 | 73 | 72 | 51 | 32 | 32 | 32 | 32 | 14 | 16 | 15 | 14 | 42 | 46 | 45 | 45 | 46 |  | 83 | 82 | 82 | 82 | 82 | 96 | 97 | 1282706
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 65 | 60 | 60 | 60 | 60 |  | 60 | 50 | 60 | 60 | 60 | 59 | 60 | 1496000
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 32 | 32 | 27 | 24 | 21 | 20 | 20 | 20 | 21 | 22 | 23 | 24 | 25 | 24 | 20 | 30 |  | 31 | 32 | 32 | 34 | 34 | 34 | 34 | 635705
141 | Noapara 100 MW PP (Bangla Trac) | 20 | [18 empty] | 6 | 100 | 99 | 100 | 100 | 80 |  | 457920
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 33 | 33 | [15 empty] | 8 | 32 | 32 | 32 | 32 | 33 | 33 | 298875
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 5 | 11 | 5 | [12 empty] | 15744
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 464 | 464 | 464 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 466 | 588 | 589 | 729 | 845 | 844 | 845 | 844 |  | 845 | 844 | 844 | 845 | 845 | 845 | 845 | 15570909
147 | Bheramara 410 MW CCPP | 355 | 395 | 395 | 360 | 355 | 320 | 320 | 350 | 360 | 385 | 350 | 370 | 330 | 350 | 350 | 355 | 355 | 300 |  | 350 | 355 | 355 | 355 | 350 | 350 | 370 | 8695872
148 | Payra 1320 MW | 410 | 450 | 480 | 510 | 460 | 450 | 450 | 440 | 440 | 440 | 420 | 380 | 380 | 400 | 400 | 420 | 430 | 430 |  | 440 | 540 | 550 | 550 | 540 | 530 | 530 | 11820100
149
150 | Barapukuria TPP Unit-1 | 75 | 75 | 75 | 74 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 74 | 74 | 75 | 77 | 77 | 77 | 77 |  | 75 | 77 | 76 | 76 | 77 | 76 | 75 | 1826618
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3682200
153 | Baghabari 71 MW GTPP | [15 empty] | 40 | 40 | 40 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 375000
156 | Baghabari 100 MW GTPP | [15 empty] | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 442000
| Baghabari 50 MW Peaking PP | [20 empty] | 7 | 50 | 50 | 50 | 50 |  | 183361
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [8 empty] | 38 | 142 | 120 | 100 | 120 | 120 | 120 | 120 | 103 | 80 |  | 86 | 113 | 114 | 119 | 126 | 128 | 133 | 1908400
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 161 | 184 | 203 | 192 | 183 | 156 | 130 | 166 | 182 | 198 | 174 | 154 | 159 | 181 | 182 | 181 | 159 | 151 |  | 142 | 149 | 153 | 162 | 188 | 188 | 194 | 4354309
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 195 | 205 | 194 | 184 | 166 | 136 | 175 | 183 | 200 | 182 | 157 | 158 | 167 | 155 | 154 | 154 | 150 |  | 139 | 153 | 154 | 171 | 183 | 187 | 193 | 4364782
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 339 | 363 | 423 | 398 | 400 | 418 | 419 | 375 | 412 | 372 | 322 | 372 | 373 | 371 | 371 | 335 | 345 | 336 |  | 352 | 317 | 343 | 426 | 426 | 424 | 418 | 9072036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | [7 empty] | 20 | 21 | 21 | 21 | 19 | 19 | 18 | 18 | 18 | 20 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 324480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | [20 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 24588
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 15 | 29 | 31 | 30 | 30 | 30 |  | 110670
168 | Santahar 50 MW Peaking PP | [17 empty] | 7 |  | 30 | 33 | 33 | 33 | 33 |  |  | 146491
169 | Natore 52 MW PP (Rajlanka) | 24 | 24 | 24 | 24 |  |  |  | 23 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 16 | 8 | 8 |  | 42 | 52 | 52 | 52 | 52 | 52 | 52 | 794400
170 | Chapainawabganj 100 MW Peaking PP | [15 empty] | 32 | 32 | 36 |  | 98 | 98 | 100 | 99 | 100 | 100 | 50 | 638032
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [10 empty] | 22 | 35 | 35 | 47 | 35 | 35 |  |  |  | 35 | 90 | 85 | 98 | 113 | 113 |  | 752448
172 | Confidence Power Bogura Unit-1 113 MW | [10 empty] | 25 | 35 | 35 | 35 | 35 |  |  |  |  | 25 | 35 | [5 empty] | 244608
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 34 |  |  |  | 34 | 38 | 36 | 100 | 113 | 113 | 113 | 71 | 44 | 34 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 58 | 1536000
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 1 |  |  |  |  | 3 | 2 | 1 | 0 | [8 empty] | 15069
178
178