## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-24 | Saturday
|  |  | Date (day): | 2021-04-24 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15038.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15828 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-23 | 2021-04-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 99 | 103 | 104 | 104
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 340 | 344 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dust in the gas line
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 7 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 225 | 285 | 285 | 20 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 140 | 200 | 200
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 16 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 214 | 218 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 16 | 100 | 100
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 35 | 35 |  | 20 | Engine problem
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 41 | 54 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 130 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 34 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 53 | 104 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 35 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 25 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 1831 | 2083 | 3667 | 3887 | 761 | 1120
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 217 | 220 | 220
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 105 | 100 | 100
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 49 | 54 | 66 | 66 |  | 36 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 27 | 40 | 11 | 21
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 45 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 20 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 90 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 755 | 1108 | 1646 | 1631 | 555 | 160
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 120 | 135 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 204 | 196 | 225 | 225 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 315 | 340 | 340 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 320 | 310 | 310 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 | 19 |  | Gas shortage
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 45 | 53 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 0 | 0 | 0 |  |  | Under ground cable fault
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint.
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 96 | 95 | 95 | 68 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 85 | 176 | 170 | 170 |  | 30 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 10 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 10 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 166 | 157 | 179
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 1 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 37 | 37 |  | 17 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1354 | 1762 | 2023 | 2195 | 537 | 202
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 196 | 204 | 205 | 205
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 74 | 74 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 150 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 33 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 421 | 587 | 687.6 | 636 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 39 | 40 | 40 | 40 |  | 30 | Engine problem
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 42 | 43 |  | 47 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 328 | 334 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 32 | 52 | 52 |  | 14 | Engine problem
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 78 | 75 | 75 |  | 11 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 145 | 135 | 210 |  | 21
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 17 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 315 | 320 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 400 | 396 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 8 | 9 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 392 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1893 | 2057 | 2084 | 2160 | 0 | 232
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 842 | 842 | 854 | 854
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 16 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 390 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 63 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 92 | 90 | 92 |  | 13 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1158 | 1518 | 1705 | 1994 | 0 | 119
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 60 | 60 | 60 |  | 134 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 93 | 96 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 360 | 560 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 109 | 110 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 50
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 532 | 877 | 1029 | 1080 | 0 | 134
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 50 | 50 | 50 | 50 | 21 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 50 | 50 | 50 | 50 | 50 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 35 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 50 | 50
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 31 |  | 19 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 60 | 130 | 144 | 144 | 66 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 146 | 199 | 180 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 153 | 201 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 379 | 404 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 30
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 50 | 50
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 861 | 1525 | 1841 | 1897 | 137 | 26
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 76 | 73 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 10 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 267 | 336 | 356 | 348 | 124 | 115
|  | Total |  |  |  |  | 21967 | 21219 | 9072 | 11853 | 15038.6 | 15828 | 2114 | 2129
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8668.6469 | 11326 | 14369.964 | 15124.2663
| A. |  | 2021-04-23 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 11853 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8277 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11853 | MW
| 3 | Day peak Generation : |  |  | 9072 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11326 | MW
| 4 | Evening peak Generation : |  |  | 11853 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 348.9198 | MKWHr | By Solar | 0.80663 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 153.485 | MKWHr |  | By Oil: | 46.7918 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 123.5365 | MKWHr |  | By Hydro: | 0.848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2114 | MW | Dhaka | 3584 | 3584 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2129 | MW | Chittagong | 1289 | 1289 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4243 | MW | Khulna | 1466 | 1466 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1253.3 | MMCFD |  |  | Rajshahi | 1215 | 1215 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 166723778.612 | ii) Oil : | Taka | 342833786.13 | Comilla | 1174 | 1174 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 549023071.08 | Total | Taka | 1058580635.822 | Mymensingh | 1018 | 1018 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0425 | MKWHr. | Sylhet | 469 | 469 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 288 | MW (E to W) at | 21:00 | hrs | Barisal | 356 | 356 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -60 | MW at | 18:30 | hrs | Rangpur | 755 | 755 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.9° C |  |  | Total | 11326 | 11326 |  | 0
| B. |  | 2021-04-24 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 40.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15828 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11300 | MW
| 4 | Reserve(Generation end) |  |  |  | 2528 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 391.5155 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7962 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.3702 | MKWHr. | ii) HVDC Flow at Peak Time |  | 842 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0816 | MKWHr. | iii) Maximum HVDC Flow : |  | 844 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.48 |  | (b) Today: | 78.34 |  | (c) Rule Curve: |  | 83.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 341 |  | 0 | 280 | 245 | 100 | 0 | 55 | 222 | 0 | 120 | 50 | 16 | 10 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 0 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 202 | 0 | 130 | 0 |  | 24 | 0 | 66 | 80 | 24 | 0 | 21 | 36 | 80 | 0 | 0 | 265 | 285 | 212 | 8 | 94 | 26 | 49 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 133 | 185 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 335 | 5 | 75 | 0 | 203 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 149 | 0 | 100 | 165 | 0 | 367 | 115 | 70 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 386 | 75 | 0 | 162 | 17 | 0 | 37 | 0 |  | 843 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 34 | 96 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 114 | 0 | 180 | 0 | 97 | 0 | 167 | 0 | 415 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 7457 | 3460 | 10917 | 4637 | 843 | 1962 | 2475 | 756 | 35 | 76 | 133 | 0 | 0 | 78.5
2:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 350 |  | 0 | 280 | 245 | 65 | 0 | 55 | 222 | 0 | 100 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 92 | 0 | 0 | 21 | 36 | 80 | 0 | 0 | 280 | 300 | 212 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 132 | 188 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 335 | 52 | 75 | 0 | 203 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 147 | 0 | 100 | 165 | 0 | 376 | 115 | 50 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 80 | 0 | 54 | 17 | 0 | 37 | 0 |  | 844 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 34 | 84 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 106 | 0 | 157 | 0 | 97 | 0 | 159 | 0 | 332 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 7353 | 3298 | 10651 | 4737 | 844 | 1887 | 2195 | 755 | 35 | 66 | 132 | 0 | 0 | 78.5
3:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 350 |  | 0 | 280 | 230 | 50 | 0 | 55 | 222 | 0 | 150 | 50 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 66 | 80 | 0 | 0 | 21 | 38 | 80 | 0 | 0 | 275 | 300 | 213 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 132 | 196 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 332 | 52 | 75 | 0 | 203 | 18 | 0 | 9 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 41 | 0 | 143 | 0 | 100 | 162 | 0 | 375 | 115 | 70 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 53 | 0 | 54 | 17 | 0 | 37 | 0 |  | 844 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 30 | 64 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 112 | 0 | 167 | 0 | 97 | 0 | 169 | 0 | 414 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 0 |  | 7413 | 3378 | 10791 | 4809 | 844 | 2005 | 2144 | 756 | 35 | 66 | 132 | 0 | 0 | 78.49
4:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 350 |  | 0 | 280 | 245 | 35 | 0 | 55 | 180 | 0 | 75 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 25 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 213 | 0 | 130 | 0 |  | 24 | 0 | 66 | 80 | 0 | 0 | 21 | 39 | 80 | 0 | 0 | 285 | 310 | 215 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 132 | 196 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 333 | 52 | 75 | 0 | 176 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 149 | 0 | 100 | 173 | 0 | 381 | 115 | 50 | 51 | 0 | 0 | 54 | 0 | 0 | 113 | 50 | 400 | 48 | 0 | 0 | 0 | 0 | 37 | 0 |  | 844 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 29 | 48 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 60 | 0 | 156 | 0 | 96 | 0 | 158 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 |  | 7057 | 3225 | 10282 | 4630 | 844 | 1887 | 1912 | 776 | 35 | 66 | 132 | 0 | 0 | 78.49
5:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 353 |  | 0 | 280 | 230 | 0 | 0 | 55 | 180 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 90 | 0 | 0 | 21 | 39 | 80 | 0 | 0 | 260 | 285 | 216 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 126 | 201 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 331 | 53 | 75 | 0 | 149 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 70 | 173 | 0 | 366 | 75 | 50 | 51 | 0 | 0 | 54 | 0 | 0 | 0 | 50 | 370 | 0 | 0 | 0 | 0 | 0 | 37 | 0 |  | 844 | 0 | 300 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 149 | 0 | 0 | 60 | 0 | 161 | 0 | 96 | 0 | 161 | 0 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 6530 | 2787 | 9317 | 4399 | 844 | 1855 | 1367 | 625 | 35 | 66 | 126 | 0 | 0 | 78.48
6:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 301 |  | 0 | 250 | 230 | 0 | 0 | 55 | 180 | 0 | 40 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 0 | 0 | 32 | 90 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 110 | 207 | 66 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 334 | 53 | 75 | 0 | 73 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 1 | 40 | 85 | 0 | 365 | 45 | 17 | 51 | 0 | 0 | 54 | 0 | 0 | 0 | 20 | 370 | 0 | 2 | 0 | 0 | 0 | 37 | 1 |  | 844 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 149 | 0 | 0 | 60 | 0 | 130 | 0 | 96 | 0 | 130 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5953 | 2597 | 8550 | 4205 | 844 | 1690 | 1005 | 625 | 35 | 32 | 110 | 4 | 0 | 78.48
7:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 301 |  | 0 | 250 | 230 | 0 | 0 | 55 | 180 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 204 | 0 | 130 | 0 |  | 0 | 0 | 32 | 90 | 0 | 0 | 21 | 36 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 96 | 26 | 47 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 100 | 206 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 130 | 332 | 53 | 30 | 0 | 0 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 4 | 20 | 85 | 0 | 365 | 24 | 17 | 17 | 1 | 0 | 54 | 0 | 0 | 0 | 20 | 370 | 0 | 13 | 0 | 0 | 0 | 37 | 7 |  | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 76 | 0 | 149 | 0 | 0 | 60 | 0 | 133 | 0 | 97 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 0 | 0 | 0 |  | 5760 | 2552 | 8312 | 4135 | 843 | 1652 | 914 | 575 | 35 | 32 | 100 | 26 | 0 | 78.47
8:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 270 |  | 0 | 250 | 255 | 0 | 0 | 55 | 160 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 32 | 90 | 0 | 0 | 21 | 28 | 80 | 0 | 0 | 260 | 260 | 216 | 8 | 95 | 26 | 46 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 98 | 208 | 74 | 20 | 1 | 40 | 43 | 53 | 0 | 110 | 334 | 52 | 30 | 0 | 0 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 10 | 20 | 85 | 0 | 367 | 24 | 17 | 17 | 2 | 0 | 54 | 0 | 0 | 0 | 20 | 384 | 0 | 29 | 0 | 0 | 0 | 36 | 11 |  | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 0 | 0 | 0 |  | 5734 | 2543 | 8277 | 4126 | 843 | 1575 | 938 | 575 | 35 | 32 | 98 | 55 | 0 | 78.47
9:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 |  | 0 | 250 | 270 | 0 | 0 | 40 | 220 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 |  | 0 | 0 | 32 | 90 | 0 | 0 | 21 | 23 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 98 | 205 | 74 | 20 | 2 | 40 | 43 | 53 | 0 | 130 | 331 | 51 | 30 | 0 | 0 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 12 | 36 | 85 | 0 | 367 | 24 | 17 | 17 | 3 | 0 | 54 | 0 | 0 | 0 | 20 | 398 | 0 | 47 | 0 | 0 | 0 | 36 | 27 |  | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 18 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 350 | 0 | 0 | 0 |  | 6007 | 2547 | 8554 | 4242 | 843 | 1687 | 946 | 576 | 35 | 32 | 98 | 95 | 0 | 78.46
10:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 344 |  | 0 | 250 | 270 | 0 | 0 | 40 | 218 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 214 | 0 | 130 | 0 |  | 0 | 0 | 42 | 90 | 0 | 0 | 21 | 30 | 80 | 0 | 0 | 260 | 260 | 198 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 98 | 203 | 74 | 20 | 2 | 40 | 43 | 53 | 0 | 130 | 333 | 51 | 30 | 0 | 0 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 6 | 50 | 85 | 0 | 396 | 43 | 17 | 44 | 4 | 0 | 54 | 0 | 0 | 0 | 20 | 397 | 0 | 57 | 0 | 0 | 0 | 36 | 20 |  | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 60 | 0 | 135 | 0 | 95 | 0 | 130 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 350 | 0 | 0 | 0 |  | 6043 | 2552 | 8595 | 4235 | 843 | 1684 | 987 | 576 | 35 | 42 | 98 | 95 | 0 | 78.46
11:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 343 |  | 0 | 280 | 275 | 0 | 0 | 40 | 217 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 215 | 0 | 130 | 0 |  | 0 | 0 | 51 | 92 | 0 | 0 | 21 | 24 | 80 | 0 | 0 | 260 | 295 | 197 | 8 | 95 | 26 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 18 | 107 | 197 | 74 | 20 | 2 | 39 | 43 | 50 | 0 | 130 | 333 | 51 | 30 | 0 | 0 | 18 | 0 | 8 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 14 | 50 | 85 | 0 | 399 | 55 | 17 | 51 | 5 | 0 | 54 | 0 | 0 | 0 | 20 | 395 | 0 | 57 | 0 | 0 | 0 | 36 | 21 |  | 843 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 14 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 60 | 0 | 146 | 0 | 96 | 0 | 130 | 0 | 286 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 350 | 0 | 0 | 0 |  | 6149 | 2601 | 8750 | 4274 | 843 | 1746 | 1013 | 575 | 35 | 51 | 107 | 106 | 0 | 78.45
12:00 | 0 | 0 | 0 | 180 | 0 | 99 | 0 | 0 | 340 |  | 0 | 280 | 275 | 0 | 0 | 40 | 214 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 16 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 217 | 0 | 130 | 0 |  | 0 | 0 | 49 | 80 | 0 | 0 | 21 | 27 | 80 | 0 | 0 | 295 | 300 | 204 | 8 | 95 | 26 | 45 | 0 | 0 | 0 | 0 | 1 | 10 | 10 | 33 | 18 | 108 | 196 | 74 | 20 | 2 | 39 | 42 | 53 | 0 | 163 | 328 | 30 | 78 | 0 | 0 | 18 | 0 | 8 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 50 | 85 | 0 | 400 | 96 | 17 | 51 | 5 | 0 | 54 | 0 | 0 | 0 | 20 | 392 | 0 | 33 | 0 | 0 | 0 | 36 | 25 |  | 842 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 60 | 0 | 146 | 0 | 93 | 0 | 153 | 0 | 379 | 0 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 360 | 0 | 0 | 0 |  | 6254 | 2818 | 9072 | 4346 | 842 | 1925 | 1093 | 586 | 35 | 49 | 108 | 88 | 0 | 78.45
13:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 343 |  | 0 | 280 | 260 | 0 | 0 | 40 | 218 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 9 | 203 | 0 | 130 | 0 |  | 4 | 0 | 52 | 80 | 0 | 0 | 21 | 28 | 80 | 0 | 0 | 280 | 300 | 183 | 8 | 94 | 26 | 50 | 0 | 0 | 0 | 0 | 10 | 19 | 10 | 33 | 18 | 124 | 198 | 74 | 20 | 2 | 39 | 42 | 53 | 0 | 163 | 330 | 31 | 77 | 0 | 0 | 18 | 0 | 8 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 100 | 100 | 0 | 368 | 115 | 17 | 67 | 4 | 0 | 54 | 0 | 0 | 7 | 50 | 370 | 0 | 45 | 0 | 2 | 0 | 36 | 35 |  | 843 | 0 | 355 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 21 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 176 | 0 | 95 | 0 | 189 | 0 | 384 | 0 | 0 | 0 | 0 | 75 | 0 | 8 | 0 | 410 | 0 | 0 | 0 |  | 6444 | 3096 | 9540 | 4474 | 843 | 1946 | 1321 | 635 | 35 | 52 | 124 | 110 | 0 | 78.44
14:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 322 |  | 0 | 280 | 275 | 0 | 0 | 40 | 160 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 23 | 19 | 25 | 16 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 215 | 0 | 130 | 0 |  | 10 | 0 | 43 | 92 | 0 | 0 | 20 | 28 | 80 | 0 | 0 | 300 | 320 | 194 | 8 | 95 | 26 | 51 | 0 | 0 | 0 | 0 | 24 | 19 | 10 | 33 | 20 | 124 | 196 | 74 | 20 | 2 | 39 | 42 | 53 | 0 | 110 | 329 | 30 | 77 | 0 | 0 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 15 | 90 | 137 | 0 | 343 | 115 | 17 | 105 | 4 | 0 | 54 | 0 | 0 | 8 | 50 | 394 | 0 | 33 | 0 | 35 | 0 | 36 | 29 |  | 842 | 0 | 385 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 16 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 100 | 0 | 173 | 0 | 96 | 0 | 175 | 0 | 344 | 0 | 0 | 0 | 0 | 88 | 0 | 7 | 0 | 440 | 0 | 0 | 0 |  | 6445 | 3152 | 9597 | 4484 | 842 | 1796 | 1517 | 666 | 35 | 43 | 124 | 90 | 0 | 78.44
15:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 339 |  | 0 | 280 | 270 | 0 | 0 | 44 | 212 | 0 | 153 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 15 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 130 | 0 |  | 15 | 0 | 43 | 92 | 0 | 0 | 20 | 31 | 80 | 0 | 0 | 305 | 305 | 188 | 8 | 97 | 26 | 52 | 0 | 0 | 0 | 0 | 30 | 19 | 10 | 33 | 20 | 124 | 195 | 71 | 20 | 2 | 39 | 42 | 53 | 0 | 163 | 331 | 30 | 74 | 0 | 30 | 18 | 0 | 8 | 315 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 12 | 50 | 175 | 0 | 338 | 115 | 17 | 105 | 1 | 0 | 54 | 0 | 0 | 8 | 50 | 394 | 0 | 33 | 0 | 17 | 0 | 30 | 18 |  | 843 | 0 | 365 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 16 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 0 | 16 | 0 | 5 | 74 | 0 | 150 | 0 | 0 | 125 | 0 | 184 | 0 | 95 | 0 | 170 | 0 | 393 | 2 | 0 | 0 | 0 | 98 | 0 | 6 | 0 | 440 | 0 | 0 | 4 |  | 6606 | 3256 | 9862 | 4578 | 843 | 1947 | 1556 | 664 | 35 | 43 | 124 | 72 | 0 | 78.43
16:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 342 |  | 0 | 280 | 240 | 0 | 0 | 55 | 212 | 0 | 142 | 24 | 10 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 15 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 46 | 92 | 0 | 0 | 20 | 38 | 80 | 0 | 0 | 295 | 290 | 182 | 8 | 94 | 26 | 52 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 33 | 20 | 112 | 198 | 66 | 20 | 0 | 39 | 43 | 53 | 0 | 163 | 333 | 31 | 30 | 0 | 80 | 17 | 0 | 8 | 280 | 14 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 7 | 50 | 175 | 0 | 331 | 75 | 17 | 105 | 2 | 0 | 54 | 0 | 0 | 25 | 20 | 370 | 12 | 12 | 16 | 17 | 0 | 36 | 12 |  | 843 | 0 | 350 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 19 | 16 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 16 | 0 | 5 | 72 | 0 | 150 | 0 | 0 | 143 | 0 | 185 | 0 | 97 | 0 | 154 | 0 | 346 | 17 | 0 | 0 | 0 | 50 | 0 | 5 | 0 | 440 | 0 | 0 | 17 |  | 6477 | 3151 | 9628 | 4519 | 843 | 1830 | 1543 | 662 | 35 | 46 | 112 | 38 | 0 | 78.43
17:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 0 | 302 |  | 0 | 280 | 265 | 3 | 0 | 55 | 213 | 0 | 120 | 32 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 53 | 19 | 25 | 15 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 90 | 0 |  | 24 | 0 | 48 | 50 | 0 | 0 | 20 | 40 | 80 | 0 | 0 | 295 | 290 | 183 | 8 | 95 | 26 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 10 | 33 | 20 | 130 | 198 | 74 | 20 | 1 | 39 | 43 | 14 | 0 | 163 | 332 | 31 | 30 | 0 | 80 | 17 | 0 | 8 | 280 | 14 | 11 | 0 | 10 | 0 | 0 | 8 | 0 | 149 | 3 | 50 | 175 | 0 | 331 | 75 | 17 | 105 | 0 | 0 | 54 | 0 | 0 | 25 | 20 | 340 | 17 | 7 | 17 | 17 | 0 | 36 | 4 |  | 843 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 20 | 32 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 5 | 71 | 0 | 150 | 0 | 0 | 100 | 0 | 161 | 0 | 65 | 0 | 154 | 0 | 364 | 17 | 0 | 0 | 0 | 50 | 0 | 4 | 0 | 440 | 0 | 0 | 17 |  | 6278 | 3106 | 9384 | 4347 | 843 | 1664 | 1637 | 661 | 35 | 48 | 130 | 19 | 0 | 78.42
18:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 0 | 281 |  | 0 | 280 | 265 | 25 | 0 | 55 | 215 | 0 | 120 | 32 | 24 | 25 | 0 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 15 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 205 | 0 | 90 | 0 |  | 24 | 0 | 66 | 50 | 25 | 7 | 20 | 40 | 80 | 0 | 0 | 300 | 305 | 188 | 8 | 95 | 26 | 20 | 0 | 0 | 0 | 0 | 25 | 0 | 10 | 33 | 20 | 152 | 197 | 73 | 20 | 0 | 39 | 43 | 14 | 0 | 110 | 334 | 31 | 30 | 0 | 80 | 17 | 0 | 8 | 295 | 14 | 11 | 0 | 31 | 0 | 0 | 15 | 0 | 128 | 0 | 50 | 175 | 0 | 333 | 75 | 17 | 105 | 0 | 0 | 54 | 0 | 8 | 25 | 20 | 370 | 20 | 1 | 25 | 20 | 0 | 36 | 1 |  | 843 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 48 | 0 | 50 | 50 | 5 | 0 | 16 | 0 | 0 | 0 | 25 | 7 | 20 | 0 | 5 | 73 | 0 | 150 | 0 | 0 | 80 | 0 | 146 | 0 | 42 | 0 | 157 | 0 | 339 | 17 | 0 | 4 | 0 | 50 | 0 | 1 | 20 | 400 | 0 | 0 | 17 |  | 6413 | 3030 | 9443 | 4349 | 843 | 1561 | 1758 | 623 | 35 | 119 | 152 | 3 | 0 | 78.42
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 282 |  | 0 | 280 | 240 | 71 | 0 | 55 | 150 | 0 | 64 | 65 | 102 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 15 | 33 | 25 | 8 | 0 | 0 | 35 | 0 | 0 | 17 | 202 | 0 | 90 | 0 |  | 24 | 0 | 66 | 100 | 34 | 22 | 20 | 40 | 80 | 0 | 0 | 275 | 260 | 182 | 8 | 92 | 26 | 20 | 0 | 0 | 0 | 0 | 37 | 9 | 10 | 33 | 20 | 158 | 203 | 74 | 20 | 0 | 41 | 43 | 49 | 0 | 163 | 334 | 33 | 78 | 0 | 120 | 17 | 0 | 9 | 290 | 14 | 11 | 0 | 134 | 0 | 0 | 96 | 0 | 130 | 0 | 100 | 175 | 0 | 331 | 115 | 65 | 105 | 0 | 0 | 54 | 0 | 34 | 84 | 90 | 340 | 70 | 0 | 131 | 80 | 0 | 36 | 0 |  | 843 | 0 | 280 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 50 | 29 | 110 | 0 | 50 | 50 | 50 | 0 | 57 | 42 | 16 | 30 | 52 | 30 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 80 | 0 | 160 | 0 | 98 | 10 | 158 | 0 | 322 | 70 | 0 | 58 | 0 | 100 | 0 | 0 | 90 | 420 | 0 | 0 | 17 |  | 7434 | 3619 | 11053 | 4156 | 843 | 1792 | 3128 | 644 | 35 | 297 | 158 | 0 | 0 | 78.4
19:30 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 346 |  | 0 | 280 | 222 | 88 | 0 | 55 | 180 | 0 | 68 | 100 | 48 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 15 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 66 | 100 | 44 | 40 | 22 | 40 | 80 | 0 | 0 | 275 | 260 | 182 | 8 | 92 | 26 | 52 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 158 | 204 | 74 | 20 | 0 | 40 | 43 | 50 | 0 | 163 | 336 | 33 | 78 | 0 | 140 | 17 | 0 | 9 | 280 | 14 | 11 | 0 | 30 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 175 | 0 | 332 | 115 | 105 | 105 | 0 | 0 | 54 | 0 | 10 | 113 | 100 | 340 | 90 | 0 | 162 | 90 | 0 | 36 | 0 |  | 842 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 32 | 50 | 29 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 18 | 16 | 31 | 52 | 33 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 90 | 0 | 160 | 0 | 98 | 40 | 158 | 0 | 347 | 90 | 0 | 90 | 0 | 113 | 0 | 0 | 109 | 490 | 0 | 0 | 17 |  | 7676 | 3934 | 11610 | 4337 | 842 | 1904 | 3324 | 714 | 35 | 296 | 158 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 |  | 0 | 280 | 225 | 65 | 0 | 55 | 180 | 0 | 120 | 100 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 28 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 62 | 100 | 45 | 18 | 22 | 40 | 80 | 0 | 0 | 290 | 295 | 185 | 8 | 97 | 26 | 51 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 158 | 203 | 74 | 20 | 0 | 40 | 43 | 53 | 0 | 163 | 334 | 32 | 78 | 0 | 145 | 17 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 176 | 0 | 348 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 85 | 0 | 35 | 90 | 0 | 36 | 0 |  | 843 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 26 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 12 | 8 | 31 | 52 | 32 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 100 | 0 | 163 | 0 | 97 | 35 | 161 | 0 | 397 | 90 | 0 | 101 | 0 | 113 | 0 | 0 | 113 | 500 | 0 | 0 | 17 |  | 7537 | 4057 | 11594 | 4596 | 843 | 1960 | 3004 | 723 | 35 | 275 | 158 | 0 | 0 | 78.41
21:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 |  | 0 | 280 | 225 | 7 | 0 | 55 | 218 | 0 | 140 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 217 | 0 | 130 | 0 |  | 24 | 0 | 54 | 100 | 45 | 0 | 21 | 40 | 120 | 0 | 0 | 315 | 320 | 196 | 8 | 96 | 26 | 53 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 166 | 204 | 74 | 20 | 0 | 40 | 43 | 53 | 0 | 163 | 334 | 32 | 78 | 0 | 145 | 17 | 0 | 9 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 176 | 0 | 396 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 53 | 0 | 35 | 90 | 0 | 36 | 0 |  | 842 | 0 | 390 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 34 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 12 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 130 | 0 | 199 | 0 | 96 | 63 | 201 | 0 | 404 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 560 | 0 | 0 | 17 |  | 7597 | 4256 | 11853 | 4952 | 842 | 2006 | 2803 | 783 | 35 | 266 | 166 | 0 | 0 | 78.4
22:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 |  | 0 | 280 | 220 | 7 | 0 | 55 | 223 | 0 | 140 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 49 | 100 | 45 | 0 | 21 | 42 | 120 | 0 | 0 | 290 | 295 | 181 | 8 | 95 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 164 | 204 | 74 | 19 | 0 | 40 | 43 | 53 | 0 | 163 | 333 | 33 | 78 | 0 | 145 | 17 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 176 | 0 | 366 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 53 | 0 | 35 | 90 | 0 | 37 | 0 |  | 843 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 33 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 12 | 0 | 30 | 52 | 33 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 144 | 0 | 192 | 0 | 96 | 70 | 195 | 0 | 396 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 580 | 0 | 0 | 17 |  | 7425 | 4237 | 11662 | 4777 | 843 | 1981 | 2797 | 803 | 35 | 262 | 164 | 0 | 0 | 78.4
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 |  | 0 | 280 | 225 | 7 | 0 | 55 | 220 | 0 | 140 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 49 | 88 | 45 | 0 | 21 | 42 | 120 | 0 | 0 | 295 | 300 | 186 | 8 | 95 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 158 | 206 | 74 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 334 | 68 | 78 | 0 | 145 | 17 | 0 | 9 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 149 | 0 | 100 | 176 | 0 | 370 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 53 | 0 | 35 | 53 | 0 | 37 | 0 |  | 843 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 60 | 33 | 96 | 0 | 50 | 50 | 0 | 0 | 97 | 12 | 0 | 30 | 52 | 0 | 21 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 136 | 0 | 184 | 0 | 97 | 0 | 185 | 0 | 403 | 92 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 0 |  | 7376 | 3873 | 11249 | 4806 | 843 | 1984 | 2466 | 781 | 35 | 176 | 158 | 0 | 0 | 78.39
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 351 |  | 0 | 280 | 225 | 7 | 0 | 55 | 220 | 0 | 140 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 49 | 90 | 24 | 0 | 21 | 42 | 120 | 0 | 0 | 290 | 295 | 184 | 8 | 95 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 154 | 208 | 74 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 334 | 69 | 78 | 0 | 145 | 17 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 176 | 0 | 366 | 115 | 17 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 47 | 0 | 17 | 0 | 0 | 37 | 0 |  | 843 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 32 | 64 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 30 | 52 | 0 | 21 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 130 | 0 | 185 | 0 | 97 | 0 | 186 | 0 | 401 | 92 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 560 | 0 | 0 | 0 |  | 7208 | 3596 | 10804 | 4784 | 843 | 1983 | 2145 | 781 | 35 | 79 | 154 | 0 | 0 | 78.39
KWH | 0 | 0 | 0 | 4378500 | 0 | 2315681 | 0 | 0 | 7924000 |  | 0 | 6561000 | 5898705 | 469440 | 0 | 1251807 | 4819129 | 0 | 2673000 | 624960 | 273456 | 101770 | 0 | 0 | 0 | 0 | 857160 | 45614 | 809559 | 403200 | 600000 | 519120 | 814900 | 803400 | 9120 | 0 | 0 | 848000 | 0 | 0 | 297556 | 4928286 | 0 | 3072054 | 0 |  | 384240 | 0 | 1217779 | 2062200 | 289920 | 64320 | 492144 | 862560 | 2095832 | 0 | 0 | 7110100 | 7055000 | 4821000 | 217454 | 2258850 | 594504 | 1128960 | 0 | 0 | 0 | 0 | 774288 | 370476 | 221580 | 811200 | 513130 | 3081600 | 4690320 | 1712640 | 405468 | 15350 | 878000 | 1025520 | 1170600 | 0 | 3535936 | 7641000 | 1044000 | 1505280 | 0 | 2107750 | 400000 | 0 | 201420 | 7373000 | 363744 | 264000 | 0 | 243382 | 0 | 0 | 1051200 | 0 | 3445920 | 99900 | 1722240 | 3514080 | 0 | 8808000 | 2209200 | 902400 | 2017309 | 33479 | 0 | 1298599 | 0 | 36480 | 1360800 | 1394880 | 9283000 | 688320 | 383430 | 839520 | 647345 | 0 | 877320 | 214643 |  | 20370182 | 0 | 8175744 | 0 | 1371840 | 0 | 0 | 0 | 0 | 0 | 168750 | 1409000 | 590316 | 1040640 | 0 | 1203000 | 1200000 | 221839 | 0 | 484456 | 86030 | 20925 | 156134 | 644160 | 134378 | 466800 | 0 | 161766 | 1776436 | 0 | 3674100 | 0 | 0 | 2465800 | 0 | 4110027 | 0 | 2223415 | 243840 | 4151227 | 0 | 8265800 | 714240 | 0 | 508032 | 0 | 1079040 | 0 | 59829 | 376416 | 118086000 | 0 | 0 | 147600 |  | 163132029 | 185787762 | 348919791 | 109142771 | 20370182 | 44342222 | 44475493 | 123536536 | 848000 | 2316356 | 3081600 | 806631 | 0
Fuel Cost | 0 | 0 | 0 | 6436395 | 0 | 3056698.92 | 0 | 0 | 8161720 |  | 0 | 7151490 | 6547562.55 | 3563049.6 | 0 | 10590287.22 | 5011894.16 | 0 | 4624290 | 4705948.8 | 2493918.72 | 1001416.8 | 0 | 0 | 0 | 0 | 6257268 | 352596.22 | 7982251.74 | 302400 | 450000 | 0 | 0 | 0 | 88190.4 | 0 | 0 | 228960 | 0 | 0 | 2764295.24 | 5371831.74 | 0 | 5222491.8 | 0 |  | 0 | 0 | 11812456.3 | 19694010 | 2522304 | 509414.4 | 620101.44 | 2561803.2 | 3101831.36 | 0 | 0 | 5261474 | 7055000 | 4435320 | 280515.66 | 2597677.5 | 671789.52 | 1580544 | 0 | 0 | 0 | 0 | 7394450.4 | 470504.52 | 166185 | 1419600 | 384847.5 | 23112000 | 4971739.2 | 15550771.2 | 514944.36 | 244679 | 1439920 | 1640832 | 2083668 | 0 | 4030967.04 | 7946640 | 2056680 | 2875084.8 | 0 | 3646407.5 | 876000 | 0 | 410896.8 | 7446730 | 272808 | 200640 | 0 | 1839967.92 | 0 | 0 | 5466240 | 0 | 33907852.8 | 1167831 | 14036256 | 38127768 | 0 | 8191440 | 20147904 | 8527680 | 17570761.39 | 0 | 0 | 11310797.29 | 0 | 364070.4 | 11662056 | 9289900.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 117332248.32 | 0 | 8584531.2 | 0 | 10782662.4 | 0 | 0 | 0 | 0 | 0 | 1758375 | 1592170 | 914989.8 | 10156646.4 | 0 | 2466150 | 2460000 | 2182895.76 | 0 | 4287435.6 | 662431 | 282906 | 1512938.46 | 6241910.4 | 1303466.6 | 896256 | 0 | 122456.862 | 10711909.08 | 0 | 19913622 | 0 | 0 | 2884986 | 0 | 5425235.64 | 0 | 3335122.5 | 4147718.4 | 4856935.59 | 0 | 8183142 | 7456665.6 | 0 | 4821223.68 | 0 | 8373350.4 | 0 | 661110.45 | 2781714.24 | 518397540 | 0 | 0 | 0 |  | 425836719.21 | 775490745.382 | 1201327464.592 | 113754149.892 | 117332248.32 | 52969628.72 | 320733176.61 | 549023071.08 | 228960 | 22100609.52 | 23112000 | 2073620.45 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 99 | 0 | 0 | 340 |  | 0 | 280 | 275 | 0 | 0 | 40 | 214 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 16 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 217 | 0 | 130 | 0 |  | 0 | 0 | 49 | 80 | 0 | 0 | 21 | 27 | 80 | 0 | 0 | 295 | 300 | 204 | 8 | 95 | 26 | 45 | 0 | 0 | 0 | 0 | 1 | 10 | 10 | 33 | 18 | 108 | 196 | 74 | 20 | 2 | 39 | 42 | 53 | 0 | 163 | 328 | 30 | 78 | 0 | 0 | 18 | 0 | 8 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 16 | 50 | 85 | 0 | 400 | 96 | 17 | 51 | 5 | 0 | 54 | 0 | 0 | 0 | 20 | 392 | 0 | 33 | 0 | 0 | 0 | 36 | 25 |  | 842 | 0 | 300 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 19 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 76 | 0 | 150 | 0 | 0 | 60 | 0 | 146 | 0 | 93 | 0 | 153 | 0 | 379 | 0 | 0 | 0 | 0 | 34 | 0 | 7 | 0 | 360 | 0 | 0 | 0 |  | 9072 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 0 | 344 | 0 | 0 | 280 | 225 | 7 | 0 | 55 | 218 | 0 | 140 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 29 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 217 | 0 | 130 | 0 | 0 | 24 | 0 | 54 | 100 | 45 | 0 | 21 | 40 | 120 | 0 | 0 | 315 | 320 | 196 | 8 | 96 | 26 | 53 | 0 | 0 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 166 | 204 | 74 | 20 | 0 | 40 | 43 | 53 | 0 | 163 | 334 | 32 | 78 | 0 | 145 | 17 | 0 | 9 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 149 | 0 | 100 | 176 | 0 | 396 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 53 | 0 | 35 | 90 | 0 | 36 | 0 |  | 842 | 0 | 390 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 60 | 34 | 110 | 0 | 50 | 50 | 50 | 0 | 100 | 12 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 130 | 0 | 199 | 0 | 96 | 63 | 201 | 0 | 404 | 92 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 560 | 0 | 0 | 17 |  | 11853 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 280 | 285 | 100 | 0 | 55 | 220 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 220 | 0 | 130 | 0 | 0 | 22 |  | 66 | 100 | 90 | 50 | 22 | 21 | 135 | 0 | 0 | 340 | 310 | 225 | 8 | 95 | 26 | 55 | 0 | 0 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 179 | 205 | 74 | 20 | 0 | 40 | 43 | 51 | 0 | 163 | 330 | 52 | 75 | 0 | 210 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 170 | 0 | 400 | 115 | 105 | 100 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 37 |  |  | 854 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 60 | 33 | 110 | 0 | 50 | 50 | 50 | 40 | 100 | 50 | 43 | 31 | 50 | 30 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 144 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 92 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 110 |  | 50
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 0 | 360 | 0 | 0 | 280 | 285 | 100 | 0 | 55 | 220 | 0 | 200 | 100 | 100 | 149 | 100 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 0 | 0 | 17 | 220 | 0 | 130 | 0 | 0 | 22 |  | 66 | 100 | 90 | 50 | 22 | 11 | 135 | 0 | 0 | 340 | 310 | 225 | 8 | 95 | 26 | 55 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 205 | 74 | 20 | 1.6 | 40 | 42 | 51 | 0 | 163 | 330 | 52 | 75 | 0 | 135 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 300 | 100 | 50 | 200 | 100 | 149 | 20 | 100 | 170 | 0 | 400 | 115 | 105 | 100 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 37 | 30 |  | 854 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 60 | 33 | 110 | 0 | 50 | 50 | 50 | 35 | 100 | 50 | 43 | 30 | 50 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 0 | 144 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 109 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 0 | 349 | 0 | 0 | 280 | 235 | 0 | 0 | 40 | 170 | 0 | 75 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 24 | 33 |  | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 203 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 21 | 3 | 80 | 0 | 0 | 275 | 275 | 191 | 8 | 95 | 26 | 20 | 0 | 0 | 0 | 0 | 8 | 21 | 10 | 33 | 20 | 116 | 206 | 74 | 16 | 1 | 0 | 43 | 50 | 0 | 110 | 310 | 66 | 40 | 0 | 135 | 0 | 0 | 9 | 310 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 11 | 40 | 51 | 0 | 338 | 46 | 23 | 68 | 3 | 0 | 35 | 0 | 0 | 0 | 10 | 350 | 0 | 27 | 0 | 0 | 0 | 36 | 15 | 0 | 839 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 21 | 0 | 0 | 50 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 96 | 0 | 156 | 0 | 61 | 0 | 157 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 410 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8277 | 8:00
| Highest Generation |  | 11853 | 21:00
| Day Peak Generation |  | 9072 | 12:00
| Evening Peak Generation |  | 11853 | 21:00
| HVDC Max Flow |  | 844 | 2:00
| HVDC EvPeak Flow |  | 842 | 21:00
| Load factor L.F |  | 122.7%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-24
Till now the maximum generation is : - |  |  | 13380 | 21:00 | Hrs on | 2021-04-15
The Summary of Yesterday's |  | 2021-04-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9072 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 7962 | MW
Evening Peak Generation : |  | 11853 | MW Hour : | 21:00 | Available Max Generation : |  | 15828 | MW
E.P. Demand (at gen end) : |  | 11853 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13300 | MW
Maximum Generation : |  | 11853 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2528 | MW
Total Gen. (MKWH) : |  | 348.9198 | System Load Factor : | 122.7% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -60 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-24
Actual : | 78.34 | Ft.(MSL) , | Rule curve : | 83.4 | Ft.( MSL )
Gas Consumed : | Total = | 1253.3 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 166723778.612
: |  | Coal : | 549023071.08 | Oil : | 342833786.13 | Total : | 1058580635.822
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4721.3971 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1611.1439 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1444.5307 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1305.6101 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1179.6653 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 951.9623 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 525.0744 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 244.9137 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 734.2351 |  |  | 0 | 0%
Total | 0 |  | 12718.5328 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-4,5
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Hathazari-Madunaghat 132 kV Ckt was under shut down from 08:42 to 16:48 for project work.
b) Barapukuria 230/132 kV T01 transformer was under shut down from 11:49 to 13:54 for C/M.
c) Barapukuria S/S-Barapukuria P/S 230 kV Ckt-1 was under shut down from 08:30 to 11:30 for C/M.
d) Khulna 132/33 kV T-3 transformer was under shut down from 08:36 to 11:20 for C/M.
e) Mymensingh-Netrokona 132 kV Ckt-1 was under shut down from 09:04 to 11:38 for C/M.
f) Rajshahi 132/33 kV T-2 transformer and its Bus were under shut down from 07:17 to 08:52 for R/H maint.
g) Feni 132/33 kV T-1 transformer was under shut down from 09:20 to 10:50 for R/H maintenance at 33 kV
isolator.
h) Sylhet 225 GT was synchronized at 14:46.
i) Dohazari-Matarbari-Cox'sbazar 132 kV Ckt was under shut down from 14:03 to 15:45 for D/W. |  |  |  |  | About 30 MW power interruption occurred under Matarbari S/S area
from 14:03 to 15:45.
j) Halishahar-Khulshi 132 kV Ckt-2 tripped at 13:56 showing Dist. A,E/F relay at Halishahar end and Dist. Z1
trip-1,2 at Khulshi end and was switched on at 21:15.
k) Khulshi-Rampur 132 kV Ckt-1 tripped at 13:56 showing Dir. E/F, Inst. E/F relay at Khulshi end and was
switched on at 14:41.
l) Khulna(c) 132/33 kV T-3 transformer was under shut down from 15:15 to 15:42 for C/M. |  |  |  |  | About 15 MW power interruption occurred under Khulna(c) S/S area
from 15:15 to 15:42.
m) Kurigram 132/33 kV T-1 transformer was under shut down from 21:15 to 22:51 for R/H maintenance at |  |  |  |  | About 10 MW power interruption occurred under Kurigram S/S area
LT bushing. |  |  |  |  | from 21:15 to 22:51.
n) Mithapukur 132/33 kV T-2 transformer tripped at 06:55(24/4/2021) showing O/C,E/F relay at both sides |  |  |  |  | About 10 MW power interruption occurred under Mithapukur S/S area
and was switched on at 07:30. |  |  |  |  | from 06:55(24/4/2021) to 07:30.
o) Fenchuganj 230/132 kV AT-2 transformer was shut down at 07:27(24/4/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | MW
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4378500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 103 | 2315681
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Dirty in Gas
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 344 | 7924000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6561000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 7 | 469440 | Low demand
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 225 | 5898705 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1251807
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 403200
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 140 | 2673000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 16 | 624960 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 218 | 4819129 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 273456 | Low demand
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 857160
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 101770 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 45614 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 809559 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1119120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 814900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 9120 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 243382 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3445920
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 902400 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 688320 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 35 | 839520 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 214643
| Dhaka area Total |  |  |  | 5829 | 2083 | 48487706
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 297556 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 99900
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 64320 | Reserve.
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 848000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 217 | 4928286 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 3072054
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2017309
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 54 | 1217779 | Low demand
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2062200
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1722240
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 492144
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 862560
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 45 | 289920 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33479
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1298599
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1394880
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 647345 | Transformer O/L.
| Chattogram area Total |  |  |  | 2382 | 1108 | 21348571
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 120 | 2095832
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4821000
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7110100 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 7055000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 594504 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1128960
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 0 | Line fault
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Line fault
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2258850 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 176 | 3514080
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 370476
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 221580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 166 | 3081600
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 811200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 774288
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 513130 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 36480 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1360800
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 877320 | Low demand
| Cumilla Area Total |  |  |  | 3034 | 1762 | 36842654
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 204 | 4690320
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 405468
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 74 | 1712640 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15350
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 150 | 1051200 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2209200
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 383430
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 384240
| Mymensingh Area Total |  |  |  | 709 | 587 | 10851848
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 40 | 878000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1025520 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3535936
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 334 | 7641000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1170600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 1044000 | GT-8 Under maint.
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1505280
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 2107750
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 400000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 363744 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7373000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 396 | 8808000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 201420
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9283000 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2057 | 45601250
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 842 | 20370182
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1371840 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 390 | 8175744 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 168750 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 63 | 243840 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 92 | 714240 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1518 | 31044596
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1040640
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 590316
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1409000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2223415
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 560 | 118086000
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 147600 | Low demand
| Barisal Area Total |  |  |  | 1826 | 877 | 123496971
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 50 | 1200000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 50 | 1203000 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 221839
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 86030 | Fuel shortage
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 20925 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 156134 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 130 | 2465800 | ST Under maint.
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 199 | 4110027 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 201 | 4151227 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 404 | 8265800 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 134378 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 466800
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 161766
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 644160
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 484456
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 508032
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 376416 | Low demand
| Rajshahi Area Total |  |  |  | 2173 | 1525 | 24656790
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1776436
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3674100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1079040
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 59829
| Rangpur Area Total |  |  |  | 605 | 336 | 6589405
| Total |  |  |  | 21219 | 11853 | 348919791
| Eastern Grid Total |  |  |  | 14331 | 7597 | 163132029
| Western Grid Total |  |  |  | 6888 | 4256 | 185787762
| National Grid Total |  |  |  | 21219 | 11853 | 348919791
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-23
(a) ENTIRE EASTERN GRID : |  | 7534 | MW | (b) ENTIRE WESTERN GRID : |  | 3792 | MW
i) Dhaka area |  | 3584 | MW | i) Khulna area |  | 1466 | MW
ii) Chittagong area |  | 1289 | MW | ii) Rajshahi area |  | 1215 | MW
iii) Comilla area |  | 1174 | MW | iii) Barisal area |  | 356 | MW
iv) Mymensingh area |  | 1018 | MW | iv) Rangpur area |  | 755 | MW
v) Sylhet area |  | 469 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11326 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 98 | 1:00 | Jamalpur | 151 | 19:00 | Jhenida | 106 | 19:30
Munsiganj | 124 | 21:00 | Sherpur | 134 | 19:00 | Bottail | 106 | 21:00
Sonargaon | 78 | 4:00 | Srimongal | 52 | 19:30 | G.K Project | 50 | 21:00
Shyampur | 190 | 1:00 | Shahjibazar | 109 | 1:00 | Faridpur | 175 | 21:00
Bhulta | 186 | 1:00 | Fenchuganj | 39 | 1:00 | Madaripur | 97 | 21:00
Madanganj | 60 | 3:00 | Kulawara | 43 | 20:00 | Sariatpur | 60 | 21:00
Shitalakhya | 97 | 1:00 | Sylhet | 103 | 18:30 | Gopalganj | 89 | 21:00
Rahim steel | 22 | 13:00 | Chatak | 31 | 21:00 | Bagerhat | 95 | 21:00
Matuail | 51 | 1:00 | Sunamganj | 41 | 21:00 | Mongla | 42 | 21:00
Ghorasal | 69 | 1:00 | Biani Bazar | 62 | 18:30 | Satkhira | 110 | 21:00
Narsingdi | 151 | 19:30 | Comilla (S) | 166 | 21:00 | Gallamari | 38 | 15:00
Haripur (SBU) | 94 | 1:00 | Comilla(N) | 119 | 1:00 | Magura | 50 | 19:30
Sreenagar |  |  | Chandpur | 72 | 22:00 | Norail | 38 | 19:30
Ullon | 72 | 19:00 | Feni | 122 | 21:00 | Chuadanga | 90 | 22:00
Hasnabad | 90 | 1:00 | Chowmuhani | 176 | 21:00 | Borguna | 16 | 1:00
Magbazar | 51 | 1:00 | Ashuganj | 26 | 23:00 | Barisal(N) | 41 | 21:00
Maniknagar | 78 | 21:00 | Daudkandi | 146 | 19:30 | Barisal (S) | 104 | 18:30
Bangabhaban | 6 | 1:00 | B.Baria | 159 | 21:00 | Patuakhali | 106 | 21:00
Narinda | 73 | 4:00 | Ramganj | 84 | 21:00 | Bhandaria | 50 | 19:00
Dhanmondi | 109 | 21:00 | Chaddagram | 47 | 22:00 | Borhan Uddin | 39 | 21:00
Lalbag | 53 | 22:00 | PHP | 10 | 16:00 | Ishurdi | 55 | 21:00
Madartek | 70 | 21:00 | Kochua | 61 | 21:00 | Ruppur Paromanobik | 3 | 9:00
Dhaka University | 19 | 11:00 | Madunaghat | 58 | 19:00 | Natore | 118 | 21:00
Aftabnagar | 9 | 20:00 | Hathazari | 89 | 21:00 | Bogra | 157 | 22:00
Fatullah | 56 | 1:00 | Khulshi | 194 | 18:30 | Noagaon | 116 | 21:00
Nawabganj | 48 | 21:00 | Halishahar | 126 | 18:30 | Rajshahi | 132 | 21:00
Mirpur | 91 | 19:00 | Baraulia | 153 | 1:00 | Rajshahi New | 13 | 21:00
Kalyanpur | 99 | 19:00 | Sikalbaha | 36 | 1:00 | C.Nawabganj | 76 | 22:00
Gulshan | 84 | 19:00 | Dohazari | 100 | 19:00 | Amnura | 55 | 21:00
Uttara | 72 | 19:00 | Cox'sbazar | 96 | 1:00 | Pabna | 84 | 21:00
Uttara New | 21 | 19:00 | Chandraghona | 28 | 18:30 | Shahjadpur | 81 | 22:00
Kamrangirchar | 72 | 21:00 | Kaptai | 4.2 | 19:00 | Serajganj | 72 | 19:00
Savar | 123 | 21:00 | A. Khaer Stl. | 10 | 6:00 | Niyamatpur | 70 | 22:00
Bhasantec | 128 | 21:00 | Bakulia | 92 | 22:00 | Joypurhat | 60 | 21:00
Agargaon | 58 | 21:00 | Julda | 21 | 18:30 | Sherpur(Bogura) | 52 | 3:00
Satmosjid | 46 | 21:00 | TK chemical | 28.5 | 19:00 | Mohastangor | 56 | 21:00
Tongi | 98 | 11:00 | Modern Steel | 0 | #N/A | Bangura | 35 | 19:30
Kabirpur | 175 | 3:00 | Shahmirpur | 25 | 1:00 | Rangpur | 114 | 19:30
Basundhara | 127 | 1:00 | Khagrachhari | 26 | 18:30 | Lalmonirhat | 41 | 19:00
Manikganj | 64 | 19:30 | Matarbari | 42 | 20:00 | Saidpur | 102 | 20:00
Joydevpur | 127 | 19:00 | Baroiar Hat | 44 | 18:30 | Purbasadipur | 93 | 19:30
New Tongi | 79 | 10:00 | Rangamati | 12 | 19:00 | Thakurgaon | 80 | 19:30
Kodda | 204 | 11:00 | Abul Khair 230 | 6 | 12:00 | Palashbari | 119 | 19:30
Dhamrai | 96 | 19:30 | BSRM | 146 | 23:00 | Barapukuria | 50 | 21:00
Rajendrapur | 90 | 1:00 | GPH Ispat | 88 | 0:00 | Panchagar | 48 | 19:30
Valuka | 96 | 1:00 | Goalpara | 25 | 21:00 | Joldhaka | 48 | 21:00
Tangail | 213 | 21:00 | Central s/s | 87 | 19:30 | Kurigram | 56 | 19:00
Mymensing | 194 | 21:00 | Noapara | 37 | 0.875 | Mithapukur | 34 | 19:30
Kishorganj | 124 | 19:00 | Jessore | 120 | 21:00
Netrokona | 116 | 21:00 | Benapol | 58/ | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 18:30 | 398 | 13:00 | Kaliakoir | 391 | 0.25 | 377 | 0.5
| Bheramara | 401 | 19:00 | 393 | 20:00 | Bhulta | 383 | 0.77083 | 367 | 0.5
| Ashuganj(N) | 390 | 18:30 | 375 | 12:00 | Gopalganj | 409 | 0.625 | 386 | 0.875
| Payra | 411 | 19:30 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 228 | 11:00 | Hathazari | 222 | 19:00 | 211 | 11:00
| Ishurdi | 234 | 6:00 | 225 | 15:00 | Megnaghat | 227 | 18:30 | 220 | 1:00
| Ashuganj | 232 | 18:30 | 224 | 15:00 | Fenchuganj | 239 | 18:00 | 234 | 23:00
| Serajganj | 230 | 6:00 | 225 | 2:00 | Siddhirganj | 229 | 18:30 | 220 | 4:00
| Baghabari | 230 | 4:00 | 227 | 3:00 | Maniknagar | 228 | 18:30 | 218 | 12:00
| Barapukuria | 233 | 6:00 | 221 | 12:00 | Agargaon | 227 | 7:00 | 214 | 12:00
| Bogra | 226 | 6:00 | 217 | 15:00 | Barisal | 249 | 22:00 | 233 | 14:00
| Rajshahi | 232 | 18:30 | 220 | 3:00 | Bhola 225 MW | 252 | 7:00 | 238 | 14:00
| Khulna South | 225 | 8:00 | 210 | 13:00 | AKSML | 223 | 22:00 | 212 | 6:00
| Rampura | 227 | 19:00 | 220 | 11:00 | BSRM | 226 | 19:00 | 214 | 5:00
| Haripur | 227 | 19:00 | 217 | 12:00 | Bibiyana | 240 | 18:30 | 233 | 10:00
| Hasnabad | 220 | 1:00 | 218 | 12:00 | Bhulta | 231 | 18:30 | 220 | 12:00
| Shyampur | 226 | 19:30 | 220 | 12:00 | Ashuganj (S) | 234 | 18:30 | 226 | 12:00
| Aminbazar | 224 | 1:00 | 215 | 2:00 | Kaliakoir | 230 | 18:30 | 217 | 12:00
| Tongi | 230 | 18:30 | 215 | 1:00 | GPH | 222 | 18:30 | 212 | 4:00
| Comilla (N) | 224 | 19:00 | 218 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 18:30 | 128 | 12:00 | Madanhat | 134 | 0.79167 | 129 | 0.20833
| Munsiganj | 136 | 19:00 | 126 | 12:00 | Hathazari | 131 | 0.79167 | 126 | 0.20833
| Sonargaon | 137 | 18:30 | 127 | 4:00 | Khulshi | 131 | 0.77083 | 126 | 0.16667
| Shyampur | 136 | 18:30 | 128 | 12:00 | Halishahar | 134 | 0.79167 | 127 | 0.25
| Bhulta | 130 | 19:00 | 123 | 1:00 | Baraulia | 131 | 0.125 | 126 | 0.41667
| Madanganj | 134 | 13:00 | 126 | 7:00 | Sikalbaha | 135 | 0.8125 | 127 | 0.25
| Shitalakhya | 140 | 19:00 | 127 | 12:00 | Dohazari | 128 | 0.58333 | 125 | 0.16667
| Rahim steal | 136 | 19:00 | 128 | 11:00 | Cox'sbazar | 119 | 0.29167 | 105 | 0.45833
| Matuail | 137 | 18:30 | 128 | 12:00 | Chandraghona | 132 | 0.8125 | 127 | 0.20833
| Ghorasal | 137 | 13:00 | 135 | 11:00 | Kaptai | 132 | 0.041667 | 128 | 0.29167
| Narsinghdi | 133 | 10:00 | 125 | 1:00 | A. Khaer Stl. | 130 | 0.29167 | 125 | 0.20833
| Haripur (SBU) | 137 | 18:30 | 128 | 12:00 | Bakulia | 133 | 0.77083 | 126 | 0.5
| Sreenagar |  |  |  |  | Julda | 136 | 0.79167 | 128 | 0.16667
| Ullon | 135 | 19:00 | 129 | 8:00 | TK Chemical | 133 | 0.79167 | 127 | 0.5
| Hasnabad | 135 | 19:00 | 128 | 11:00 | Modern Steel
| Magbazar | 135 | 19:00 | 129 | 12:00 | Shahmirpur | 134 | 0.79167 | 127 | 0.25
| Maniknagar | 136 | 18:30 | 131 | 4:00 | Khagrachhari | 130 | 0.77083 | 126 | 0.20833
| Bangabhaban | 136 | 18:30 | 131 | 4:00 | Matarbari | 123 | 0.66667 | 100 | 0.45833
| Narinda | 136 | 18:30 | 131 | 4:00 | Baroiar Hat | 129 | 0.77083 | 120 | 0.625
| Dhanmondi | 135 | 19:00 | 129 | 8:00 | Rangamati | 131 | 0.79167 | 126 | 0.16667
| Lalbag | 138 | 18:30 | 125 | 10:00 | Goalpara S/S | 136 | 22:00 | 125 | 15:00
| Madartek | 135 | 18:30 | 129 | 12:00 | Khulna Central S/S | 135 | 22:00 | 125 | 13:00
| Dhaka University | 135 | 2:00 | 129 | 12:00 | Noapara | 132 | 20:00 | 125 | 0.625
| Aftabnagar | 135 | 18:00 | 129 | 12:00 | Jessore | 128 | 7:00 | 118 | 0.58333
| Fatullah | 135 | 18:30 | 128 | 12:00 | Benapol | 129 | 6:00 | 117 | 0.625
| Nawabganj | 127 | 19:30 | 123 | 11:00 | Jhenida | 128 | 6:00 | 114 | 0.875
| Mirpur | 135 | 19:00 | 126 | 12:00 | Bottail | 132 | 0.25 | 124 | 0.875
| Kalyanpur | 137 | 19:00 | 127 | 12:00 | G.K Project | 138 | 6:00 | 134 | 0.083333
| Gulshan | 135 | 19:00 | 128 | 12:00 | Faridpur | 136 | 0.25 | 126 | 0.875
| Uttara | 136 | 19:00 | 126 | 12:00 | Madaripur | 141 | 0.25 | 131 | 0.875
| Uttara New | 135 | 19:00 | 126 | 12:00 | Shariyatpur S/S | 140 | 0.25 | 130 | 0.875
| Kamrangirchar | 137 | 19:00 | 128 | 12:00 | Gopalganj | 144 | 0.29167 | 132 | 0.83333
| Savar | 139 | 19:00 | 125 | 12:00 | Bagerhat | 132 | 22:00 | 120 | 0.625
| Bhasantec | 136 | 19:00 | 127 | 12:00 | Mongla | 131 | 0.77083 | 121 | 0.54167
| Agargaon | 136 | 19:00 | 127 | 12:00 | Satkhira | 134 | 6:00 | 124 | 0.54167
| Satmosjid | 136 | 19:00 | 128 | 12:00 | Gallamari | 136 | 8:00 | 128 | 0.54167
| Tongi | 140 | 18:30 | 131 | 11:00 | Magura | 127 | 7:00 | 112 | 21:00
| Kabirpur | 137 | 18:30 | 131 | 21:00 | Narail | 125 | 0.25 | 111 | 21:00
| Basundhara | 134 | 19:30 | 128 | 12:00 | Chuadanga | 123 | 7:00 | 104 | 0.875
| Manikganj | 140 | 18:30 | 132 | 21:00 | Borguna | 137 | 0.041667 | 129 | 0.54167
| Joydevpur | 139 | 19:00 | 130 | 22:00 | Barisal(N) | 140 | 6:00 | 130 | 0.58333
| New Tongi | 139 | 18:30 | 129 | 14:00 | Barisal (S) | 139 | 5:00 | 129 | 0.58333
| Kodda | 134 | 19:00 | 124 | 12:00 | Patuakhali(S) | 137 | 5:00 | 116 | 14:00
| Dhamrai | 134 | 19:00 | 129 | 21:00 | Bhandaria | 138 | 0.29167 | 127 | 0.54167
| Rajendrapur | 136 | 19:00 | 124 | 13:00 | Ishurdi | 136 | 0.25 | 130 | 0.125
| Valuka | 126 | 3:00 | 117 | 21:00 | Ruppur Paromanobik | 134 | 0.16667 | 132 | 0.875
| Tangail | 131 | 5:00 | 124 | 21:00 | Natore | 133 | 5:00 | 127 | 15:00
| Mymensing | 128 | 5:00 | 120 | 18:30 | Bogra | 133 | 5:00 | 127 | 15:00
| Kishorganj | 130 | 5:00 | 123 | 21:00 | Noagaon | 130 | 5:00 | 121 | 23:00
| Netrokona | 126 | 6:00 | 116 | 18:00 | Rajshahi | 133 | 19:00 | 127 | 14:00
| Jamalpur | 135 | 23:00 | 120 | 16:00 | Rajshahi New | 134 | 18:30 | 126 | 3:00
| Sherpur | 134 | 3:00 | 117 | 16:00 | C.Nawabganj | 132 | 19:00 | 124 | 14:00
| Srimongal | 136 | 10:00 | 133 | 21:00 | Amnura | 133 | 19:00 | 123 | 2:00
| Shahjibazar | 135 | 18:30 | 130 | 22:00 | Pabna | 135 | 6:00 | 130 | 3:00
| Fenchuganj | 136 | 6:00 | 132 | 22:00 | Shahjadpur | 137 | 18:30 | 134 | 10:00
| Khulawara | 134 | 5:00 | 132 | 14:00 | Serajganj | 133 | 5:00 | 128 | 12:00
| Sylhet | 133 | 3:00 | 128 | 14:00 | Niyamatpur | 129 | 5:00 | 118 | 21:00
| Chatak | 133 | 6:00 | 126 | 14:00 | Joypurhat | 130 | 5:00 | 120 | 17:00
| Sunamganj | 132 | 6:00 | 125 | 21:00 | Sherpur(Bogura) | 133 | 6:00 | 127 | 3:00
| Biani Bazar | 132 | 5:00 | 126 | 21:00 | Mohastangor | 132 | 5:00 | 125 | 15:00
| Comilla(s) | 127 | 16:00 | 120 | 1:00 | Bangura | 135 | 5:00 | 132 | 3:00
| Comilla(n) | 135 | 18:30 | 129 | 12:00 | Rangpur | 128 | 6:00 | 116 | 12:00
| Chandpur | 137 | 23:00 | 130 | 9:00 | Lalmonirhat | 128 | 4:00 | 117 | 12:00
| Feni | 130 | 18:30 | 121 | 12:00 | Saidpur | 130 | 5:00 | 116 | 12:00
| Chowmuhani | 130 | 19:00 | 122 | 12:00 | Purbasadipur | 128 | 5:00 | 115 | 12:00
| Ashuganj | 139 | 20:00 | 134 | 21:00 | Thakurgaon | 128 | 6:00 | 112 | 12:00
| Daudkandi | 133 | 18:30 | 126 | 2:00 | Palashbari | 131 | 6:00 | 120 | 17:00
| B.Baria | 134 | 8:00 | 128 | 21:00 | Barapukuria | 133 | 6:00 | 121 | 12:00
| Ramganj | 132 | 19:00 | 123 | 12:00 | Panchagar | 127 | 5:00 | 111 | 10:00
| Chaddagram | 133 | 18:30 | 123 | 12:00 | Joldhaka | 128 | 5:00 | 114 | 12:00
| PHP | 130 | 18:30 | 122 | 11:00 | Kurigram | 127 | 6:00 | 114 | 17:00
| Kochua | 134 | 19:00 | 128 | 11:00 | Mithapukur | 130 | 0.20833 | 118 | 0.5

## L-Curve
Date | 2021-04-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 208 | 7208 | 3596 | 10804 |  |  |  | QF-LDC-11
0:30 | 169 | 7332.5 | 3528 | 10860.5 | Date: | 2021-04-23
1:00 | 130 | 7457 | 3460 | 10917
1:30 | 112.5 | 7405 | 3379 | 10784
2:00 | 95 | 7353 | 3298 | 10651
2:30 | 77.5 | 7383 | 3338 | 10721 | [5 empty] | Gen. at Eve. Peak | 11853 | 11853 MW (21:00 )
3:00 | 60 | 7413 | 3378 | 10791 | [6 empty] | 21:00
3:30 | 164 | 7235 | 3301.5 | 10536.5 | [5 empty] | Gen. at Day Peak | 9072 | 9072 MW (12:00 )
4:00 | 268 | 7057 | 3225 | 10282 | [6 empty] | 12:00
4:30 | 253 | 6793.5 | 3006 | 9799.5 | [5 empty] | Highest Generation | 11853
5:00 | 238 | 6530 | 2787 | 9317 | [6 empty] | 21:00
5:30 | 265.5 | 6241.5 | 2692 | 8933.5
6:00 | 293 | 5953 | 2597 | 8550
6:30 | 276.5 | 5856.5 | 2574.5 | 8431
7:00 | 260 | 5760 | 2552 | 8312
7:30 | 251 | 5747 | 2547.5 | 8294.5
8:00 | 242 | 5734 | 2543 | 8277
8:30 | 211 | 5870.5 | 2545 | 8415.5
9:00 | 180 | 6007 | 2547 | 8554
9:30 | 161 | 6025 | 2549.5 | 8574.5
10:00 | 142 | 6043 | 2552 | 8595
10:30 | 136 | 6096 | 2576.5 | 8672.5
11:00 | 130 | 6149 | 2601 | 8750
11:30 | 172 | 6201.5 | 2709.5 | 8911
12:00 | 214 | 6254 | 2818 | 9072
12:30 | 197 | 6349 | 2957 | 9306
13:00 | 180 | 6444 | 3096 | 9540
13:30 | 175 | 6444.5 | 3124 | 9568.5
14:00 | 170 | 6445 | 3152 | 9597
14:30 | 211 | 6525.5 | 3204 | 9729.5
15:00 | 252 | 6606 | 3256 | 9862
15:30 | 226.5 | 6541.5 | 3203.5 | 9745
16:00 | 201 | 6477 | 3151 | 9628
16:30 | 190.5 | 6377.5 | 3128.5 | 9506
17:00 | 180 | 6278 | 3106 | 9384
17:30 | 129 | 6345.5 | 3068 | 9413.5
18:00 | 78 | 6413 | 3030 | 9443
18:30 | 59 | 6923.5 | 3324.5 | 10248
19:00 | 40 | 7434 | 3619 | 11053
19:30 | 34 | 7676 | 3934 | 11610
20:00 | 242 | 7537 | 4057 | 11594 |  |  |  | Executive Engineer
20:30 | 265 | 7567 | 4156.5 | 11723.5 |  |  |  | Network Operation Division
21:00 | 288 | 7597 | 4256 | 11853
21:30 | 308 | 7511 | 4246.5 | 11757.5
22:00 | 328 | 7425 | 4237 | 11662 |  |  |  |  | Page 6 of 7
22:30 | 287.5 | 7400.5 | 4055 | 11455.5
23:00 | 247 | 7376 | 3873 | 11249
23:30 | 227.5 | 7292 | 3734.5 | 11026.5
24:00 | 208 | 7208 | 3596 | 10804
11853 MW (21:00 )
9072 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-23 |  | Energy | 348919791
[11 empty] | 2021-04-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4784 | 843 | 1983 | 2466 | 781 | 35 | 79 | 0 | 154 | 0
0:30 | 4710.5 | 843 | 1972.5 | 2470.5 | 768.5 | 35 | 77.5 | 0 | 143.5 | 0 | Date: | 2021-04-23
1:00 | 4637 | 843 | 1962 | 2475 | 756 | 35 | 76 | 0 | 133 | 0
1:30 | 4687 | 843.5 | 1924.5 | 2335 | 755.5 | 35 | 71 | 0 | 132.5 | 0 | [7 empty] | Total Energy | 348.9198 | Total Energy Gen 348.920 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 348.920 MKWHr
2:00 | 4737 | 844 | 1887 | 2195 | 755 | 35 | 66 | 0 | 132 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4773 | 844 | 1946 | 2169.5 | 755.5 | 35 | 66 | 0 | 132 | 0 | [7 empty] | Energy Requirement | 348.9198
3:00 | 4809 | 844 | 2005 | 2144 | 756 | 35 | 66 | 0 | 132 | 0
3:30 | 4719.5 | 844 | 1946 | 2028 | 766 | 35 | 66 | 0 | 132 | 0 | [6 empty] | Shortage
4:00 | 4630 | 844 | 1887 | 1912 | 776 | 35 | 66 | 0 | 132 | 0
4:30 | 4514.5 | 844 | 1871 | 1639.5 | 700.5 | 35 | 66 | 0 | 129 | 0
5:00 | 4399 | 844 | 1855 | 1367 | 625 | 35 | 66 | 0 | 126 | 0
5:30 | 4302 | 844 | 1772.5 | 1186 | 625 | 35 | 49 | 0 | 118 | 2
6:00 | 4205 | 844 | 1690 | 1005 | 625 | 35 | 32 | 0 | 110 | 4
6:30 | 4170 | 843.5 | 1671 | 959.5 | 600 | 35 | 32 | 0 | 105 | 15 |  |  |  |  | Coal
7:00 | 4135 | 843 | 1652 | 914 | 575 | 35 | 32 | 0 | 100 | 26
7:30 | 4130.5 | 843 | 1613.5 | 926 | 575 | 35 | 32 | 0 | 99 | 40.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4126 | 843 | 1575 | 938 | 575 | 35 | 32 | 0 | 98 | 55
8:30 | 4184 | 843 | 1631 | 942 | 575.5 | 35 | 32 | 0 | 98 | 75
9:00 | 4242 | 843 | 1687 | 946 | 576 | 35 | 32 | 0 | 98 | 95
9:30 | 4238.5 | 843 | 1685.5 | 966.5 | 576 | 35 | 37 | 0 | 98 | 95
10:00 | 4235 | 843 | 1684 | 987 | 576 | 35 | 42 | 0 | 98 | 95
10:30 | 4254.5 | 843 | 1715 | 1000 | 575.5 | 35 | 46.5 | 0 | 102.5 | 100.5
11:00 | 4274 | 843 | 1746 | 1013 | 575 | 35 | 51 | 0 | 107 | 106
11:30 | 4310 | 842.5 | 1835.5 | 1053 | 580.5 | 35 | 50 | 0 | 107.5 | 97
12:00 | 4346 | 842 | 1925 | 1093 | 586 | 35 | 49 | 0 | 108 | 88
12:30 | 4410 | 842.5 | 1935.5 | 1207 | 610.5 | 35 | 50.5 | 0 | 116 | 99
13:00 | 4474 | 843 | 1946 | 1321 | 635 | 35 | 52 | 0 | 124 | 110
13:30 | 4474 | 843 | 1946 | 1321 | 635 | 35 | 52 | 0 | 124 | 110
14:00 | 4474 | 843 | 1946 | 1321 | 635 | 35 | 52 | 0 | 124 | 110
14:30 | 4526 | 843 | 1946.5 | 1438.5 | 649.5 | 35 | 47.5 | 0 | 124 | 91
15:00 | 4578 | 843 | 1947 | 1556 | 664 | 35 | 43 | 0 | 124 | 72
15:30 | 4548.5 | 843 | 1888.5 | 1549.5 | 663 | 35 | 44.5 | 0 | 118 | 55
16:00 | 4519 | 843 | 1830 | 1543 | 662 | 35 | 46 | 0 | 112 | 38
16:30 | 4433 | 843 | 1747 | 1590 | 661.5 | 35 | 47 | 0 | 121 | 28.5
17:00 | 4347 | 843 | 1664 | 1637 | 661 | 35 | 48 | 0 | 130 | 19
17:30 | 4348 | 843 | 1612.5 | 1697.5 | 642 | 35 | 83.5 | 0 | 141 | 11
18:00 | 4349 | 843 | 1561 | 1758 | 623 | 35 | 119 | 0 | 152 | 3
18:30 | 4252.5 | 843 | 1676.5 | 2443 | 633.5 | 35 | 208 | 0 | 155 | 1.5
19:00 | 4156 | 843 | 1792 | 3128 | 644 | 35 | 297 | 0 | 158 | 0
19:30 | 4337 | 842 | 1904 | 3324 | 714 | 35 | 296 | 0 | 158 | 0
20:00 | 4596 | 843 | 1960 | 3004 | 723 | 35 | 275 | 0 | 158 | 0
20:30 | 4774 | 842.5 | 1983 | 2903.5 | 753 | 35 | 270.5 | 0 | 162 | 0
21:00 | 4952 | 842 | 2006 | 2803 | 783 | 35 | 266 | 0 | 166 | 0
21:30 | 4864.5 | 842.5 | 1993.5 | 2800 | 793 | 35 | 264 | 0 | 165 | 0
22:00 | 4777 | 843 | 1981 | 2797 | 803 | 35 | 262 | 0 | 164 | 0
22:30 | 4791.5 | 843 | 1982.5 | 2631.5 | 792 | 35 | 219 | 0 | 161 | 0
23:00 | 4806 | 843 | 1984 | 2466 | 781 | 35 | 176 | 0 | 158 | 0
23:30 | 4795 | 843 | 1983.5 | 2466 | 781 | 35 | 127.5 | 0 | 156 | 0 | Max Temp. in Dhaka |  | 34.9° C
24:00 | 4784 | 843 | 1983 | 2466 | 781 | 35 | 79 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 348.920 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 348.920 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | [6 empty] | 9 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 297556
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 10 | 12 | 6 | 14 | 16 | 16 | 15 | 12 | 7 | 3 | 0 | [8 empty] | 99900
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 203 | 204 | 213 | 203 | 203 | 204 | 203 | 203 | 214 | 215 | 217 | 203 | 215 | 204 | 204 | 204 | 205 |  | 202 | 203 | 204 | 217 | 203 | 203 | 203 | 4928286
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 90 | 90 |  | 90 | 130 | 130 | 130 | 130 | 130 | 130 | 3072054
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 66 | 66 | 66 | 66 | 66 | 32 | 32 | 32 | 32 | 42 | 51 | 49 | 52 | 43 | 43 | 46 | 48 | 66 |  | 66 | 66 | 62 | 54 | 49 | 49 | 49 | 1217779
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 51 | 51 | 51 | 17 | 17 | 17 | 44 | 51 | 51 | 67 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2017309
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 100 | 150 | 75 | 40 | 40 | 40 | 37 | 87 | 90 | 90 | 90 | 150 | 120 | 153 | 142 | 120 | 120 |  | 64 | 68 | 120 | 140 | 140 | 140 | 140 | 2673000
17 | Siddhirganj 335 MW CCPP | 222 | 222 | 222 | 180 | 180 | 180 | 180 | 160 | 220 | 218 | 217 | 214 | 218 | 160 | 212 | 212 | 213 | 215 |  | 150 | 180 | 180 | 218 | 223 | 220 | 220 | 4819129
18 | Kodda 300 MW PP Unit-2 (Summit) | [16 empty] | 10 | 31 |  | 134 | 30 |  |  |  |  | 0 | 243382
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 120 | 120 | 120 | 120 | 2095832
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 594504
33 | Ashuganj 225 MW CCPP | 212 | 212 | 213 | 215 | 216 | 217 | 217 | 216 | 217 | 198 | 197 | 204 | 183 | 194 | 188 | 182 | 183 | 188 |  | 182 | 182 | 185 | 196 | 181 | 186 | 184 | 4821000
34 | Ashuganj 450 MW CCPP(South) | 285 | 300 | 300 | 310 | 285 | 260 | 260 | 260 | 260 | 260 | 295 | 300 | 300 | 320 | 305 | 290 | 290 | 305 |  | 260 | 260 | 295 | 320 | 295 | 300 | 295 | 7055000
| Ashuganj 450 MW CCPP(North) | 265 | 280 | 275 | 285 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 295 | 280 | 300 | 305 | 295 | 295 | 300 |  | 275 | 275 | 290 | 315 | 290 | 295 | 290 | 7110100
35 | Ashuganj 55 MW PP (Precision) | 49 | 48 | 48 | 48 | 48 | 48 | 47 | 46 | 48 | 48 | 48 | 45 | 50 | 51 | 52 | 52 | 20 | 20 |  | 20 | 52 | 51 | 53 | 55 | 55 | 55 | 1128960
36 | Chandpur 150 MW CCPP | 94 | 95 | 95 | 95 | 95 | 95 | 96 | 95 | 95 | 95 | 95 | 95 | 94 | 95 | 97 | 94 | 95 | 95 |  | 92 | 92 | 97 | 96 | 95 | 95 | 95 | 2258850
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6561000
41 | Haripur 360MW CCPP(HPL) | 341 | 350 | 350 | 350 | 353 | 301 | 301 | 270 | 344 | 344 | 343 | 340 | 343 | 322 | 339 | 342 | 302 | 281 |  | 282 | 346 | 344 | 344 | 344 | 344 | 351 | 7924000
42 | RPCL 210MW CCPP | 185 | 188 | 196 | 196 | 201 | 207 | 206 | 208 | 205 | 203 | 197 | 196 | 198 | 196 | 195 | 198 | 198 | 197 |  | 203 | 204 | 203 | 204 | 204 | 206 | 208 | 4690320
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 13 | 29 | 47 | 57 | 57 | 33 | 45 | 33 | 33 | 12 | 7 | 1 | [8 empty] | 383430
44 | Fenchugonj CCPP Phase-1 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 |  | 41 | 40 | 40 | 40 | 40 | 0 |  | 878000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025520
46 | Shajibazar 330 MW CCPP | 335 | 335 | 332 | 333 | 331 | 334 | 332 | 334 | 331 | 333 | 333 | 328 | 330 | 329 | 331 | 333 | 332 | 334 |  | 334 | 336 | 334 | 334 | 333 | 334 | 334 | 7641000
47 | Shahjibazar GTPP Unit- 8 & 9 | 5 | 52 | 52 | 52 | 53 | 53 | 53 | 52 | 51 | 51 | 51 | 30 | 31 | 30 | 30 | 31 | 31 | 31 |  | 33 | 33 | 32 | 32 | 33 | 68 | 69 | 1044000
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 75 | 30 | 30 | 30 | 30 | 30 | 78 | 77 | 77 | 74 | 30 | 30 | 30 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1505280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 203 | 203 | 203 | 176 | 149 | 73 | [8 empty] | 30 | 80 | 80 | 80 |  | 120 | 140 | 145 | 145 | 145 | 145 | 145 | 2107750
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 400000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 201420
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 53 | 53 | 53 | 53 | 53 | 14 | 14 |  | 49 | 50 | 53 | 53 | 53 | 53 | 53 | 1170600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 |  | 14 | 14 | 16 | 16 | 16 | 16 | 16 | 363744
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 310 | 315 | 300 | 305 | 290 | 300 | 290 | 310 | 305 | 310 | 315 | 315 | 280 | 315 | 280 | 280 | 295 |  | 290 | 280 | 290 | 320 | 300 | 295 | 290 | 7373000
| Bibiyana South 400 MW | 386 | 400 | 400 | 400 | 370 | 370 | 370 | 384 | 398 | 397 | 395 | 392 | 370 | 394 | 394 | 370 | 340 | 370 |  | 340 | 340 | 400 | 400 | 370 | 400 | 400 | 9283000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 23 | 17 | 17 | 53 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 809559
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | [7 empty] | 4 | 10 | 15 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 384240
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 |  | 20 | 22 | 22 | 21 | 21 | 21 | 21 | 492144
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 403200
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 405468
63 | Impoprt (Tripura) | 133 | 132 | 132 | 132 | 126 | 110 | 100 | 98 | 98 | 98 | 107 | 108 | 124 | 124 | 124 | 112 | 130 | 152 |  | 158 | 158 | 158 | 166 | 164 | 158 | 154 | 3081600
64 | Malancha, Ctg. EPZ (United) | 36 | 36 | 38 | 39 | 39 | 40 | 36 | 28 | 23 | 30 | 24 | 27 | 28 | 28 | 31 | 38 | 40 | 40 |  | 40 | 40 | 40 | 40 | 42 | 42 | 42 | 862560
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 10 | 19 | 19 | 19 |  |  |  |  | 9 | 22 | 22 | 22 | 22 | 22 | 22 | 370476
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 221580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 513130
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 0 | 29 | 29 | 25 | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 15 | 15 | 15 | 15 |  | 15 | 15 | 28 | 29 | 29 | 30 | 30 | 519120
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 803400
73 | Ghorashal 108MW PP (Regent) | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 100 | 100 | 99 | 103 | 102 | 97 | 98 | 52 | 52 |  | 103 | 103 | 103 | 103 | 103 | 103 | 103 | 2315681
| Feni Lanka Power | [17 empty] | 8 |  | 34 | 10 |  |  |  |  | 0 | 36480
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | [8 empty] | 7 | 8 | 8 | 25 | 25 | 25 |  | 84 | 113 | 113 | 113 | 113 | 113 | 113 | 1360800
| Manikgonj 162MW PP(MPGL) | 162 | 54 | 54 | [12 empty] | 16 | 17 | 25 |  | 131 | 162 | 35 | 35 | 35 | 35 | 17 | 839520
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 50 | 50 | 50 | 7 | 7 | [7 empty] | 7 | 7 | 24 | 32 | 32 |  | 65 | 100 | 100 | 16 | 7 | 7 | 7 | 624960
78 | Gazipur 52 MW PP | [19 empty] | 8 | [5 empty] | 0 | 9120
79 | Kodda 150MW PP | 10 | [16 empty] | 25 |  | 64 | 16 |  |  |  |  | 0 | 101770
80 | Jamalpur 95 MW PP(Powerpac) | 74 | 74 | 74 | 74 | 74 | 66 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 71 | 66 | 74 | 73 |  | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 1712640
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 |  |  |  | 1 | 10 | 24 | 30 | 40 | 25 | 25 |  | 37 | 52 | 52 | 52 | 52 | 52 | 52 | 774288
| Gazipur 100 MW PP | 70 | 50 | 70 | 50 | 50 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 65 | 105 | 34 | 34 | 34 | 34 | 17 | 902400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 5 | 5 | 4 | 4 | 1 | 2 | 0 | [9 empty] | 33479
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1298599
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 245 | 245 | 230 | 245 | 230 | 230 | 230 | 255 | 270 | 270 | 275 | 275 | 260 | 275 | 270 | 240 | 265 | 265 |  | 240 | 222 | 225 | 225 | 220 | 225 | 225 | 5898705
87 | Meghnaghat 100 MW(IEL) | 100 | 65 | 50 | 35 | [12 empty] | 3 | 25 |  | 71 | 88 | 65 | 7 | 7 | 7 | 7 | 469440
| Meghnaghat 104 MW PP (OPCL) | 75 | 80 | 53 | 48 | [11 empty] | 12 | 17 | 20 |  | 70 | 90 | 85 | 53 | 53 | 53 | 47 | 688320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 92 | 80 | 80 | 90 | 90 | 90 | 90 | 90 | 90 | 92 | 80 | 80 | 92 | 92 | 92 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 88 | 90 | 2062200
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland)
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 7 | 7 | [12 empty] | 10 | 24 | 24 |  | 102 | 48 | 16 | 16 | 16 | 7 | 7 | 273456
95 | Patenga 50MW PP (Baraka) | [17 empty] | 7 |  | 22 | 40 | 18 |  |  |  | 0 | 64320
96 | Chattogram 108 MW PP (ECPV) | 24 | [16 empty] | 25 |  | 34 | 44 | 45 | 45 | 45 | 45 | 24 | 289920
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 44 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1251807
100 | Manikganj 55 MW PP (Northern) | [17 empty] | 17 |  | 35 | 17 |  |  |  |  | 0 | 45614
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 163 | 130 | 130 | 130 | 130 | 110 | 130 | 130 | 130 | 163 | 163 | 110 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3535936
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 1 | [9 empty] | 15350
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 857160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 50 | 16 | 41 | 32 | [12 empty] | 8 | 15 |  | 96 | 150 | 150 | 150 | 150 | 120 | 60 | 1051200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 147 | 143 | 149 | 149 | 149 | 149 | 149 | 149 | 130 | 130 | 130 | 130 | 130 | 131 | 148 | 149 | 128 |  | 130 | 149 | 149 | 149 | 149 | 149 | 149 | 3445920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 70 | 40 | 20 | 20 | 36 | 50 | 50 | 50 | 100 | 90 | 50 | 50 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1722240
116 | Chandpur 200MW (Desh energy) | 165 | 165 | 162 | 173 | 173 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 100 | 137 | 175 | 175 | 175 | 175 |  | 175 | 175 | 176 | 176 | 176 | 176 | 176 | 3514080
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 367 | 376 | 375 | 381 | 366 | 365 | 365 | 367 | 367 | 396 | 399 | 400 | 368 | 343 | 338 | 331 | 331 | 333 |  | 331 | 332 | 348 | 396 | 366 | 370 | 366 | 8808000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 75 | 45 | 24 | 24 | 24 | 43 | 55 | 96 | 115 | 115 | 115 | 75 | 75 | 75 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2209200
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 50 | 50 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 50 | 50 | 50 | 20 | 20 | 20 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1394880
| Anlima Energy Ltd. | 17 | 17 | 17 | [9 empty] | 2 | 35 | 17 | 17 | 17 | 20 |  | 80 | 90 | 90 | 90 | 90 | 53 | 0 | 647345
| Bhairob 54.5 MW | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 30 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 37 | 37 | 37 | 877320
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 11 | 27 | 20 | 21 | 25 | 35 | 29 | 18 | 12 | 4 | 1 | [8 empty] | 214643
120 | Eastern Zone Total | 7457 | 7353 | 7413 | 7057 | 6530 | 5953 | 5760 | 5734 | 6007 | 6043 | 6149 | 6254 | 6444 | 6445 | 6606 | 6477 | 6278 | 6413 |  | 7434 | 7676 | 7537 | 7597 | 7425 | 7376 | 7208 | 163132029
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 19 | [6 empty] | 16 | 49 | 66 | 50 | 49 | 83 | 83 |  | 83 | 83 | 99 | 99 | 99 | 99 | 99 | 1371840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 17 | 17 | [11 empty] | 2 | 17 | 17 | 17 |  | 70 | 90 | 90 | 92 | 92 | 92 | 92 | 714240
130
131
132 | United Payra Power Ltd. | [14 empty] | 4 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  | 0 | 147600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 96 | 84 | 64 | 48 | [10 empty] | 16 | 16 | 32 | 48 |  | 110 | 110 | 110 | 110 | 110 | 96 | 64 | 1040640
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 97 | 96 | 96 | 96 | 97 | 95 | 95 | 95 | 96 | 93 | 95 | 96 | 95 | 97 | 65 | 42 |  | 98 | 98 | 97 | 96 | 96 | 97 | 97 | 2223415
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 55 | 60 | 60 | 52 | 57 | 60 |  | 50 | 50 | 60 | 60 | 60 | 60 | 60 | 1409000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 30 | 29 | 25 | 22 | 21 | 17 | 18 | 17 | 14 | 19 | 21 | 21 | 23 | 19 | 20 | 22 |  | 29 | 29 | 26 | 34 | 33 | 33 | 32 | 590316
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 10 | 40 | 35 | 63 | 70 |  | 0 | 243840
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 8 | 32 | 32 | 32 | 32 | 33 | 0 | 168750
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 843 | 844 | 844 | 844 | 844 | 844 | 843 | 843 | 843 | 843 | 843 | 842 | 843 | 842 | 843 | 843 | 843 | 843 |  | 843 | 842 | 843 | 842 | 843 | 843 | 843 | 20370182
147 | Bheramara 410 MW CCPP | 350 | 375 | 370 | 375 | 300 | 260 | 260 | 260 | 260 | 260 | 260 | 300 | 355 | 385 | 365 | 350 | 330 | 300 |  | 280 | 330 | 360 | 390 | 350 | 360 | 355 | 8175744
148 | Payra 1320 MW | 530 | 530 | 530 | 550 | 400 | 400 | 350 | 350 | 350 | 350 | 350 | 360 | 410 | 440 | 440 | 440 | 440 | 400 |  | 420 | 490 | 500 | 560 | 580 | 560 | 560 | 118086000
149
150 | Barapukuria TPP Unit-1 | 76 | 75 | 76 | 76 | 76 | 76 | 76 | 75 | 76 | 76 | 75 | 76 | 75 | 76 | 74 | 72 | 71 | 73 |  | 74 | 74 | 73 | 73 | 73 | 71 | 71 | 1776436
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3674100
153 | Baghabari 71 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1200000
156 | Baghabari 100 MW GTPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1203000
| Baghabari 50 MW Peaking PP | [17 empty] | 5 |  | 50 | 50 | 50 | 50 | 50 |  |  | 221839
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 114 | 106 | 112 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 100 | 125 | 143 | 100 | 80 |  | 80 | 90 | 100 | 130 | 144 | 136 | 130 | 2465800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 180 | 157 | 167 | 156 | 161 | 130 | 133 | 130 | 130 | 135 | 146 | 146 | 176 | 173 | 184 | 185 | 161 | 146 |  | 160 | 160 | 163 | 199 | 192 | 184 | 185 | 4110027
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 167 | 159 | 169 | 158 | 161 | 130 | 130 | 130 | 130 | 130 | 130 | 153 | 189 | 175 | 170 | 154 | 154 | 157 |  | 158 | 158 | 161 | 201 | 195 | 185 | 186 | 4151227
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 332 | 414 | 345 | 309 | 243 | 245 | 245 | 245 | 245 | 286 | 379 | 384 | 344 | 393 | 346 | 364 | 339 |  | 322 | 347 | 397 | 404 | 396 | 403 | 401 | 8265800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 19 | 18 | 18 | 16 | 16 | 16 | 18 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 466800
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 161766
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 42 | 18 | 12 | 12 | 12 | 12 | 0 | 86030
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 16 | 16 | 8 |  |  |  |  | 20925
167 | Katakhali 50 MW Peaking PP | [19 empty] | 30 | 31 | 31 | 30 | 30 | 30 | 30 | 156134
168 | Santahar 50 MW Peaking PP | [17 empty] | 7 |  | 30 | 33 | 32 | 32 | 33 |  |  | 134378
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | [8 empty] | 8 | 8 | 37 | 25 | 25 | 25 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 644160
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 16 |  | 57 | 100 | 100 | 100 | 100 | 97 | 0 | 484456
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [17 empty] | 4 |  | 58 | 90 | 101 | 113 | 113 | 35 | 0 | 508032
172 | Confidence Power Bogura Unit-1 113 MW | [17 empty] | 20 |  | 90 | 109 | 113 | 70 | 70 |  | 0 | 376416
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 34 | 75 | 88 | 98 | 50 | 50 | 50 |  | 100 | 113 | 113 | 113 | 113 | 113 | 57 | 1079040
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 6 | 7 | 7 | 8 | 7 | 6 | 5 | 4 | 1 | [8 empty] | 59829
178
178