## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-27 | Tuesday
|  |  | Date (day): | 2021-04-27 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14369.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15300 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-26 | 2021-04-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 102 | 100 | 102
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Dust in the gas line
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 335 | 301 | 345 | 345
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 290 | 290 | 300 | 300 | 150 |  | Dust in the gas line
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 100 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 248 | 245 | 250 | 250 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Project work
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 175 | 185 | 150 | 180
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 94 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 201 | 215 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 140 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 49 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 50 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 193 | 75 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 300 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Project work
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 138 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 80 | 85 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 88 | 89 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2792 | 3435 | 3128 | 3555 | 721 | 1403
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 80 | 80 | 80 | 100 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 16 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 43 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 208 | 205 | 205
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 105 | 120 | 120
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 32 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 20 | 20 | 20 | 80 |  | Fuel shortage
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 25
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 90 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 80 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 35 | 90 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 946 | 1142 | 1575 | 1565 | 555 | 210
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 100 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 90 | 100 | 100 | 34 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 184 | 194 | 225 | 225 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 330 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 310 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 40 | 52 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 19 | 43 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 40 | 100 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 94 | 96 | 95 | 96 | 67 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 154 | 158 | 158 | 158 |  | 42 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 160 | 156 | 171
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 185 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 38 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 34 | 35 | 35 | 35 |  | 19 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1686 | 2136 | 2131 | 2347 | 552 | 88
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 174 | 165 | 170 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 73 | 73 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 131 | 200 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 95 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 51 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 569 | 595 | 652.6 | 601 | 32 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 42 | 42 | 42 |  | 48 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 265 | 272 | 275 | 275
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 49 | 64 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 76 | 76 | 76 |  | 10 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 225 | 218 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 14 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 315 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 368 | 377 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 9 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 380 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1951 | 2014 | 2094 | 2094 | 0 | 237
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 725 | 724 | 737 | 737
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 66 | 83 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 6 | 18 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 8 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 340 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 8 | 32 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 71 | 91 | 90 | 91 |  | 14 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | SWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1244 | 1386 | 1588 | 1876 | 0 | 120
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 61 | 67 | 66 | 67 |  | 127 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 96 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 590 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 109 | 110 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 89 | 80 | 90
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 720 | 986 | 1115 | 1127 | 0 | 127
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 41 | 40 | 45
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 42 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 27 | 30 | 30 | 30 |  | 20 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 117 | 129 | 144 | 144
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 178 | 171 | 180 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 185 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 399 | 415 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 19 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 200 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 108 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 1257 | 1745 | 1740 | 1797 | 171 | 35
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 75 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 343 | 338 | 346 | 338 | 124 | 125
|  | Total |  |  |  |  | 21967 | 21219 | 11508 | 13777 | 14369.6 | 15300 | 2155 | 2366
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10913.2627 | 13065 | 13626.9742 | 14509.2908
| A. |  | 2021-04-26 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13777 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9950 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13777 | MW
| 3 | Day peak Generation : |  |  | 11508 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13065 | MW
| 4 | Evening peak Generation : |  |  | 13777 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 289.7751 | MKWHr | By Solar | 0.80293 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 159.6378 | MKWHr |  | By Oil: | 87.7178 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.8378 | MKWHr |  | By Hydro: | 0.848 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2155 | MW | Dhaka | 4451 | 4451 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2366 | MW | Chittagong | 1380 | 1380 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4521 | MW | Khulna | 1621 | 1621 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1300.5 | MMCFD |  |  | Rajshahi | 1453 | 1453 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 174253070.336 | ii) Oil : | Taka | 701286144.97 | Comilla | 1318 | 1318 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 93799683.08 | Total | Taka | 969338898.386 | Mymensingh | 1103 | 1103 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.9505 | MKWHr. | Sylhet | 535 | 535 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -160 | MW (E to W) at | 21:00 | hrs | Barisal | 406 | 406 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -290 | MW at | 24:00 | hrs | Rangpur | 798 | 798 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 39.4° C |  |  | Total | 13065 | 13065 |  | 0
| B. |  | 2021-04-27 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 41.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13950 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15300 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11700 | MW
| 4 | Reserve(Generation end) |  |  |  | 1350 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 293.4138 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10354 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.5055 | MKWHr. | ii) HVDC Flow at Peak Time |  | 724 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.4253 | MKWHr. | iii) Maximum HVDC Flow : |  | 725 | MW at | 3:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.86 |  | (b) Today: | 77.51 |  | (c) Rule Curve: |  | 82.8
.

## YesterdayGen
2021-04-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 346 |  | 0 | 290 | 235 | 100 | 0 | 55 | 218 | 0 | 150 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 19 | 25 | 24 | 33 | 33 | 51 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 66 | 92 | 90 | 50 | 21 | 29 | 135 | 0 | 0 | 300 | 300 | 173 | 45 | 93 | 26 | 40 | 0 | 0 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 150 | 188 | 70 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 268 | 67 | 77 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 11 | 100 | 0 | 0 | 0 | 199 | 0 | 139 | 0 | 100 | 158 | 1 | 366 | 108 | 102 | 105 | 0 | 0 | 54 | 0 | 114 | 113 | 100 | 370 | 90 | 0 | 162 | 111 | 0 | 36 | 0 |  | 724 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 19 | 0 | 32 | 67 | 34 | 96 | 0 | 0 | 65 | 50 | 35 | 98 | 12 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 145 | 0 | 189 | 0 | 96 | 100 | 42 | 0 | 417 | 92 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 8590 | 4016 | 12606 | 4591 | 724 | 2031 | 3744 | 803 | 35 | 528 | 150 | 0 | 0 | 77.91
2:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 344 |  | 0 | 290 | 240 | 100 | 0 | 55 | 220 | 0 | 150 | 70 | 102 | 64 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 19 | 25 | 24 | 33 | 33 | 51 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 66 | 92 | 84 | 0 | 21 | 29 | 135 | 0 | 0 | 300 | 300 | 170 | 45 | 95 | 26 | 40 | 0 | 0 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 146 | 200 | 73 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 268 | 67 | 77 | 0 | 225 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 138 | 0 | 100 | 158 | 1 | 365 | 108 | 102 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 370 | 90 | 0 | 162 | 111 | 0 | 36 | 0 |  | 724 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 19 | 0 | 32 | 67 | 34 | 96 | 0 | 0 | 65 | 50 | 35 | 98 | 0 | 0 | 30 | 44 | 32 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 146 | 0 | 186 | 0 | 96 | 0 | 79 | 0 | 412 | 92 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 8193 | 3926 | 12119 | 4646 | 724 | 2014 | 3309 | 803 | 35 | 442 | 146 | 0 | 0 | 77.9
3:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 346 |  | 0 | 290 | 240 | 100 | 0 | 55 | 220 | 0 | 150 | 70 | 102 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 24 | 33 | 33 | 32 | 0 | 0 | 35 | 0 | 0 | 17 | 214 | 0 | 120 | 0 |  | 23 | 0 | 66 | 92 | 55 | 0 | 21 | 36 | 100 | 0 | 0 | 315 | 315 | 181 | 45 | 95 | 26 | 40 | 0 | 0 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 142 | 194 | 73 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 271 | 68 | 78 | 0 | 225 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 133 | 0 | 100 | 158 | 1 | 379 | 108 | 102 | 105 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 377 | 90 | 0 | 162 | 111 | 0 | 36 | 0 |  | 725 | 0 | 380 | 0 | 83 | 0 | 0 | 0 | 19 | 0 | 32 | 67 | 34 | 96 | 0 | 0 | 65 | 50 | 0 | 98 | 0 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 145 | 0 | 194 | 0 | 96 | 0 | 165 | 0 | 421 | 92 | 0 | 95 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 0 |  | 8156 | 4033 | 12189 | 4805 | 725 | 2043 | 3244 | 804 | 35 | 391 | 142 | 0 | 0 | 77.89
4:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 347 |  | 0 | 290 | 245 | 100 | 0 | 55 | 222 | 0 | 145 | 70 | 102 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 22 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 23 | 0 | 66 | 92 | 50 | 0 | 21 | 34 | 100 | 0 | 0 | 300 | 300 | 209 | 45 | 95 | 26 | 40 | 0 | 0 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 142 | 199 | 73 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 268 | 68 | 78 | 0 | 225 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 131 | 0 | 100 | 158 | 0 | 370 | 109 | 85 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 369 | 90 | 0 | 162 | 111 | 0 | 36 | 0 |  | 725 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 67 | 34 | 64 | 0 | 0 | 65 | 50 | 0 | 98 | 0 | 0 | 12 | 52 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 147 | 0 | 188 | 0 | 96 | 0 | 181 | 0 | 415 | 92 | 0 | 95 | 0 | 113 | 0 | 0 | 50 | 580 | 0 | 0 | 0 |  | 7867 | 3820 | 11687 | 4758 | 725 | 2026 | 2969 | 803 | 35 | 229 | 142 | 0 | 0 | 77.88
5:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 348 |  | 0 | 290 | 245 | 60 | 0 | 55 | 222 | 0 | 150 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 92 | 0 | 0 | 21 | 38 | 100 | 0 | 0 | 310 | 310 | 213 | 45 | 94 | 23 | 40 | 0 | 1 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 130 | 202 | 73 | 19 | 0 | 0 | 43 | 53 | 0 | 163 | 268 | 68 | 78 | 0 | 226 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 148 | 0 | 100 | 158 | 0 | 365 | 115 | 50 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 75 | 0 | 35 | 35 | 0 | 36 | 0 |  | 724 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 28 | 16 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 148 | 0 | 187 | 0 | 95 | 0 | 186 | 0 | 405 | 53 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 580 | 0 | 0 | 0 |  | 7349 | 3390 | 10739 | 4794 | 724 | 2020 | 2230 | 803 | 35 | 3 | 130 | 0 | 0 | 77.87
6:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 302 |  | 0 | 290 | 240 | 7 | 0 | 55 | 222 | 0 | 120 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 92 | 0 | 0 | 21 | 31 | 100 | 0 | 0 | 300 | 300 | 214 | 45 | 94 | 23 | 40 | 0 | 2 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 120 | 205 | 73 | 19 | 0 | 0 | 43 | 53 | 0 | 130 | 268 | 68 | 78 | 0 | 226 | 18 | 0 | 9 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 1 | 100 | 158 | 0 | 364 | 115 | 17 | 95 | 0 | 0 | 37 | 0 | 0 | 55 | 100 | 370 | 36 | 2 | 17 | 35 | 0 | 36 | 1 |  | 725 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 148 | 0 | 170 | 0 | 96 | 0 | 163 | 0 | 388 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 540 | 0 | 0 | 0 |  | 6899 | 3191 | 10090 | 4702 | 725 | 1919 | 1818 | 764 | 35 | 3 | 120 | 4 | 0 | 77.86
7:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 302 |  | 0 | 290 | 235 | 7 | 0 | 55 | 222 | 0 | 120 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 216 | 0 | 120 | 0 |  | 11 | 0 | 0 | 92 | 0 | 0 | 21 | 6 | 100 | 0 | 0 | 285 | 310 | 195 | 45 | 95 | 23 | 40 | 0 | 2 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 110 | 205 | 73 | 19 | 1 | 0 | 43 | 53 | 0 | 130 | 275 | 67 | 78 | 0 | 225 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 3 | 100 | 158 | 0 | 374 | 115 | 17 | 48 | 1 | 0 | 35 | 0 | 0 | 55 | 70 | 400 | 17 | 10 | 17 | 0 | 0 | 36 | 6 |  | 724 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 67 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 148 | 0 | 159 | 0 | 71 | 0 | 160 | 0 | 388 | 0 | 0 | 0 | 0 | 54 | 0 | 1 | 0 | 540 | 0 | 0 | 0 |  | 6771 | 3179 | 9950 | 4755 | 724 | 1869 | 1668 | 764 | 35 | 3 | 110 | 22 | 0 | 77.85
8:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 302 |  | 0 | 290 | 245 | 7 | 0 | 55 | 222 | 0 | 120 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 0 | 0 | 17 | 216 | 0 | 120 | 0 |  | 17 | 0 | 0 | 92 | 0 | 0 | 21 | 3 | 100 | 0 | 0 | 305 | 330 | 203 | 45 | 94 | 23 | 40 | 0 | 3 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 116 | 200 | 73 | 19 | 1 | 0 | 43 | 53 | 0 | 130 | 274 | 64 | 78 | 0 | 225 | 18 | 0 | 9 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 9 | 100 | 158 | 0 | 411 | 115 | 54 | 34 | 2 | 0 | 35 | 0 | 0 | 55 | 70 | 387 | 17 | 23 | 17 | 0 | 0 | 36 | 14 |  | 725 | 0 | 405 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 66 | 22 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 147 | 0 | 170 | 0 | 72 | 0 | 171 | 0 | 391 | 0 | 0 | 0 | 0 | 50 | 0 | 2 | 0 | 540 | 0 | 0 | 0 |  | 6911 | 3190 | 10101 | 4839 | 725 | 1880 | 1686 | 765 | 35 | 4 | 116 | 51 | 0 | 77.84
9:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 342 |  | 0 | 290 | 237 | 26 | 0 | 55 | 217 | 0 | 150 | 40 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 22 | 33 | 33 | 2 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 120 | 0 |  | 18 | 0 | 0 | 92 | 1 | 0 | 21 | 2 | 100 | 0 | 0 | 280 | 310 | 183 | 45 | 94 | 20 | 40 | 0 | 12 | 0 | 0 | 52 | 19 | 11 | 33 | 20 | 124 | 196 | 73 | 19 | 1 | 0 | 43 | 50 | 0 | 163 | 270 | 64 | 78 | 0 | 225 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 4 | 100 | 158 | 0 | 372 | 115 | 75 | 50 | 3 | 0 | 35 | 0 | 0 | 75 | 100 | 373 | 40 | 35 | 46 | 0 | 0 | 36 | 16 |  | 725 | 0 | 375 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 146 | 0 | 180 | 0 | 71 | 0 | 192 | 0 | 418 | 51 | 0 | 14 | 0 | 79 | 0 | 4 | 25 | 540 | 0 | 0 | 0 |  | 7074 | 3328 | 10402 | 4710 | 725 | 1974 | 2002 | 765 | 35 | 4 | 124 | 63 | 0 | 77.83
10:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 338 |  | 0 | 290 | 247 | 60 | 0 | 55 | 211 | 0 | 150 | 70 | 40 | 16 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 22 | 25 | 33 | 23 | 0 | 0 | 35 | 0 | 0 | 17 | 227 | 0 | 120 | 0 |  | 18 | 0 | 0 | 92 | 11 | 11 | 21 | 2 | 100 | 0 | 0 | 275 | 300 | 183 | 45 | 94 | 23 | 40 | 0 | 19 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 146 | 184 | 65 | 19 | 2 | 0 | 43 | 50 | 0 | 163 | 271 | 62 | 76 | 0 | 225 | 17 | 0 | 7 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 4 | 0 | 149 | 9 | 100 | 158 | 0 | 369 | 115 | 86 | 96 | 4 | 0 | 35 | 0 | 0 | 96 | 100 | 378 | 89 | 43 | 121 | 0 | 0 | 36 | 27 |  | 724 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 144 | 0 | 188 | 0 | 85 | 0 | 200 | 0 | 414 | 53 | 0 | 52 | 0 | 113 | 0 | 6 | 35 | 540 | 0 | 0 | 0 |  | 7474 | 3389 | 10863 | 4662 | 724 | 1978 | 2442 | 765 | 35 | 20 | 146 | 91 | 0 | 77.82
11:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 338 |  | 0 | 290 | 240 | 87 | 0 | 40 | 204 | 0 | 150 | 74 | 50 | 82 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 21 | 33 | 33 | 19 | 0 | 0 | 35 | 0 | 0 | 17 | 204 | 0 | 120 | 0 |  | 20 | 0 | 34 | 80 | 12 | 43 | 21 | 2 | 100 | 0 | 0 | 270 | 300 | 181 | 45 | 94 | 23 | 40 | 0 | 17 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 138 | 174 | 65 | 19 | 2 | 0 | 43 | 50 | 0 | 163 | 273 | 62 | 73 | 0 | 226 | 17 | 0 | 6 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 62 | 0 | 149 | 19 | 100 | 158 | 0 | 366 | 105 | 86 | 105 | 4 | 0 | 35 | 0 | 17 | 110 | 80 | 370 | 89 | 49 | 162 | 15 | 0 | 34 | 28 |  | 724 | 0 | 360 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 62 | 21 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 4 | 0 | 0 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 142 | 0 | 187 | 0 | 95 | 0 | 198 | 0 | 386 | 72 | 0 | 87 | 0 | 113 | 0 | 6 | 90 | 540 | 0 | 0 | 0 |  | 7684 | 3474 | 11158 | 4597 | 724 | 1944 | 2715 | 764 | 35 | 133 | 138 | 108 | 0 | 77.8
12:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 0 | 335 |  | 0 | 290 | 248 | 90 | 0 | 40 | 201 | 0 | 175 | 94 | 102 | 140 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 21 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 120 | 0 |  | 24 | 0 | 32 | 92 | 12 | 43 | 21 | 2 | 100 | 0 | 0 | 270 | 300 | 184 | 45 | 94 | 20 | 40 | 0 | 19 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 144 | 174 | 73 | 19 | 2 | 0 | 43 | 50 | 0 | 163 | 265 | 49 | 70 | 0 | 225 | 17 | 0 | 6 | 300 | 14 | 11 | 0 | 0 | 0 | 0 | 131 | 0 | 138 | 19 | 90 | 154 | 0 | 368 | 95 | 80 | 105 | 5 | 0 | 35 | 0 | 38 | 110 | 80 | 370 | 88 | 51 | 162 | 35 | 0 | 34 | 31 |  | 725 | 0 | 360 | 0 | 66 | 0 | 0 | 0 | 6 | 8 | 8 | 61 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 27 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 117 | 0 | 178 | 0 | 94 | 0 | 173 | 0 | 399 | 71 | 0 | 108 | 0 | 113 | 0 | 6 | 113 | 540 | 0 | 0 | 0 |  | 7944 | 3564 | 11508 | 4537 | 725 | 1947 | 2979 | 764 | 35 | 263 | 144 | 114 | 0 | 77.78
13:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 0 | 324 |  | 0 | 290 | 250 | 89 | 0 | 40 | 200 | 0 | 175 | 94 | 102 | 148 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 21 | 33 | 33 | 49 | 0 | 0 | 35 | 0 | 0 | 16 | 206 | 0 | 120 | 0 |  | 24 | 0 | 32 | 92 | 13 | 44 | 21 | 9 | 100 | 0 | 0 | 285 | 310 | 176 | 45 | 95 | 26 | 40 | 0 | 15 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 148 | 155 | 65 | 19 | 2 | 0 | 43 | 48 | 0 | 163 | 262 | 50 | 70 | 0 | 219 | 17 | 0 | 8 | 305 | 14 | 5 | 0 | 5 | 0 | 0 | 168 | 0 | 145 | 18 | 100 | 141 | 0 | 380 | 104 | 78 | 105 | 5 | 0 | 35 | 0 | 98 | 110 | 80 | 380 | 89 | 48 | 162 | 44 | 0 | 33 | 30 |  | 724 | 0 | 390 | 0 | 66 | 0 | 0 | 0 | 5 | 0 | 32 | 62 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 57 | 18 | 0 | 30 | 52 | 0 | 17 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 131 | 0 | 176 | 0 | 93 | 0 | 187 | 0 | 401 | 90 | 0 | 99 | 0 | 111 | 0 | 7 | 113 | 550 | 33 | 0 | 0 |  | 8081 | 3754 | 11835 | 4611 | 724 | 1979 | 3133 | 773 | 35 | 322 | 148 | 110 | 0 | 77.76
14:00 | 0 | 0 | 0 | 180 | 0 | 94 | 0 | 0 | 323 |  | 0 | 290 | 247 | 95 | 0 | 40 | 197 | 0 | 175 | 98 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 15 | 22 | 25 | 21 | 33 | 33 | 49 | 0 | 0 | 35 | 0 | 0 | 16 | 211 | 0 | 120 | 0 |  | 23 | 0 | 32 | 20 | 17 | 44 | 21 | 3 | 100 | 0 | 0 | 325 | 315 | 153 | 38 | 96 | 22 | 40 | 0 | 18 | 0 | 47 | 50 | 16 | 11 | 33 | 20 | 158 | 159 | 57 | 19 | 2 | 0 | 43 | 46 | 0 | 163 | 263 | 50 | 70 | 0 | 219 | 17 | 0 | 8 | 305 | 14 | 8 | 30 | 29 | 122 | 8 | 178 | 0 | 141 | 16 | 100 | 141 | 0 | 397 | 103 | 85 | 105 | 4 | 0 | 35 | 0 | 114 | 113 | 80 | 375 | 89 | 40 | 162 | 74 | 0 | 35 | 27 |  | 725 | 0 | 385 | 0 | 66 | 0 | 0 | 0 | 2 | 0 | 32 | 62 | 22 | 16 | 0 | 0 | 0 | 50 | 0 | 57 | 42 | 0 | 30 | 52 | 0 | 17 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 131 | 0 | 179 | 0 | 94 | 19 | 186 | 0 | 395 | 90 | 0 | 95 | 0 | 110 | 0 | 7 | 113 | 580 | 59 | 0 | 0 |  | 8306 | 3850 | 12156 | 4647 | 725 | 1985 | 3342 | 803 | 35 | 365 | 158 | 96 | 0 | 77.74
15:00 | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 4 | 233 |  | 0 | 290 | 240 | 96 | 0 | 40 | 197 | 0 | 85 | 98 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 21 | 33 | 8 | 49 | 0 | 0 | 35 | 0 | 0 | 16 | 207 | 0 | 120 | 0 |  | 22 | 0 | 32 | 20 | 72 | 44 | 21 | 2 | 80 | 0 | 0 | 325 | 305 | 179 | 8 | 96 | 22 | 40 | 0 | 22 | 0 | 48 | 43 | 16 | 11 | 33 | 18 | 152 | 160 | 57 | 19 | 2 | 0 | 43 | 48 | 0 | 130 | 261 | 62 | 70 | 0 | 212 | 17 | 0 | 9 | 300 | 14 | 8 | 177 | 47 | 260 | 95 | 180 | 0 | 140 | 0 | 90 | 159 | 4 | 380 | 103 | 85 | 105 | 3 | 0 | 35 | 0 | 114 | 110 | 80 | 375 | 89 | 33 | 162 | 90 | 0 | 35 | 21 |  | 724 | 0 | 380 | 0 | 66 | 0 | 0 | 0 | 2 | 0 | 32 | 63 | 22 | 16 | 0 | 0 | 0 | 50 | 10 | 56 | 42 | 43 | 29 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 137 | 0 | 164 | 0 | 94 | 99 | 190 | 0 | 418 | 90 | 50 | 94 | 0 | 109 | 0 | 6 | 113 | 530 | 58 | 0 | 0 |  | 8473 | 3991 | 12464 | 4504 | 724 | 1846 | 4010 | 754 | 35 | 374 | 152 | 65 | 0 | 77.72
16:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 121 | 233 |  | 0 | 290 | 238 | 96 | 0 | 40 | 203 | 0 | 85 | 98 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 8 | 47 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 120 | 0 |  | 17 | 0 | 32 | 20 | 90 | 44 | 21 | 3 | 80 | 0 | 0 | 330 | 315 | 173 | 8 | 95 | 20 | 40 | 0 | 22 | 0 | 48 | 43 | 19 | 11 | 31 | 19 | 150 | 158 | 57 | 19 | 1 | 0 | 41 | 53 | 0 | 110 | 262 | 61 | 71 | 0 | 212 | 17 | 0 | 9 | 310 | 14 | 8 | 150 | 70 | 0 | 0 | 182 | 0 | 149 | 6 | 90 | 158 | 10 | 383 | 104 | 85 | 105 | 2 | 0 | 35 | 0 | 114 | 113 | 80 | 370 | 88 | 21 | 162 | 90 | 0 | 10 | 13 |  | 724 | 0 | 370 | 0 | 66 | 0 | 0 | 0 | 2 | 0 | 32 | 63 | 20 | 16 | 0 | 0 | 0 | 50 | 31 | 56 | 42 | 43 | 29 | 52 | 0 | 17 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 134 | 0 | 168 | 0 | 95 | 50 | 192 | 0 | 402 | 90 | 0 | 94 | 0 | 110 | 0 | 3 | 113 | 530 | 38 | 0 | 0 |  | 8226 | 3868 | 12094 | 4620 | 724 | 1813 | 3556 | 755 | 35 | 395 | 150 | 46 | 0 | 77.7
17:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 263 |  | 0 | 290 | 246 | 97 | 0 | 50 | 205 | 0 | 140 | 100 | 102 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 8 | 47 | 0 | 0 | 35 | 10 | 0 | 16 | 203 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 44 | 21 | 7 | 80 | 0 | 0 | 320 | 305 | 173 | 8 | 95 | 22 | 40 | 0 | 22 | 0 | 48 | 50 | 19 | 11 | 33 | 19 | 144 | 144 | 57 | 19 | 0 | 0 | 41 | 52 | 0 | 130 | 265 | 52 | 71 | 0 | 210 | 17 | 0 | 9 | 305 | 14 | 11 | 0 | 92 | 0 | 0 | 192 | 0 | 134 | 2 | 100 | 158 | 18 | 376 | 114 | 85 | 105 | 1 | 0 | 35 | 0 | 88 | 113 | 80 | 370 | 89 | 9 | 162 | 90 | 0 | 35 | 6 |  | 724 | 0 | 360 | 0 | 70 | 0 | 0 | 0 | 2 | 0 | 32 | 63 | 23 | 16 | 0 | 0 | 0 | 50 | 35 | 94 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 127 | 0 | 163 | 0 | 97 | 20 | 180 | 0 | 380 | 90 | 0 | 94 | 0 | 110 | 0 | 2 | 113 | 540 | 7 | 0 | 0 |  | 8116 | 3698 | 11814 | 4489 | 724 | 1819 | 3374 | 766 | 35 | 443 | 144 | 20 | 0 | 77.68
18:00 | 0 | 0 | 0 | 180 | 0 | 54 | 0 | 0 | 263 |  | 0 | 290 | 248 | 98 | 0 | 55 | 171 | 0 | 120 | 100 | 102 | 146 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 23 | 33 | 33 | 47 | 0 | 0 | 35 | 30 | 0 | 16 | 215 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 38 | 21 | 8 | 80 | 0 | 45 | 340 | 320 | 163 | 8 | 95 | 23 | 40 | 0 | 26 | 0 | 48 | 52 | 19 | 11 | 33 | 19 | 148 | 142 | 57 | 19 | 0 | 0 | 41 | 14 | 0 | 130 | 265 | 40 | 20 | 0 | 184 | 17 | 0 | 9 | 290 | 14 | 8 | 0 | 97 | 0 | 0 | 196 | 0 | 149 | 1 | 100 | 158 | 28 | 326 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 88 | 113 | 80 | 380 | 89 | 1 | 162 | 90 | 0 | 35 | 1 |  | 724 | 0 | 350 | 0 | 83 | 0 | 0 | 0 | 11 | 0 | 32 | 64 | 34 | 64 | 0 | 0 | 0 | 50 | 39 | 97 | 0 | 24 | 0 | 52 | 13 | 17 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 122 | 0 | 158 | 0 | 97 | 20 | 171 | 0 | 274 | 90 | 0 | 94 | 0 | 110 | 0 | 0 | 113 | 520 | 0 | 0 | 0 |  | 7993 | 3660 | 11653 | 4453 | 724 | 1574 | 3498 | 746 | 35 | 472 | 148 | 3 | 0 | 77.66
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 291 |  | 0 | 290 | 245 | 100 | 0 | 55 | 210 | 0 | 180 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 45 | 0 | 0 | 35 | 40 | 0 | 16 | 202 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 38 | 21 | 12 | 70 | 0 | 70 | 310 | 295 | 150 | 8 | 95 | 23 | 40 | 0 | 31 | 0 | 48 | 52 | 21 | 11 | 33 | 19 | 156 | 153 | 73 | 19 | 0 | 0 | 41 | 53 | 0 | 130 | 268 | 64 | 78 | 0 | 218 | 17 | 0 | 9 | 280 | 16 | 11 | 162 | 122 | 300 | 97 | 200 | 0 | 149 | 0 | 90 | 158 | 35 | 367 | 106 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 17 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 39 | 100 | 0 | 43 | 24 | 52 | 34 | 18 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 127 | 0 | 171 | 0 | 97 | 67 | 177 | 0 | 385 | 90 | 170 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 0 | 0 | 10 |  | 8933 | 4152 | 13085 | 4600 | 724 | 1856 | 4428 | 756 | 35 | 530 | 156 | 0 | 0 | 77.6
19:30 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 312 |  | 0 | 290 | 240 | 100 | 0 | 55 | 213 | 0 | 145 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 50 | 0 | 0 | 35 | 60 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 38 | 21 | 19 | 10 | 0 | 80 | 310 | 295 | 151 | 8 | 96 | 23 | 40 | 0 | 38 | 0 | 48 | 52 | 21 | 11 | 33 | 19 | 156 | 165 | 73 | 19 | 0 | 0 | 41 | 53 | 0 | 130 | 270 | 64 | 78 | 0 | 218 | 17 | 0 | 9 | 305 | 16 | 11 | 185 | 145 | 305 | 100 | 200 | 0 | 149 | 0 | 90 | 158 | 35 | 367 | 106 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 725 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 20 | 0 | 32 | 67 | 34 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 31 | 52 | 34 | 18 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 120 | 0 | 175 | 0 | 97 | 97 | 167 | 0 | 406 | 91 | 200 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 0 | 0 | 54 |  | 9010 | 4390 | 13400 | 4549 | 725 | 1938 | 4630 | 826 | 35 | 541 | 156 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 307 |  | 0 | 290 | 250 | 100 | 0 | 55 | 180 | 0 | 95 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 50 | 0 | 0 | 35 | 70 | 0 | 16 | 203 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 21 | 0 | 0 | 90 | 310 | 295 | 205 | 8 | 95 | 23 | 40 | 0 | 40 | 0 | 48 | 52 | 22 | 11 | 33 | 19 | 150 | 166 | 73 | 19 | 0 | 0 | 41 | 53 | 0 | 110 | 270 | 64 | 76 | 0 | 218 | 18 | 0 | 9 | 300 | 16 | 11 | 185 | 175 | 305 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 33 | 368 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 345 | 0 | 83 | 0 | 0 | 0 | 20 | 0 | 32 | 67 | 32 | 110 | 0 | 0 | 0 | 50 | 38 | 100 | 42 | 43 | 31 | 52 | 32 | 18 | 0 | 10 | 75 | 0 | 150 | 0 | 0 | 121 | 0 | 176 | 0 | 96 | 97 | 171 | 0 | 408 | 91 | 200 | 94 | 0 | 113 | 0 | 0 | 113 | 600 | 0 | 0 | 54 |  | 9017 | 4388 | 13405 | 4538 | 724 | 1909 | 4687 | 825 | 35 | 537 | 150 | 0 | 0 | 77.62
21:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 301 |  | 0 | 290 | 245 | 100 | 0 | 55 | 215 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 16 | 208 | 0 | 105 | 0 |  | 23 | 0 | 68 | 20 | 90 | 43 | 21 | 26 | 0 | 0 | 90 | 330 | 310 | 194 | 8 | 96 | 23 | 52 | 0 | 43 | 0 | 48 | 52 | 22 | 11 | 33 | 19 | 160 | 165 | 73 | 19 | 0 | 0 | 42 | 53 | 0 | 163 | 272 | 64 | 76 | 0 | 218 | 18 | 0 | 9 | 315 | 16 | 11 | 185 | 193 | 300 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 40 | 377 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 380 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 340 | 0 | 83 | 0 | 0 | 0 | 18 | 0 | 32 | 67 | 34 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 42 | 43 | 30 | 52 | 32 | 19 | 0 | 10 | 75 | 0 | 150 | 0 | 0 | 129 | 0 | 171 | 0 | 96 | 98 | 185 | 0 | 415 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 89 |  | 9322 | 4455 | 13777 | 4743 | 724 | 2002 | 4761 | 815 | 35 | 537 | 160 | 0 | 0 | 77.6
22:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 297 |  | 0 | 290 | 250 | 100 | 0 | 55 | 218 | 0 | 150 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 16 | 208 | 0 | 105 | 0 |  | 23 | 0 | 68 | 20 | 90 | 42 | 21 | 29 | 0 | 0 | 90 | 340 | 325 | 203 | 8 | 95 | 23 | 55 | 0 | 43 | 0 | 48 | 52 | 22 | 11 | 33 | 19 | 156 | 165 | 73 | 19 | 0 | 0 | 42 | 50 | 0 | 130 | 270 | 65 | 77 | 0 | 218 | 18 | 0 | 9 | 310 | 16 | 11 | 185 | 195 | 300 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 43 | 399 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 393 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 18 | 0 | 32 | 68 | 34 | 110 | 0 | 0 | 0 | 50 | 34 | 100 | 42 | 43 | 30 | 52 | 33 | 19 | 0 | 10 | 73 | 0 | 150 | 0 | 0 | 131 | 0 | 170 | 0 | 96 | 98 | 180 | 0 | 410 | 91 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 89 |  | 9327 | 4335 | 13662 | 4768 | 724 | 1959 | 4686 | 803 | 35 | 531 | 156 | 0 | 0 | 77.58
23:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 300 |  | 0 | 290 | 245 | 100 | 0 | 55 | 218 | 0 | 145 | 90 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 17 | 205 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 33 | 0 | 0 | 90 | 315 | 305 | 210 | 8 | 95 | 23 | 55 | 0 | 43 | 0 | 48 | 52 | 22 | 11 | 33 | 19 | 162 | 166 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 130 | 273 | 65 | 78 | 0 | 218 | 18 | 0 | 9 | 310 | 16 | 11 | 185 | 195 | 306 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 53 | 371 | 108 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 725 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 67 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 30 | 52 | 32 | 20 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 128 | 0 | 169 | 0 | 96 | 97 | 192 | 0 | 414 | 91 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 89 |  | 9256 | 4314 | 13570 | 4684 | 725 | 1972 | 4677 | 803 | 35 | 512 | 162 | 0 | 0 | 77.56
24:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 311 |  | 0 | 290 | 240 | 100 | 0 | 55 | 222 | 0 | 145 | 97 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 30 | 0 | 0 | 90 | 310 | 300 | 213 | 8 | 95 | 23 | 55 | 0 | 49 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 156 | 169 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 130 | 270 | 68 | 78 | 0 | 218 | 18 | 0 | 9 | 300 | 16 | 11 | 185 | 200 | 181 | 100 | 200 | 0 | 140 | 0 | 100 | 158 | 61 | 367 | 108 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 90 | 0 | 162 | 90 | 0 | 35 | 0 |  | 725 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 117 | 0 | 171 | 0 | 96 | 98 | 194 | 0 | 400 | 91 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 0 | 0 | 72 |  | 9133 | 4196 | 13329 | 4673 | 725 | 1963 | 4493 | 773 | 35 | 511 | 156 | 0 | 0 | 77.54
KWH | 0 | 0 | 0 | 4347000 | 0 | 2282227 | 0 | 195262 | 7446000 |  | 0 | 6835550 | 5528698 | 1936320 | 0 | 1238167 | 5164966 | 0 | 3653000 | 2005344 | 1856880 | 2239200 | 0 | 0 | 0 | 0 | 874800 | 828575 | 1271399 | 384552 | 600000 | 550620 | 764200 | 800800 | 846240 | 0 | 0 | 848000 | 500000 | 0 | 409204 | 4920381 | 0 | 2788406 | 0 |  | 518880 | 0 | 971970 | 1428360 | 1258560 | 663360 | 499728 | 420480 | 1947542 | 0 | 520936 | 7732500 | 7457000 | 4535000 | 736000 | 2235650 | 508680 | 1037280 | 0 | 455837 | 0 | 668104 | 1236700 | 468900 | 243360 | 801900 | 505100 | 3425280 | 4150880 | 1646400 | 414108 | 13350 | 0 | 993600 | 1206600 | 0 | 3566045 | 6141000 | 1495680 | 1771200 | 0 | 5286749 | 403000 | 0 | 191700 | 7497000 | 349176 | 243100 | 1488000 | 1455272 | 1969069 | 738516 | 3249600 | 0 | 3489120 | 120150 | 2355840 | 3788160 | 334545 | 9016000 | 2635200 | 1900800 | 2393672 | 33121 | 0 | 957657 | 0 | 1539000 | 2592240 | 2224320 | 8960300 | 1895040 | 364300 | 3320640 | 1678582 | 0 | 836640 | 220811 |  | 17505455 | 0 | 8911296 | 0 | 1835520 | 0 | 0 | 0 | 212480 | 4999 | 468000 | 1568000 | 670065 | 1142880 | 0 | 0 | 565000 | 855520 | 418040 | 1380440 | 394630 | 336638 | 383500 | 1234560 | 313840 | 435840 | 0 | 258858 | 1776436 | 0 | 3687600 | 0 | 0 | 3385500 | 0 | 4437882 | 0 | 2222720 | 952320 | 4359827 | 0 | 9545000 | 1733280 | 882594 | 1921344 | 0 | 2506560 | 0 | 51203 | 2074368 | 14373800 | 252791 | 0 | 397200 |  | 196319081 | 93455986 | 289775067 | 113065439 | 17505455 | 46572335 | 80269694 | 19837836 | 848000 | 7448093 | 3425280 | 802935 | 0
Fuel Cost | 0 | 0 | 0 | 6390090 | 0 | 3012539.64 | 0 | 197214.62 | 7669380 |  | 0 | 7450749.5 | 6136854.78 | 14696668.8 | 0 | 10474892.82 | 5371564.64 | 0 | 6319690 | 15100240.32 | 16934745.6 | 22033728 | 0 | 0 | 0 | 0 | 6386040 | 6404884.75 | 12535994.14 | 288414 | 450000 | 0 | 0 | 0 | 8183140.8 | 0 | 0 | 228960 | 905000 | 0 | 3801505.16 | 5363215.29 | 0 | 4740290.2 | 0 |  | 0 | 0 | 9428109 | 13640838 | 10949472 | 5253811.2 | 629657.28 | 1248825.6 | 2882362.16 | 0 | 765775.92 | 5722050 | 7457000 | 4172200 | 949440 | 2570997.5 | 574808.4 | 1452192 | 0 | 779481.27 | 0 | 6747850.4 | 11810485 | 595503 | 182520 | 1403325 | 378825 | 25689600 | 4399932.8 | 14949312 | 525917.16 | 212799 | 0 | 1589760 | 2147748 | 0 | 4065291.3 | 6386640 | 2946489.6 | 3382992 | 0 | 9146075.77 | 882570 | 0 | 391068 | 7571970 | 261882 | 184756 | 25310880 | 11001856.32 | 33434791.62 | 12347987.52 | 16897920 | 0 | 34332940.8 | 1404553.5 | 19200096 | 41101536 | 2358542.25 | 8384880 | 24033024 | 17962560 | 20848883.12 | 0 | 0 | 8341192.47 | 0 | 15359220 | 22215496.8 | 14813971.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100831420.8 | 0 | 9356860.8 | 0 | 14427187.2 | 0 | 0 | 0 | 2228915.2 | 52389.52 | 4876560 | 1771840 | 1038600.75 | 11154508.8 | 0 | 0 | 1158250 | 8418316.8 | 4247286.4 | 12216894 | 3038651 | 4551345.76 | 3716115 | 11962886.4 | 3044248 | 836812.8 | 0 | 195955.506 | 10711909.08 | 0 | 19986792 | 0 | 0 | 3961035 | 0 | 5858004.24 | 0 | 3334080 | 16198963.2 | 5100997.59 | 0 | 9449550 | 18095443.2 | 15012923.94 | 18233554.56 | 0 | 19450905.6 | 0 | 565793.15 | 15329579.52 | 63100982 | 0 | 0 | 0 |  | 674756467.02 | 423515557.816 | 1098272024.836 | 119472349.476 | 100831420.8 | 54780720.86 | 629152292.65 | 93799683.08 | 228960 | 72133852.32 | 25689600 | 2183145.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 0 | 335 |  | 0 | 290 | 248 | 90 | 0 | 40 | 201 | 0 | 175 | 94 | 102 | 140 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 21 | 33 | 33 | 50 | 0 | 0 | 35 | 0 | 0 | 16 | 204 | 0 | 120 | 0 |  | 24 | 0 | 32 | 92 | 12 | 43 | 21 | 2 | 100 | 0 | 0 | 270 | 300 | 184 | 45 | 94 | 20 | 40 | 0 | 19 | 0 | 0 | 52 | 18 | 11 | 33 | 20 | 144 | 174 | 73 | 19 | 2 | 0 | 43 | 50 | 0 | 163 | 265 | 49 | 70 | 0 | 225 | 17 | 0 | 6 | 300 | 14 | 11 | 0 | 0 | 0 | 0 | 131 | 0 | 138 | 19 | 90 | 154 | 0 | 368 | 95 | 80 | 105 | 5 | 0 | 35 | 0 | 38 | 110 | 80 | 370 | 88 | 51 | 162 | 35 | 0 | 34 | 31 |  | 725 | 0 | 360 | 0 | 66 | 0 | 0 | 0 | 6 | 8 | 8 | 61 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 27 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 117 | 0 | 178 | 0 | 94 | 0 | 173 | 0 | 399 | 71 | 0 | 108 | 0 | 113 | 0 | 6 | 113 | 540 | 0 | 0 | 0 |  | 11508 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 301 | 0 | 0 | 290 | 245 | 100 | 0 | 55 | 215 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 16 | 208 | 0 | 105 | 0 | 0 | 23 | 0 | 68 | 20 | 90 | 43 | 21 | 26 | 0 | 0 | 90 | 330 | 310 | 194 | 8 | 96 | 23 | 52 | 0 | 43 | 0 | 48 | 52 | 22 | 11 | 33 | 19 | 160 | 165 | 73 | 19 | 0 | 0 | 42 | 53 | 0 | 163 | 272 | 64 | 76 | 0 | 218 | 18 | 0 | 9 | 315 | 16 | 11 | 185 | 193 | 300 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 40 | 377 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 380 | 89 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 340 | 0 | 83 | 0 | 0 | 0 | 18 | 0 | 32 | 67 | 34 | 110 | 0 | 0 | 0 | 50 | 41 | 100 | 42 | 43 | 30 | 52 | 32 | 19 | 0 | 10 | 75 | 0 | 150 | 0 | 0 | 129 | 0 | 171 | 0 | 96 | 98 | 185 | 0 | 415 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 89 |  | 13777 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 345 | 0 | 0 | 300 | 250 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 80 | 0 | 17 | 205 | 0 | 120 | 0 | 0 | 22 |  | 68 | 20 | 90 | 43 | 22 | 25 | 0 | 0 | 100 | 330 | 330 | 225 | 8 | 96 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 171 | 170 | 74 | 20 | 0 | 0 | 42 | 51 | 0 | 163 | 275 | 66 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 150 | 400 | 115 | 85 | 105 | 0 | 300 | 35 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 90 | 0 | 35 |  |  | 737 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 67 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 100 | 42 | 43 | 30 | 52 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 144 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 91 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 110 |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 345 | 0 | 0 | 300 | 250 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 80 | 0 | 17 | 205 | 0 | 120 | 0 | 0 | 22 |  | 68 | 20 | 90 | 43 | 22 | 10 | 0 | 0 | 100 | 330 | 330 | 225 | 8 | 95 | 23 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 170 | 74 | 20 | 1.6 | 0 | 42 | 51 | 0 | 163 | 275 | 66 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 75 | 100 | 50 | 200 | 0 | 149 | 20 | 100 | 158 | 100 | 400 | 115 | 85 | 105 | 5 | 300 | 35 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 90 | 0 | 35 | 30 |  | 737 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 66 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 144 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 109 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 348 | 0 | 0 | 290 | 240 | 16 | 0 | 55 | 222 | 0 | 120 | 55 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 24 | 33 |  | 0 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 | 0 | 0 | 0 | 68 | 20 | 25 | 1 | 21 | 2 | 0 | 0 | 100 | 310 | 300 | 180 | 8 | 95 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 132 | 197 | 67 | 19 | 1 | 0 | 43 | 50 | 0 | 163 | 0 | 66 | 78 | 0 | 217 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 6 | 90 | 158 | 74 | 365 | 115 | 80 | 105 | 2 | 0 | 35 | 0 | 17 | 113 | 100 | 370 | 58 | 21 | 54 | 40 | 0 | 35 | 13 | 0 | 725 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 132 | 0 | 177 | 0 | 96 | 0 | 160 | 0 | 402 | 17 | 0 | 35 | 0 | 106 | 0 | 2 | 20 | 480 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9950 | 7:00
| Highest Generation |  | 13777 | 21:00
| Day Peak Generation |  | 11508 | 12:00
| Evening Peak Generation |  | 13777 | 21:00
| HVDC Max Flow |  | 725 | 3:00
| HVDC EvPeak Flow |  | 724 | 21:00
| Load factor L.F |  | 87.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-27
Till now the maximum generation is : - |  |  | 13777 | 21:00 | Hrs on | 2021-04-26
The Summary of Yesterday's |  | 2021-04-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11508 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10354 | MW
Evening Peak Generation : |  | 13777 | MW Hour : | 21:00 | Available Max Generation : |  | 15300 | MW
E.P. Demand (at gen end) : |  | 13777 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13950 | MW
Maximum Generation : |  | 13777 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1350 | MW
Total Gen. (MKWH) : |  | 289.7751 | System Load Factor : | 87.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -290 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-27
Actual : | 77.51 | Ft.(MSL) , | Rule curve : | 82.8 | Ft.( MSL )
Gas Consumed : | Total = | 1300.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 174253070.336
: |  | Coal : | 93799683.08 | Oil : | 701286144.97 | Total : | 969338898.386
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4913.2532 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1677.7766 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1504.4792 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1359.8667 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1228.6477 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 991.4928 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 545.388 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 255.0444 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 764.7316 |  |  | 0 | 0%
Total | 0 |  | 13240.6802 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
7) Haripur-412 MW.
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Mithapukur 132/33 kV T-2 transformer tripped at 07:38 showing O/C & E/F relays at 33 kV end and was |  |  |  |  | About 4 MW power interruption occurred under Mithapukur S/S
switched on at 08:17. |  |  |  |  | area from 07:38 to 08:17.
b) Ashuganj-B.Baria 132 kV Ckt-1 was under shut down from 10:36 to 11:41 due to red hot maintenance
at CT R-phase at B.Baria end.
c) Sikalbaha-TK Chemical 132 kV Ckt was under shut down from 09:03 to 13:33 for D/W.
d) Haripur-412 MW CCPP GT was synchronized at 14:51 and tripped at 16:32 due to problem with turbine
cooling air fan.
e) After restoration of gas Ashuganj #5 was synchronized at 17:09.
f) Siddirganj Peaking GT-2 tripped at 14:48 due to load tunnel temperature high and was synchronized at 16:21.
g) After restoration of gas Raozan#1 was synchronized at 16:41.
h) Rajshahi-Natore 132 kV Ckt-2 tripped at 16:44 showing dist.Y-phase at Rajshahi end & dist.B-phase
at Natore end and was switched on at 17:02.
i) Ashuganj #3 was shut down at 19:31 due to gas shortage.
j) Hathazari-Kaptai 132 kV Ckt-1 & 2 tripped at 03:01(27/4/21) showing E/F relay and were switched on at 03:43.
k) Kaliakoir 132 kV Bus-2 is under shut down since 07:14(27/4/21) for D/W.
m) Shahjibazar-330 MW tripped at 05:08(27/4/21) showing E/F relay.
n) Kaptai #4 tripped at 03:01(27/4/21) due to line trip.
o) Chandraghona-Kaptai 132 kV Ckt-1 tripped at 03:01(27/4/21) showing dist.Z2,R-phase and was switched
on at 04:03(27/4/21).
p) Rajshahi(O)-Rajshahi(N) 132 kV Ckt is under shut down since 07:29(27/4/210 for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2282227
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 195262 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 301 | 7446000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 290 | 6835550 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 100 | 1936320
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 245 | 5528698 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1238167
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Devolopment work.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 384552
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3653000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2005344
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 215 | 5164966 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1856880
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 874800 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2239200
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 828575 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1271399
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 49 | 1150620 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 764200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 800800
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 50 | 846240
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 193 | 1455272 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 1969069
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 738516
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Devolopment work.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3489120
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 85 | 1900800 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 89 | 1895040 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3320640
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 220811
| Dhaka area Total |  |  |  | 5829 | 3435 | 66639068
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 80 | 500000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 409204 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120150
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 43 | 663360
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 848000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 208 | 4920381 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 105 | 2788406
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2393672
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 971970 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 1428360 | Engine problem
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2355840
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 499728
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 420480
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 1258560 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33121
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 35 | 957657 | Engine problem
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Transformer O/L.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2224320
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 90 | 1678582 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1142 | 24471791
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 1947542 | S/D at 19:31 due to gas shortage.
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 90 | 520936 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 4535000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7732500 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7457000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 508680 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1037280
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 736000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 455837 | Engine problem
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 40 | 334545 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 668104
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 96 | 2235650 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 158 | 3788160 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 468900
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243360
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3425280
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 801900
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1236700
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 505100 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 185 | 1488000
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1539000
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2592240
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 836640 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 2136 | 45094354
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 165 | 4150880 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 414108
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 73 | 1646400 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13350
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3249600
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2635200
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 364300
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 518880
| Mymensingh Area Total |  |  |  | 709 | 595 | 12992718
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 993600 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3566045
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 272 | 6141000 | Gas shortage
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1206600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 243100
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1495680
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1771200
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 5286749
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 403000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 349176 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7497000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 377 | 9016000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 191700
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 8960300 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2014 | 47121150
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 724 | 17505455
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 83 | 1835520 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 18 | 212480 | Low demand
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 4999 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 8911296 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 468000 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 952320
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 91 | 1733280 | Engine problem
111 | Madhumati 100 MW PP |  | SWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1386 | 31623350
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1142880
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 670065
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 67 | 1568000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2222720
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 590 | 14373800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 252791 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 89 | 397200 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 986 | 20627456
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 565000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 855520
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 41 | 418040
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 394630 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 336638 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 383500 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 129 | 3385500 | FGMO
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 171 | 4437882 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 185 | 4359827 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 9545000 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 313840 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 435840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 258858
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1234560
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1380440
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 200 | 882594
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1921344
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2074368
| Rajshahi Area Total |  |  |  | 2173 | 1745 | 33183381
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1776436
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3687600 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2506560
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 51203
| Rangpur Area Total |  |  |  | 605 | 338 | 8021799
| Total |  |  |  | 21219 | 13777 | 289775067
| Eastern Grid Total |  |  |  | 14331 | 9322 | 196319081
| Western Grid Total |  |  |  | 6888 | 4455 | 93455986
| National Grid Total |  |  |  | 21219 | 13777 | 289775067
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-26
(a) ENTIRE EASTERN GRID : |  | 8787 | MW | (b) ENTIRE WESTERN GRID : |  | 4278 | MW
i) Dhaka area |  | 4451 | MW | i) Khulna area |  | 1621 | MW
ii) Chittagong area |  | 1380 | MW | ii) Rajshahi area |  | 1453 | MW
iii) Comilla area |  | 1318 | MW | iii) Barisal area |  | 406 | MW
iv) Mymensingh area |  | 1103 | MW | iv) Rangpur area |  | 798 | MW
v) Sylhet area |  | 535 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13065 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 136 | 10:00 | Jamalpur | 165 | 21:00 | Jhenida | 113 | 23:00
Munsiganj | 149 | 21:00 | Sherpur | 140 | 21:00 | Bottail | 132 | 22:00
Sonargaon | 84 | 24:00 | Srimongal | 52 | 20:00 | G.K Project | 66 | 21:00
Shyampur | 204 | 24:00 | Shahjibazar | 122 | 22:00 | Faridpur | 211 | 21:00
Bhulta | 197 | 23:00 | Fenchuganj | 52 | 21:00 | Madaripur | 111 | 21:00
Madanganj | 58 | 1:00 | Kulawara | 49 | 18:30 | Sariatpur | 72 | 21:00
Shitalakhya | 126 | 15:00 | Sylhet | 122 | 14:00 | Gopalganj | 99 | 22:00
Rahim steel | 35 | 10:00 | Chatak | 32 | 19:30 | Bagerhat | 105 | 21:00
Matuail | 60 | 9:00 | Sunamganj | 49 | 21:00 | Mongla | 42 | 18:00
Ghorasal | 68 | 22:00 | Biani Bazar | 68 | 21:00 | Satkhira | 113 | 23:00
Narsingdi | 172 | 22:00 | Comilla (S) | 162 | 23:00 | Gallamari | 43 | 19:30
Haripur (SBU) | 111 | 13:00 | Comilla(N) | 143 | 18:30 | Magura | 54 | 20:00
Sreenagar |  |  | Chandpur | 84 | 21:00 | Norail | 41 | 21:00
Ullon | 91 | 24:00 | Feni | 138 | 21:00 | Chuadanga | 90 | 2:00
Hasnabad | 87 | 4:00 | Chowmuhani | 200 | 21:00 | Borguna | 20 | 21:00
Magbazar | 86 | 14:00 | Ashuganj | 34 | 16:00 | Barisal(N) | 49 | 21:00
Maniknagar | 89 | 15:00 | Daudkandi | 168 | 21:00 | Barisal (S) | 120 | 20:00
Bangabhaban | 23 | 11:00 | B.Baria | 178 | 21:00 | Patuakhali | 122 | 23:00
Narinda | 82 | 11:00 | Ramganj | 98 | 22:00 | Bhandaria | 59 | 21:00
Dhanmondi | 200 | 13:00 | Chaddagram | 52 | 20:00 | Borhan Uddin | 43 | 20:00
Lalbag | 86 | 13:00 | PHP | 10 | 11:00 | Ishurdi | 70 | 21:00
Madartek | 86 | 23:00 | Kochua | 69 | 3:00 | Ruppur Paromanobik | 3 | 9:00
Dhaka University | 40 | 13:00 | Madunaghat | 68 | 19:00 | Natore | 149 | 21:00
Aftabnagar | 11 | 14:00 | Hathazari | 98 | 19:00 | Bogra | 177 | 3:00
Fatullah | 62 | 9:00 | Khulshi | 222 | 16:00 | Noagaon | 135 | 21:00
Nawabganj | 57 | 21:00 | Halishahar | 152 | 9:00 | Rajshahi | 160 | 21:00
Mirpur | 119 | 19:30 | Baraulia | 156 | 1:00 | Rajshahi New | 26 | 21:00
Kalyanpur | 123 | 19:30 | Sikalbaha | 36 | 12:00 | C.Nawabganj | 65 | 21:00
Gulshan | 136 | 14:00 | Dohazari | 104 | 21:00 | Amnura | 58 | 3:00
Uttara | 106 | 19:30 | Cox'sbazar | 97 | 19:00 | Pabna | 105 | 20:00
Uttara New | 32 | 21:00 | Chandraghona | 32 | 19:00 | Shahjadpur | 112 | 21:00
Kamrangirchar | 85 | 15:00 | Kaptai | 4.3 | 19:00 | Serajganj | 110 | 21:00
Savar | 183 | 15:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 80 | 21:00
Bhasantec | 164 | 15:00 | Bakulia | 112 | 12:00 | Joypurhat | 64 | 21:00
Agargaon | 72 | 19:30 | Julda | 24 | 9:00 | Sherpur(Bogura) | 56 | 21:00
Satmosjid | 105 | 24:00 | TK chemical | 30.3 | 19:30 | Mohastangor | 66 | 21:00
Tongi | 130 | 14:00 | Modern Steel | 0 | #N/A | Bangura | 42 | 21:00
Kabirpur | 238 | 15:00 | Shahmirpur | 29.5 | 1:00 | Rangpur | 123 | 18:00
Basundhara | 161 | 15:00 | Khagrachhari | 26 | 1:00 | Lalmonirhat | 49 | 19:00
Manikganj | 72 | 21:00 | Matarbari | 40 | 20:00 | Saidpur | 108 | 19:30
Joydevpur | 177 | 16:00 | Baroiar Hat | 46 | 19:00 | Purbasadipur | 107 | 8:00
New Tongi | 109 | 15:00 | Rangamati | 12 | 18:30 | Thakurgaon | 84 | 19:30
Kodda | 269 | 10:00 | Abul Khair 230 | 139 | 15:00 | Palashbari | 114 | 19:30
Dhamrai | 112 | 19:30 | BSRM | 152 | 15:00 | Barapukuria | 58 | 21:00
Rajendrapur | 96 | 23:00 | GPH Ispat | 92 | 15:00 | Panchagar | 45 | 18:30
Valuka | 124 | 14:00 | Goalpara | 29 | 21:00 | Joldhaka | 61 | 19:00
Tangail | 237 | 19:00 | Central s/s | 93 | 19:00 | Kurigram | 59 | 21:00
Mymensing | 224 | 19:00 | Noapara | 55 | 0.875 | Mithapukur | 41 | 21:00
Kishorganj | 138 | 21:00 | Jessore | 113 | 21:00
Netrokona | 128 | 19:30 | Benapol | 70 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 4:00 | 395 | 15:00 | Kaliakoir | 380 | 0.25 | 371 | 0.375
| Bheramara | 404 | 24:00 | 398 | 1:00 | Bhulta | 375 | 0.77083 | 365 | 0.375
| Ashuganj(N) | 383 | 1:00 | 372 | 10:00 | Gopalganj | 404 | 0.625 | 383 | 0.875
| Payra | 406 | 2:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 21:00 | 225 | 8:00 | Hathazari | 221 | 2:00 | 206 | 14:00
| Ishurdi | 234 | 1:00 | 223 | 19:30 | Megnaghat | 226 | 3:00 | 220 | 9:00
| Ashuganj | 232 | 1:00 | 228 | 9:00 | Fenchuganj | 238 | 1:00 | 234 | 23:00
| Serajganj | 230 | 18:30 | 225 | 6:00 | Siddhirganj | 225 | 4:00 | 217 | 10:00
| Baghabari | 231 | 1:00 | 226 | 19:30 | Maniknagar | 223 | 4:00 | 215 | 14:00
| Barapukuria | 230 | 5:00 | 220 | 19:00 | Agargaon | 221 | 6:00 | 212 | 8:00
| Bogra | 223 | 12:00 | 214 | 20:00 | Barisal | 245 | 1:00 | 234 | 14:00
| Rajshahi | 235 | 18:30 | 222 | 20:00 | Bhola 225 MW | 249 | 24:00 | 238 | 13:00
| Khulna South | 229 | 14:00 | 207 | 19:30 | AKSML | 222 | 1:00 | 206 | 14:00
| Rampura | 223 | 2:00 | 218 | 9:00 | BSRM | 224 | 1:00 | 207 | 15:00
| Haripur | 221 | 1:00 | 215 | 8:00 | Bibiyana | 237 | 1:00 | 234 | 24:00
| Hasnabad | 224 | 1:00 | 215 | 9:00 | Bhulta | 225 | 4:00 | 218 | 9:00
| Shyampur | 220 | 2:00 | 220 | 9:00 | Ashuganj (S) | 231 | 1:00 | 225 | 14:00
| Aminbazar | 222 | 1:00 | 213 | 2:00 | Kaliakoir | 221 | 24:00 | 210 | 9:00
| Tongi | 218 | 23:00 | 211 | 8:00 | GPH | 221 | 1:00 | 205 | 15:00
| Comilla (N) | 225 | 1:00 | 218 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 2:00 | 128 | 7:00 | Madanhat | 133 | 0.041667 | 126 | 0.375
| Munsiganj | 133 | 18:30 | 126 | 14:00 | Hathazari | 131 | 0.041667 | 123 | 0.58333
| Sonargaon | 134 | 1:00 | 129 | 9:00 | Khulshi | 130 | 0.041667 | 122 | 0.58333
| Shyampur | 138 | 6:00 | 127 | 8:00 | Halishahar | 131 | 0.041667 | 123 | 0.58333
| Bhulta | 127 | 19:00 | 120 | 10:00 | Baraulia | 130 | 0.041667 | 122 | 0.625
| Madanganj | 130 | 3:00 | 123 | 13:00 | Sikalbaha | 133 | 0.041667 | 127 | 0.29167
| Shitalakhya | 136 | 19:00 | 125 | 8:00 | Dohazari | 127 | 0.041667 | 122 | 0.375
| Rahim steal | 132 | 1:00 | 128 | 8:00 | Cox'sbazar | 116 | 0.125 | 108 | 0.875
| Matuail | 133 | 2:00 | 128 | 7:00 | Chandraghona | 131 | 0.041667 | 123 | 0.58333
| Ghorasal | 136 | 1:00 | 135 | 8:00 | Kaptai | 130 | 0.041667 | 125 | 0.29167
| Narsinghdi | 133 | 8:00 | 122 | 23:00 | A. Khaer Stl. | 128 | 0.041667 | 123 | 0.66667
| Haripur (SBU) | 133 | 3:00 | 127 | 11:00 | Bakulia | 131 | 0.041667 | 124 | 0.58333
| Sreenagar |  |  |  |  | Julda | 132 | 0.16667 | 126 | 0.58333
| Ullon | 132 | 4:00 | 126 | 10:00 | TK Chemical | 133 | 0.125 | 125 | 0.41667
| Hasnabad | 135 | 1:00 | 126 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 131 | 4:00 | 124 | 14:00 | Shahmirpur | 133 | 0.041667 | 125 | 0.58333
| Maniknagar | 133 | 1:00 | 128 | 10:00 | Khagrachhari | 130 | 0.041667 | 123 | 0.54167
| Bangabhaban | 133 | 1:00 | 128 | 10:00 | Matarbari | 120 | 0.70833 | 111 | 0.875
| Narinda | 133 | 1:00 | 128 | 10:00 | Baroiar Hat | 132 | 0.041667 | 126 | 0.58333
| Dhanmondi | 132 | 4:00 | 126 | 10:00 | Rangamati | 130 | 0.041667 | 123 | 0.58333
| Lalbag | 134 | 18:30 | 125 | 9:00 | Goalpara S/S | 138 | 18:30 | 123 | 19:30
| Madartek | 131 | 1:00 | 125 | 13:00 | Khulna Central S/S | 137 | 14:00 | 122 | 19:30
| Dhaka University | 132 | 1:00 | 125 | 13:00 | Noapara | 135 | 14:00 | 120 | 0.8125
| Aftabnagar | 132 | 1:00 | 125 | 13:00 | Jessore | 127 | 18:00 | 110 | 0.8125
| Fatullah | 132 | 1:00 | 127 | 8:00 | Benapol | 127 | 14:00 | 109 | 0.8125
| Nawabganj | 126 | 2:00 | 122 | 9:00 | Jhenida | 123 | 11:00 | 103 | 0.91667
| Mirpur | 132 | 3:00 | 126 | 12:00 | Bottail | 129 | 0.33333 | 118 | 0.83333
| Kalyanpur | 133 | 3:00 | 129 | 12:00 | G.K Project | 138 | 6:00 | 131 | 0.8125
| Gulshan | 130 | 3:00 | 126 | 12:00 | Faridpur | 133 | 0.41667 | 125 | 0.875
| Uttara | 132 | 3:00 | 126 | 12:00 | Madaripur | 139 | 0.77083 | 132 | 0.91667
| Uttara New | 133 | 3:00 | 126 | 12:00 | Shariyatpur S/S | 138 | 0.25 | 129 | 0.91667
| Kamrangirchar | 131 | 3:00 | 126 | 12:00 | Gopalganj | 143 | 0.25 | 132 | 0.875
| Savar | 134 | 3:00 | 129 | 12:00 | Bagerhat | 134 | 11:00 | 116 | 0.8125
| Bhasantec | 131 | 3:00 | 125 | 12:00 | Mongla | 134 | 0.77083 | 116 | 0.83333
| Agargaon | 132 | 3:00 | 127 | 12:00 | Satkhira | 136 | 18:30 | 118 | 0.8125
| Satmosjid | 131 | 3:00 | 126 | 12:00 | Gallamari | 137 | 11:00 | 124 | 0.8125
| Tongi | 133 | 1:00 | 128 | 8:00 | Magura | 122 | 7:00 | 100 | 22:00
| Kabirpur | 133 | 5.00 | 128 | 15:00 | Narail | 122 | 0.25 | 99 | 22:00
| Basundhara | 133 | 3:00 | 126 | 8:00 | Chuadanga | 120 | 8:00 | 90 | 0.91667
| Manikganj | 136 | 18:30 | 130 | 8:00 | Borguna | 136 | 0.95833 | 128 | 0.041667
| Joydevpur | 137 | 13:00 | 129 | 9:00 | Barisal(N) | 138 | 6:00 | 131 | 0.58333
| New Tongi | 134 | 18:30 | 126 | 9:00 | Barisal (S) | 137 | 23:00 | 130 | 0.54167
| Kodda | 132 | 1:00 | 123 | 7.00 | Patuakhali(S) | 138 | 23:00 | 125 | 14:00
| Dhamrai | 131 | 4.00 | 126 | 9:00 | Bhandaria | 135 | 0.33333 | 125 | 0.58333
| Rajendrapur | 131 | 2:00 | 122 | 9:00 | Ishurdi | 135 | 0.5 | 125 | 0.041667
| Valuka | 121 | 6:00 | 109 | 19:30 | Ruppur Paromanobik | 135 | 0.083333 | 130 | 0.875
| Tangail | 128 | 6:00 | 118 | 21:00 | Natore | 135 | 18:30 | 128 | 20:00
| Mymensing | 125 | 6:00 | 113 | 19:00 | Bogra | 132 | 12:00 | 125 | 21:00
| Kishorganj | 127 | 6:00 | 117 | 21:00 | Noagaon | 125 | 17:00 | 117 | 21:00
| Netrokona | 124 | 7:00 | 108 | 19:30 | Rajshahi | 134 | 18:30 | 129 | 5:00
| Jamalpur | 134 | 12:00 | 124 | 9:00 | Rajshahi New | 135 | 18:30 | 128 | 20:00
| Sherpur | 131 | 12:00 | 121 | 9:00 | C.Nawabganj | 134 | 18:00 | 129 | 5:00
| Srimongal | 137 | 7:00 | 132 | 1:00 | Amnura | 134 | 16:00 | 124 | 5:00
| Shahjibazar | 135 | 7:00 | 129 | 21:00 | Pabna | 136 | 2:00 | 127 | 19:30
| Fenchuganj | 135 | 6:00 | 132 | 20:00 | Shahjadpur | 136 | 12:00 | 133 | 21:00
| Khulawara | 134 | 5:00 | 130 | 20:00 | Serajganj | 132 | 18:30 | 125 | 19:30
| Sylhet | 133 | 8:00 | 129 | 20:00 | Niyamatpur | 123 | 11:00 | 114 | 21:00
| Chatak | 131 | 5:00 | 126 | 20:00 | Joypurhat | 124 | 17:00 | 114 | 21:00
| Sunamganj | 131 | 7:00 | 124 | 20:00 | Sherpur(Bogura) | 131 | 4:00 | 126 | 19:00
| Biani Bazar | 131 | 5:00 | 125 | 19:30 | Mohastangor | 130 | 12:00 | 122 | 19:30
| Comilla(s) | 126 | 2:00 | 122 | 19:00 | Bangura | 134 | 18:30 | 129 | 19:30
| Comilla(n) | 136 | 19:30 | 132 | 7:00 | Rangpur | 128 | 5:00 | 112 | 20:00
| Chandpur | 137 | 10:00 | 132 | 19:00 | Lalmonirhat | 125 | 4:00 | 112 | 21:00
| Feni | 132 | 1:00 | 126 | 16:00 | Saidpur | 124 | 6:00 | 111 | 19:00
| Chowmuhani | 131 | 7:00 | 128 | 19:00 | Purbasadipur | 124 | 6:00 | 104 | 20:00
| Ashuganj | 136 | 6:00 | 132 | 23:00 | Thakurgaon | 125 | 5:00 | 100 | 19:00
| Daudkandi | 136 | 19:00 | 126 | 8:00 | Palashbari | 125 | 4:00 | 116 | 19:00
| B.Baria | 134 | 7:00 | 125 | 21:00 | Barapukuria | 130 | 5:00 | 120 | 19:00
| Ramganj | 132 | 6:00 | 127 | 21:00 | Panchagar | 125 | 5:00 | 105 | 19:00
| Chaddagram | 133 | 1:00 | 129 | 14:00 | Joldhaka | 125 | 6:00 | 105 | 19:00
| PHP | 132 | 1:00 | 125 | 14:00 | Kurigram | 125 | 5:00 | 107 | 21:00
| Kochua | 135 | 18:00 | 130 | 21:00 | Mithapukur | 126 | 0.20833 | 117 | 0.79167

## L-Curve
Date | 2021-04-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 290 | 9133 | 4196 | 13329 |  |  |  | QF-LDC-11
0:30 | 222.5 | 8861.5 | 4106 | 12967.5 | Date: | 2021-04-26
1:00 | 155 | 8590 | 4016 | 12606
1:30 | 81 | 8391.5 | 3971 | 12362.5
2:00 | 7 | 8193 | 3926 | 12119
2:30 | 23.5 | 8174.5 | 3979.5 | 12154 | [5 empty] | Gen. at Eve. Peak | 13777 | 13777 MW (21:00 )
3:00 | 40 | 8156 | 4033 | 12189 | [6 empty] | 21:00
3:30 | 65 | 8011.5 | 3926.5 | 11938 | [5 empty] | Gen. at Day Peak | 11508 | 11508 MW (12:00 )
4:00 | 90 | 7867 | 3820 | 11687 | [6 empty] | 12:00
4:30 | 92.5 | 7608 | 3605 | 11213 | [5 empty] | Highest Generation | 13777
5:00 | 95 | 7349 | 3390 | 10739 | [6 empty] | 21:00
5:30 | 112.5 | 7124 | 3290.5 | 10414.5
6:00 | 130 | 6899 | 3191 | 10090
6:30 | 179 | 6835 | 3185 | 10020
7:00 | 228 | 6771 | 3179 | 9950
7:30 | 229 | 6841 | 3184.5 | 10025.5
8:00 | 230 | 6911 | 3190 | 10101
8:30 | 301 | 6992.5 | 3259 | 10251.5
9:00 | 372 | 7074 | 3328 | 10402
9:30 | 340 | 7274 | 3358.5 | 10632.5
10:00 | 308 | 7474 | 3389 | 10863
10:30 | 296 | 7579 | 3431.5 | 11010.5
11:00 | 284 | 7684 | 3474 | 11158
11:30 | 318 | 7814 | 3519 | 11333
12:00 | 352 | 7944 | 3564 | 11508
12:30 | 348 | 8012.5 | 3659 | 11671.5
13:00 | 344 | 8081 | 3754 | 11835
13:30 | 425.5 | 8193.5 | 3802 | 11995.5
14:00 | 507 | 8306 | 3850 | 12156
14:30 | 458.5 | 8389.5 | 3920.5 | 12310
15:00 | 410 | 8473 | 3991 | 12464
15:30 | 391 | 8349.5 | 3929.5 | 12279
16:00 | 372 | 8226 | 3868 | 12094
16:30 | 357 | 8171 | 3783 | 11954
17:00 | 342 | 8116 | 3698 | 11814
17:30 | 243 | 8054.5 | 3679 | 11733.5
18:00 | 144 | 7993 | 3660 | 11653
18:30 | 119.5 | 8463 | 3906 | 12369
19:00 | 95 | 8933 | 4152 | 13085
19:30 | 52 | 9010 | 4390 | 13400
20:00 | 92 | 9017 | 4388 | 13405 |  |  |  | Executive Engineer
20:30 | 126 | 9169.5 | 4421.5 | 13591 |  |  |  | Network Operation Division
21:00 | 160 | 9322 | 4455 | 13777
21:30 | 207 | 9324.5 | 4395 | 13719.5
22:00 | 254 | 9327 | 4335 | 13662 |  |  |  |  | Page 6 of 7
22:30 | 216 | 9291.5 | 4324.5 | 13616
23:00 | 178 | 9256 | 4314 | 13570
23:30 | 234 | 9194.5 | 4255 | 13449.5
24:00 | 290 | 9133 | 4196 | 13329
13777 MW (21:00 )
11508 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-26 |  | Energy | 289775067
[11 empty] | 2021-04-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4673 | 725 | 1963 | 4677 | 773 | 35 | 511 | 0 | 156 | 0
0:30 | 4632 | 724.5 | 1997 | 4210.5 | 788 | 35 | 519.5 | 0 | 153 | 0 | Date: | 2021-04-26
1:00 | 4591 | 724 | 2031 | 3744 | 803 | 35 | 528 | 0 | 150 | 0
1:30 | 4618.5 | 724 | 2022.5 | 3526.5 | 803 | 35 | 485 | 0 | 148 | 0 | [7 empty] | Total Energy | 289.7751 | Total Energy Gen 289.775 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 289.775 MKWHr
2:00 | 4646 | 724 | 2014 | 3309 | 803 | 35 | 442 | 0 | 146 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4725.5 | 724.5 | 2028.5 | 3276.5 | 803.5 | 35 | 416.5 | 0 | 144 | 0 | [7 empty] | Energy Requirement | 289.7751
3:00 | 4805 | 725 | 2043 | 3244 | 804 | 35 | 391 | 0 | 142 | 0
3:30 | 4781.5 | 725 | 2034.5 | 3106.5 | 803.5 | 35 | 310 | 0 | 142 | 0 | [6 empty] | Shortage
4:00 | 4758 | 725 | 2026 | 2969 | 803 | 35 | 229 | 0 | 142 | 0
4:30 | 4776 | 724.5 | 2023 | 2599.5 | 803 | 35 | 116 | 0 | 136 | 0
5:00 | 4794 | 724 | 2020 | 2230 | 803 | 35 | 3 | 0 | 130 | 0
5:30 | 4748 | 724.5 | 1969.5 | 2024 | 783.5 | 35 | 3 | 0 | 125 | 2
6:00 | 4702 | 725 | 1919 | 1818 | 764 | 35 | 3 | 0 | 120 | 4
6:30 | 4728.5 | 724.5 | 1894 | 1743 | 764 | 35 | 3 | 0 | 115 | 13 |  |  |  |  | Coal
7:00 | 4755 | 724 | 1869 | 1668 | 764 | 35 | 3 | 0 | 110 | 22
7:30 | 4797 | 724.5 | 1874.5 | 1677 | 764.5 | 35 | 3.5 | 0 | 113 | 36.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4839 | 725 | 1880 | 1686 | 765 | 35 | 4 | 0 | 116 | 51
8:30 | 4774.5 | 725 | 1927 | 1844 | 765 | 35 | 4 | 0 | 120 | 57
9:00 | 4710 | 725 | 1974 | 2002 | 765 | 35 | 4 | 0 | 124 | 63
9:30 | 4686 | 724.5 | 1976 | 2222 | 765 | 35 | 12 | 0 | 135 | 77
10:00 | 4662 | 724 | 1978 | 2442 | 765 | 35 | 20 | 0 | 146 | 91
10:30 | 4629.5 | 724 | 1961 | 2578.5 | 764.5 | 35 | 76.5 | 0 | 142 | 99.5
11:00 | 4597 | 724 | 1944 | 2715 | 764 | 35 | 133 | 0 | 138 | 108
11:30 | 4567 | 724.5 | 1945.5 | 2847 | 764 | 35 | 198 | 0 | 141 | 111
12:00 | 4537 | 725 | 1947 | 2979 | 764 | 35 | 263 | 0 | 144 | 114
12:30 | 4574 | 724.5 | 1963 | 3056 | 768.5 | 35 | 292.5 | 0 | 146 | 112
13:00 | 4611 | 724 | 1979 | 3133 | 773 | 35 | 322 | 0 | 148 | 110
13:30 | 4611 | 724 | 1979 | 3133 | 773 | 35 | 322 | 0 | 148 | 110
14:00 | 4611 | 724 | 1979 | 3133 | 773 | 35 | 322 | 0 | 148 | 110
14:30 | 4557.5 | 724 | 1912.5 | 3571.5 | 763.5 | 35 | 348 | 0 | 150 | 87.5
15:00 | 4504 | 724 | 1846 | 4010 | 754 | 35 | 374 | 0 | 152 | 65
15:30 | 4562 | 724 | 1829.5 | 3783 | 754.5 | 35 | 384.5 | 0 | 151 | 55.5
16:00 | 4620 | 724 | 1813 | 3556 | 755 | 35 | 395 | 0 | 150 | 46
16:30 | 4554.5 | 724 | 1816 | 3465 | 760.5 | 35 | 419 | 0 | 147 | 33
17:00 | 4489 | 724 | 1819 | 3374 | 766 | 35 | 443 | 0 | 144 | 20
17:30 | 4471 | 724 | 1696.5 | 3436 | 756 | 35 | 457.5 | 0 | 146 | 11.5
18:00 | 4453 | 724 | 1574 | 3498 | 746 | 35 | 472 | 0 | 148 | 3
18:30 | 4526.5 | 724 | 1715 | 3963 | 751 | 35 | 501 | 0 | 152 | 1.5
19:00 | 4600 | 724 | 1856 | 4428 | 756 | 35 | 530 | 0 | 156 | 0
19:30 | 4549 | 725 | 1938 | 4630 | 826 | 35 | 541 | 0 | 156 | 0
20:00 | 4538 | 724 | 1909 | 4687 | 825 | 35 | 537 | 0 | 150 | 0
20:30 | 4640.5 | 724 | 1955.5 | 4724 | 820 | 35 | 537 | 0 | 155 | 0
21:00 | 4743 | 724 | 2002 | 4761 | 815 | 35 | 537 | 0 | 160 | 0
21:30 | 4755.5 | 724 | 1980.5 | 4723.5 | 809 | 35 | 534 | 0 | 158 | 0
22:00 | 4768 | 724 | 1959 | 4686 | 803 | 35 | 531 | 0 | 156 | 0
22:30 | 4726 | 724.5 | 1965.5 | 4681.5 | 803 | 35 | 521.5 | 0 | 159 | 0
23:00 | 4684 | 725 | 1972 | 4677 | 803 | 35 | 512 | 0 | 162 | 0
23:30 | 4678.5 | 725 | 1967.5 | 4677 | 788 | 35 | 511.5 | 0 | 159 | 0 | Max Temp. in Dhaka |  | 39.4° C
24:00 | 4673 | 725 | 1963 | 4677 | 773 | 35 | 511 | 0 | 156 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
Total Energy Gen 289.775 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 289.775 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 848000
3 | Chattogram TPP-1 | [16 empty] | 10 | 30 |  | 40 | 60 | 70 | 80 | 80 | 80 | 80 | 500000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 17 | 16 | 16 | 16 | 17 | 17 | 409204
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 9 | 4 | 9 | 19 | 19 | 18 | 16 |  | 6 | 2 | 1 | [8 empty] | 120150
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 214 | 202 | 203 | 203 | 216 | 216 | 204 | 227 | 204 | 204 | 206 | 211 | 207 | 204 | 203 | 215 |  | 202 | 203 | 203 | 208 | 208 | 205 | 204 | 4920381
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 105 | 105 | 120 | 120 | 2788406
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 66 | 66 | 66 | 66 | [6 empty] | 34 | 32 | 32 | 32 | 32 | 32 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 971970
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 95 | 48 | 34 | 50 | 96 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2393672
| Daudkandi 200 MW PP (B.Trac) | 100 | [12 empty] | 30 | 177 | 150 |  |  |  | 162 | 185 | 185 | 185 | 185 | 185 | 185 | 1488000
14 | Titas 50 MW Peaking PP | 48 | 48 | 48 | [10 empty] | 47 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 668104
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 150 | 150 | 145 | 150 | 120 | 120 | 120 | 150 | 150 | 150 | 175 | 175 | 175 | 85 | 85 | 140 | 120 |  | 180 | 145 | 95 | 185 | 150 | 145 | 145 | 3653000
17 | Siddhirganj 335 MW CCPP | 218 | 220 | 220 | 222 | 222 | 222 | 222 | 222 | 217 | 211 | 204 | 201 | 200 | 197 | 197 | 203 | 205 | 171 |  | 210 | 213 | 180 | 215 | 218 | 218 | 222 | 5164966
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 5 | 29 | 47 | 70 | 92 | 97 |  | 122 | 145 | 175 | 193 | 195 | 195 | 200 | 1455272
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 38 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 736000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 |  | 70 | 10 |  |  |  |  | 0 | 1947542
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [17 empty] | 45 |  | 70 | 80 | 90 | 90 | 90 | 90 | 90 | 520936
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 20 | 26 | 22 | 22 | 20 | 22 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 508680
33 | Ashuganj 225 MW CCPP | 173 | 170 | 181 | 209 | 213 | 214 | 195 | 203 | 183 | 183 | 181 | 184 | 176 | 153 | 179 | 173 | 173 | 163 |  | 150 | 151 | 205 | 194 | 203 | 210 | 213 | 4535000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 315 | 300 | 310 | 300 | 310 | 330 | 310 | 300 | 300 | 300 | 310 | 315 | 305 | 315 | 305 | 320 |  | 295 | 295 | 295 | 310 | 325 | 305 | 300 | 7457000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 315 | 300 | 310 | 300 | 285 | 305 | 280 | 275 | 270 | 270 | 285 | 325 | 325 | 330 | 320 | 340 |  | 310 | 310 | 310 | 330 | 340 | 315 | 310 | 7732500
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 40 | 52 | 55 | 55 | 55 | 1037280
36 | Chandpur 150 MW CCPP | 93 | 95 | 95 | 95 | 94 | 94 | 95 | 94 | 94 | 94 | 94 | 94 | 95 | 96 | 96 | 95 | 95 | 95 |  | 95 | 96 | 95 | 96 | 95 | 95 | 95 | 2235650
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [14 empty] | 4 | 121 | [9 empty] | 0 | 195262
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 6835550
41 | Haripur 360MW CCPP(HPL) | 346 | 344 | 346 | 347 | 348 | 302 | 302 | 302 | 342 | 338 | 338 | 335 | 324 | 323 | 233 | 233 | 263 | 263 |  | 291 | 312 | 307 | 301 | 297 | 300 | 311 | 7446000
42 | RPCL 210MW CCPP | 188 | 200 | 194 | 199 | 202 | 205 | 205 | 200 | 196 | 184 | 174 | 174 | 155 | 159 | 160 | 158 | 144 | 142 |  | 153 | 165 | 166 | 165 | 165 | 166 | 169 | 4150880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 10 | 23 | 35 | 43 | 49 | 51 | 48 | 40 | 33 | 21 | 9 | 1 | [8 empty] | 364300
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 41 | 41 |  | 41 | 41 | 41 | 42 | 42 | 43 | 43 | 993600
46 | Shajibazar 330 MW CCPP | 268 | 268 | 271 | 268 | 268 | 268 | 275 | 274 | 270 | 271 | 273 | 265 | 262 | 263 | 261 | 262 | 265 | 265 |  | 268 | 270 | 270 | 272 | 270 | 273 | 270 | 6141000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 67 | 68 | 68 | 68 | 68 | 67 | 64 | 64 | 62 | 62 | 49 | 50 | 50 | 62 | 61 | 52 | 40 |  | 64 | 64 | 64 | 64 | 65 | 65 | 68 | 1495680
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 76 | 73 | 70 | 70 | 70 | 70 | 71 | 71 | 20 |  | 78 | 78 | 76 | 76 | 77 | 78 | 78 | 1771200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 225 | 225 | 225 | 226 | 226 | 225 | 225 | 225 | 225 | 226 | 225 | 219 | 219 | 212 | 212 | 210 | 184 |  | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 5286749
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 403000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 6 | 6 | 8 | 8 | 9 | 9 | 9 | 9 |  | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 191700
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 8 | 8 | 8 | 11 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243100
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 48 | 46 | 48 | 53 | 52 | 14 |  | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 1206600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 349176
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 310 | 300 | 305 | 305 | 310 | 320 | 310 | 305 | 305 | 300 | 305 | 305 | 300 | 310 | 305 | 290 |  | 280 | 305 | 300 | 315 | 310 | 310 | 300 | 7497000
| Bibiyana South 400 MW | 370 | 370 | 377 | 369 | 370 | 370 | 400 | 387 | 373 | 378 | 370 | 370 | 380 | 375 | 375 | 370 | 370 | 380 |  | 370 | 370 | 370 | 380 | 393 | 370 | 370 | 8960300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 15 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1271399
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 23 | 23 | 23 | 23 | 11 | 17 | 18 | 18 | 20 | 24 | 24 | 23 | 22 | 17 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 518880
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 499728
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 |  |  |  |  | 22 | 22 | 22 | 22 | 384552
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 414108
63 | Impoprt (Tripura) | 150 | 146 | 142 | 142 | 130 | 120 | 110 | 116 | 124 | 146 | 138 | 144 | 148 | 158 | 152 | 150 | 144 | 148 |  | 156 | 156 | 150 | 160 | 156 | 162 | 156 | 3425280
64 | Malancha, Ctg. EPZ (United) | 29 | 29 | 36 | 34 | 38 | 31 | 6 | 3 | 2 | 2 | 2 | 2 | 9 | 3 | 2 | 3 | 7 | 8 |  | 12 | 19 | 21 | 26 | 29 | 33 | 30 | 420480
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 18 | 18 | 18 | 18 | 16 | 16 | 19 | 19 | 19 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 468900
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243360
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 31 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 505100
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 22 | 24 | 24 | 24 | 24 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 23 |  | 18 | 24 | 24 | 24 | 27 | 27 | 28 | 550620
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 764200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 | 8 | 8 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 800800
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 101 | 96 | 92 | 92 | 94 | 85 | 92 | 98 | 54 |  | 100 | 101 | 101 | 102 | 102 | 102 | 102 | 2282227
| Feni Lanka Power | 114 | 17 | 17 | [7 empty] | 17 | 38 | 98 | 114 | 114 | 114 | 88 | 88 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1539000
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 55 | 55 | 55 | 75 | 96 | 110 | 110 | 110 | 113 | 110 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2592240
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 35 | 17 | 17 | 17 | 46 | 121 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3320640
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 70 | 70 | 70 | 70 | 30 | 30 | 30 | 40 | 70 | 74 | 94 | 94 | 98 | 98 | 98 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 97 | 2005344
78 | Gazipur 52 MW PP | 51 | 51 | 32 | [5 empty] | 2 | 23 | 19 | 50 | 49 | 49 | 49 | 47 | 47 | 47 |  | 45 | 50 | 50 | 50 | 50 | 50 | 50 | 846240
79 | Kodda 150MW PP | 150 | 64 | 48 | [6 empty] | 16 | 82 | 140 | 148 | 147 | 147 | 147 | 146 | 146 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2239200
80 | Jamalpur 95 MW PP(Powerpac) | 70 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 65 | 65 | 73 | 65 | 57 | 57 | 57 | 57 | 57 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1646400
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 50 | 43 | 43 | 50 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1236700
| Gazipur 100 MW PP | 102 | 102 | 102 | 85 | 50 | 17 | 17 | 54 | 75 | 86 | 86 | 80 | 78 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1900800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 33121
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 37 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 957657
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 235 | 240 | 240 | 245 | 245 | 240 | 235 | 245 | 237 | 247 | 240 | 248 | 250 | 247 | 240 | 238 | 246 | 248 |  | 245 | 240 | 250 | 245 | 250 | 245 | 240 | 5528698
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 60 | 7 | 7 | 7 | 26 | 60 | 87 | 90 | 89 | 95 | 96 | 96 | 97 | 98 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1936320
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 75 | 36 | 17 | 17 | 40 | 89 | 89 | 88 | 89 | 89 | 89 | 88 | 89 | 89 |  | 89 | 89 | 89 | 89 | 89 | 89 | 90 | 1895040
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 80 | 92 | 92 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 1428360
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) |  |  |  |  | 1 | 2 | 2 | 3 | 12 | 19 | 17 | 19 | 15 | 18 | 22 | 22 | 22 | 26 |  | 31 | 38 | 40 | 43 | 43 | 43 | 49 | 455837
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 |  |  |  |  | 16 | 40 | 50 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1856880
95 | Patenga 50MW PP (Baraka) | 50 | [8 empty] | 11 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 38 |  | 38 | 38 | 39 | 43 | 42 | 39 | 39 | 663360
96 | Chattogram 108 MW PP (ECPV) | 90 | 84 | 55 | 50 |  |  |  |  | 1 | 11 | 12 | 12 | 13 | 17 | 72 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1258560
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1238167
100 | Manikganj 55 MW PP (Northern) | 37 | 37 | 17 | 17 |  |  |  |  | 17 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 828575
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 110 | 130 | 130 |  | 130 | 130 | 110 | 163 | 130 | 130 | 130 | 3566045
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 13350
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 874800
104 | Keranigonj 300 MW PP (APR) | [13 empty] | 122 | 260 |  |  |  |  | 300 | 305 | 305 | 300 | 300 | 306 | 181 | 1969069
105 | Bramhangoan 100 MW PP (Aggreko) | [13 empty] | 8 | 95 |  |  |  |  | 97 | 100 | 100 | 100 | 100 | 100 | 100 | 738516
106 | Mymensingh 200 MW PP (United) | 199 | 160 | 160 | 80 | 40 |  |  |  |  | 4 | 62 | 131 | 168 | 178 | 180 | 182 | 192 | 196 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 3249600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 139 | 138 | 133 | 131 | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 138 | 145 | 141 | 140 | 149 | 134 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 140 | 3489120
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 90 | 100 | 100 |  | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 2355840
116 | Chandpur 200MW (Desh energy) | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 154 | 141 | 141 | 159 | 158 | 158 | 158 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 3788160
117 | Ashuganj 150MW PP (Midland) | 1 | 1 | 1 | [11 empty] | 4 | 10 | 18 | 28 |  | 35 | 35 | 33 | 40 | 43 | 53 | 61 | 334545
118 | Bibiyana-III 400 MW CCPP | 366 | 365 | 379 | 370 | 365 | 364 | 374 | 411 | 372 | 369 | 366 | 368 | 380 | 397 | 380 | 383 | 376 | 326 |  | 367 | 367 | 368 | 377 | 399 | 371 | 367 | 9016000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 109 | 115 | 115 | 115 | 115 | 115 | 115 | 105 | 95 | 104 | 103 | 103 | 104 | 114 | 115 |  | 106 | 106 | 115 | 115 | 115 | 108 | 108 | 2635200
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2224320
| Anlima Energy Ltd. | 111 | 111 | 111 | 111 | 35 | 35 |  |  |  |  | 15 | 35 | 44 | 74 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1678582
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 34 | 34 | 33 | 35 | 35 | 10 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 836640
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 14 | 16 | 27 | 28 | 31 | 30 | 27 | 21 | 13 | 6 | 1 | [8 empty] | 220811
120 | Eastern Zone Total | 8590 | 8193 | 8156 | 7867 | 7349 | 6899 | 6771 | 6911 | 7074 | 7474 | 7684 | 7944 | 8081 | 8306 | 8473 | 8226 | 8116 | 7993 |  | 8933 | 9010 | 9017 | 9322 | 9327 | 9256 | 9133 | 196319081
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 70 | 83 |  | 83 | 83 | 83 | 83 | 99 | 99 | 99 | 1835520
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 19 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 6 | 5 | 2 | 2 | 2 | 2 | 11 |  | 17 | 20 | 20 | 18 | 18 | 14 | 14 | 212480
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 53 |  |  |  | 51 | 53 | 72 | 71 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 1733280
130
131
132 | United Payra Power Ltd. | [19 empty] | 10 | 54 | 54 | 89 | 89 | 89 | 72 | 397200
133 | Bhola Nutan Biddut BD LTD (GAS) | [12 empty] | 33 | 59 | 58 | 38 | 7 | [9 empty] | 252791
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 96 | 96 | 96 | 64 | 16 | [8 empty] | 16 | 16 | 16 | 16 | 64 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1142880
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 96 | 96 | 95 | 96 | 71 | 72 | 71 | 85 | 95 | 94 | 93 | 94 | 94 | 95 | 97 | 97 |  | 97 | 97 | 96 | 96 | 96 | 96 | 96 | 2222720
| Bhola 225 MW CCPP | 67 | 67 | 67 | 67 | 65 | 65 | 67 | 66 | 65 | 64 | 62 | 61 | 62 | 62 | 63 | 63 | 63 | 64 |  | 66 | 67 | 67 | 67 | 68 | 67 | 66 | 1568000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 34 | 28 | 28 | 23 | 22 | 24 | 24 | 21 | 25 | 26 | 22 | 22 | 20 | 23 | 34 |  | 34 | 34 | 32 | 34 | 34 | 34 | 34 | 670065
141 | Noapara 100 MW PP (Bangla Trac) | 100 | [12 empty] | 19 | 99 | 50 | 20 | 20 |  | 67 | 97 | 97 | 98 | 98 | 97 | 98 | 952320
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | [8 empty] | 8 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 468000
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 8 | [14 empty] | 4999
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 724 | 724 | 725 | 725 | 724 | 725 | 724 | 725 | 725 | 724 | 724 | 725 | 724 | 725 | 724 | 724 | 724 | 724 |  | 724 | 725 | 724 | 724 | 724 | 725 | 725 | 17505455
147 | Bheramara 410 MW CCPP | 350 | 350 | 380 | 355 | 360 | 355 | 390 | 405 | 375 | 370 | 360 | 360 | 390 | 385 | 380 | 370 | 360 | 350 |  | 345 | 345 | 345 | 340 | 330 | 315 | 315 | 8911296
148 | Payra 1320 MW | 580 | 580 | 580 | 580 | 580 | 540 | 540 | 540 | 540 | 540 | 540 | 540 | 550 | 580 | 530 | 530 | 540 | 520 |  | 530 | 600 | 600 | 590 | 580 | 580 | 550 | 14373800
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 74 | 73 | 73 | 74 | 74 | 75 | 75 | 75 | 74 | 74 | 73 | 73 | 74 | 75 | 76 | 76 |  | 76 | 76 | 75 | 75 | 73 | 73 | 73 | 1776436
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3687600
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 60 | 50 | 40 | [16 empty] | 0 | 565000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | [6 empty] | 13 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 855520
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 145 | 146 | 145 | 147 | 148 | 148 | 148 | 147 | 146 | 144 | 142 | 117 | 131 | 131 | 137 | 134 | 127 | 122 |  | 127 | 120 | 121 | 129 | 131 | 128 | 117 | 3385500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 189 | 186 | 194 | 188 | 187 | 170 | 159 | 170 | 180 | 188 | 187 | 178 | 176 | 179 | 164 | 168 | 163 | 158 |  | 171 | 175 | 176 | 171 | 170 | 169 | 171 | 4437882
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 42 | 79 | 165 | 181 | 186 | 163 | 160 | 171 | 192 | 200 | 198 | 173 | 187 | 186 | 190 | 192 | 180 | 171 |  | 177 | 167 | 171 | 185 | 180 | 192 | 194 | 4359827
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 417 | 412 | 421 | 415 | 405 | 388 | 388 | 391 | 418 | 414 | 386 | 399 | 401 | 395 | 418 | 402 | 380 | 274 |  | 385 | 406 | 408 | 415 | 410 | 414 | 400 | 9545000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 35 | 35 | [12 empty] | 10 | 31 | 35 | 39 |  | 39 | 40 | 38 | 41 | 34 | 20 | 20 | 418040
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 19 | 19 | 20 | 21 | 435840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 10 | 10 | 10 | 11 | 11 | 258858
165 | Amnura 50 MW PP(Sinha) | 12 | [9 empty] | 4 | 12 | 18 | 42 | 42 | 42 |  |  |  |  | 42 | 42 | 42 | 42 | 42 | 42 | 394630
166 | Katakhali 50 MW PP (Northern) | [14 empty] | 43 | 43 |  | 24 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 336638
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 12 | [7 empty] | 27 | 30 | 30 | 29 | 29 |  |  |  | 24 | 31 | 31 | 30 | 30 | 30 | 30 | 383500
168 | Santahar 50 MW Peaking PP | 32 | 32 | 32 | [14 empty] | 13 |  | 34 | 34 | 32 | 32 | 33 | 32 | 31 | 313840
169 | Natore 52 MW PP (Rajlanka) | 52 | 44 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1234560
170 | Chapainawabganj 100 MW Peaking PP | 98 | 98 | 98 | 98 | [8 empty] | 57 | 57 | 56 | 56 | 94 | 97 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1380440
171 | Baghabari 200 MW PP (Paramount) | [14 empty] | 50 |  |  |  |  | 170 | 200 | 200 | 200 | 100 | 100 | 50 | 882594
| Bagura 113 MW PP (Confidence)-2 | 95 | 95 | 95 | 95 |  |  |  |  | 14 | 52 | 87 | 108 | 99 | 95 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 113 | 113 | 113 | 113 | 1921344
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 50 |  |  |  |  | 25 | 35 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2074368
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 85 | 54 | 54 | 50 | 79 | 113 | 113 | 113 | 111 | 110 | 109 | 110 | 110 | 110 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2506560
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 6 | 6 | 6 | 7 | 7 | 6 | 3 | 2 | 0 | [8 empty] | 51203
178
178