## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-04-28 | Wednesday
|  |  | Date (day): | 2021-04-28 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14468.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15398 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-04-27 | 2021-04-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 97 | 102 | 100 | 102
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 273 | 283 | 283 | 129
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 303 | 188 | 345 | 345
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 290 | 290 | 300 | 300 | 150
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 99 | 99 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 240 | 275 | 250 | 250 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Project work
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 145 | 185 | 150 | 180
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 182 | 215 | 220 | 220 |  | 115 | ST Under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 140 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 53 | 50 | 50 |  | 30 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 50 | 38 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 209 | 225 | 75 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 304 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 50 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Project work
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 145 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 87 | 85 | 85 |  | 20 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 89 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 145 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 31 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2887 | 3655 | 3411 | 3838 | 438 | 1403
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 80 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 16 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 37 | 45 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 35 | 35 | 35 | 35 | 195 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 228 | 230 | 230
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 99 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 33 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 20 | 10 | 20 | 20 | 80 |  | Fuel shortage
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 26 | 10 | 25
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 19 | 19 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 35 | 35 |  | 19 | Engine problem
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 32 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 114 | 90 | 90 |  | 26 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1067 | 1193 | 1620 | 1610 | 535 | 210
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 207 | 141 | 225 | 225 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 335 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 330 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 50 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 102 | 45 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 83 | 100 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 95 | 95 | 95 | 96 | 67 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 136 | 140 | 158 | 158 |  | 42 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 144 | 162 | 156 | 171
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 197 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1845 | 2160 | 2068 | 2284 | 615 | 88
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 162 | 152 | 177 | 177 | 25 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 72 | 81 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 139 | 200 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 96 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 555 | 590 | 659.6 | 608 | 25 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 0 | 0 |  | 70 | Under maint.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 41 | 42 | 42 |  | 48 | Engine problem
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 0 | 130 | 275 | 275
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 66 | 66
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 73 | 76 | 76 |  | 10 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 211 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 315 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 391 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 8 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 371 | 384 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1700 | 1875 | 2094 | 2094 | 0 | 237
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 725 | 629 | 737 | 737
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 10 | 20 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 160 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 210 | 400 | 400
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 32 | 32 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 91 | 91 | 90 | 91 |  | 14 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1261 | 1341 | 1588 | 1876 | 0 | 120
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 16 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 61 | 66 | 66 | 67 |  | 127 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 96 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 510 | 622 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 72 | 80 | 90
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 707 | 1000 | 1006 | 1017 | 0 | 127
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 43 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 40 | 45
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 33 | 42 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 16 | 43 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 30 | 30 |  | 20 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 80 | 89 | 80 | 80
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 154 | 180 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 196 | 158 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 397 | 413 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 32
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 10 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 40 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 200 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 1262 | 1641 | 1676 | 1733 | 171 | 35
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 73 | 75 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 330 | 337 | 346 | 338 | 124 | 125
|  | Total |  |  |  |  | 21967 | 21219 | 11614 | 13792 | 14468.6 | 15398 | 1908 | 2366
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11259.4833 | 13371 | 14026.9468 | 14927.9769
| A. |  | 2021-04-27 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 13792 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 10354 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 14097 | MW
| 3 | Day peak Generation : |  |  | 11614 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 13371 | MW
| 4 | Evening peak Generation : |  |  | 13792 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 295.4025 | MKWHr | By Solar | 0.74792 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 153.8565 | MKWHr |  | By Oil: | 99.5226 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 19.8908 | MKWHr |  | By Hydro: | 0.788 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1908 | MW | Dhaka | 4588 | 4543 |  | 45
|  |  |  | For Plants S/D or M/C prob = |  |  | 2366 | MW | Chittagong | 1348 | 1348 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4274 | MW | Khulna | 1708 | 1653 |  | 55 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1314 | MMCFD |  |  | Rajshahi | 1484 | 1447 |  | 37 |  | 19:00 |  | 119
| 8 | Fuel Cost : | i) Gas : | Taka | 168710633.002 | ii) Oil : | Taka | 786973470.33 | Comilla | 1328 | 1288 |  | 40 |  | 19:30 |  | 192
|  |  | iii) Coal : |  | 94309642.19 | Total | Taka | 1049993745.522 | Mymensingh | 1133 | 1089 |  | 44 |  | 20:00 |  | 275
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.4865 | MKWHr. | Sylhet | 545 | 545 |  | 0 |  | 21:00 |  | 273
|  | ii) During Peak Demand : |  |  | -398 | MW (E to W) at | 20:00 | hrs | Barisal | 392 | 392 |  | 0 |  | 22:00 |  | 231
|  | iii) Maximum : |  |  | -500 | MW at | 19:30 | hrs | Rangpur | 845 | 791 |  | 54 |  | 23:00 |  | 146
| 10 | Maximum Temperature in Dhaka was |  |  |  | 38.0° C |  |  | Total | 13371 | 13096 |  | 0
| B. |  | 2021-04-28 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 40.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14100 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15398 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1298 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 301.9994 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10603 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.04 | MKWHr. | ii) HVDC Flow at Peak Time |  | 629 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.5568 | MKWHr. | iii) Maximum HVDC Flow : |  | 725 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 77.51 |  | (b) Today: | 77.35 |  | (c) Rule Curve: |  | 82.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-04-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 332 |  | 0 | 290 | 230 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 80 | 0 | 17 | 203 | 0 | 130 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 30 | 0 | 0 | 90 | 310 | 300 | 212 | 8 | 92 | 23 | 56 | 0 | 49 | 0 | 48 | 49 | 22 | 11 | 33 | 20 | 152 | 182 | 65 | 19 | 0 | 0 | 43 | 50 | 0 | 110 | 271 | 67 | 78 | 0 | 217 | 18 | 0 | 9 | 295 | 16 | 11 | 185 | 235 | 81 | 100 | 200 | 0 | 134 | 0 | 100 | 158 | 73 | 367 | 108 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 90 | 0 | 162 | 90 | 0 | 35 | 0 |  | 725 | 0 | 305 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 68 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 113 | 0 | 175 | 0 | 96 | 98 | 186 | 0 | 342 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 550 | 0 | 0 | 72 |  | 9039 | 4066 | 13105 | 4647 | 725 | 1902 | 4360 | 773 | 35 | 511 | 152 | 0 | 0 | 77.54
2:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 347 |  | 0 | 290 | 230 | 100 | 0 | 50 | 221 | 0 | 116 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 0 | 35 | 80 | 0 | 17 | 203 | 0 | 130 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 30 | 0 | 0 | 90 | 310 | 300 | 212 | 8 | 95 | 23 | 56 | 0 | 49 | 0 | 48 | 49 | 20 | 11 | 33 | 20 | 150 | 184 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 110 | 270 | 68 | 78 | 0 | 217 | 18 | 0 | 9 | 290 | 16 | 5 | 50 | 235 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 158 | 73 | 380 | 108 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 90 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 310 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 67 | 34 | 110 | 0 | 0 | 0 | 0 | 20 | 100 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 113 | 0 | 177 | 0 | 96 | 98 | 160 | 0 | 346 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 530 | 0 | 0 | 72 |  | 8757 | 3979 | 12736 | 4634 | 724 | 1916 | 4063 | 753 | 35 | 461 | 150 | 0 | 0 | 77.53
3:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 347 |  | 0 | 290 | 235 | 100 | 0 | 44 | 221 | 0 | 110 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 28 | 33 | 33 | 51 | 0 | 0 | 35 | 80 | 0 | 17 | 203 | 0 | 130 | 0 |  | 23 | 0 | 68 | 20 | 90 | 39 | 21 | 38 | 0 | 0 | 90 | 310 | 300 | 213 | 8 | 91 | 23 | 57 | 0 | 49 | 0 | 48 | 52 | 20 | 11 | 33 | 20 | 150 | 187 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 110 | 270 | 68 | 78 | 0 | 217 | 18 | 0 | 9 | 295 | 16 | 5 | 50 | 235 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 158 | 78 | 366 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 114 | 113 | 100 | 370 | 90 | 0 | 162 | 90 | 0 | 35 | 0 |  | 724 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 68 | 34 | 110 | 0 | 0 | 0 | 0 | 20 | 99 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 125 | 0 | 178 | 0 | 96 | 97 | 160 | 0 | 408 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 108 | 530 | 0 | 0 | 72 |  | 8743 | 4053 | 12796 | 4611 | 724 | 1992 | 4071 | 753 | 35 | 460 | 150 | 0 | 0 | 77.53
4:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 348 |  | 0 | 290 | 225 | 100 | 0 | 55 | 222 | 0 | 116 | 100 | 102 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 26 | 33 | 33 | 51 | 0 | 0 | 0 | 80 | 0 | 17 | 213 | 0 | 120 | 0 |  | 21 | 0 | 68 | 20 | 90 | 39 | 21 | 38 | 0 | 0 | 90 | 310 | 300 | 216 | 8 | 95 | 23 | 57 | 0 | 49 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 150 | 187 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 110 | 271 | 68 | 78 | 0 | 217 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 160 | 0 | 0 | 120 | 0 | 149 | 0 | 100 | 158 | 80 | 372 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 76 | 113 | 100 | 370 | 90 | 0 | 162 | 90 | 0 | 35 | 0 |  | 725 | 0 | 325 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 68 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 99 | 0 | 0 | 30 | 52 | 32 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 126 | 0 | 179 | 0 | 96 | 0 | 160 | 0 | 409 | 92 | 0 | 113 | 0 | 106 | 0 | 0 | 108 | 530 | 0 | 0 | 72 |  | 8377 | 3857 | 12234 | 4640 | 725 | 1989 | 3647 | 754 | 0 | 329 | 150 | 0 | 0 | 77.52
5:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 350 |  | 0 | 290 | 220 | 100 | 0 | 55 | 222 | 0 | 118 | 100 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 26 | 33 | 33 | 0 | 0 | 0 | 35 | 80 | 0 | 17 | 205 | 0 | 120 | 0 |  | 22 | 0 | 68 | 20 | 69 | 26 | 21 | 38 | 0 | 0 | 100 | 310 | 300 | 216 | 8 | 94 | 23 | 57 | 0 | 49 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 140 | 193 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 110 | 272 | 68 | 78 | 0 | 215 | 18 | 0 | 9 | 295 | 16 | 5 | 0 | 45 | 0 | 0 | 40 | 0 | 149 | 0 | 100 | 158 | 80 | 367 | 115 | 85 | 105 | 0 | 0 | 35 | 0 | 30 | 113 | 100 | 370 | 90 | 0 | 108 | 90 | 0 | 35 | 0 |  | 725 | 0 | 345 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 69 | 33 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 125 | 0 | 180 | 0 | 96 | 0 | 160 | 0 | 404 | 53 | 0 | 50 | 0 | 106 | 0 | 0 | 50 | 530 | 0 | 0 | 35 |  | 7879 | 3531 | 11410 | 4687 | 725 | 1990 | 2942 | 753 | 35 | 138 | 140 | 0 | 0 | 77.52
6:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 351 |  | 0 | 290 | 230 | 28 | 0 | 55 | 222 | 0 | 110 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 80 | 0 | 17 | 208 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 27 | 0 | 21 | 30 | 0 | 0 | 100 | 310 | 300 | 207 | 8 | 95 | 23 | 57 | 0 | 40 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 130 | 204 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 163 | 0 | 67 | 78 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 45 | 0 | 0 | 40 | 0 | 149 | 1 | 100 | 158 | 73 | 380 | 115 | 70 | 105 | 0 | 0 | 35 | 0 | 17 | 113 | 50 | 384 | 62 | 2 | 54 | 35 | 0 | 35 | 1 |  | 725 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 68 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 130 | 0 | 180 | 0 | 96 | 0 | 160 | 0 | 404 | 35 | 0 | 50 | 0 | 106 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 7201 | 3331 | 10532 | 4438 | 725 | 2038 | 2317 | 723 | 35 | 122 | 130 | 4 | 0 | 77.51
7:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 0 | 350 |  | 0 | 290 | 225 | 16 | 0 | 55 | 222 | 0 | 120 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 80 | 0 | 17 | 206 | 0 | 120 | 0 |  | 23 | 0 | 68 | 20 | 25 | 0 | 21 | 10 | 0 | 0 | 100 | 330 | 320 | 200 | 8 | 96 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 130 | 202 | 73 | 19 | 0 | 0 | 43 | 50 | 0 | 163 | 0 | 66 | 78 | 0 | 217 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 4 | 90 | 158 | 75 | 380 | 115 | 70 | 105 | 1 | 0 | 35 | 0 | 17 | 113 | 50 | 395 | 53 | 9 | 54 | 35 | 0 | 35 | 5 |  | 724 | 0 | 340 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 124 | 0 | 178 | 0 | 96 | 0 | 160 | 0 | 418 | 17 | 0 | 35 | 0 | 106 | 0 | 1 | 0 | 500 | 0 | 0 | 0 |  | 7168 | 3302 | 10470 | 4479 | 724 | 2034 | 2203 | 723 | 35 | 122 | 130 | 20 | 0 | 77.51
8:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 348 |  | 0 | 290 | 240 | 16 | 0 | 55 | 222 | 0 | 120 | 55 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 24 | 33 | 33 | 0 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 |  | 0 | 0 | 68 | 20 | 25 | 1 | 21 | 2 | 0 | 0 | 100 | 310 | 300 | 180 | 8 | 95 | 23 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 5 | 33 | 20 | 132 | 197 | 67 | 19 | 1 | 0 | 43 | 50 | 0 | 163 | 0 | 66 | 78 | 0 | 217 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 149 | 6 | 90 | 158 | 74 | 365 | 115 | 80 | 105 | 2 | 0 | 35 | 0 | 17 | 113 | 100 | 370 | 58 | 21 | 54 | 40 | 0 | 35 | 13 |  | 725 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 25 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 132 | 0 | 177 | 0 | 96 | 0 | 160 | 0 | 402 | 17 | 0 | 35 | 0 | 106 | 0 | 2 | 20 | 480 | 0 | 0 | 0 |  | 7131 | 3223 | 10354 | 4363 | 725 | 2002 | 2236 | 702 | 35 | 114 | 132 | 45 | 0 | 77.5
9:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 343 |  | 0 | 290 | 245 | 62 | 0 | 55 | 220 | 0 | 118 | 90 | 72 | 10 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 24 | 33 | 33 | 2 | 0 | 0 | 35 | 80 | 0 | 17 | 216 | 0 | 120 | 0 |  | 11 | 0 | 0 | 20 | 20 | 17 | 21 | 2 | 0 | 0 | 100 | 325 | 310 | 178 | 8 | 95 | 20 | 56 | 0 | 51 | 0 | 0 | 45 | 21 | 5 | 33 | 20 | 134 | 189 | 73 | 19 | 1 | 0 | 43 | 50 | 0 | 163 | 0 | 65 | 78 | 0 | 218 | 18 | 0 | 7 | 295 | 16 | 5 | 0 | 11 | 0 | 0 | 40 | 0 | 149 | 8 | 90 | 145 | 66 | 379 | 115 | 88 | 105 | 0 | 0 | 35 | 0 | 17 | 113 | 100 | 370 | 90 | 33 | 54 | 72 | 0 | 35 | 19 |  | 725 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 66 | 18 | 16 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 176 | 0 | 94 | 0 | 160 | 0 | 402 | 52 | 0 | 101 | 0 | 106 | 0 | 3 | 35 | 480 | 0 | 0 | 0 |  | 7360 | 3281 | 10641 | 4344 | 725 | 1973 | 2606 | 705 | 35 | 55 | 134 | 64 | 0 | 77.49
10:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 333 |  | 0 | 290 | 238 | 91 | 0 | 55 | 215 | 0 | 180 | 100 | 84 | 48 | 0 | 0 | 0 | 0 | 35 | 37 | 55 | 22 | 25 | 24 | 33 | 33 | 19 | 0 | 0 | 35 | 80 | 0 | 17 | 221 | 0 | 120 | 0 |  | 24 | 0 | 0 | 20 | 20 | 24 | 21 | 2 | 0 | 0 | 100 | 345 | 330 | 181 | 8 | 95 | 23 | 52 | 0 | 51 | 0 | 0 | 48 | 18 | 5 | 33 | 20 | 132 | 179 | 72 | 19 | 1 | 0 | 43 | 50 | 0 | 163 | 0 | 65 | 75 | 0 | 218 | 18 | 0 | 7 | 315 | 16 | 5 | 0 | 106 | 0 | 0 | 53 | 0 | 149 | 8 | 90 | 141 | 73 | 400 | 107 | 88 | 105 | 4 | 0 | 35 | 10 | 24 | 110 | 100 | 389 | 90 | 40 | 94 | 75 | 0 | 35 | 23 |  | 725 | 0 | 325 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 64 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 173 | 0 | 95 | 0 | 174 | 0 | 404 | 53 | 0 | 113 | 0 | 0 | 0 | 5 | 50 | 480 | 0 | 0 | 0 |  | 7814 | 3232 | 11046 | 4483 | 725 | 1986 | 2807 | 705 | 35 | 92 | 132 | 81 | 0 | 77.48
11:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 313 |  | 0 | 290 | 230 | 91 | 0 | 40 | 215 | 0 | 185 | 100 | 102 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 46 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 20 | 19 | 26 | 21 | 2 | 0 | 0 | 100 | 300 | 300 | 192 | 8 | 95 | 23 | 51 | 0 | 43 | 0 | 0 | 52 | 18 | 5 | 33 | 20 | 140 | 164 | 64 | 19 | 2 | 0 | 43 | 48 | 0 | 163 | 0 | 63 | 74 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 197 | 0 | 0 | 98 | 0 | 149 | 16 | 75 | 141 | 72 | 368 | 115 | 88 | 105 | 5 | 0 | 35 | 17 | 85 | 110 | 100 | 370 | 90 | 40 | 144 | 114 | 0 | 35 | 31 |  | 725 | 0 | 325 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 32 | 62 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 40 | 18 | 16 | 0 | 52 | 0 | 17 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 80 | 0 | 171 | 0 | 95 | 0 | 198 | 0 | 388 | 92 | 0 | 113 | 0 | 60 | 0 | 6 | 70 | 500 | 0 | 0 | 0 |  | 8036 | 3452 | 11488 | 4359 | 725 | 1917 | 3330 | 724 | 35 | 158 | 140 | 100 | 0 | 77.47
12:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 303 |  | 0 | 290 | 240 | 99 | 0 | 40 | 182 | 0 | 145 | 100 | 102 | 140 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 0 | 16 | 50 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 |  | 24 | 0 | 33 | 20 | 19 | 37 | 21 | 2 | 0 | 0 | 100 | 300 | 300 | 207 | 8 | 95 | 23 | 50 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 144 | 162 | 72 | 19 | 2 | 0 | 43 | 44 | 0 | 163 | 0 | 62 | 76 | 0 | 218 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 209 | 0 | 0 | 139 | 0 | 145 | 17 | 90 | 136 | 75 | 367 | 96 | 88 | 99 | 5 | 0 | 35 | 17 | 114 | 110 | 100 | 371 | 89 | 41 | 145 | 116 | 0 | 35 | 31 |  | 725 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 10 | 0 | 32 | 61 | 24 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 33 | 16 | 0 | 52 | 0 | 20 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 80 | 0 | 171 | 0 | 96 | 0 | 196 | 0 | 397 | 91 | 0 | 113 | 0 | 100 | 0 | 7 | 90 | 510 | 0 | 0 | 0 |  | 8054 | 3560 | 11614 | 4217 | 725 | 1930 | 3461 | 733 | 35 | 266 | 144 | 103 | 0 | 77.46
13:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 290 |  | 0 | 290 | 248 | 98 | 0 | 40 | 208 | 0 | 185 | 100 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 80 | 0 | 17 | 217 | 0 | 120 | 0 |  | 23 | 0 | 66 | 20 | 19 | 41 | 21 | 13 | 0 | 0 | 0 | 335 | 320 | 207 | 8 | 96 | 26 | 50 | 0 | 51 | 0 | 21 | 52 | 0 | 0 | 33 | 20 | 152 | 157 | 72 | 19 | 2 | 0 | 43 | 45 | 0 | 163 | 0 | 62 | 72 | 0 | 218 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 202 | 0 | 0 | 183 | 0 | 138 | 17 | 100 | 121 | 80 | 396 | 96 | 88 | 105 | 4 | 0 | 36 | 17 | 114 | 109 | 100 | 371 | 89 | 47 | 162 | 115 | 0 | 35 | 29 |  | 724 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 11 | 0 | 32 | 62 | 26 | 16 | 0 | 0 | 0 | 50 | 15 | 40 | 42 | 16 | 27 | 52 | 0 | 20 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 80 | 0 | 169 | 0 | 96 | 0 | 196 | 0 | 402 | 90 | 0 | 113 | 0 | 102 | 0 | 7 | 113 | 550 | 0 | 0 | 0 |  | 8300 | 3687 | 11987 | 4328 | 724 | 1938 | 3555 | 772 | 35 | 377 | 152 | 106 | 0 | 77.45
14:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 77 | 243 |  | 0 | 290 | 260 | 98 | 0 | 40 | 204 | 0 | 178 | 91 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 80 | 0 | 16 | 222 | 0 | 120 | 0 |  | 24 | 0 | 64 | 10 | 19 | 45 | 21 | 3 | 0 | 0 | 0 | 335 | 310 | 199 | 45 | 96 | 25 | 47 | 0 | 51 | 0 | 48 | 52 | 0 | 5 | 33 | 20 | 156 | 157 | 72 | 19 | 2 | 0 | 40 | 47 | 0 | 163 | 105 | 60 | 69 | 0 | 210 | 18 | 0 | 7 | 305 | 16 | 5 | 0 | 194 | 0 | 0 | 193 | 0 | 138 | 15 | 100 | 120 | 90 | 399 | 96 | 88 | 105 | 4 | 0 | 54 | 17 | 114 | 106 | 100 | 373 | 89 | 43 | 162 | 115 | 0 | 35 | 26 |  | 724 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 11 | 0 | 32 | 61 | 26 | 32 | 0 | 0 | 0 | 50 | 42 | 40 | 42 | 34 | 29 | 52 | 0 | 17 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 120 | 0 | 165 | 0 | 94 | 0 | 194 | 0 | 398 | 90 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 560 | 0 | 0 | 0 |  | 8468 | 3791 | 12259 | 4510 | 724 | 1900 | 3623 | 783 | 35 | 431 | 156 | 97 | 0 | 77.44
15:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 217 | 203 |  | 0 | 290 | 260 | 96 | 0 | 40 | 210 | 0 | 180 | 97 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 80 | 0 | 16 | 224 | 0 | 120 | 0 |  | 21 | 0 | 48 | 10 | 19 | 45 | 21 | 6 | 0 | 0 | 0 | 325 | 305 | 204 | 45 | 95 | 25 | 46 | 0 | 51 | 0 | 48 | 52 | 11 | 11 | 33 | 20 | 158 | 145 | 81 | 19 | 1 | 0 | 40 | 47 | 0 | 163 | 104 | 60 | 69 | 0 | 212 | 18 | 0 | 6 | 300 | 16 | 5 | 0 | 202 | 0 | 0 | 194 | 0 | 138 | 12 | 100 | 120 | 88 | 374 | 95 | 88 | 105 | 3 | 0 | 54 | 17 | 114 | 108 | 100 | 378 | 90 | 33 | 162 | 116 | 0 | 35 | 20 |  | 725 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 11 | 0 | 32 | 63 | 22 | 32 | 0 | 0 | 0 | 50 | 40 | 40 | 42 | 34 | 29 | 52 | 15 | 18 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 129 | 0 | 160 | 0 | 96 | 0 | 190 | 0 | 405 | 90 | 0 | 113 | 0 | 110 | 0 | 5 | 113 | 600 | 0 | 0 | 17 |  | 8552 | 3848 | 12400 | 4622 | 725 | 1860 | 3677 | 821 | 35 | 428 | 158 | 74 | 0 | 77.43
16:00 | 0 | 0 | 0 | 180 | 0 | 94 | 0 | 245 | 200 |  | 0 | 290 | 265 | 97 | 0 | 40 | 206 | 0 | 180 | 100 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 16 | 228 | 0 | 120 | 0 |  | 22 | 0 | 45 | 10 | 19 | 45 | 21 | 7 | 0 | 0 | 0 | 315 | 295 | 206 | 81 | 91 | 25 | 45 | 0 | 51 | 0 | 48 | 52 | 19 | 11 | 33 | 20 | 150 | 149 | 64 | 19 | 1 | 0 | 41 | 44 | 0 | 163 | 105 | 62 | 69 | 0 | 212 | 18 | 0 | 8 | 270 | 16 | 5 | 88 | 209 | 0 | 0 | 194 | 0 | 145 | 7 | 100 | 130 | 90 | 368 | 115 | 88 | 105 | 2 | 0 | 54 | 15 | 114 | 113 | 100 | 370 | 89 | 18 | 162 | 116 | 0 | 35 | 12 |  | 725 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 11 | 0 | 32 | 65 | 28 | 32 | 0 | 0 | 0 | 50 | 40 | 40 | 42 | 34 | 29 | 52 | 33 | 19 | 0 | 11 | 71 | 0 | 149 | 0 | 0 | 128 | 0 | 164 | 0 | 97 | 27 | 190 | 0 | 374 | 90 | 0 | 113 | 0 | 110 | 0 | 3 | 113 | 622 | 0 | 0 | 17 |  | 8672 | 3900 | 12572 | 4645 | 725 | 1840 | 3849 | 842 | 35 | 443 | 150 | 43 | 0 | 77.42
17:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 243 | 192 |  | 0 | 290 | 265 | 96 | 0 | 40 | 204 | 0 | 150 | 100 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 16 | 203 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 14 | 0 | 0 | 0 | 270 | 270 | 191 | 81 | 94 | 25 | 43 | 0 | 51 | 0 | 48 | 43 | 19 | 11 | 33 | 20 | 140 | 134 | 64 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 105 | 62 | 69 | 0 | 215 | 18 | 0 | 8 | 290 | 16 | 5 | 0 | 209 | 0 | 0 | 195 | 0 | 149 | 3 | 100 | 140 | 93 | 371 | 115 | 87 | 105 | 1 | 0 | 54 | 13 | 114 | 113 | 100 | 370 | 90 | 8 | 162 | 115 | 0 | 35 | 6 |  | 724 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 65 | 23 | 32 | 0 | 0 | 0 | 50 | 40 | 65 | 42 | 43 | 29 | 52 | 32 | 19 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 120 | 0 | 164 | 0 | 97 | 0 | 190 | 0 | 339 | 90 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 560 | 0 | 0 | 17 |  | 8458 | 3791 | 12249 | 4475 | 724 | 1829 | 3752 | 781 | 35 | 493 | 140 | 20 | 0 | 77.42
18:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 226 | 192 |  | 0 | 290 | 265 | 100 | 0 | 55 | 170 | 0 | 110 | 100 | 102 | 147 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 49 | 0 | 0 | 35 | 100 | 0 | 16 | 215 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 17 | 0 | 0 | 0 | 285 | 285 | 196 | 130 | 95 | 25 | 46 | 0 | 51 | 0 | 48 | 52 | 19 | 11 | 33 | 20 | 144 | 131 | 72 | 19 | 0 | 0 | 41 | 53 | 0 | 110 | 105 | 63 | 71 | 0 | 211 | 18 | 0 | 8 | 300 | 16 | 5 | 0 | 209 | 0 | 0 | 197 | 0 | 149 | 0 | 100 | 140 | 85 | 321 | 115 | 87 | 105 | 0 | 0 | 54 | 17 | 114 | 113 | 100 | 384 | 90 | 1 | 162 | 115 | 0 | 35 | 1 |  | 725 | 0 | 265 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 8 | 66 | 26 | 64 | 0 | 0 | 0 | 50 | 33 | 96 | 42 | 34 | 29 | 52 | 32 | 20 | 0 | 11 | 73 | 0 | 148 | 0 | 0 | 100 | 0 | 148 | 0 | 98 | 0 | 140 | 0 | 335 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 0 | 0 | 17 |  | 8413 | 3654 | 12067 | 4290 | 725 | 1848 | 3785 | 721 | 35 | 517 | 144 | 2 | 0 | 77.41
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 181 | 208 |  | 0 | 290 | 270 | 100 | 0 | 55 | 214 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 0 | 35 | 100 | 0 | 16 | 208 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 21 | 0 | 0 | 0 | 315 | 305 | 193 | 158 | 95 | 26 | 49 | 0 | 51 | 0 | 48 | 52 | 19 | 11 | 33 | 20 | 152 | 139 | 72 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 128 | 64 | 72 | 0 | 211 | 18 | 0 | 8 | 290 | 16 | 11 | 190 | 218 | 220 | 97 | 198 | 0 | 149 | 0 | 100 | 140 | 86 | 379 | 115 | 87 | 105 | 0 | 0 | 54 | 17 | 114 | 113 | 100 | 370 | 89 | 0 | 162 | 115 | 0 | 35 | 0 |  | 724 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 14 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 30 | 100 | 42 | 34 | 30 | 52 | 32 | 20 | 0 | 11 | 74 | 0 | 149 | 0 | 0 | 95 | 0 | 150 | 0 | 97 | 57 | 162 | 0 | 411 | 90 | 150 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 40 |  | 9179 | 4089 | 13268 | 4457 | 724 | 2027 | 4558 | 793 | 35 | 522 | 152 | 0 | 119 | 77.4
19:30 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 274 | 208 |  | 0 | 290 | 275 | 100 | 0 | 55 | 212 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 27 | 33 | 33 | 25 | 0 | 0 | 35 | 100 | 0 | 16 | 228 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 23 | 0 | 0 | 0 | 350 | 330 | 165 | 158 | 96 | 26 | 50 | 0 | 51 | 0 | 48 | 52 | 22 | 11 | 25 | 20 | 160 | 145 | 81 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 129 | 64 | 72 | 0 | 211 | 18 | 0 | 8 | 330 | 16 | 8 | 195 | 225 | 306 | 100 | 200 | 0 | 149 | 0 | 100 | 140 | 86 | 404 | 115 | 87 | 105 | 0 | 0 | 54 | 34 | 114 | 113 | 100 | 387 | 89 | 0 | 162 | 115 | 0 | 35 | 0 |  | 629 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 22 | 100 | 42 | 34 | 30 | 52 | 32 | 21 | 0 | 10 | 74 | 0 | 149 | 0 | 0 | 90 | 0 | 154 | 0 | 96 | 100 | 159 | 0 | 410 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 72 |  | 9588 | 4149 | 13737 | 4636 | 629 | 2069 | 4843 | 845 | 35 | 520 | 160 | 0 | 192 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 273 | 188 |  | 0 | 290 | 275 | 99 | 0 | 55 | 215 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 38 | 0 | 0 | 35 | 100 | 0 | 16 | 228 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 26 | 0 | 0 | 0 | 335 | 330 | 141 | 102 | 95 | 26 | 50 | 0 | 51 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 162 | 152 | 81 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 130 | 64 | 73 | 0 | 211 | 18 | 0 | 8 | 315 | 16 | 8 | 197 | 225 | 304 | 100 | 200 | 0 | 149 | 0 | 100 | 140 | 83 | 391 | 115 | 87 | 105 | 0 | 0 | 54 | 32 | 114 | 113 | 100 | 384 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 629 | 0 | 210 | 0 | 99 | 160 | 0 | 0 | 20 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 31 | 52 | 32 | 21 | 0 | 10 | 75 | 0 | 149 | 0 | 0 | 89 | 0 | 154 | 0 | 96 | 100 | 158 | 0 | 413 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 72 |  | 9473 | 4319 | 13792 | 4597 | 629 | 1985 | 4859 | 846 | 35 | 679 | 162 | 0 | 275 | 77.4
21:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 269 | 166 |  | 0 | 290 | 275 | 92 | 0 | 55 | 213 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 34 | 0 | 0 | 0 | 300 | 305 | 123 | 45 | 94 | 10 | 50 | 0 | 51 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 166 | 151 | 81 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 129 | 64 | 74 | 0 | 211 | 18 | 0 | 8 | 320 | 16 | 8 | 200 | 225 | 302 | 100 | 200 | 0 | 149 | 0 | 100 | 140 | 97 | 404 | 115 | 87 | 105 | 0 | 0 | 54 | 51 | 114 | 113 | 100 | 388 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 629 | 0 | 190 | 0 | 99 | 160 | 0 | 0 | 19 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 30 | 52 | 32 | 21 | 0 | 10 | 72 | 0 | 210 | 0 | 0 | 85 | 0 | 144 | 0 | 97 | 100 | 162 | 0 | 410 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 107 |  | 9369 | 4378 | 13747 | 4483 | 629 | 1919 | 4934 | 904 | 35 | 677 | 166 | 0 | 273 | 77.4
22:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 268 | 165 |  | 0 | 290 | 280 | 92 | 0 | 55 | 216 | 0 | 183 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 50 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 27 | 0 | 0 | 0 | 280 | 285 | 144 | 45 | 95 | 10 | 49 | 0 | 51 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 164 | 150 | 81 | 19 | 0 | 0 | 42 | 53 | 0 | 163 | 129 | 65 | 74 | 0 | 211 | 18 | 0 | 8 | 310 | 16 | 8 | 200 | 224 | 301 | 100 | 200 | 0 | 149 | 0 | 100 | 140 | 103 | 382 | 115 | 87 | 105 | 0 | 0 | 54 | 51 | 114 | 113 | 100 | 389 | 90 | 0 | 162 | 111 | 0 | 35 | 0 |  | 628 | 0 | 190 | 0 | 99 | 164 | 0 | 0 | 18 | 0 | 32 | 68 | 34 | 110 | 0 | 0 | 0 | 50 | 40 | 99 | 42 | 43 | 30 | 52 | 32 | 21 | 0 | 10 | 73 | 0 | 250 | 0 | 0 | 81 | 0 | 140 | 0 | 96 | 100 | 153 | 0 | 413 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 107 |  | 9316 | 4427 | 13743 | 4430 | 628 | 1902 | 4940 | 945 | 35 | 699 | 164 | 0 | 231 | 77.39
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 268 | 170 |  | 0 | 290 | 280 | 92 | 0 | 55 | 220 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 51 | 45 | 20 | 35 | 0 | 0 | 0 | 280 | 285 | 206 | 45 | 95 | 10 | 51 | 0 | 51 | 0 | 48 | 52 | 16 | 11 | 33 | 20 | 166 | 149 | 73 | 19 | 0 | 0 | 42 | 53 | 0 | 163 | 130 | 65 | 74 | 0 | 217 | 18 | 0 | 9 | 300 | 16 | 8 | 200 | 227 | 303 | 100 | 193 | 0 | 149 | 0 | 100 | 140 | 107 | 383 | 115 | 87 | 105 | 0 | 0 | 54 | 51 | 114 | 113 | 100 | 378 | 90 | 0 | 162 | 109 | 0 | 35 | 0 |  | 629 | 0 | 170 | 0 | 99 | 164 | 0 | 0 | 18 | 0 | 32 | 67 | 35 | 110 | 0 | 0 | 0 | 50 | 41 | 98 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 10 | 73 | 0 | 250 | 0 | 0 | 75 | 0 | 133 | 0 | 95 | 100 | 143 | 0 | 412 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 107 |  | 9406 | 4382 | 13788 | 4443 | 629 | 1907 | 4965 | 945 | 35 | 698 | 166 | 0 | 146 | 77.39
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 268 | 172 |  | 0 | 290 | 275 | 92 | 0 | 55 | 222 | 0 | 120 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 0 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 |  | 23 | 0 | 68 | 10 | 84 | 45 | 21 | 37 | 0 | 0 | 0 | 280 | 265 | 213 | 45 | 95 | 10 | 54 | 0 | 51 | 0 | 48 | 52 | 14 | 11 | 33 | 20 | 158 | 151 | 73 | 19 | 0 | 0 | 42 | 53 | 0 | 163 | 219 | 66 | 74 | 0 | 217 | 18 | 0 | 9 | 300 | 16 | 8 | 200 | 227 | 302 | 100 | 193 | 0 | 149 | 0 | 100 | 140 | 115 | 367 | 115 | 85 | 105 | 0 | 0 | 40 | 51 | 114 | 113 | 100 | 371 | 90 | 0 | 162 | 109 | 0 | 35 | 0 |  | 629 | 0 | 170 | 0 | 99 | 164 | 0 | 0 | 19 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 42 | 98 | 42 | 43 | 30 | 52 | 31 | 21 | 0 | 11 | 72 | 0 | 250 | 0 | 0 | 75 | 0 | 133 | 0 | 97 | 100 | 142 | 0 | 394 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 107 |  | 9361 | 4323 | 13684 | 4434 | 629 | 1897 | 4929 | 902 | 35 | 700 | 158 | 0 | 0 | 77.38
KWH | 0 | 0 | 0 | 4347000 | 0 | 2346000 | 0 | 2535237 | 6512000 |  | 0 | 6837300 | 5688611 | 2072540 | 0 | 1212753 | 5231457 | 0 | 3867000 | 2274192 | 2129616 | 2608320 | 0 | 0 | 0 | 0 | 831240 | 1089869 | 1252658 | 413028 | 600000 | 586440 | 762900 | 764700 | 926880 | 0 | 0 | 788000 | 2000000 | 0 | 399709 | 5055476 | 0 | 2950752 | 0 |  | 540960 | 0 | 1307754 | 385920 | 912960 | 847200 | 501072 | 473760 | 0 | 0 | 0 | 7723500 | 7322000 | 4657000 | 920000 | 2237920 | 482688 | 1239840 | 0 | 1061349 | 0 | 720040 | 1228786 | 404676 | 186660 | 799200 | 496020 | 3556800 | 3886880 | 1710720 | 396072 | 12750 | 0 | 987360 | 1207200 | 0 | 3554754 | 2509000 | 1542144 | 1784640 | 0 | 5118550 | 403000 | 0 | 188640 | 7469050 | 352680 | 147210 | 1499328 | 4182653 | 1731263 | 676209 | 3655200 | 0 | 3538080 | 115830 | 2338560 | 3460320 | 2018981 | 9053000 | 2631600 | 2052000 | 2599418 | 29895 | 0 | 1054901 | 419016 | 2208180 | 2795520 | 2298240 | 8934800 | 2070720 | 331770 | 3428640 | 2327182 | 0 | 862560 | 215201 |  | 17040000 | 0 | 7093440 | 0 | 2201280 | 685506 | 0 | 0 | 240480 | 0 | 569250 | 1571000 | 686926 | 1709280 | 0 | 0 | 0 | 717927 | 435833 | 1646656 | 685220 | 532688 | 428176 | 1233120 | 412030 | 465120 | 0 | 251406 | 1786473 | 0 | 3941100 | 0 | 0 | 2667500 | 0 | 4172727 | 0 | 2309109 | 988800 | 4373500 | 0 | 9415782 | 1904640 | 1086562 | 2505984 | 0 | 2515200 | 0 | 42478 | 2113056 | 14163200 | 0 | 0 | 921600 |  | 201889500 | 93513049 | 295402549 | 107384995 | 17040000 | 46471470 | 90319865 | 19890773 | 788000 | 9202722 | 3556800 | 747924 | 0
Fuel Cost | 0 | 0 | 0 | 6390090 | 0 | 3096720 | 0 | 2560589.37 | 6707360 |  | 0 | 7452657 | 6314358.21 | 15730578.6 | 0 | 10259890.38 | 5440715.28 | 0 | 6689910 | 17124665.76 | 19422097.92 | 25665868.8 | 0 | 0 | 0 | 0 | 6068052 | 8424687.37 | 12351207.88 | 309771 | 450000 | 0 | 0 | 0 | 8962929.6 | 0 | 0 | 212760 | 3620000 | 0 | 3713296.61 | 5510468.84 | 0 | 5016278.4 | 0 |  | 0 | 0 | 12685213.8 | 3685536 | 7942752 | 6709824 | 631350.72 | 1407067.2 | 0 | 0 | 0 | 5715390 | 7322000 | 4284440 | 1186800 | 2573608 | 545437.44 | 1735776 | 0 | 1814906.79 | 0 | 7272404 | 11734906.3 | 513938.52 | 139995 | 1398600 | 372015 | 26676000 | 4120092.8 | 15533337.6 | 503011.44 | 203235 | 0 | 1579776 | 2148816 | 0 | 4052419.56 | 2609360 | 3038023.68 | 3408662.4 | 0 | 8855091.5 | 882570 | 0 | 384825.6 | 7543740.5 | 264510 | 111879.6 | 25503569.28 | 31620856.68 | 29396845.74 | 11306214.48 | 19007040 | 0 | 34814707.2 | 1354052.7 | 19059264 | 37544472 | 14233816.05 | 8419290 | 24000192 | 19391400 | 22640930.78 | 0 | 0 | 9188187.71 | 3683150.64 | 22037636.4 | 23957606.4 | 15306278.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98150400 | 0 | 7448112 | 0 | 17302060.8 | 9501113.16 | 0 | 0 | 2522635.2 | 0 | 5931585 | 1775230 | 1064735.3 | 16682572.8 | 0 | 0 | 0 | 7064401.68 | 4428063.28 | 14572905.6 | 5276194 | 7201941.76 | 4149025.44 | 11948932.8 | 3996691 | 893030.4 | 0 | 190314.342 | 10772432.19 | 0 | 21360762 | 0 | 0 | 3120975 | 0 | 5507999.64 | 0 | 3463663.5 | 16819488 | 5116995 | 0 | 9321624.18 | 19884441.6 | 18482419.62 | 23781788.16 | 0 | 19517952 | 0 | 469381.9 | 15615483.84 | 62176448 | 0 | 0 | 0 |  | 721547775.93 | 455511799.192 | 1177059575.122 | 113027828.572 | 98150400 | 55682804.43 | 695115148.37 | 94309642.19 | 212760 | 91858321.96 | 26676000 | 2026669.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 0 | 303 |  | 0 | 290 | 240 | 99 | 0 | 40 | 182 | 0 | 145 | 100 | 102 | 140 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 0 | 16 | 50 | 0 | 0 | 35 | 80 | 0 | 17 | 204 | 0 | 120 | 0 |  | 24 | 0 | 33 | 20 | 19 | 37 | 21 | 2 | 0 | 0 | 100 | 300 | 300 | 207 | 8 | 95 | 23 | 50 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 33 | 20 | 144 | 162 | 72 | 19 | 2 | 0 | 43 | 44 | 0 | 163 | 0 | 62 | 76 | 0 | 218 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 209 | 0 | 0 | 139 | 0 | 145 | 17 | 90 | 136 | 75 | 367 | 96 | 88 | 99 | 5 | 0 | 35 | 17 | 114 | 110 | 100 | 371 | 89 | 41 | 145 | 116 | 0 | 35 | 31 |  | 725 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 10 | 0 | 32 | 61 | 24 | 16 | 0 | 0 | 0 | 43 | 0 | 40 | 33 | 16 | 0 | 52 | 0 | 20 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 80 | 0 | 171 | 0 | 96 | 0 | 196 | 0 | 397 | 91 | 0 | 113 | 0 | 100 | 0 | 7 | 90 | 510 | 0 | 0 | 0 |  | 11614 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 273 | 188 | 0 | 0 | 290 | 275 | 99 | 0 | 55 | 215 | 0 | 185 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 38 | 0 | 0 | 35 | 100 | 0 | 16 | 228 | 0 | 120 | 0 | 0 | 23 | 0 | 68 | 10 | 19 | 45 | 21 | 26 | 0 | 0 | 0 | 335 | 330 | 141 | 102 | 95 | 26 | 50 | 0 | 51 | 0 | 48 | 52 | 22 | 11 | 33 | 20 | 162 | 152 | 81 | 19 | 0 | 0 | 41 | 53 | 0 | 163 | 130 | 64 | 73 | 0 | 211 | 18 | 0 | 8 | 315 | 16 | 8 | 197 | 225 | 304 | 100 | 200 | 0 | 149 | 0 | 100 | 140 | 83 | 391 | 115 | 87 | 105 | 0 | 0 | 54 | 32 | 114 | 113 | 100 | 384 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 629 | 0 | 210 | 0 | 99 | 160 | 0 | 0 | 20 | 0 | 32 | 66 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 100 | 42 | 43 | 31 | 52 | 32 | 21 | 0 | 10 | 75 | 0 | 149 | 0 | 0 | 89 | 0 | 154 | 0 | 96 | 100 | 158 | 0 | 413 | 91 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 622 | 0 | 0 | 72 |  | 13792 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 283 | 345 | 0 | 0 | 300 | 250 | 100 | 0 | 55 | 220 | 0 | 180 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 | 0 | 22 |  | 68 | 20 | 90 | 43 | 22 | 25 | 0 | 0 | 0 | 330 | 330 | 225 | 45 | 96 | 23 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 171 | 177 | 74 | 20 | 0 | 0 | 42 | 51 | 0 | 163 | 275 | 66 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 0 | 149 | 0 | 100 | 158 | 150 | 400 | 115 | 85 | 105 | 0 | 300 | 35 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 90 | 0 | 35 |  |  | 737 | 16 | 400 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 67 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 100 | 42 | 43 | 30 | 52 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 91 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 90
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 283 | 345 | 0 | 0 | 300 | 250 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 25 | 33 | 33 | 52 | 0 | 0 | 35 | 100 | 0 | 17 | 230 | 0 | 120 | 0 | 0 | 22 |  | 68 | 20 | 90 | 43 | 22 | 10 | 0 | 0 | 0 | 330 | 330 | 225 | 45 | 95 | 23 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 177 | 74 | 20 | 1.6 | 0 | 42 | 51 | 0 | 163 | 275 | 66 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 75 | 100 | 50 | 200 | 0 | 149 | 20 | 100 | 158 | 100 | 400 | 115 | 85 | 105 | 5 | 300 | 35 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 90 | 0 | 35 | 30 |  | 737 | 0 | 400 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 66 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 80 | 0 | 180 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 283 | 204 | 0 | 0 | 290 | 240 | 78 | 0 | 55 | 180 | 0 | 137 | 100 | 58 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 28 | 33 |  | 7 | 0 | 0 | 35 | 100 | 0 | 17 | 231 | 0 | 120 | 0 | 0 | 24 | 0 | 0 | 10 | 12 | 18 | 21 | 2 | 0 | 0 | 0 | 265 | 265 | 214 | 45 | 94 | 10 | 53 | 0 | 51 | 0 | 0 | 52 | 14 | 11 | 33 | 20 | 130 | 177 | 73 | 16 | 1 | 0 | 42 | 53 | 0 | 130 | 111 | 66 | 75 | 0 | 217 | 18 | 0 | 9 | 310 | 16 | 5 | 0 | 30 | 0 | 0 | 80 | 0 | 149 | 9 | 100 | 140 | 128 | 364 | 115 | 86 | 105 | 2 | 0 | 35 | 0 | 0 | 113 | 100 | 370 | 71 | 5 | 118 | 72 | 0 | 36 | 13 | 0 | 725 | 0 | 175 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 81 | 0 | 151 | 0 | 97 | 0 | 160 | 0 | 406 | 53 | 0 | 50 | 0 | 113 | 0 | 2 | 50 | 500 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 10354 | 8:00
| Highest Generation |  | 13792 | 20:00
| Day Peak Generation |  | 11614 | 12:00
| Evening Peak Generation |  | 13792 | 20:00
| HVDC Max Flow |  | 725 | 1:00
| HVDC EvPeak Flow |  | 629 | 20:00
| Load factor L.F |  | 89.24%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-04-28
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-04-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11614 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10603 | MW
Evening Peak Generation : |  | 13792 | MW Hour : | 20:00 | Available Max Generation : |  | 15398 | MW
E.P. Demand (at gen end) : |  | 14097 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 14100 | MW
Maximum Generation : |  | 13792 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1298 | MW
Total Gen. (MKWH) : |  | 295.4025 | System Load Factor : | 89.24% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -500 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-04-28
Actual : | 77.35 | Ft.(MSL) , | Rule curve : | 82.6 | Ft.( MSL )
Gas Consumed : | Total = | 1314 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168710633.002
: |  | Coal : | 94309642.19 | Oil : | 786973470.33 | Total : | 1049993745.522
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 1080:00 | 5073.1641 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1733.3145 |  |  | 0 | 0%
Khulna Area | 0 | 1320:00 | 1554.446 |  |  | 0 | 0%
Rajshahi Area | 0 | 888:00 | 1405.0892 |  |  | 0 | 0%
Cumilla Area | 0 | 960:00 | 1269.4741 |  |  | 0 | 0%
Mymensingh Area | 0 | 1056:00 | 1024.4413 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 562.3192 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 263.4883 |  |  | 0 | 0%
Rangpur Area | 0 | 1296:00 | 790.1502 |  |  | 0 | 0%
Total | 0 |  | 13675.8868 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
6) Siddirganj-335 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sikalbaha GIS-Dohazari 132 kV Ckt-2 was under shut down from 09:39 to 16:42 for D/W.
b) Barapukuria-Saidpur 132 kV Ckt-1 tripped at 09:50 showing dist relay and was switched on at 09:58.
c) Barapukuria 230/132 kV TR-1 transformer was under shut down from 12:03 to 13:37 for red hot
maintenance at 132 kV bushing.
d) Ashuganj #05 tripped at 12:48 DCS system fault.
e) Shahjibazar 330 MW GT-1,2 were synchronized at 13:09 ,18:22 respectively.
f) Haripur EGCB 412 MW GT was synchronized at 13:18.
g) Bagura-Sherpur 132 kV Ckt-1 was under shut down from 11:04 to 18:22 for D/W.
h) Sreemangal 132/33 kV T2 & T3 transformer tripped at 14:57 due to 33 kV REB feeder fault and were |  |  |  |  | About 26 MW power interruption occurred under Sreemangal S/S
switched on at 15:02. |  |  |  |  | areas from 14:57 to 15:02.
i) Khulna 225 MW GT was synchronized at 19:30 and was shut down at 00:41due to Low demand.
j) Naogaon-Joypurhat 132 kV Ckt tripped at 22:11 from Naogaon end showing dist 3 phase Z1 and was |  |  |  |  | About 60 MW power interruption occurred under Joypurhat S/S
switched on at 22:35. |  |  |  |  | areas from 22:11 to 22:35.
k) Shahjibazar 330 MW GT-1 tripped at 03:25 due to fuel flow out of range.
l) Rajshahi old-Rajshahi new 132 kV Ckt-2 was under shut down since 07:10(28-04-21) for D/W.
m) Chattak-Sunamganj 132 kV Ckt tripped at 07:20(28-04-21) from Sunamganj end showing dist relay and |  |  |  |  | About 12 MW power interruption occurred under Sunamganj S/S
was switched on at 07:32(28-04-2021). |  |  |  |  | areas from 07:20 to 07:32.
n) Barapukuria 230/132 kV TR-2 transformer was under shut down since 07:37(28-04-2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-04-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4347000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 2346000
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 273 | 2535237 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 188 | 6512000 | Gas Shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 290 | 6837300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 99 | 2072540
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 5688611 | Gas shortage
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1212753
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Devolopment work.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 413028
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3867000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2274192
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 215 | 5231457 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2129616
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 831240 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2608320
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1089869
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1252658
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1186440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 762900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 764700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 38 | 926880 | Machine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 225 | 4182653 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 304 | 1731263
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 676209
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Devolopment work.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3538080
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 87 | 2052000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2070720 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3428640
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 215201
| Dhaka area Total |  |  |  | 5829 | 3655 | 72784507
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2000000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 16 | 399709 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 115830
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 45 | 847200 | Engine problem
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 35 | 788000 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 228 | 5055476 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2950752 | Gas shortage
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2599418
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 1307754 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 10 | 385920 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2338560
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 501072
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 473760
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 19 | 912960 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29895
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1054901
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 32 | 419016 | Transformer O/L.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2298240
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 114 | 2327182
| Chattogram area Total |  |  |  | 2382 | 1193 | 26805645
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 141 | 4657000 | gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7723500 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 330 | 7322000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 482688 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 50 | 1239840
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 102 | 920000 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1061349
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 83 | 2018981 | Engine problem
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 720040
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 95 | 2237920 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 140 | 3460320 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 404676
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 186660
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3556800
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 799200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1228786
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 496020 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 197 | 1499328
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2208180
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2795520
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 862560 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 2160 | 45881368
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 152 | 3886880 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 396072
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 81 | 1710720 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12750
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 3655200
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2631600
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 331770
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 540960
| Mymensingh Area Total |  |  |  | 709 | 590 | 13165952
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Under maint.
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 987360 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3554754
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 130 | 2509000 | Engine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1207200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 147210 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1542144
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 73 | 1784640 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 211 | 5118550
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 403000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 352680 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 315 | 7469050 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 391 | 9053000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 188640 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 384 | 8934800 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1875 | 43252028
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 629 | 17040000
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2201280 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 240480 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 160 | 685506 | only GT Synch
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 210 | 7093440 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 569250 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 988800
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 91 | 1904640 | Engine problem
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1341 | 30723396
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1709280
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 686926
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 66 | 1571000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2309109
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 14163200
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 921600 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 1000 | 21361115
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 717927
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 435833 | Engine problem
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 685220 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 532688 | Engine problem
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 428176 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 89 | 2667500 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 154 | 4172727 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 158 | 4373500 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 413 | 9415782 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 412030 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 465120
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 10 | 251406
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1233120
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 1646656
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 200 | 1086562
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2505984
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2113056
| Rajshahi Area Total |  |  |  | 2173 | 1641 | 33143287
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1786473
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3941100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2515200
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42478
| Rangpur Area Total |  |  |  | 605 | 337 | 8285251
| Total |  |  |  | 21219 | 13792 | 295402549
| Eastern Grid Total |  |  |  | 14331 | 9473 | 201889500
| Western Grid Total |  |  |  | 6888 | 4319 | 93513049
| National Grid Total |  |  |  | 21219 | 13792 | 295402549
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-04-27
(a) ENTIRE EASTERN GRID : |  | 8813 | MW | (b) ENTIRE WESTERN GRID : |  | 4283 | MW
i) Dhaka area |  | 4543 | MW | i) Khulna area |  | 1653 | MW
ii) Chittagong area |  | 1348 | MW | ii) Rajshahi area |  | 1447 | MW
iii) Comilla area |  | 1288 | MW | iii) Barisal area |  | 392 | MW
iv) Mymensingh area |  | 1089 | MW | iv) Rangpur area |  | 791 | MW
v) Sylhet area |  | 545 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 13096 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 23:00 | Jamalpur | 170 | 20:00 | Jhenida | 116 | 20:00
Munsiganj | 141 | 0:00 | Sherpur | 148 | 21:00 | Bottail | 142 | 22:00
Sonargaon | 90 | 23:00 | Srimongal | 55 | 21:00 | G.K Project | 65 | 21:00
Shyampur | 208 | 16:00 | Shahjibazar | 126 | 21:00 | Faridpur | 214 | 21:00
Bhulta | 205 | 0:00 | Fenchuganj | 50 | 19:00 | Madaripur | 116 | 23:00
Madanganj | 57 | 2:00 | Kulawara | 50 | 22:00 | Sariatpur | 74 | 23:00
Shitalakhya | 131 | 16:00 | Sylhet | 127 | 21:00 | Gopalganj | 100 | 22:00
Rahim steel | 24 | 8:00 | Chatak | 34 | 21:00 | Bagerhat | 112 | 21:00
Matuail | 60 | 7:00 | Sunamganj | 51 | 21:00 | Mongla | 42 | 1:00
Ghorasal | 75 | 21:00 | Biani Bazar | 72 | 21:00 | Satkhira | 123 | 21:00
Narsingdi | 177 | 23:00 | Comilla (S) | 166 | 21:00 | Gallamari | 42 | 1:00
Haripur (SBU) | 111 | 20:00 | Comilla(N) | 153 | 21:00 | Magura | 58 | 24:00
Sreenagar |  |  | Chandpur | 83 | 20:00 | Norail | 45 | 20:00
Ullon | 84 | 1:00 | Feni | 142 | 23:00 | Chuadanga | 96 | 23:00
Hasnabad | 96 | 19:30 | Chowmuhani | 201 | 22:00 | Borguna | 20 | 21:00
Magbazar | 96 | 16:00 | Ashuganj | 37 | 15:00 | Barisal(N) | 50 | 21:00
Maniknagar | 92 | 13:00 | Daudkandi | 173 | 22:00 | Barisal (S) | 124 | 19:30
Bangabhaban | 24 | 11:00 | B.Baria | 175 | 22:00 | Patuakhali | 123 | 21:00
Narinda | 88 | 13:00 | Ramganj | 100 | 19:00 | Bhandaria | 59 | 21:00
Dhanmondi | 202 | 13:00 | Chaddagram | 53 | 20:00 | Borhan Uddin | 43 | 21:00
Lalbag | 87 | 13:00 | PHP | 10 | 18:30 | Ishurdi | 70 | 19:30
Madartek | 87 | 19:00 | Kochua | 68 | 18:00 | Ruppur Paromanobik | 3 | 11:00
Dhaka University | 41 | 13:00 | Madunaghat | 66 | 19:00 | Natore | 148 | 22:00
Aftabnagar | 11 | 14:00 | Hathazari | 98 | 20:00 | Bogra | 179 | 3:00
Fatullah | 66 | 15:00 | Khulshi | 229 | 16:00 | Noagaon | 138 | 24:00
Nawabganj | 60 | 21:00 | Halishahar | 147 | 13:00 | Rajshahi | 176 | 21:00
Mirpur | 123 | 18:00 | Baraulia | 160 | 4:00 | Rajshahi New | 26 | 21:00
Kalyanpur | 123 | 23:00 | Sikalbaha | 38 | 1:00 | C.Nawabganj | 73 | 21:00
Gulshan | 138 | 15:00 | Dohazari | 96 | 3:00 | Amnura | 59 | 21:00
Uttara | 102 | 13:00 | Cox'sbazar | 103 | 19:30 | Pabna | 110 | 20:00
Uttara New | 32 | 14:00 | Chandraghona | 32 | 18:30 | Shahjadpur | 113 | 20:00
Kamrangirchar | 89 | 16:00 | Kaptai | 4.2 | 19:00 | Serajganj | 111 | 21:00
Savar | 164 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 73 | 21:00
Bhasantec | 171 | 19:00 | Bakulia | 110 | 13:00 | Joypurhat | 65 | 23:00
Agargaon | 77 | 19:00 | Julda | 26 | 1:00 | Sherpur(Bogura) | 56 | 3:00
Satmosjid | 111 | 19:00 | TK chemical | 29 | 18:30 | Mohastangor | 66 | 20:00
Tongi | 132 | 10:00 | Modern Steel |  |  | Bangura | 42 | 19:30
Kabirpur | 261 | 12:00 | Shahmirpur | 28 | 0:00 | Rangpur | 126 | 17:00
Basundhara | 175 | 19:30 | Khagrachhari | 26 | 22:00 | Lalmonirhat | 41 | 20:00
Manikganj | 78 | 24:00 | Matarbari | 40 | 2:00 | Saidpur | 106 | 16:00
Joydevpur | 176 | 16:00 | Baroiar Hat | 48 | 12:00 | Purbasadipur | 107 | 20:00
New Tongi | 114 | 14:00 | Rangamati | 12 | 18:30 | Thakurgaon | 88 | 19:30
Kodda | 271 | 16:00 | Abul Khair 230 | 168 | 11:00 | Palashbari | 123 | 23:00
Dhamrai | 126 | 15:00 | BSRM | 156 | 7:00 | Barapukuria | 56 | 23:00
Rajendrapur | 96 | 24:00 | GPH Ispat | 90 | 23:00 | Panchagar | 54 | 21:00
Valuka | 104 | 12:00 | Goalpara | 30 | 20:00 | Joldhaka | 67 | 21:00
Tangail | 232 | 20:00 | Central s/s | 102 | 20:00 | Kurigram | 55 | 20:00
Mymensing | 231 | 21:00 | Noapara | 56 | 0.83333 | Mithapukur | 40 | 21:00
Kishorganj | 132 | 1:00 | Jessore | 133 | 20:00
Netrokona | 116 | 3:00 | Benapol | 64 | 14:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-04-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 24:00 | 395 | 16:00 | Kaliakoir | 383 | 0.75 | 375 | 0.58333
| Bheramara | 404 | 4:00 | 397 | 14:00 | Bhulta | 379 | 0.77083 | 367 | 0.41667
| Ashuganj(N) | 386 | 3:00 | 376 | 8:00 | Gopalganj | 404 | 0.625 | 379 | 0.91667
| Payra | 406 | 18:30 | 395 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 228 | 8:00 | Hathazari | 219 | 21:00 | 210 | 10:00
| Ishurdi | 234 | 6:00 | 224 | 19:00 | Megnaghat | 228 | 11:00 | 220 | 9:00
| Ashuganj | 235 | 3:00 | 230 | 6:00 | Fenchuganj | 237 | 24:00 | 234 | 4:00
| Serajganj | 230 | 1:00 | 225 | 10:00 | Siddhirganj | 226 | 3:00 | 219 | 12:00
| Baghabari | 232 | 24:00 | 226 | 19:00 | Maniknagar | 224 | 3:00 | 217 | 10:00
| Barapukuria | 231 | 5:00 | 217 | 13:00 | Agargaon | 222 | 5:00 | 214 | 10:00
| Bogra | 224 | 5:00 | 216 | 19:00 | Barisal | 250 | 24:00 | 236 | 13:00
| Rajshahi | 234 | 2:00 | 222 | 19:00 | Bhola 225 MW | 252 | 5:00 | 240 | 22:00
| Khulna South | 228 | 6:00 | 208 | 19:30 | AKSML | 221 | 24:00 | 210 | 10:00
| Rampura | 223 | 19:00 | 219 | 14:00 | BSRM | 222 | 18:30 | 212 | 7:00
| Haripur | 222 | 19:00 | 216 | 10:00 | Bibiyana | 238 | 18:30 | 234 | 15:00
| Hasnabad | 225 | 18:30 | 216 | 13:00 | Bhulta | 227 | 24:00 | 219 | 10:00
| Shyampur | 222 | 18:30 | 220 | 9:00 | Ashuganj (S) | 234 | 18:30 | 227 | 10:00
| Aminbazar | 223 | 1:00 | 216 | 2:00 | Kaliakoir | 222 | 3:00 | 214 | 7:00
| Tongi | 222 | 4:00 | 215 | 13:00 | GPH | 221 | 18:30 | 211 | 10:00
| Comilla (N) | 226 | 21:00 | 220 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 18:30 | 129 | 10:00 | Madanhat | 132 | 0.77083 | 127 | 0.41667
| Munsiganj | 133 | 18:30 | 128 | 10:00 | Hathazari | 129 | 0.041667 | 125 | 0.41667
| Sonargaon | 134 | 19:00 | 129 | 11:00 | Khulshi | 128 | 0.75 | 123 | 0.41667
| Shyampur | 134 | 18:30 | 128 | 10:00 | Halishahar | 132 | 0.77083 | 124 | 0.41667
| Bhulta | 127 | 18:30 | 121 | 10:00 | Baraulia | 130 | 0.20833 | 124 | 0.375
| Madanganj | 133 | 0:00 | 126 | 9:00 | Sikalbaha | 131 | 0.041667 | 128 | 0.20833
| Shitalakhya | 138 | 0:00 | 128 | 8:00 | Dohazari | 126 | 0.75 | 115 | 0.41667
| Rahim steal | 134 | 19:00 | 129 | 10:00 | Cox'sbazar | 123 | 0.58333 | 106 | 0.45833
| Matuail | 134 | 18:30 | 129 | 10:00 | Chandraghona | 130 | 0.75 | 126 | 0.41667
| Ghorasal | 136 | 1:00 | 135 | 7:00 | Kaptai | 128 | 0.041667 | 125 | 0.29167
| Narsinghdi | 131 | 7:00 | 124 | 23:00 | A. Khaer Stl. | 127 | 0.29167 | 124 | 0.45833
| Haripur (SBU) | 134 | 19:00 | 129 | 9:00 | Bakulia | 130 | 0.75 | 126 | 0.375
| Sreenagar |  |  |  |  | Julda | 131 | 0.041667 | 128 | 0.41667
| Ullon | 131 | 1:00 | 126 | 14:00 | TK Chemical | 129 | 0.041667 | 127 | 0.29167
| Hasnabad | 135 | 19:00 | 128 | 14:00 | Modern Steel
| Magbazar | 132 | 3:00 | 125 | 10:00 | Shahmirpur | 131 | 0.70833 | 126 | 0.375
| Maniknagar | 134 | 3:00 | 129 | 10:00 | Khagrachhari | 129 | 0.91667 | 124 | 0.58333
| Bangabhaban | 134 | 3:00 | 129 | 10:00 | Matarbari | 124 | 0.58333 | 110 | 0.45833
| Narinda | 134 | 3:00 | 129 | 10:00 | Baroiar Hat | 131 | 0.75 | 127 | 0.41667
| Dhanmondi | 131 | 1:00 | 126 | 14:00 | Rangamati | 130 | 0.77083 | 125 | 0.45833
| Lalbag | 135 | 18:30 | 126 | 14:00 | Goalpara S/S | 138 | 16:00 | 125 | 19:30
| Madartek | 132 | 3:00 | 125 | 12:00 | Khulna Central S/S | 138 | 18:30 | 125 | 19:30
| Dhaka University | 132 | 1:00 | 125 | 14:00 | Noapara | 136 | 16:00 | 121 | 0.8125
| Aftabnagar | 132 | 2:00 | 126 | 12:00 | Jessore | 127 | 16:00 | 112 | 0.8125
| Fatullah | 133 | 3:00 | 127 | 13:00 | Benapol | 128 | 13:00 | 112 | 0.8125
| Nawabganj | 127 | 24:00 | 123 | 10:00 | Jhenida | 123 | 6:00 | 106 | 0.8125
| Mirpur | 135 | 23:00 | 127 | 10:00 | Bottail | 129 | 0.25 | 119 | 0.8125
| Kalyanpur | 134 | 23:00 | 129 | 9:00 | G.K Project | 137 | 7:00 | 130 | 0.8125
| Gulshan | 131 | 23:00 | 126 | 9:00 | Faridpur | 134 | 0.25 | 124 | 0.91667
| Uttara | 133 | 23:00 | 128 | 9:00 | Madaripur | 139 | 0.20833 | 130 | 0.79167
| Uttara New | 134 | 23:00 | 127 | 9:00 | Shariyatpur S/S | 138 | 0.20833 | 128 | 0.91667
| Kamrangirchar | 133 | 23:00 | 127 | 9:00 | Gopalganj | 144 | 0.20833 | 129 | 0.91667
| Savar | 132 | 23:00 | 127 | 9:00 | Bagerhat | 135 | 16:00 | 119 | 0.8125
| Bhasantec | 132 | 23:00 | 126 | 9:00 | Mongla | 131 | 0.45833 | 118 | 0.8125
| Agargaon | 133 | 23:00 | 128 | 9:00 | Satkhira | 136 | 16:00 | 120 | 0.8125
| Satmosjid | 132 | 23:00 | 128 | 9:00 | Gallamari | 139 | 16:00 | 125 | 0.8125
| Tongi | 135 | 4:00 | 130 | 13:00 | Magura | 122 | 6:00 | 103 | 19:30
| Kabirpur | 133 | 3:00 | 128 | 16:00 | Narail | 121 | 0.33333 | 114 | 19:30
| Basundhara | 135 | 3:00 | 126 | 15:00 | Chuadanga | 117 | 8:00 | 97 | 0.8125
| Manikganj | 138 | 4:00 | 130 | 8:00 | Borguna | 140 | 0.16667 | 130 | 0.54167
| Joydevpur | 139 | 2:00 | 131 | 8:00 | Barisal(N) | 141 | 5:00 | 133 | 0.54167
| New Tongi | 136 | 3:00 | 128 | 8:00 | Barisal (S) | 141 | 5:00 | 131 | 0.54167
| Kodda | 134 | 21:00 | 123 | 15:00 | Patuakhali(S) | 140 | 3:00 | 128 | 14:00
| Dhamrai | 131 | 2:00 | 127 | 17:00 | Bhandaria | 135 | 0.125 | 127 | 0.625
| Rajendrapur | 133 | 4:00 | 122 | 17:00 | Ishurdi | 135 | 0.25 | 129 | 0.8125
| Valuka | 122 | 7:00 | 110 | 23:00 | Ruppur Paromanobik | 134 | 0.16667 | 131 | 0.8125
| Tangail | 127 | 9:00 | 121 | 19:00 | Natore | 134 | 4:00 | 128 | 19:00
| Mymensing | 127 | 12:00 | 114 | 24:00 | Bogra | 132 | 4:00 | 127 | 19:30
| Kishorganj | 128 | 7:00 | 118 | 23:00 | Noagaon | 127 | 16:00 | 120 | 14:00
| Netrokona | 124 | 8:00 | 110 | 23:00 | Rajshahi | 134 | 18:00 | 128 | 18:30
| Jamalpur | 134 | 8:00 | 126 | 23:00 | Rajshahi New | 136 | 18:30 | 128 | 19:00
| Sherpur | 132 | 3:00 | 122 | 23:00 | C.Nawabganj | 134 | 17:00 | 128 | 19:00
| Srimongal | 136 | 6:00 | 132 | 21:00 | Amnura | 135 | 3:00 | 128 | 19:00
| Shahjibazar | 136 | 9:00 | 129 | 22:00 | Pabna | 132 | 4:00 | 127 | 19:00
| Fenchuganj | 135 | 10:00 | 131 | 20:00 | Shahjadpur | 137 | 5:00 | 132 | 18:30
| Khulawara | 134 | 5:00 | 131 | 21:00 | Serajganj | 131 | 4:00 | 126 | 19:00
| Sylhet | 132 | 5:00 | 129 | 20:00 | Niyamatpur | 125 | 16:00 | 116 | 13:00
| Chatak | 131 | 8:00 | 126 | 21:00 | Joypurhat | 125 | 8:00 | 115 | 14:00
| Sunamganj | 131 | 7:00 | 124 | 18:30 | Sherpur(Bogura) | 132 | 4:00 | 126 | 19:30
| Biani Bazar | 131 | 6:00 | 125 | 21:00 | Mohastangor | 130 | 4:00 | 124 | 19:00
| Comilla(s) | 126 | 5:00 | 120 | 15:00 | Bangura | 133 | 4:00 | 129 | 19:30
| Comilla(n) | 136 | 21:00 | 132 | 10:00 | Rangpur | 125 | 6:00 | 113 | 12:00
| Chandpur | 137 | 5:00 | 130 | 23:00 | Lalmonirhat | 126 | 5:00 | 113 | 13:00
| Feni | 131 | 18:30 | 127 | 14:00 | Saidpur | 127 | 5:00 | 110 | 13:00
| Chowmuhani | 130 | 6:00 | 127 | 19:30 | Purbasadipur | 125 | 5:00 | 104 | 13:00
| Ashuganj | 137 | 9:00 | 132 | 23:00 | Thakurgaon | 127 | 6:00 | 101 | 13:00
| Daudkandi | 138 | 21:00 | 128 | 10:00 | Palashbari | 127 | 5:00 | 120 | 10:00
| B.Baria | 133 | 7:00 | 125 | 22:00 | Barapukuria | 131 | 5:00 | 117 | 13:00
| Ramganj | 132 | 7:00 | 126 | 14:00 | Panchagar | 124 | 5:00 | 97 | 13:00
| Chaddagram | 134 | 11:00 | 129 | 14:00 | Joldhaka | 123 | 5:00 | 103 | 14:00
| PHP | 131 | 18:30 | 126 | 10:00 | Kurigram | 125 | 6:00 | 111 | 13:00
| Kochua | 133 | 6:00 | 131 | 21:00 | Mithapukur | 129 | 0.20833 | 117 | 0.5

## L-Curve
Date | 2021-04-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 316 | 9361 | 4323 | 13684 |  |  |  | QF-LDC-11
0:30 | 310 | 9200 | 4194.5 | 13394.5 | Date: | 2021-04-27
1:00 | 304 | 9039 | 4066 | 13105
1:30 | 287 | 8898 | 4022.5 | 12920.5
2:00 | 270 | 8757 | 3979 | 12736
2:30 | 239 | 8750 | 4016 | 12766 | [5 empty] | Gen. at Eve. Peak | 13792 | 13792 MW (20:00 )
3:00 | 208 | 8743 | 4053 | 12796 | [6 empty] | 20:00
3:30 | 150 | 8560 | 3955 | 12515 | [5 empty] | Gen. at Day Peak | 11614 | 11614 MW (12:00 )
4:00 | 92 | 8377 | 3857 | 12234 | [6 empty] | 12:00
4:30 | 53 | 8128 | 3694 | 11822 | [5 empty] | Highest Generation | 13792
5:00 | 14 | 7879 | 3531 | 11410 | [6 empty] | 20:00
5:30 | 135 | 7540 | 3431 | 10971
6:00 | 256 | 7201 | 3331 | 10532
6:30 | 283 | 7184.5 | 3316.5 | 10501
7:00 | 310 | 7168 | 3302 | 10470
7:30 | 267 | 7149.5 | 3262.5 | 10412
8:00 | 224 | 7131 | 3223 | 10354
8:30 | 263 | 7245.5 | 3252 | 10497.5
9:00 | 302 | 7360 | 3281 | 10641
9:30 | 252 | 7587 | 3256.5 | 10843.5
10:00 | 202 | 7814 | 3232 | 11046
10:30 | 267 | 7925 | 3342 | 11267
11:00 | 332 | 8036 | 3452 | 11488
11:30 | 302 | 8045 | 3506 | 11551
12:00 | 272 | 8054 | 3560 | 11614
12:30 | 176 | 8177 | 3623.5 | 11800.5
13:00 | 80 | 8300 | 3687 | 11987
13:30 | 165 | 8384 | 3739 | 12123
14:00 | 250 | 8468 | 3791 | 12259
14:30 | 265 | 8510 | 3819.5 | 12329.5
15:00 | 280 | 8552 | 3848 | 12400
15:30 | 261 | 8612 | 3874 | 12486
16:00 | 242 | 8672 | 3900 | 12572
16:30 | 186 | 8565 | 3845.5 | 12410.5
17:00 | 130 | 8458 | 3791 | 12249
17:30 | 68 | 8435.5 | 3722.5 | 12158
18:00 | 6 | 8413 | 3654 | 12067
18:30 | 158 | 8796 | 3871.5 | 12667.5
19:00 | 310 | 9179 | 4089 | 13268
19:30 | 500 | 9588 | 4149 | 13737
20:00 | 398 | 9473 | 4319 | 13792 |  |  |  | Executive Engineer
20:30 | 353 | 9421 | 4348.5 | 13769.5 |  |  |  | Network Operation Division
21:00 | 308 | 9369 | 4378 | 13747
21:30 | 304 | 9342.5 | 4402.5 | 13745
22:00 | 300 | 9316 | 4427 | 13743 |  |  |  |  | Page 6 of 7
22:30 | 294 | 9361 | 4404.5 | 13765.5
23:00 | 288 | 9406 | 4382 | 13788
23:30 | 302 | 9383.5 | 4352.5 | 13736
24:00 | 316 | 9361 | 4323 | 13684
13792 MW (20:00 )
11614 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-04-27 |  | Energy | 295402549
[11 empty] | 2021-04-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4434 | 629 | 1897 | 4965 | 902 | 35 | 700 | 0 | 158 | 0
0:30 | 4540.5 | 677 | 1899.5 | 4662.5 | 837.5 | 35 | 605.5 | 0 | 155 | 0 | Date: | 2021-04-27
1:00 | 4647 | 725 | 1902 | 4360 | 773 | 35 | 511 | 0 | 152 | 0
1:30 | 4640.5 | 724.5 | 1909 | 4211.5 | 763 | 35 | 486 | 0 | 151 | 0 | [7 empty] | Total Energy | 295.4025 | Total Energy Gen 295.403 MKWHr Energy Not Served 0.762 MKWHr Energy Requirement 296.165 MKWHr
2:00 | 4634 | 724 | 1916 | 4063 | 753 | 35 | 461 | 0 | 150 | 0 | [7 empty] | Energy not Served | 0.762
2:30 | 4622.5 | 724 | 1954 | 4067 | 753 | 35 | 460.5 | 0 | 150 | 0 | [7 empty] | Energy Requirement | 296.1645
3:00 | 4611 | 724 | 1992 | 4071 | 753 | 35 | 460 | 0 | 150 | 0
3:30 | 4625.5 | 724.5 | 1990.5 | 3859 | 753.5 | 17.5 | 394.5 | 0 | 150 | 0 | [6 empty] | Shortage
4:00 | 4640 | 725 | 1989 | 3647 | 754 | 0 | 329 | 0 | 150 | 0
4:30 | 4663.5 | 725 | 1989.5 | 3294.5 | 753.5 | 17.5 | 233.5 | 0 | 145 | 0
5:00 | 4687 | 725 | 1990 | 2942 | 753 | 35 | 138 | 0 | 140 | 0
5:30 | 4562.5 | 725 | 2014 | 2629.5 | 738 | 35 | 130 | 0 | 135 | 2
6:00 | 4438 | 725 | 2038 | 2317 | 723 | 35 | 122 | 0 | 130 | 4
6:30 | 4458.5 | 724.5 | 2036 | 2260 | 723 | 35 | 122 | 0 | 130 | 12 |  |  |  |  | Coal
7:00 | 4479 | 724 | 2034 | 2203 | 723 | 35 | 122 | 0 | 130 | 20
7:30 | 4421 | 724.5 | 2018 | 2219.5 | 712.5 | 35 | 118 | 0 | 131 | 32.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4363 | 725 | 2002 | 2236 | 702 | 35 | 114 | 0 | 132 | 45
8:30 | 4353.5 | 725 | 1987.5 | 2421 | 703.5 | 35 | 84.5 | 0 | 133 | 54.5
9:00 | 4344 | 725 | 1973 | 2606 | 705 | 35 | 55 | 0 | 134 | 64
9:30 | 4413.5 | 725 | 1979.5 | 2706.5 | 705 | 35 | 73.5 | 0 | 133 | 72.5
10:00 | 4483 | 725 | 1986 | 2807 | 705 | 35 | 92 | 0 | 132 | 81
10:30 | 4421 | 725 | 1951.5 | 3068.5 | 714.5 | 35 | 125 | 0 | 136 | 90.5
11:00 | 4359 | 725 | 1917 | 3330 | 724 | 35 | 158 | 0 | 140 | 100
11:30 | 4288 | 725 | 1923.5 | 3395.5 | 728.5 | 35 | 212 | 0 | 142 | 101.5
12:00 | 4217 | 725 | 1930 | 3461 | 733 | 35 | 266 | 0 | 144 | 103
12:30 | 4272.5 | 724.5 | 1934 | 3508 | 752.5 | 35 | 321.5 | 0 | 148 | 104.5
13:00 | 4328 | 724 | 1938 | 3555 | 772 | 35 | 377 | 0 | 152 | 106
13:30 | 4328 | 724 | 1938 | 3555 | 772 | 35 | 377 | 0 | 152 | 106
14:00 | 4328 | 724 | 1938 | 3555 | 772 | 35 | 377 | 0 | 152 | 106
14:30 | 4475 | 724.5 | 1899 | 3616 | 796.5 | 35 | 402.5 | 0 | 155 | 90
15:00 | 4622 | 725 | 1860 | 3677 | 821 | 35 | 428 | 0 | 158 | 74
15:30 | 4633.5 | 725 | 1850 | 3763 | 831.5 | 35 | 435.5 | 0 | 154 | 58.5
16:00 | 4645 | 725 | 1840 | 3849 | 842 | 35 | 443 | 0 | 150 | 43
16:30 | 4560 | 724.5 | 1834.5 | 3800.5 | 811.5 | 35 | 468 | 0 | 145 | 31.5
17:00 | 4475 | 724 | 1829 | 3752 | 781 | 35 | 493 | 0 | 140 | 20
17:30 | 4382.5 | 724.5 | 1838.5 | 3768.5 | 751 | 35 | 505 | 0 | 142 | 11
18:00 | 4290 | 725 | 1848 | 3785 | 721 | 35 | 517 | 0 | 144 | 2
18:30 | 4373.5 | 724.5 | 1937.5 | 4171.5 | 757 | 35 | 519.5 | 59.5 | 148 | 1
19:00 | 4457 | 724 | 2027 | 4558 | 793 | 35 | 522 | 119 | 152 | 0
19:30 | 4636 | 629 | 2069 | 4843 | 845 | 35 | 520 | 192 | 160 | 0
20:00 | 4597 | 629 | 1985 | 4859 | 846 | 35 | 679 | 275 | 162 | 0
20:30 | 4540 | 629 | 1952 | 4896.5 | 875 | 35 | 678 | 273 | 164 | 0
21:00 | 4483 | 629 | 1919 | 4934 | 904 | 35 | 677 | 231 | 166 | 0
21:30 | 4456.5 | 628.5 | 1910.5 | 4937 | 924.5 | 35 | 688 | 146 | 165 | 0
22:00 | 4430 | 628 | 1902 | 4940 | 945 | 35 | 699 | 0 | 164 | 0
22:30 | 4436.5 | 628.5 | 1904.5 | 4952.5 | 945 | 35 | 698.5 | 73 | 165 | 0
23:00 | 4443 | 629 | 1907 | 4965 | 945 | 35 | 698 | 146 | 166 | 0
23:30 | 4438.5 | 629 | 1902 | 4965 | 923.5 | 35 | 699 | 73 | 162 | 0 | Max Temp. in Dhaka |  | 38.0° C
24:00 | 4434 | 629 | 1897 | 4965 | 902 | 35 | 700 | 0 | 158 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 295.403 MKWHr Energy Not Served 0.762 MKWHr Energy Requirement 296.165 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-04-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 35 | 35 | 35 | 0 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 788000
3 | Chattogram TPP-1 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2000000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 17 | 17 | 17 | 17 | 399709
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 6 | 8 | 8 | 16 | 17 | 17 | 15 | 12 | 7 | 3 | 0 | [8 empty] | 115830
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 213 | 205 | 208 | 206 | 204 | 216 | 221 | 204 | 204 | 217 | 222 | 224 | 228 | 203 | 215 |  | 208 | 228 | 228 | 230 | 230 | 230 | 230 | 5055476
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2950752
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  |  |  | 33 | 66 | 64 | 48 | 45 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1307754
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 99 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2599418
| Daudkandi 200 MW PP (B.Trac) | 185 | 50 | 50 | [12 empty] | 88 |  |  |  | 190 | 195 | 197 | 200 | 200 | 200 | 200 | 1499328
14 | Titas 50 MW Peaking PP | 48 | 48 | 48 | 48 | [8 empty] | 21 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 720040
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 116 | 110 | 116 | 118 | 110 | 120 | 120 | 118 | 180 | 185 | 145 | 185 | 178 | 180 | 180 | 150 | 110 |  | 185 | 185 | 185 | 185 | 183 | 185 | 120 | 3867000
17 | Siddhirganj 335 MW CCPP | 220 | 221 | 221 | 222 | 222 | 222 | 222 | 222 | 220 | 215 | 215 | 182 | 208 | 204 | 210 | 206 | 204 | 170 |  | 214 | 212 | 215 | 213 | 216 | 220 | 222 | 5231457
18 | Kodda 300 MW PP Unit-2 (Summit) | 235 | 235 | 235 | 160 | 45 | 45 |  |  | 11 | 106 | 197 | 209 | 202 | 194 | 202 | 209 | 209 | 209 |  | 218 | 225 | 225 | 225 | 224 | 227 | 227 | 4182653
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 81 | 81 | 130 |  | 158 | 158 | 102 | 45 | 45 | 45 | 45 | 920000
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4347000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 23 | 26 | 25 | 25 | 25 | 25 | 25 |  | 26 | 26 | 26 | 10 | 10 | 10 | 10 | 482688
33 | Ashuganj 225 MW CCPP | 212 | 212 | 213 | 216 | 216 | 207 | 200 | 180 | 178 | 181 | 192 | 207 | 207 | 199 | 204 | 206 | 191 | 196 |  | 193 | 165 | 141 | 123 | 144 | 206 | 213 | 4657000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 300 | 310 | 330 | 300 | 300 | 320 | 310 | 305 | 295 | 270 | 285 |  | 305 | 330 | 330 | 305 | 285 | 285 | 265 | 7322000
| Ashuganj 450 MW CCPP(North) | 310 | 310 | 310 | 310 | 310 | 310 | 330 | 310 | 325 | 345 | 300 | 300 | 335 | 335 | 325 | 315 | 270 | 285 |  | 315 | 350 | 335 | 300 | 280 | 280 | 280 | 7723500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 57 | 57 | 57 | 57 | 56 | 56 | 56 | 52 | 51 | 50 | 50 | 47 | 46 | 45 | 43 | 46 |  | 49 | 50 | 50 | 50 | 49 | 51 | 54 | 1239840
36 | Chandpur 150 MW CCPP | 92 | 95 | 91 | 95 | 94 | 95 | 96 | 95 | 95 | 95 | 95 | 95 | 96 | 96 | 95 | 91 | 94 | 95 |  | 95 | 96 | 95 | 94 | 95 | 95 | 95 | 2237920
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | [13 empty] | 77 | 217 | 245 | 243 | 226 |  | 181 | 274 | 273 | 269 | 268 | 268 | 268 | 2535237
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 |  | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 6837300
41 | Haripur 360MW CCPP(HPL) | 332 | 347 | 347 | 348 | 350 | 351 | 350 | 348 | 343 | 333 | 313 | 303 | 290 | 243 | 203 | 200 | 192 | 192 |  | 208 | 208 | 188 | 166 | 165 | 170 | 172 | 6512000
42 | RPCL 210MW CCPP | 182 | 184 | 187 | 187 | 193 | 204 | 202 | 197 | 189 | 179 | 164 | 162 | 157 | 157 | 145 | 149 | 134 | 131 |  | 139 | 145 | 152 | 151 | 150 | 149 | 151 | 3886880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 9 | 21 | 33 | 40 | 40 | 41 | 47 | 43 | 33 | 18 | 8 | 1 | [8 empty] | 331770
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 40 | 40 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 987360
46 | Shajibazar 330 MW CCPP | 271 | 270 | 270 | 271 | 272 | [8 empty] | 105 | 104 | 105 | 105 | 105 |  | 128 | 129 | 130 | 129 | 129 | 130 | 219 | 2509000
47 | Shahjibazar GTPP Unit- 8 & 9 | 67 | 68 | 68 | 68 | 68 | 67 | 66 | 66 | 65 | 65 | 63 | 62 | 62 | 60 | 60 | 62 | 62 | 63 |  | 64 | 64 | 64 | 64 | 65 | 65 | 66 | 1542144
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 74 | 76 | 72 | 69 | 69 | 69 | 69 | 71 |  | 72 | 72 | 73 | 74 | 74 | 74 | 74 | 1784640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 217 | 217 | 217 | 217 | 215 | 217 | 217 | 217 | 218 | 218 | 218 | 218 | 218 | 210 | 212 | 212 | 215 | 211 |  | 211 | 211 | 211 | 211 | 211 | 217 | 217 | 5118550
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 403000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 188640
54 | Hobiganj 11MW PP Cofidence-E | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 147210
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 48 | 44 | 45 | 47 | 47 | 44 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1207200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 352680
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 290 | 295 | 290 | 295 | 310 | 305 | 305 | 295 | 315 | 300 | 310 | 310 | 305 | 300 | 270 | 290 | 300 |  | 290 | 330 | 315 | 320 | 310 | 300 | 300 | 7469050
| Bibiyana South 400 MW | 370 | 370 | 370 | 370 | 370 | 384 | 395 | 370 | 370 | 389 | 370 | 371 | 371 | 373 | 378 | 370 | 370 | 384 |  | 370 | 387 | 384 | 388 | 389 | 378 | 371 | 8934800
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 0 | 1252658
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 23 | 21 | 22 | 23 | 23 |  | 11 | 24 | 24 | 24 | 23 | 24 | 21 | 22 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 540960
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 501072
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 413028
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 396072
63 | Impoprt (Tripura) | 152 | 150 | 150 | 150 | 140 | 130 | 130 | 132 | 134 | 132 | 140 | 144 | 152 | 156 | 158 | 150 | 140 | 144 |  | 152 | 160 | 162 | 166 | 164 | 166 | 158 | 3556800
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 38 | 38 | 38 | 30 | 10 | 2 | 2 | 2 | 2 | 2 | 13 | 3 | 6 | 7 | 14 | 17 |  | 21 | 23 | 26 | 34 | 27 | 35 | 37 | 473760
65 | Feni 22MW PP (Doreen) | 22 | 20 | 20 | 21 | 22 | 22 | 22 | 22 | 21 | 18 | 18 |  |  |  | 11 | 19 | 19 | 19 |  | 19 | 22 | 22 | 22 | 22 | 16 | 14 | 404676
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 |  |  | 5 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 186660
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 799200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 496020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 26 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 |  | 13 | 27 | 28 | 28 | 28 | 28 | 28 | 586440
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 762900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 764700
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 102 | 101 | 98 | 95 | 97 | 95 | 97 | 95 | 95 | 93 | 94 | 97 | 101 |  | 102 | 102 | 102 | 103 | 103 | 103 | 103 | 2346000
| Feni Lanka Power | 114 | 114 | 114 | 76 | 30 | 17 | 17 | 17 | 17 | 24 | 85 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2208180
| Chowmuhani 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 110 | 110 | 110 | 109 | 106 | 108 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2795520
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 108 | 54 | 54 | 54 | 54 | 94 | 144 | 145 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3428640
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 55 | 90 | 100 | 100 | 100 | 100 | 91 | 97 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2274192
78 | Gazipur 52 MW PP | 50 | 51 | 51 | 51 |  |  |  |  | 2 | 19 | 46 | 50 | 49 | 49 | 49 | 49 | 49 | 49 |  |  | 25 | 38 | 50 | 50 | 51 | 51 | 926880
79 | Kodda 150MW PP | 150 | 150 | 150 | 48 | 16 |  |  |  | 10 | 48 | 115 | 140 | 147 | 147 | 147 | 147 | 147 | 147 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2608320
80 | Jamalpur 95 MW PP(Powerpac) | 65 | 73 | 73 | 73 | 73 | 73 | 73 | 67 | 73 | 72 | 64 | 72 | 72 | 72 | 81 | 64 | 64 | 72 |  | 72 | 81 | 81 | 81 | 81 | 73 | 73 | 1710720
81 | Jangalia 52 MW PP (Lakdanavi) | 49 | 49 | 52 | 52 | 52 | 52 | 52 | 52 | 45 | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1228786
| Gazipur 100 MW PP | 85 | 85 | 85 | 85 | 85 | 70 | 70 | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 85 | 2052000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 |  | 4 | 5 | 5 | 4 | 4 | 3 | 2 | 1 | [9 empty] | 29895
| Jodiac Power | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 1054901
| Karnaphuli Power Ltd. | [9 empty] | 10 | 17 | 17 | 17 | 17 | 17 | 15 | 13 | 17 |  | 17 | 34 | 32 | 51 | 51 | 51 | 51 | 419016
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 230 | 230 | 235 | 225 | 220 | 230 | 225 | 240 | 245 | 238 | 230 | 240 | 248 | 260 | 260 | 265 | 265 | 265 |  | 270 | 275 | 275 | 275 | 280 | 280 | 275 | 5688611
87 | Meghnaghat 100 MW(IEL) | 100 | 100 | 100 | 100 | 100 | 28 | 16 | 16 | 62 | 91 | 91 | 99 | 98 | 98 | 96 | 97 | 96 | 100 |  | 100 | 100 | 99 | 92 | 92 | 92 | 92 | 2072540
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 62 | 53 | 58 | 90 | 90 | 90 | 89 | 89 | 89 | 90 | 89 | 90 | 90 |  | 89 | 89 | 90 | 90 | 90 | 90 | 90 | 2070720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 385920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 49 | 49 | 49 | 49 | 49 | 40 | 51 | 51 | 51 | 51 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1061349
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 48 | 24 | 24 | 24 | 72 | 84 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2129616
95 | Patenga 50MW PP (Baraka) | 39 | 39 | 39 | 39 | 26 |  |  | 1 | 17 | 24 | 26 | 37 | 41 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 847200
96 | Chattogram 108 MW PP (ECPV) | 90 | 90 | 90 | 90 | 69 | 27 | 25 | 25 | 20 | 20 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 51 | 84 | 912960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 50 | 44 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1212753
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 17 |  |  |  | 17 | 37 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1089869
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3554754
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 12750
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 831240
104 | Keranigonj 300 MW PP (APR) | 81 | [18 empty] | 220 | 306 | 304 | 302 | 301 | 303 | 302 | 1731263
105 | Bramhangoan 100 MW PP (Aggreko) | 100 | [18 empty] | 97 | 100 | 100 | 100 | 100 | 100 | 100 | 676209
106 | Mymensingh 200 MW PP (United) | 200 | 200 | 200 | 120 | 40 | 40 | 40 | 40 | 40 | 53 | 98 | 139 | 183 | 193 | 194 | 194 | 195 | 197 |  | 198 | 200 | 200 | 200 | 200 | 193 | 193 | 3655200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 134 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 145 | 138 | 138 | 138 | 145 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3538080
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 90 | 75 | 90 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2338560
116 | Chandpur 200MW (Desh energy) | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 145 | 141 | 141 | 136 | 121 | 120 | 120 | 130 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3460320
117 | Ashuganj 150MW PP (Midland) | 73 | 73 | 78 | 80 | 80 | 73 | 75 | 74 | 66 | 73 | 72 | 75 | 80 | 90 | 88 | 90 | 93 | 85 |  | 86 | 86 | 83 | 97 | 103 | 107 | 115 | 2018981
118 | Bibiyana-III 400 MW CCPP | 367 | 380 | 366 | 372 | 367 | 380 | 380 | 365 | 379 | 400 | 368 | 367 | 396 | 399 | 374 | 368 | 371 | 321 |  | 379 | 404 | 391 | 404 | 382 | 383 | 367 | 9053000
| Jamalpur 115 MW PP (United) | 108 | 108 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 107 | 115 | 96 | 96 | 96 | 95 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2631600
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2298240
| Anlima Energy Ltd. | 90 | 90 | 90 | 90 | 90 | 35 | 35 | 40 | 72 | 75 | 114 | 116 | 115 | 115 | 116 | 116 | 115 | 115 |  | 115 | 115 | 114 | 114 | 111 | 109 | 109 | 2327182
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 862560
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 13 | 19 | 23 | 31 | 31 | 29 | 26 | 20 | 12 | 6 | 1 | [8 empty] | 215201
120 | Eastern Zone Total | 9039 | 8757 | 8743 | 8377 | 7879 | 7201 | 7168 | 7131 | 7360 | 7814 | 8036 | 8054 | 8300 | 8468 | 8552 | 8672 | 8458 | 8413 |  | 9179 | 9588 | 9473 | 9369 | 9316 | 9406 | 9361 | 201889500
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2201280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 14 | 14 | 14 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 10 | 11 | 11 | 11 | 11 | 14 | 14 |  | 14 | 20 | 20 | 19 | 18 | 18 | 19 | 240480
| Khulna 225 MW CCPP | [21 empty] | 160 | 160 | 164 | 164 | 164 | 685506
129 | Rupsha 105 MW PP (Orion rupsha) | 92 | 92 | 92 | 92 | 53 | 35 | 17 | 17 | 52 | 53 | 92 | 91 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 1904640
130
131
132 | United Payra Power Ltd. | 72 | 72 | 72 | 72 | 35 | [9 empty] | 17 | 17 | 17 | 17 |  | 40 | 72 | 72 | 107 | 107 | 107 | 107 | 921600
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 48 | 48 | 16 | 16 | 32 | 48 | 16 | 16 | 32 | 32 | 32 | 32 | 64 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1709280
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 94 | 95 | 95 | 96 | 96 | 94 | 96 | 97 | 97 | 98 |  | 97 | 96 | 96 | 97 | 96 | 95 | 97 | 2309109
| Bhola 225 MW CCPP | 68 | 67 | 68 | 68 | 69 | 68 | 67 | 65 | 66 | 64 | 62 | 61 | 62 | 61 | 63 | 65 | 65 | 66 |  | 66 | 66 | 66 | 66 | 68 | 67 | 66 | 1571000
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 34 | 33 | 28 | 27 | 25 | 18 | 23 | 23 | 24 | 26 | 26 | 22 | 28 | 23 | 26 |  | 34 | 34 | 34 | 34 | 34 | 35 | 34 | 686926
141 | Noapara 100 MW PP (Bangla Trac) | 98 | 98 | 97 | [12 empty] | 27 |  |  |  | 57 | 100 | 100 | 100 | 100 | 100 | 100 | 988800
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | [6 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 569250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 725 | 724 | 724 | 725 | 725 | 725 | 724 | 725 | 725 | 725 | 725 | 725 | 724 | 724 | 725 | 725 | 724 | 725 |  | 724 | 629 | 629 | 629 | 628 | 629 | 629 | 17040000
147 | Bheramara 410 MW CCPP | 305 | 310 | 315 | 325 | 345 | 340 | 340 | 330 | 330 | 325 | 325 | 320 | 320 | 315 | 300 | 290 | 280 | 265 |  | 225 | 210 | 210 | 190 | 190 | 170 | 170 | 7093440
148 | Payra 1320 MW | 550 | 530 | 530 | 530 | 530 | 500 | 500 | 480 | 480 | 480 | 500 | 510 | 550 | 560 | 600 | 622 | 560 | 500 |  | 570 | 622 | 622 | 622 | 622 | 622 | 580 | 14163200
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 74 | 73 | 73 | 73 | 72 | 75 | 75 | 74 | 73 | 72 | 73 | 72 | 71 | 72 | 73 |  | 74 | 74 | 75 | 72 | 73 | 73 | 72 | 1786473
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 148 |  | 149 | 149 | 149 | 210 | 250 | 250 | 250 | 3941100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [10 empty] | 43 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 717927
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 113 | 113 | 125 | 126 | 125 | 130 | 124 | 132 | 80 | 80 | 80 | 80 | 80 | 120 | 129 | 128 | 120 | 100 |  | 95 | 90 | 89 | 85 | 81 | 75 | 75 | 2667500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 175 | 177 | 178 | 179 | 180 | 180 | 178 | 177 | 176 | 173 | 171 | 171 | 169 | 165 | 160 | 164 | 164 | 148 |  | 150 | 154 | 154 | 144 | 140 | 133 | 133 | 4172727
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 174 | 198 | 196 | 196 | 194 | 190 | 190 | 190 | 140 |  | 162 | 159 | 158 | 162 | 153 | 143 | 142 | 4373500
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 342 | 346 | 408 | 409 | 404 | 404 | 418 | 402 | 402 | 404 | 388 | 397 | 402 | 398 | 405 | 374 | 339 | 335 |  | 411 | 410 | 413 | 410 | 413 | 412 | 394 | 9415782
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 20 | 20 | 20 | [9 empty] | 15 | 42 | 40 | 40 | 40 | 33 |  | 30 | 22 | 20 | 20 | 40 | 41 | 42 | 435833
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 21 | 21 | 21 | 17 | 20 | 20 | 17 | 18 | 19 | 19 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 465120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 10 | 10 | 10 | 10 | 10 | 11 | 251406
165 | Amnura 50 MW PP(Sinha) | 42 | 42 | 42 | [7 empty] | 18 | 33 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 685220
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | [7 empty] | 16 | 16 | 16 | 34 | 34 | 34 | 43 | 34 |  | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 532688
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 30 | [8 empty] | 27 | 29 | 29 | 29 | 29 | 29 |  | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 428176
168 | Santahar 50 MW Peaking PP | 31 | 31 | 31 | 32 | [10 empty] | 15 | 33 | 32 | 32 |  | 32 | 32 | 32 | 32 | 32 | 31 | 31 | 412030
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1233120
170 | Chapainawabganj 100 MW Peaking PP | 100 | 100 | 99 | 99 | 50 | 50 | 50 | 42 | 42 | 41 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 96 |  | 100 | 100 | 100 | 100 | 99 | 98 | 98 | 1646656
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 150 | 200 | 200 | 200 | 200 | 200 | 200 | 1086562
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 50 | 50 | 35 | 35 | 101 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2505984
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 108 | 108 | 50 |  |  | 20 | 35 | 50 | 70 | 90 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2113056
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 106 |  | 60 | 100 | 102 | 113 | 110 | 110 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2515200
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 6 | 7 | 7 | 7 | 5 | 3 | 2 | 0 | [8 empty] | 42478
178
178