## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | March 2021 |  | February 2021 |  | March 2020
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 12790 | 24-03-2021 | 10603 | 28-02.2021 | 10790 | 18/03/20 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:00 |  | 19:30 |  | 21:00
2 | Minimum Generation (MW) | 6990 | 04/03/21 | 5490 | 06/02/21 | 5676.1 | 03/03/20 | - | -
|  |  | 5:00 |  | 5:00 |  | 5:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 12790 | 24-03-2021 | 10603 | 28-02.2021 | 10790 | 18/03/20 | 12893 | 29/05/19
|  |  | 21:00 |  | 19:00 |  | 19:30 |  | 21:00
4 | Maximum Day Peak Generation (MW) | 11146 | 23-03-2021 | 9477 | 28-02.2021 | 9428.9 | 18/03/20 | 10888 | 05/09/20
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 12790 | 24-03-2021 | 10603 | 28-02.2021 | 10790 | 18/03/20 | 12893 | 29/05/19
|  |  | 19:00 |  | 19:00 |  | 19:30 |  | 21:00
6 | Average Generation (MW) at Evening Peak | 11476.6774 |  | 9322.5714 |  | 9878.5806 |  | 11890.0667 | Sept'20
7 | Average Generation (MW) at Day Peak | 9678.4516 |  | 8098.1429 |  | 8156.329 |  | 9378.1933 | 2019-09-19
8 | Maximum Power Import from India, BIPTC (MW) | 850 | 29/03/2021 | 914 | 07/02/2021 | 943 | 23/03/2020 | 956 | 27/3/2019
|  |  | 1:00 |  | 22:30 |  | 20:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 186 | 27/03/2021 | 146 | 27/02/2021 | 152 | 15/03/2020 | 194 | 12/06/19
|  |  | 18:30 |  | 18:30 |  | 18:30 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 1459 | 04/05/2010
20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 3707.5 | 05/04/10
20:00
12 | Minimum Load Shed (MW) at Evening Peak | - | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | - |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1525.7498 |  | 1022.6216 |  | 3315.9631 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 100.5824 |  | 74.8015 |  | 120.7397
22 | Net Generation of BPDB (MKWH) | 1425.1675 |  | 947.8201 |  | 3195.2234
23 | Net Generation of IPP (MKWH) | 3900.6099 |  | 3226.3213 |  | 1441.9411
24 | Net Generation of REB (MKWH) | 123.4508 |  | 123.6043 |  | 138.6817
24 | Net Generation of Rental Power Plant (MKWH) | 358.3773 |  | 326.6792 |  | 370.9007
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 5807.6055 |  | 4624.4249 |  | 5146.7469 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 3953.2485 |  | 3020.1887 |  | 4289.7961 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 286.3058 |  | 280.0725 |  | 118.3913 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1161.4759 |  | 918.8193 |  | 676.8041 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 45.441 |  | 44.929 |  | 52.3268 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 18.2866 |  | 15.6531 |  | 3.9096 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 443.4301 |  | 419.5638 |  | 126.2587 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 584.9063 |  | 510.4868 |  | 611.4663 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 68.2352 |  | 73.1166 |  | 72.2749 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:March' 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quintity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 12790 | 24-03-2021 | 21:00
Generation Period
| Dhaka | MW | 4324
| Chattogram | MW | 1247
| Cumilla | MW | 1190
| Mymensingh | MW | 1016
| Sylhet | MW | 469
a) | Total supply in East zone | MW | 8246
| Khulna | MW | 1483
| Barisal | MW | 333
| Rajshahi | MW | 1319
| Rangpur | MW | 744
b) | Total supply in West zone | MW | 3879
c) | Total supply in both zone ( a+b) | MW | 12125
Ref: | 27.21.0000.603.16.087.20.400 | Date: 18/04/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:March' 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 575 | 2021-03-13 | 16:00
| b) Ishurdi end | MW | 130 | 2021-03-01 | 8:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 350 | 2021-03-01 | 8:00
| b) Ishurdi end | MW | 262 | 2021-03-13 | 15:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 6.4223
| b) Ishurdi end | MKWH | 27.5883
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 28.023
| b) Ishurdi end | MKWH | 6.2353
23 | Transmission loss of EWI/ NO-1 | % | 2.91
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 580 | 2021-03-13 | 15:00
| b)Serajganj end | MW | 320 | 2021-03-01 | 7:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 340 | 2021-03-03 | 19:00
| b)Sirajganj end | MW | 560 | 2021-03-13 | 15:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 0.701 | 2021-03-30
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 0.711 | 2021-03-30
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 21.924
| b)Sirajganj end | MKWH | 52.042
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 50.88
| b)Sirajganj end | MKWH | 22.176
30 | Transmission loss of EWI /NO-2 | % | 1.23
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Sherpur | 132/33 kV Transformers-T1 & T3 | 2021-03-02 02:42 | 2021-03-02 02:54 | 0:12 | T | Due to 33 kV feeder fault | 50 | 10 | Power interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-03-02 10:06 | 2021-03-02 18:13 | 8:07 | T | Due to widing temperature high | 73 | 592.5167 | Power interruption
Manikganj | 132/33 kV Transformer-GT3 | 2021-03-03 11:28 | 2021-03-03 11:33 | 0:05 | T | Due to tripping of Solar plant | 0 | 0 | No interruption
| 132/33 kV Transformer-GT3 | 2021-03-06 21:09 | 2021-03-06 21:11 | 0:02 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2021-03-08 08:55 | 2021-03-08 09:50 | 0:55 | T |  | 75 | 68.75 | Power interruption
Mirpur | 132/33 kV Transformer-T2 | 2021-02-08 16:35 | 2021-02-08 17:45 | 1:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajendrapur | 132/33 kV Transformers-T1 & T2 | 2021-03-12 05:42 | 2021-03-12 07:30 | 1:48 | T | Tripped showing dist. relay | 76 | 136.8 | Power interruption
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2021-03-13 17:20 | 2021-03-13 17:28 | 0:08 | T | Tripped showing O/C relay at 33 kV side | 15 | 2 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2021-03-14 00:17 | 2021-03-14 00:28 | 0:11 | T | Due to 33 kV feeder fault | 80 | 14.6667 | Power interruption
Kadda | 132/33 kV Transformers-T1 & T2 | 2021-03-15 10:29 | 2021-03-15 10:51 | 0:22 | T | Tripped showing O/C relay | 64 | 23.4667 | Power interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-03-20 20:16 | 2021-03-20 22:28 | 2:12 | E/O | Due to red-hot maintenance at 33 kV side | 45 | 99 | Power interruption
| 132/33 kV Transformer-T2 | 2021-03-21 15:50 | 2021-03-21 17:44 | 1:54 | E/O | Due to red-hot maintenance at 33 kV side | 60 | 114 | Power interruption
Aminbazar | 230/132 kV Transformer-T01 | 2021-03-23 09:31 | 2021-03-23 13:17 | 3:46 | T | Tripped showing Differential. relay | 0 | 0 | No interruption
Tongi(O) | 132/33 kV Transformer-T1 | 2021-03-28 12:14 | 2021-03-28 16:57 | 4:43 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-28 13:16 | 2021-03-28 13:33 | 0:17 | T | Due to winding temterature high | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2021-03-29 22:35 | 2021-03-29 22:44 | 0:09 | T | Due to 33 kV feeder fault | 126 | 18.9 | Power interruption
Kishoreganj | 33 kV Bus | 2021-03-30 19:57 | 2021-03-30 20:42 | 0:45 | T | Due to 33 kV feeder fault | 100 | 75 | Power interruption
Kodda | 132/33 kV Transformers-T3 T-4 & T5 | 2021-03-31 11:28 | 2021-03-31 11:40 | 0:12 | T | Due winding temperature high | 0 | 0 | No interruption
|  |  | Total : | 26:58 |  | Unserved Energy: |  | 1155.1
Dhaka (South) Grid Circle :
Haripur | 132 kV reserve Bus | 2021-03-14 12:40 | 2021-03-14 14:29 | 1:49 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Ghorashal | 132 kV Bus-2 | 2021-03-27 06:39 | 2021-03-27 09:54 | 3:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
|  |  | Total : | 5:04 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Cox'sbazar | 132/33 kV Transformer-T3 | 2021-03-03 18:33 | 2021-03-03 18:45 | 0:12 | T | Tripped showing O/C relay | 42 | 8.4 | Power interruption
| 132/33 kV Transformer-T3 | 2021-03-03 19:08 | 2021-03-03 19:35 | 0:27 | T |  | 36 | 16.2 | Power interruption
Hathazari | 132/33 kV Transformer-T1 | 2021-03-04 07:55 | 2021-03-04 08:54 | 0:59 | E/O | Due to sparking at R-phase Breaker | 0 | 0 | No interruption
Halishahar | 132/33 kV Transformers-T1 & T3 | 2021-03-05 15:52 | 2021-03-05 16:51 | 0:59 | E/O | Due to emergency maintenance | 30 | 29.5 | Power interruption
BSRM | BSRM 230 kV Bus extension- 1 | 2021-03-12 07:53 | 2021-03-12 13:12 | 5:19 | E/O | Due to flashing at sectionalizer isolator Bus-1 | 0 | 0 | No interruption
| BSRM 230 kV Bus extension- 2 | 2021-03-12 07:53 | 2021-03-12 17:07 | 9:14 | E/O |  | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformers-T1 & T2 | 2021-03-13 08:45 | 2021-03-13 09:04 | 0:19 | T | Tripped showing O/C & E/F relay at 33 kV side | 35 | 11.0833 | Power interruption
| 132/33 kV Transformers-T1 & T2 | 2021-03-26 01:23 | 2021-03-26 01:48 | 0:25 | T | Due to 33 kV feeder fault | 55 | 22.9167 | Power interruption
Khulshi | 132/33 kV Transformer-T1 | 2021-03-30 06:52 | 2021-03-30 08:40 | 1:48 | E/O | Due to Oil leakage | 0 | 0 | No interruption
|  |  | Total : | 19:42 |  | Unserved Energy: |  | 88.1
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T1 | 2021-03-02 11:55 | 2021-03-02 12:54 | 0:59 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Chandpur | 132/33 kV Transformers-T1 ,T 2& T3 | 2021-03-04 11:56 | 2021-03-04 12:11 | 0:15 | T | Tripped showing O/V relay | 27 | 6.75 | Power interruption
Feni | 132/33 kV Transformer-T1 | 2021-03-07 06:58 | 2021-03-07 15:32 | 8:34 | E/O | Due to 33 kV post insulator Burst | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T2 | 2021-03-07 08:17 | 2021-03-07 15:49 | 7:32 | E/O | Due to Oil centrifuge | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformers-T1 & T2 | 2021-03-08 07:58 | 2021-03-08 08:11 | 0:13 | T | Due to 33 feeder fault | 100 | 21.6667 | Power interruption
Sreemongal | 132/33 kV Transformers-T2 & T3 | 2021-03-09 04:59 | 2021-03-09 05:06 | 0:07 | T | Tripped showing O/C relay at 33 kV side | 14 | 1.6333 | Power interruption
Kulaura | 132/33 kV Transformer-T2 | 2021-03-09 09:34 | 2021-03-09 10:23 | 0:49 | T | Tripped showing Buchholz relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: March 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Sylhet | 132/33 kV Transformer-T2 & 33 kV Bus | 2021-03-12 06:57 | 2021-03-12 08:19 | 1:22 | E/O | Due to red-hot maintenance at 33 kV Bus | 43 | 58.7667 | Power interruption
Chowmuhani | 132/33 kV Transformers-T1 & T2 | 2021-03-14 14:45 | 2021-03-14 14:55 | 0:10 | T | Due to 33 feeder fault | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2021-03-22 14:48 | 2021-03-22 14:48 | 0:00 | T | Tripped showing Operating PRD relay | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformers-T1 A& B | 2021-03-24 18:55 | 2021-03-24 20:47 | 1:52 | E/O | Due to red-hot maintenance at 33 kV Bus | 20 | 37.3333 | Power interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2021-03-25 07:15 | 2021-03-25 08:55 | 1:40 | E/O | Due to red-hot maintenance at 33 kV Bus | 30 | 50 | Power interruption
Cumilla(N) | 132/33 kV Transformers-T3 & T4 | 2021-03-27 19:23 | 2021-03-27 19:40 | 0:17 | E/O | Due to cable bursting of 33 kV Transformer T3 | 100 | 28.3333 | Power interruption
B.Baria | 132/33 kV Transformer-T1 | 2021-03-28 11:14 | 2021-03-28 12:34 | 1:20 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2021-03-31 07:20 | 2021-03-31 08:32 | 1:12 | E/O | Due to red-hot maintenance at 33 kV side | 40 | 48 | Power interruption
|  |  | Total : | 26:22 |  |  |  | 252.4833
Khulna Grid Circle :
Norail | 132/33 kV Transformer-T2 | 2021-03-06 15:14 | 2021-03-06 17:49 | 2:35 | E/O | Due to Oil leakage of (B-phase) PT | 5 | 12.9167 | Power interruption
Khulna© | 132 kV main Bus | 2021-03-12 07:53 | 2021-03-12 11:55 | 4:02 | E/O | Due to flashing at sectionalizer isolator Bus-1 | 144 | 148.8 | Power interruption 7:53 to 08:55
Barishal(N) | 132/33 kV Transformer-T5 | 2021-03-13 20:02 | 2021-03-13 20:37 | 0:35 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T5 | 2021-03-14 12:29 | 2021-03-14 12:58 | 0:29 | T | Tripped showing Diff. relay at 33 kV side | 0 | 0 | No interruption
Khulna(S) | capacitor bank | 2021-03-15 21:20 | 2021-03-15 21:20 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T-2 | 2021-03-16 22:50 | 2021-03-16 22:50 | 0:00 | T | Due to CB problem | 0 | 0 | No interruption
Bottail | 132/33 kV Transformer-T-1 | 2021-03-22 13:55 | 2021-03-22 14:40 | 0:45 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Barishal(N) | 132/33 kV Transformer-T-1 | 2021-03-24 06:17 | 2021-03-24 06:36 | 0:19 | E/O | Due to Oil leakage at 33 kV side | 10 | 3.1667 | Power interruption
Faridpur | 132/33 kV Transformer-T-3 | 2021-03-25 13:44 | 2021-03-25 14:08 | 0:24 | E/O | Due to red-hot maintenance at 33 kV side | 7 | 2.8 | Power interruption
|  |  | Total : | 9:09 |  | Unserved Energy: |  | 167.6833
HVDC Grid Circle :
Ishurdi | 132/33 kV Transformer-T-1 | 2021-03-18 22:13 | 2021-03-18 23:48 | 1:35 | E/O | Due to red-hot maintenance | 10 | 15.8333 | Power interruption
|  |  | Total : | 1:35 |  |  |  | 15.8333
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformers-T-1 | 2021-03-08 07:01 | 2021-03-08 10:15 | 3:14 | E/O | Due to 33 kV feeder fault
| 132/33 kV Transformers-T-2 | 2021-03-08 07:01 | 2021-03-08 12:22 | 5:21 | E/O |  | 70 | 374.5 | Power interruption 07:01 to 12:22
| 132/33 kV Transformers-T-3 | 2021-03-08 07:01 | 2021-03-08 10:56 | 3:55 | E/O
Amnura | 132/33 kV Transformer-T1 | 2021-03-13 16:16 | 2021-03-14 15:33 | 23:17 | E/O | Due to to flashing in LT Bushing | 0 | 0 | No interruption
Mahasthangar | 33 kV Bus | 2021-03-14 08:47 | 2021-03-14 09:43 | 0:56 | E/O | Due to red-hot maintenance at 33 kV side | 20 | 18.6667 | Power interruption
Bogura | 132/33 kV Transformer-T2 | 2021-03-17 12:24 | 2021-03-17 12:45 | 0:21 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Niyamatpur | 33 kV Bus | 2021-03-21 23:37 | 2021-03-22 00:33 | 0:56 | E/O | Due to red-hot maintenance at 33 kV side | 24 | 22.4 | Power interruption
Rangpur | 132/33 kV Transformer-T1 | 2021-03-22 10:22 | 2021-03-22 11:45 | 1:23 | E/O | Due to to flashing at Rangpur S/S | 10 | 13.8333 | Power interruption
Sirajganj | 132/33 kV Transformer-T1 | 2021-03-24 07:36 | 2021-03-24 09:25 | 1:49 | E/O | Due to red-hot maintenance at 33 kV side | 30 | 54.5 | Power interruption
Palashbari | 132/33 kV Transformer-T3 | 2021-03-24 10:48 | 2021-03-24 13:09 | 2:21 | E/O | Due to Oil leakage | 0 | 0 | No interruption
Ruppur | 132/33 kV Transformer-T2 | 2021-03-25 01:01 | 2021-03-25 12:55 | 11:54 | T | Tripped showing diff. relay | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T4 | 2021-03-25 07:38 | 2021-03-25 08:50 | 1:12 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
Niyamatpur | 132/33 kV Transformer-T1 | 2021-03-31 06:15 | 2021-03-31 08:25 | 2:10 | E/O | Due to red-hot maintenance at 33 kV side | 0 | 0 | No interruption
|  |  | Total : | 58:49 |  |  |  | 483.9
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 147:39 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-1 | 2021-03-12 05:42 | 2021-03-12 05:55 | 0:13 | T | Tripped showing dist. relay | 300 | 65 | Power interruption 05:42 to 05:55
| Tongi-Kabirpur 132 kV line-2 | 2021-03-12 05:42 | 2021-03-12 05:56 | 0:14 | T | Tripped showing dist. relay
| Tongi-Kabirpur 132 kV line-1 | 2021-03-23 02:10 | 2021-03-23 02:31 | 0:21 | T | Tripped showing dist. relay | 342 | 153.9 | Full interruption at Manikganj(48 MW) & Rajendrapur(70 MW) S/S area and partial at Kabirpur(94 MW) and Kodda(130MW) till 02:37
| Tongi-Kabirpur 132 kV line-2 | 2021-03-23 02:10 | 2021-03-23 02:25 | 0:15 | T | Tripped showing O/C & E/F relay
Kodda | Kodda-Gazipur 100 MW 132 kV line | 2021-03-23 02:10 | 2021-03-23 02:37 | 0:27 | T | Tripped showing dist. relay
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2021-03-24 10:29 | 2021-03-24 11:51 | 1:22 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Jamalpur-UMPL 132 kV line-2 | 2021-03-24 11:54 | 2021-03-24 12:52 | 0:58 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2021-03-25 17:28 | 2021-03-25 17:38 | 0:10 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Kabirpur-Tongi 132 kV line-2 | 2021-03-25 17:28 | 2021-03-25 17:34 | 0:06 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrakona 132 kV line-1 | 2021-03-30 20:03 | 2021-03-30 20:36 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2021-03-31 18:06 | 2021-03-31 20:17 | 2:11 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 6:50 |  | Unserved Energy: |  | 218.9
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 230 kV line-1 | 2021-03-02 10:58 | 2021-03-02 14:11 | 3:13 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2021-03-07 20:51 | 2021-03-07 21:01 | 0:10 | T | Tripped showing O/C & E/F relay | 95 | 15.8333 | Power interruption
Rampura | Rampura-Bashundhara 132 kV line-1 | 2021-03-13 16:45 | 2021-03-13 17:54 | 1:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Rampura-Bhulta 230 kV line-4 | 2021-03-13 16:56 | 2021-03-13 16:56 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line | 2021-03-14 16:07 | 2021-03-14 18:08 | 2:01 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| Rampura-Bhulta 132 kV line | 2021-03-18 13:47 | 2021-03-18 15:55 | 2:08 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV line-1 &2 | 2021-03-18 20:35 | 2021-03-18 20:59 | 0:24 | T | Tripped showing dist. relay | 100 | 40 | Power interruption
Haripur | Haripur-Ullon 132 kV line | 2021-03-21 10:09 | 2021-03-21 10:30 | 0:21 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hasnabad | Hasnabad-Brahmangaon 132 kV line | 2021-03-25 10:15 | 2021-03-25 13:26 | 3:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara - 2& Rampura-Gulshan 132 kV line-1 | 2021-03-26 03:30 | 2021-03-26 04:40 | 1:10 | E/O | Due to CT burst of Rampura-Bashundhara S/S | 58 | 16.4333 | Power interruption 03:30 to 03:47
| Rampura-Bashundhara 132 kV line-1 | 2021-03-26 03:30 | 2021-03-26 08:26 | 4:56 | E/O
Shyampur(N) | Shyampur(N)-Shyampur(O) 132 kV line-2 | 2021-03-27 09:42 | 2021-03-27 22:54 | 13:12 | T | Tripped showing E/F relay | 180 | 150 | Power interruption 09:42 to 10:32
| Shyampur(N)-Shyampur(O) 132 kV line-1 | 2021-03-27 09:42 | 2021-03-27 10:32 | 0:50 | T | Tripped showing main protection relay
|  |  | Total : | 32:45 |  | Unserved Energy: |  | 222.2667
Chattogram Grid Circle :
Hathazari | Hathazari-Raozan 230 kV line-1 & 2 | 2021-03-04 21:37 | 2021-03-04 22:25 | 0:48 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Hathazari-Baraulia 230 kV line-1 | 2021-03-12 10:04 | 2021-03-12 15:46 | 5:42 | T | Tripped showing dist. relay | 0 | 0 | No interruption
BSRM | BSRM-Power P/P 230 kV line-2 | 2021-03-12 07:53 | 2021-03-12 14:01 | 6:08 | E/O | Due to flashing at sectionalizer isolator Bus-1 | 0 | 0 | No interruption
| BSRM-Mirersorai 230 kV line-1 | 2021-03-12 07:53 | 2021-03-12 14:56 | 7:03 | E/O |  | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K chemical 132 kV line | 2021-03-14 09:52 | 2021-03-14 12:46 | 2:54 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV line-2 | 2021-03-30 17:30 | 2021-03-30 17:55 | 0:25 | E/O | Due to CB trouble Shahmirpur end | 0 | 0 | No interruption
|  |  | Total : | 23:00 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2021-03-02 01:07 | 2021-03-02 02:01 | 0:54 | T | Tripped showing dist. relay | 26 | 23.4 | Power interruption
Cumilla(S) | Cumilla(S)-Tripura 132 kV line-1 & 2 | 2021-03-03 11:23 | 2021-03-03 11:56 | 0:33 | T | Tripped showing SPS maltifunction | 0 | 0 | No interruption
| Cumilla(S)-Tripura 132 kV line-1 & 2 | 2021-03-03 12:17 | 2021-03-03 12:44 | 0:27 | T |  | 110 | 49.5 | Power interruption
Fenchuganj | Fenchuganj-Sreemongal 132 kV line | 2021-03-03 14:29 | 2021-03-03 16:14 | 1:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chandpur Desh | Chandpur Desh-Ramganj 132 kV line-1 & 2 | 2021-03-04 11:56 | 2021-03-04 12:11 | 0:15 | T | Tripped showing O/V relay | 0 | 0 | No interruption
Page: 2/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month: March 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Chandpur S/S | Chandpur S/S-Chandpur Desh 132 kV line-1 & 2 | 2021-03-04 11:56 | 2021-03-04 12:09 | 0:13 | T |  | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2021-03-06 17:52 | 2021-03-06 18:01 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj(N) | Ashuganj(N)-Bhulta 400 kV line-2 | 2021-03-10 13:49 | 2021-03-10 15:07 | 1:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj S/S 132 kV line | 2021-03-13 04:43 | 2021-03-13 05:02 | 0:19 | T | Tripped showing dist. relay | 28 | 8.8667 | Power interruption
| Sylhet-Chatak 132 kV line-2 | 2021-03-14 07:57 | 2021-03-14 08:08 | 0:11 | T | Tripped showing dist.(C-phase) relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhani 132 kV line-1 | 2021-03-18 20:56 | 2021-03-18 22:00 | 1:04 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2021-03-29 05:43 | 2021-03-29 05:52 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj -Shahjibazar 132 kV line | 2021-03-30 01:14 | 2021-03-30 01:14 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV line-2 | 2021-03-30 01:25 | 2021-03-30 01:31 | 0:06 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chatak 132 kV line | 2021-03-30 02:08 | 2021-03-30 02:34 | 0:26 | T | Tripped showing VT fuse fail | 20 | 8.6667 | Power interruption
Sylhet | Sylhet-Fenchuganj 132 kV line | 2021-03-30 02:23 | 2021-03-30 02:35 | 0:12 | T | Tripped showing dist. relay | 40 | 12.6667 | Power interruption 02:23 to 02:42
| Sreemongal-Shahjibazar 132 kV line-1 | 2021-03-30 22:04 | 2021-03-30 22:26 | 0:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sreemongal | Sreemongal-Fenchuganj 132 kV line-2 | 2021-03-31 01:00 | 2021-03-31 01:33 | 0:33 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Daudkandi | Daudkandi-Cumill(N) 132 kV line-1 | 2021-03-31 15:06 | 2021-03-31 15:14 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 9:04 |  | Unserved Energy: |  | 103.1
Khulna Grid Circle :
Madaripur | Madaripur-Gopalganj 132 kV line-2 | 2021-03-17 12:28 | 2021-03-17 12:35 | 0:07 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Bhola 230 kV line-2 | 2021-03-22 12:01 | 2021-03-22 12:39 | 0:38 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Barishal(N)-Bhola 230 kV line-2 | 2021-03-23 10:41 | 2021-03-23 14:43 | 4:02 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Faridpur 132 kV line-1 | 2021-03-26 22:59 | 2021-03-26 23:22 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 5:10 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2021-03-01 03:24 | 2021-03-01 04:25 | 1:01 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-1 | 2021-03-06 12:07 | 2021-03-06 13:23 | 1:16 | T | Tripped showing E/F. relay | 0 | 0 | No interruption
| Bheramara-Bottail 132 kV line-2 | 2021-03-06 11:37 | 2021-03-06 12:07 | 0:30 | T | Tripped showing E/F. relay | 258 | 129 | Power interruption 11: 37 to 12:07
Jessore | Jessore-Noapara 132 kV line-1 & 2 | 2021-03-06 11:37 | 2021-03-06 11:48 | 0:11 | T |  | 0 | 0 | No interruption
| Jessore-Jhenidah 132 kV line-1 & 2 | 2021-03-06 11:37 | 2021-03-06 12:06 | 0:29 | T |  | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line-1 | 2021-03-07 12:49 | 2021-03-08 19:50 | 31:01 | E/O | Due to Oil leakage at CB | 0 | 0 | No interruption
|  |  | Total : | 34:28 |  | Unserved Energy: |  | 129
Bogura Grid Circle:
Sirajganj | Sirajganj-Ashuganj 230 kV line-1 | 2021-03-07 01:08 | 2021-03-07 01:57 | 0:49 | T | Tripped showing dist. relay | 28 | 22.8667 | No interruption
Bogura Confidence | Bogura Confidence -Bogura New 132 kV line | 2021-03-13 14:20 | 2021-03-13 14:47 | 0:27 | T | Tripped showing O/V. relay | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV line-2 | 2021-03-29 14:49 | 2021-03-29 17:15 | 2:26 | E/O | Due to red-hot maintenance | 85 | 138.8333 | Power interruption 14:49 16:27
Natore | Natore-Bogura 132 kV line-2 | 2021-03-30 10:55 | 2021-03-30 11:08 | 0:13 | T | Tripped showing dist. relay | 0 | 0 | No interruption
| Natore-Rajshahi 132 kV line-1 | 2021-03-30 10:55 | 2021-03-30 11:15 | 0:20 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2021-03-31 06:35 | 2021-03-31 08:26 | 1:51 | T | Tripped showing dist.& E/F relay | 0 | 0 | No interruption
|  |  | Total : | 6:06 |  | Unserved Energy: |  | 161.7
Others :
Ullon | Ullon-Haripur 132 kV line-2 | 2020-03-18 06:45 | 2020-03-18 07:08 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
|  |  | Total : | 0:23 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 117:46 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Netrakona | 132/33 kV Transformer-T4 | 2021-03-02 08:24 | 2021-03-02 16:34 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 | 2021-03-02 10:02 | 2021-03-02 10:18 | 0:16 | S/O |  | 0 | 0 | No interruption
Kaliakoir | 132 kV Bus | 2021-03-02 10:14 | 2021-03-02 10:14 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T3 | 2021-03-03 07:02 | 2021-03-05 17:14 | 58:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T1 | 2021-03-03 09:52 | 2021-03-03 16:12 | 6:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-GT2 | 2021-03-03 08:20 | 2021-03-03 15:25 | 7:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | 132/33 kV Transformer-GT3 | 2021-02-03 09:15 | 2021-02-03 16:27 | 7:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-GT1 | 2021-03-04 07:18 | 2021-03-04 18:38 | 11:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 230/132 kV Transformer-T2 | 2021-03-04 10:53 | 2021-03-04 11:20 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2021-03-04 09:20 | 2021-03-04 11:50 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | 400/132 kV Transformer-T2 | 2021-03-05 07:55 | 2021-03-05 09:03 | 1:08 | S/O | Due to C/M work | 50 | 56.6667 | Power interruption
Mymensingh | 132/33 kV Transformer-T2 | 2021-03-05 09:13 | 2021-03-05 09:13 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T4 | 2021-03-06 06:25 | 2021-03-06 06:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2021-03-06 08:52 | 2021-03-06 12:07 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2021-03-06 10:52 | 2021-03-06 15:15 | 4:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2021-03-07 11:40 | 2021-03-07 16:30 | 4:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T3 | 2021-03-08 09:22 | 2021-03-08 17:25 | 8:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2021-03-08 12:54 | 2021-03-08 14:34 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Manikganj | 132/33 kV Transformer-T2 |  | 2021-03-08 17:30 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-03-08 13:04 | 2021-03-08 19:24 | 6:20 | S/O | Due to 33 kVPT test | 14 | 88.6667 | Power interruption
Mirpur | 132/33 kV Transformer-T3 | 2021-03-09 10:07 | 2021-03-09 10:07 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2021-03-09 10:32 | 2021-03-09 11:52 | 1:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T01 | 2021-03-09 10:43 | 2021-03-09 13:30 | 2:47 | S/O | Due to A/M work | 0 | 0 | No interruption
Netrakona | 132/33 kV Transformer-T4 | 2021-03-09 17:07 | 2021-03-09 18:06 | 0:59 | S/O | Due to Oil level alarm | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2021-03-10 09:31 | 2021-03-10 09:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2021-03-10 10:42 | 2021-03-10 11:32 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T2 | 2021-03-13 08:17 | 2021-03-13 11:15 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajendrapur | 132 kV Bus-2 |  | 2021-03-13 11:42 |  | S/O | After maintenance work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 |  | 2021-03-14 11:35 |  | S/O |  | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 |  | 2021-03-14 16:10 |  | S/O | After maintenance work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2021-03-16 08:34 | 2021-03-16 17:18 | 8:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T1 | 2021-03-16 09:11 | 2021-03-16 15:49 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-03-17 06:45 | 2021-03-17 08:51 | 2:06 | S/O | Due to under ground cable work | 40 | 84 | Power interruption
Kodda | 132/33 kV Transformer-T1 | 2021-03-18 13:47 | 2021-03-18 20:40 | 6:53 | S/O | Due to Bus protection test | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 |  | 2021-03-18 16:43 |  | S/O | After maintenance work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2021-03-19 07:29 | 2021-03-19 09:44 | 2:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2021-03-20 09:50 | 2021-03-20 11:46 | 1:56 | S/O | Due to C/M work
| 132/33 kV Transformer-T4 | 2021-03-20 09:50 | 2021-03-20 11:26 | 1:36 | S/O |  | 35 | 67.6667 | Power interruption 09:50 to 11:26
Bhaluka | 132/33 kV Transformer-T2 | 2021-03-20 13:05 | 2021-03-20 13:28 | 0:23 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-21 10:00 | 2021-03-21 17:14 | 7:14 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-22 09:19 | 2021-03-22 18:05 | 8:46 | S/O | Due to D/W work | 15 | 131.5 | Power interruption
Savar | 132/33 kV Transformer-T1 | 2021-03-22 13:15 | 2021-03-22 13:59 | 0:44 | S/O | Due to removing kite | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-03-23 09:31 | 2021-03-23 17:09 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-24 10:02 | 2021-03-24 16:30 | 6:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-25 09:28 | 2021-03-25 14:33 | 5:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 kV Transformer-T03 | 2021-03-26 17:24 | 2021-03-26 17:48 | 0:24 | S/O | Due to maintenance work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2021-03-28 08:30 | 2021-03-28 13:00 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| 400/230 kV Transformer-T02(new) |  | 2021-03-28 13:48 |  |  | New connection
Mirpur | 132/33 kV Transformer-T2 | 2021-03-28 08:56 | 2021-03-28 10:28 | 1:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 2/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mirpur | 132/33 kV Transformer-T3 | 2021-03-28 10:32 | 2021-03-28 16:14 | 5:42 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | 230/132 kV Transformer-T01 | 2021-03-29 06:27 | 2021-03-29 09:03 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2021-03-29 07:04 | 2021-03-29 07:04 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Agargaon | 132/33 kV Transformer-T1 | 2021-03-29 10:33 | 2021-03-29 13:55 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-03-29 09:32 | 2021-03-29 17:32 | 8:00 | S/O | Due to C/M work | 10 | 80 | Power interruption
| 132/33 kV Transformer-T2 | 2021-03-30 08:10 | 2021-03-30 12:32 | 4:22 | S/O | Due to C/M work | 10 | 43.6667 | Power interruption
Aminbazar | 230/132 kV Transformer-Tr-2 | 2021-03-30 10:36 | 2021-03-30 16:06 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T2 | 2021-03-30 11:50 | 2021-03-30 15:21 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformer-T2 | 2021-03-31 07:42 | 2021-03-31 09:28 | 1:46 | S/O | Due to C/M work | 20 | 35.3333 | Power interruption
Agargaon | 230/132 kV Transformer-T2 | 2021-03-31 06:49 | 2021-03-31 09:03 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-31 10:34 | 2021-03-31 10:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132 kV reserve Bus | 2021-03-31 12:50 | 2021-03-31 18:09 | 5:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2021-03-31 11:22 | 2021-03-31 15:51 | 4:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T2 |  | 2021-03-31 16:19 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 259:48 |  | Unserved Energy: |  | 587.5
Dhaka (South) Grid Circle :
Siddhirganj | 230/132 kV Transformer-T-01 | 2021-03-01 10:07 | 2021-03-01 17:58 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Maniknagar | 132 kV reserve Bus | 2021-03-03 10:05 | 2021-03-03 13:14 | 3:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 132/33 kV Transformer-T2 | 2021-03-03 11:13 | 2021-03-03 13:23 | 2:10 | S/O | Due to D/W work | 42 | 91 | Power interruption
Maniknagar | 132 kV reserve Bus | 2021-03-03 10:05 | 2021-03-03 13:14 | 3:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | 132/33 kV Transformer-T1 | 2021-03-04 08:19 | 2021-03-04 14:54 | 6:35 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-06 10:20 | 2021-03-06 12:38 | 2:18 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV reserve Bus | 2021-03-06 10:34 | 2021-03-06 12:30 | 1:56 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-10 08:40 | 2021-03-10 17:20 | 8:40 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV mai Bus | 2021-03-10 10:00 | 2021-03-10 17:12 | 7:12 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-11 09:27 | 2021-03-11 13:47 | 4:20 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132 kV mai Bus | 2021-03-11 09:42 | 2021-03-11 13:47 | 4:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Haripur | 132 kV mai Bus | 2021-03-14 10:00 | 2021-03-14 11:37 | 1:37 | S/O | Due to maintenance work | 0 | 0 | No interruption
Rampura | 132 kV mai Bus-2 | 2021-03-19 12:20 | 2021-03-19 12:50 | 0:30 | S/O | Due to removing nest | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-20 10:22 | 2021-03-20 18:07 | 7:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 230/132 kV AuxilirayTransformer-T1 | 2021-03-20 12:10 | 2021-03-20 14:08 | 1:58 | S/O | Due to replacement work | 0 | 0 | No interruption
Rampura | 230/132 kV Transformer-T1 | 2021-03-22 06:38 | 2021-03-22 07:49 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-T03 | 2021-03-23 07:11 | 2021-03-23 09:33 | 2:22 | S/O | Due to NLDC Transformer work | 0 | 0 | No interruption
Sonargaon | 132/33 kV Transformer-T2 | 2021-03-25 06:28 | 2021-03-25 07:44 | 1:16 | S/O | Due to C/M work | 30 | 38 | Power interruption
Rampura | 230 kV Bus-1 | 2021-03-28 08:15 | 2021-03-28 15:31 | 7:16 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-2 | 2021-03-28 15:46 | 2021-03-28 17:01 | 1:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus-1 | 2021-03-31 08:24 | 2021-03-31 18:18 | 9:54 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 86:29 |  | Unserved Energy: |  | 129
Chattogram Grid Circle :
Hathazari | 230 kV breaker 822B | 2021-03-02 09:37 | 2021-03-02 12:42 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230 kV breaker 822B | 2021-03-02 12:57 | 2021-03-02 12:57 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132kV breakers 801B 812B | 2021-03-03 10:14 | 2021-03-03 12:40 | 2:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanaghat | 132/33 kV Transformer-T2 | 2021-03-03 07:03 | 2021-03-03 17:48 | 10:45 | S/O | Due to C/M work | 0 | 0 | No interruption
BSRM | 230 kV Bus coupler | 2021-03-04 11:47 | 2021-03-04 15:41 | 3:54 | S/O | Due to D/W work | 0 | 0 | No interruption
| 230 kV Bus coupler | 2021-03-04 11:47 | 2021-03-04 16:28 | 4:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformers-T1 & T2 | 2021-03-06 06:53 | 2021-03-06 06:53 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2021-03-06 08:47 | 2021-03-06 16:18 | 7:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaghrachari | 132/33 kV Transformer-T2 | 2021-03-06 15:00 | 2021-03-06 16:04 | 1:04 | S/O | Due to 33 kV R-phase under gound cable flashing | 0 | 0 | No interruption
Sikalbaha | 132/33 kV Transformer-T4 | 2021-03-12 09:05 | 2021-03-12 10:05 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Baraulia | 132/33 kV Transformer-T1 | 2021-03-16 11:20 | 2021-03-16 12:11 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Baraulia | 132/33 kV Transformer-T2 | 2021-03-16 12:40 | 2021-03-16 13:10 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T2 | 2021-03-18 08:35 | 2021-03-18 17:10 | 8:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | 132/33 kV Transformer-T2 | 2021-03-18 10:02 | 2021-03-18 11:35 | 1:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132/33 kV Transformer-T1 | 2021-03-20 07:20 | 2021-03-20 13:03 | 5:43 | S/O | Due to 33 kV Bus maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-20 13:19 | 2021-03-20 15:45 | 2:26 | S/O | Due to PDB work | 0 | 0 | No interruption
Hathazari | 132/33 kV Transformer-T1 | 2021-03-21 10:43 | 2021-03-21 11:30 | 0:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-21 11:32 | 2021-03-21 11:50 | 0:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT03 | 2021-03-22 11:36 | 2021-03-22 11:50 | 0:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT02 | 2021-03-22 12:04 | 2021-03-22 13:05 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer-MT01 | 2021-03-22 13:10 | 2021-03-22 13:58 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | 132 kV Bus coupler | 2021-03-22 16:03 | 2021-03-22 16:59 | 0:56 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-23 09:44 | 2021-03-23 10:53 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T1 | 2021-03-27 09:42 | 2021-03-27 13:01 | 3:19 | S/O | Due to under ground cable work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-28 09:50 | 2021-03-28 18:00 | 8:10 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T1 | 2021-03-29 06:10 | 2021-03-29 10:41 | 4:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Agrabad | 132/33 kV Transformer-T2 |  | 2021-03-29 16:32 |  | S/O | New connection | 0 | 0 | No interruption
|  |  | Total : | 75:17 |  | Unserved Energy : |  | 0
Cumilla Grid Circle :
Chatak | 132/33 kV Transformer-T3 | 2021-03-01 08:59 | 2021-03-01 13:32 | 4:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T1 | 2021-03-01 09:05 | 2021-03-01 09:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 | 2021-03-01 07:36 | 2021-03-01 16:50 | 9:14 | S/O | Due to PBS work | 0 | 0 | No interruption
Sunamganj | 132/33 kV Transformer-T2 | 2021-03-02 11:43 | 2021-03-02 11:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T1 | 2021-03-03 09:49 | 2021-03-03 10:26 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T1 | 2021-03-04 08:52 | 2021-03-04 16:57 | 8:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2021-03-04 10:24 | 2021-03-04 14:28 | 4:04 | S/O | Due to C/M work | 10 | 40.6667 | Power interruption
Daudkandi | 132/33 kV Transformer-T2 | 2021-03-04 08:20 | 2021-03-04 14:59 | 6:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Sreemongal | 132/33 kV Transformer-T1 |  | 2021-03-04 12:13 |  | S/O | After maintenance work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T1 | 2021-03-05 08:47 | 2021-03-05 16:54 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-06 09:12 | 2021-03-06 17:09 | 7:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T2 | 2021-03-09 10:40 | 2021-03-09 17:30 | 6:50 | S/O | Due to 33 kV PBS work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T1 | 2021-03-10 09:32 | 2021-03-10 15:02 | 5:30 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-10 15:10 | 2021-03-10 18:47 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-03-14 19:10 | 2021-03-14 20:40 | 1:30 | S/O | Due to CT problem | 33 | 49.5 | Power interruption
Baroierhat | 132/33 kV Transformer-T1 | 2021-03-15 08:18 | 2021-03-15 14:16 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-03-18 07:21 | 2021-03-18 09:01 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV Transformer-T3 | 2021-03-20 08:08 | 2021-03-20 12:08 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
B.Baria | 132/33 kV Transformer-T2 | 2021-03-23 12:15 | 2021-03-23 15:34 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | 132/33 kV Transformer-T2 |  | 2021-03-23 13:21 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ashuganj | 132/33 kV Transformer-T1 |  | 2021-03-27 10:14 |  | S/O |  | 0 | 0 | No interruption
Cumilla | 132/33 kV Transformer-T4 | 2021-03-30 10:05 | 2021-03-30 16:42 | 6:37 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 88:17 |  | Unserved Energy : |  | 90.1667
Khulna Grid Circle :
Khulna© | 132/33 kV Transformer-T3 | 2021-03-03 07:02 | 2021-03-03 09:22 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal | 132/33 kV Transformer-T1 | 2021-03-04 06:57 | 2021-03-04 08:19 | 1:22 | S/O | Due to C/M work | 5 | 6.8333 | Power interruption
| 132/33 kV Transformer-T1 | 2021-03-05 06:00 | 2021-03-05 08:14 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T4 | 2021-03-09 10:33 | 2021-03-09 11:57 | 1:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2021-03-09 10:58 | 2021-03-09 12:10 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(O) | 132 kV Bus-A | 2021-03-19 10:20 | 2021-03-19 10:50 | 0:30 | S/O | Due to removing nest | 0 | 0 | No interruption
Khulna(S) | 230/132 kV Transformer T03 | 2021-03-22 09:28 | 2021-03-22 11:42 | 2:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(C) | 132/33 kV Transformer-T3 | 2021-03-23 07:10 | 2021-03-23 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | 132/33 kV Transformer-T2 | 2021-03-25 11:06 | 2021-03-25 11:28 | 0:22 | S/O | Due to C/M work | 20 | 7.3333 | Power interruption
|  |  | Total : | 11:38 |  | Unserved Energy : |  | 14.1667
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :
Ishurdi | 230/132 kV Transformer-T-03 & 230 kV Bus | 2021-03-02 10:00 | 2021-03-02 18:18 | 8:18 | S/O | Due to C/M work | 0 | 0 | No interruption
| 230/132 kV Transformer T03 | 2021-03-10 09:13 | 2021-03-10 20:32 | 11:19 | S/O | Due to replacement work | 0 | 0 | No interruption
| 230/132 kV Transformer T01 | 2021-03-11 08:45 | 2021-03-11 15:16 | 6:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Benapole | 132/33 kV Transformer-T1 | 2021-03-11 11:51 | 2021-03-11 12:06 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-03-13 15:41 | 2021-03-13 15:55 | 0:14 | S/O | Due to changing work | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 | 2021-03-20 06:12 | 2021-03-20 08:02 | 1:50 | S/O | Due to C/M work | 10 | 18.3333 | Power interruption
Bheramara | Bheramara HVDC 400 kV 10CO2B |  | 2021-03-22 15:31 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Bheramara HVDC 400 kV 10COCB |  | 2021-03-22 15:32 |  |  |  | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T3 | 2021-03-28 10:12 | 2021-03-28 12:09 | 1:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T2 | 2021-03-31 07:51 | 2021-03-31 07:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 30:24 |  | Unserved Energy : |  | 18.3333
Bogura Grid Circle:
Rajshahi | 132/33 kV Transformer-T-1 | 2021-03-02 09:35 | 2021-03-02 13:47 | 4:12 | S/O | Due to SAS work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-03-02 09:05 | 2021-03-02 14:37 | 5:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2021-03-04 09:10 | 2021-03-04 14:19 | 5:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-2 | 2021-03-05 08:34 | 2021-03-05 11:14 | 2:40 | S/O | Due to A/M work | 25 | 65.8333 | Power interruption 08:42 to 11:20
Mithapukur | 132/33 kV Transformer-T-1 |  | 2021-03-08 16:52 |  |  | new connection | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 |  | 2021-03-08 17:28 |  |  |  | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-2 | 2021-03-11 08:10 | 2021-03-11 10:28 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-3 | 2021-03-13 09:22 | 2021-03-13 16:10 | 6:48 | S/O | Due to D/W work by PBS | 15 | 102 | Power interruption
Mahastangarth | 132 kV Bus-2 | 2021-03-13 15:26 | 2021-03-13 15:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 230 kV Bus-2 | 2021-03-18 10:22 | 2021-03-18 10:22 | 0:00
Mahastangarth | 132/33 kV Transformer-T-1 | 2021-03-19 10:32 | 2021-03-19 12:12 | 1:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T-4 | 2021-03-20 07:11 | 2021-03-21 22:40 | 39:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T-1 | 2021-03-21 07:24 | 2021-03-21 08:52 | 1:28 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-03-21 08:55 | 2021-03-21 09:50 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-03-22 07:32 | 2021-03-22 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhangura | 132/33 kV Transformer-T-1 | 2021-03-22 11:15 | 2021-03-22 11:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132/33 kV Transformer-T-2 | 2021-03-26 12:25 | 2021-03-26 12:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T-3 | 2021-03-27 10:12 | 2021-03-27 13:22 | 3:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-2 |  | 2021-03-30 09:40 |  |  | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 73:21 |  | Unserved Energy : |  | 167.8333
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 625:14 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
UMPL | UMPL-Jamalpur 132 kV line-2 | 2021-03-01 00:47 | 2021-03-01 06:45 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2021-03-02 08:18 | 2021-03-02 22:18 | 14:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kishoreganj | Kishoreganj-Ashuganj 132 kV line-2 | 2021-03-02 08:37 | 2021-03-02 17:42 | 9:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 | 2021-03-02 09:15 | 2021-03-02 12:14 | 2:59 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-1 | 2021-03-02 09:43 | 2021-03-02 18:32 | 8:49 | S/O | Due to A/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj P.P 132 kV line-1 | 2021-03-03 08:33 | 2021-03-03 12:23 | 3:50 | S/O | Due to A/M work | 0 | 0 | No interruption
| Savar-Manikganj P.P 132 kV line-2 | 2021-03-03 12:14 | 2021-03-03 13:55 | 1:41 | S/O | Due to A/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P/P 132 kV line-1 | 2021-03-03 10:01 | 2021-03-03 16:32 | 6:31 | S/O | Due to A/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2021-03-03 09:51 | 2021-03-03 20:40 | 10:49 | S/O | Due to C/M work | 0 | 0 | No interruption
| Kabirpur-Kodda 132 kV line-2 | 2021-03-04 10:40 | 2021-03-04 15:43 | 5:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2021-03-04 09:42 | 2021-03-04 20:40 | 10:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2021-03-04 09:36 | 2021-03-04 16:33 | 6:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2021-02-03 09:04 | 2021-03-07 18:21 | 777:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV line-2 | 2021-03-07 09:20 | 2021-03-07 23:15 | 13:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kaliakoir 230 kV line-1 | 2021-03-07 11:34 | 2021-03-07 13:24 | 1:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 KV line-1 | 2021-03-08 10:40 | 2021-03-08 12:52 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2021-03-08 12:54 | 2021-03-08 14:34 | 1:40 | S/O | Due to A/M work | 0 | 0 | No interruption
Uttara | Uttara-3rd phase -Metro rail 132 kV line |  | 2021-03-08 17:15 |  |  | new connection | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV line-2 | 2021-03-09 11:04 | 2021-03-09 12:12 | 1:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-1 | 2021-03-09 13:38 | 2021-03-09 16:59 | 3:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV line-2 | 2021-03-09 13:44 | 2021-03-09 14:28 | 0:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-Mymensingh 132 kV line-2 | 2021-03-10 06:59 | 2021-03-11 00:04 | 17:05 | S/O | Due to A/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-1 | 2021-03-11 07:01 | 2021-03-12 00:04 | 17:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-2 | 2021-03-11 10:13 | 2021-03-11 18:23 | 8:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Aminbazar 132 kV line-1 | 2021-03-12 07:10 | 2021-03-12 07:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamari 132 kV line-1 | 2021-03-13 08:19 | 2021-03-13 16:18 | 7:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi -Kabirpur 132 kV line-1 | 2021-03-13 11:20 | 2021-03-13 17:23 | 6:03 | S/O | Due to relay test | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamari 132 kV line-2 | 2021-03-14 09:12 | 2021-03-14 15:05 | 5:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Uttara | Uttara 3rd Phase-Metro Rail 132 kV line | 2021-03-14 14:55 | 2021-03-14 16:27 | 1:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Kallyanpur 132 kV line-2 | 2021-03-16 06:36 | 2021-03-16 06:36 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kodda S/S | Kodda S/S-ACE Kodda 149 MW 132 kV line | 2021-03-16 09:38 | 2021-03-16 17:10 | 7:32 | S/O | Due to A/M work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2021-03-23 07:18 | 2021-03-23 12:01 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Bhaluka 132 kV line-2 | 2021-03-23 10:41 | 2021-03-23 17:41 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-03-24 07:38 | 2021-03-24 10:32 | 2:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-1 | 2021-03-25 10:15 | 2021-03-25 13:26 | 3:11 | S/O | Due to removing kite | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2021-03-26 09:56 | 2021-03-26 12:16 | 2:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Keraniganj 230 kV line-1 | 2021-03-29 09:44 | 2021-03-29 14:47 | 5:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2021-03-29 08:57 | 2021-03-29 13:30 | 4:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi -Kabirpur 132 kV line-1 | 2021-03-29 09:58 | 2021-03-29 17:32 | 7:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Mynensingh 132 kV line-1 | 2021-03-30 09:31 | 2021-03-30 12:15 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | Bhaluka-Mymensingh 132 kV line-2 | 2021-03-30 13:03 | 2021-03-30 14:22 | 1:19 | S/O | Due to SAS work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2021-03-31 09:12 | 2021-03-31 18:10 | 8:58 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 1010:23 |  | Unserved Energy: |  | 0
Page: 2/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2021-03-03 08:15 | 2021-03-03 17:58 | 1:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-Meghanaghat 230 kV line-1 | 2021-03-03 09:15 | 2021-03-03 10:34 | 1:19 | S/O | Due to D/W work | 0 | 0 | No interruption
| Haripur-Meghanaghat 230 kV line-2 | 2021-03-03 12:21 | 2021-03-03 13:28 | 1:07 | S/O |  | 0 | 0 | No interruption
| Haripur-HPL 230 kV line-2 | 2021-03-03 11:21 | 2021-03-03 13:16 | 1:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2021-03-04 07:37 | 2021-03-04 17:58 | 10:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Haripur | Haripur-HPL 230 kV line-1 | 2021-03-04 08:07 | 2021-03-04 11:38 | 3:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 | 2021-03-05 08:30 | 2021-03-05 17:35 | 9:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2021-03-06 10:52 | 2021-03-06 17:04 | 6:12 | S/O | Due to D/W work | 20 | 124 | Power interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-1 | 2021-03-07 09:27 | 2021-03-07 17:27 | 8:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Kajla 132 kV line-1 |  | 2021-03-08 14:31 |  |  | new connection | 0 | 0 | No interruption
| Maniknagar-Kajla 132 kV line-2 |  | 2021-03-08 14:34 |  |  |  | 0 | 0 | No interruption
Sonargaon | Sonargaon-Haripur 132 kV line-1 | 2021-03-09 09:50 | 2021-03-09 11:02 | 1:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| Sonargaon-Daudkandi 132 kV line-1 | 2021-03-09 13:10 | 2021-03-09 13:42 | 0:32 | S/O | Due to D/W work | 0 | 0 | No interruption
APR | APR-Hasnabad 230 kV line | 2021-03-10 07:41 | 2021-03-10 17:01 | 9:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Hasnabad 132 kV line-2 | 2021-03-12 07:27 | 2021-03-12 07:27 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2021-03-13 07:07 | 2021-03-13 20:27 | 13:20 | S/O | Due to project work | 0 | 0 | No interruption
Haripur | Haripur-Fatulla 132 kV line | 2021-03-14 09:53 | 2021-03-14 11:55 | 2:02 | S/O | Due to maintenance work | 0 | 0 | No interruption
| Haripur-Bhulta 230 kV line-2 | 2021-03-15 07:36 | 2021-03-15 20:05 | 12:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 |  | 2021-03-16 11:26 |  | S/O | After maintenance work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Matuail 132 kV line | 2021-03-16 14:51 | 2021-03-16 14:51 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
| Maniknagar-Haripur 132 kV line-2 | 2021-03-16 14:52 | 2021-03-16 14:52 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-2 |  | 2021-03-16 15:27 |  | S/O | After maintenance work | 0 | 0 | No interruption
Maniknagar | Maniknagar-Siddhirganj 132 kV line-1 | 2021-03-18 06:13 | 2021-03-18 09:07 | 2:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Maniknagar 230 kV line-1 |  | 2021-03-16 11:26 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Joydevpur 132 kV line-2 |  | 2021-03-27 10:08 |  | S/O | After maintenance work | 0 | 0 | No interruption
| Ghorashal-Ashuganj 132 kV line-2 |  | 2021-03-27 10:03 |  | S/O |  | 0 | 0 | No interruption
|  |  | Total : | 85:06 |  | Unserved Energy: |  | 124
Chattogram Grid Circle :
Baroaulia | Baroaulia-BSRM 132 kV line | 2021-03-01 09:51 | 2021-03-01 15:41 | 5:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line-1 | 2021-03-01 08:24 | 2021-03-01 12:54 | 4:30 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-AKSML 132 kV line | 2021-03-02 08:22 | 2021-03-02 17:46 | 9:24 | S/O | Due to A/M work | 0 | 0 | No interruption
| Khulshi-AKSML 132 kV line | 2021-03-03 08:34 | 2021-03-03 18:43 | 10:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-1 | 2021-03-03 14:32 | 2021-03-03 17:01 | 2:29 | S/O | Due to CB test | 0 | 0 | No interruption
| Hathazari-Raozan 230 kV line-2 | 2021-03-04 09:41 | 2021-03-04 12:32 | 2:51 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Bakulia 132 kV line-2 | 2021-03-04 08:34 | 2021-03-04 14:50 | 6:16 | S/O | Due to A/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-03-08 07:26 | 2021-03-08 17:10 | 9:44 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Khulshi 132 kV line | 2021-03-08 23:35 | 2021-03-09 13:26 | 13:51 | S/O | Due to flashing at Y-phase dead end clamp at khulshi end | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-03-09 11:48 | 2021-03-09 15:42 | 3:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2021-03-09 08:37 | 2021-03-09 12:20 | 3:43 | S/O | Due to Rampur CKt LILO work | 0 | 0 | No interruption
BSRM | BSRM-Cumilla(N) 230 kV line-1 | 2021-03-10 11:39 | 2021-03-10 15:39 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-2 | 2021-03-10 08:37 | 2021-03-10 13:30 | 4:53 | S/O | Due to Rampur CKt LILO work | 0 | 0 | No interruption
| Khulshi-Halishahar 132 kV line-1 | 2021-03-10 14:32 | 2021-03-10 14:32 | 0:00 | S/O | Due to Rampur CKt LILO work | 0 | 0 | No interruption
| Khulshi-Rampur 132 kV line-1 |  | 2021-03-10 20:04 |  | S/O | After maintenance work | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur 132 kV line-1 |  | 2021-03-10 20:17 |  | S/O | After maintenance work | 0 | 0 | No interruption
Khulshi | Khulshi-AKSML 132 kV line | 2021-03-11 08:31 | 2021-03-11 15:56 | 7:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2021-03-12 07:22 | 2021-03-12 07:22 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Abul Khair 132 kV line | 2021-03-12 08:24 | 2021-03-12 11:43 | 3:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2021-03-13 09:33 | 2021-03-13 15:04 | 5:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Hathazari 132 kV line | 2021-03-13 08:27 | 2021-03-13 14:59 | 6:32 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulshi-Hathazari 132 kV line | 2021-03-14 07:12 | 2021-03-14 07:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Khulshi-Hathazari 132 kV line | 2021-03-14 07:13 | 2021-03-14 16:21 | 9:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2021-03-14 10:10 | 2021-03-14 10:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Baroirhat 132 kV line-1 | 2021-03-14 12:37 | 2021-03-14 13:40 | 1:03 | S/O | Due to CB timing test | 0 | 0 | No interruption
| Hathazari-Baroirhat 132 kV line-2 | 2021-03-14 14:25 | 2021-03-14 16:19 | 1:54 | S/O |  | 0 | 0 | No interruption
| Khulshi-Baraulia 132 kV line | 2021-03-15 08:20 | 2021-03-15 12:47 | 4:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line-1 | 2021-03-16 08:20 | 2021-03-16 15:10 | 6:50 | S/O | Due to A/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2021-03-16 09:22 | 2021-03-16 15:35 | 6:13 | S/O | Due to A/M work | 0 | 0 | No interruption
| Hathazari-Baroierhat 132 kV line-2 | 2021-03-16 15:40 | 2021-03-16 17:27 | 1:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahmirpur | Shahmirpur-Juldah 132 kV line-1 | 2021-03-18 07:42 | 2021-03-18 13:20 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Page: 3/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Chattogram Grid Circle :
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-03-18 09:54 | 2021-03-18 10:40 | 0:46 | S/O | Due to CB test | 0 | 0 | No interruption
Baraulia | Baraulia-AKS(mil) 132 kV line | 2021-03-18 12:35 | 2021-03-18 13:07 | 0:32 | S/O |  | 0 | 0 | No interruption
| Baraulia-Khulshi 132 kV line | 2021-03-18 10:50 | 2021-03-18 12:30 | 1:40 | S/O |  | 0 | 0 | No interruption
Juldah S/S | Juldah S/S-Juldah unit-1 | 2021-03-19 08:38 | 2021-03-19 10:37 | 1:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-3 | 2021-03-19 08:22 | 2021-03-19 15:12 | 6:50 | S/O | Due to protection test | 0 | 0 | No interruption
Juldah S/S | Juldah S/S-Shahmirpur 132 kV line-2 | 2021-03-20 07:36 | 2021-03-20 13:34 | 5:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-AKSM 230 kV line | 2021-03-21 12:54 | 2021-03-21 13:20 | 0:26 | S/O | Due to C/M work | 0 | 0 | No interruption
| Hathazari-AKSM 230 kV line | 2021-03-21 16:33 | 2021-03-21 16:48 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-03-22 10:28 | 2021-03-22 17:05 | 6:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Khagrachari 132 kV line-1 | 2021-03-22 11:03 | 2021-03-22 12:53 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangamati-Khagrachari 132 kV line-2 | 2021-03-22 12:58 | 2021-03-22 14:15 | 1:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2021-03-22 16:15 | 2021-03-22 16:25 | 0:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-1 | 2021-03-23 07:48 | 2021-03-23 09:01 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-03-23 08:15 | 2021-03-23 12:51 | 4:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Chandraghona 132 kV line-2 | 2021-03-23 09:15 | 2021-03-23 11:15 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Barierhat 132 kV line-1 | 2021-03-24 13:45 | 2021-03-24 17:41 | 3:56 | S/O | Due to DC ground fault | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-2 | 2021-03-25 10:10 | 2021-03-25 17:34 | 7:24 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Madunaghat 132 kV line | 2021-03-25 06:47 | 2021-03-25 06:47 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroierhat 132 kV line-2 | 2021-03-27 08:37 | 2021-03-27 16:48 | 8:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Juldah | Juldah-Sikalbaha 132 kV line | 2021-03-27 08:04 | 2021-03-27 14:40 | 6:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 & 2 | 2021-03-28 10:04 | 2021-03-28 17:37 | 7:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-03-29 06:51 | 2021-03-29 06:51 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-1 | 2021-03-29 08:17 | 2021-03-29 16:51 | 8:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-T.K chemical 132 kV line | 2021-03-30 07:01 | 2021-03-30 07:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-03-30 08:18 | 2021-03-30 16:40 | 8:22 | S/O | Due to D/W work | 0 | 0
| Hathazari-Baraulia 132 kV line-2 | 2021-03-31 08:52 | 2021-03-31 16:03 | 7:11 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 235:17 |  | Unserved Energy: |  | 0
Cumilla Grid Circle :
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2021-03-01 08:52 | 2021-03-01 17:17 | 8:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2021-03-01 09:49 | 2021-03-01 20:52 | 11:03 | S/O | Due to A/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV line-3 | 2021-03-01 12:44 | 2021-03-01 16:38 | 3:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2021-03-02 08:42 | 2021-03-02 13:31 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2021-03-02 08:57 | 2021-03-02 16:50 | 7:53 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2021-03-02 09:02 | 2021-03-02 18:03 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2021-03-02 02:36 | 2021-03-02 14:49 | 12:13 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria-Shahjibazar 132 kV line-1 | 2021-03-03 06:03 | 2021-03-03 17:29 | 11:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2021-03-03 09:03 | 2021-03-03 15:59 | 6:56 | S/O | Due to A/M work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-2 | 2021-03-03 09:22 | 2021-03-03 18:23 | 9:01 | S/O | Due to A/M work | 0 | 0 | No interruption
B.Baria | B.Baria -Shahjibazar 132 kV line-2 | 2021-03-04 06:22 | 2021-03-04 17:32 | 11:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-1 | 2021-03-04 09:20 | 2021-03-04 15:30 | 6:10 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV line | 2021-03-05 09:31 | 2021-03-05 11:16 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-03-06 08:29 | 2021-03-06 19:41 | 11:12 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ashuganj-B.Baria 132 kV line-2 | 2021-03-06 10:52 | 2021-03-06 11:55 | 1:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2021-03-06 08:47 | 2021-03-06 16:54 | 8:07 | S/O | Due to A/M work | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Bianibazar -Sylhet 132 kV line | 2021-03-06 10:52 | 2021-03-06 13:58 | 3:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-03-07 08:38 | 2021-03-07 10:23 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2021-03-07 09:00 | 2021-03-07 17:28 | 8:28 | S/O | Due to A/M work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Shahjibazar 230 kV line-2 | 2021-03-08 08:51 | 2021-03-08 17:15 | 8:24 | S/O | Due to A/M work | 0 | 0 | No interruption
Feni | Feni-Chaddagram 132 kV line-2 | 2021-03-08 08:37 | 2021-03-08 14:07 | 5:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-BSRM 230 kV line-1 | 2021-03-08 10:27 | 2021-03-08 13:29 | 3:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Barierhat | Barierhat-Feni 132 kV line-1 | 2021-03-09 10:30 | 2021-03-09 12:02 | 1:32 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barierhat-Hathazri 132 kV line-1 | 2021-03-09 09:59 | 2021-03-09 11:51 | 1:52 | S/O | Due to D/W work | 0 | 0 | No interruption
| Barierhat-Hathazri 132 kV line-2 | 2021-03-09 13:23 | 2021-03-09 14:00 | 0:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Page: 4/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Cumilla Grid Circle :
Shahjibazar | Shahjibazar-Cumilla(N) 230 kV line-1 | 2021-03-10 10:04 | 2021-03-10 15:25 | 5:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Desh energy 132 kV line-1 | 2021-03-10 11:37 | 2021-03-10 13:18 | 1:41 | S/O | Due to SCADA intergration work | 0 | 0 | No interruption
Feni | Feni-Baroierhat 132 kV line-1 | 2021-03-10 08:45 | 2021-03-10 08:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-Hathazari 132 kV line-1 | 2021-03-11 13:13 | 2021-03-11 16:47 | 3:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Ramganj | Ramganj-Desh energy 132 kV line-1 | 2021-03-14 09:54 | 2021-03-14 17:19 | 7:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2021-03-14 09:43 | 2021-03-14 14:52 | 5:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-03-15 08:36 | 2021-03-15 18:31 | 9:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV line | 2021-03-15 11:17 | 2021-03-15 12:54 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-03-16 08:17 | 2021-03-16 11:54 | 3:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ashuganj-Shahjibazar 132 kV line | 2021-03-16 08:39 | 2021-03-16 15:12 | 6:33 | S/O | Due to A/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Kochua 132 kV line-1 | 2021-03-16 09:26 | 2021-03-16 12:39 | 3:13 | S/O | Due to A/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2021-03-18 08:18 | 2021-03-18 17:06 | 8:48 | S/O | Due to A/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhani 132 kV line-1 | 2021-03-18 11:33 | 2021-03-18 20:00 | 8:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandpur | Chandpur-Chandpur 150 MW P/P 132 kV line | 2021-03-20 10:26 | 2021-03-20 10:26 | 0:00 | S/O | Due to P/P work | 0 | 0 | No interruption
B.baria | B.baria-Narshingdi 132 kV line-2 | 2021-03-23 09:31 | 2021-03-23 11:59 | 2:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2021-03-25 07:26 | 2021-03-25 07:26 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-1 | 2021-03-25 08:08 | 2021-03-25 08:58 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV line-1 | 2021-03-27 08:06 | 2021-03-27 10:15 | 2:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| Daudkandi-Sonargaon 132 kV line-2 | 2021-03-27 10:15 | 2021-03-27 13:07 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Shahjibazar 132 kV line-3 | 2021-03-30 09:39 | 2021-03-30 09:39 | 0:00 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 232:03 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Goalpara | Goalpara-Bagerhat 132 kV line | 2021-03-03 08:16 | 2021-03-03 13:28 | 5:12 | S/O | Due to D/W work | 0 | 0 | No interruption
| Goalpara-Madaripur 132 kV line-3 | 2021-03-03 08:11 | 2021-03-03 20:58 | 12:47 | S/O | Due to C/M work | 0 | 0 | No interruption
| Goalpara-Bagerhat 132 kV line | 2021-03-04 07:51 | 2021-03-04 15:47 | 7:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | Goalpara-Orion Rupsha 132 kV line | 2021-03-05 07:47 | 2021-03-05 07:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Bhandaria 132 kV line | 2021-03-06 07:15 | 2021-03-06 13:06 | 5:51 | S/O | Due to A/M work | 0 | 0 | No interruption
| Bagerhat-Mongla 132 kV line-1 | 2021-03-09 07:30 | 2021-03-09 16:38 | 9:08 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bagerhat-Mongla 132 kV line-1 | 2021-03-11 13:12 | 2021-03-11 14:11 | 0:59 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bagerhat-Bhandaria 132 kV line | 2021-03-15 00:03 | 2021-03-15 11:53 | 11:50 | S/O | Due to removing bird nest | 0 | 0 | No interruption
Magura | Magura-Jhenidah 132 kV line-1 | 2021-03-15 12:50 | 2021-03-15 19:50 | 7:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Magura-Jhenidah 132 kV line-2 | 2021-03-16 10:45 | 2021-03-16 12:28 | 1:43 | S/O | Due to A/M work | 0 | 0 | No interruption
Norail | Norail-Magura 132 kV line-2 | 2021-03-16 15:12 | 2021-03-16 17:46 | 2:34 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagerhat | Bagerhat-Mongla 132 kV line-1 | 2021-03-19 07:08 | 2021-03-19 12:01 | 4:53 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 69:53 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Ishurdi | Ishurdi-Ghorashal 230 kV line-2 | 2021-03-05 08:38 | 2021-03-05 23:07 | 14:29 | S/O | Due to D/W work | 0 | 0 | No interruption
| Ishurdi-Ghorashal 230 kV line-1 | 2021-03-06 07:44 | 2021-03-06 07:44 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Ishurdi-Natore 132 kV line-2 | 2021-03-13 09:10 | 2021-03-13 15:27 | 6:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV line | 2021-03-20 14:54 | 2021-03-20 17:03 | 2:09 | S/O | Due to protection test | 0 | 0 | No interruption
| Bheramara-G.K 230 kV line-1 |  | 2021-03-24 09:47 |  |  | new connection | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-1 | 2021-03-29 09:04 | 2021-03-29 10:04 | 1:00 | S/O | Due to removing kite | 0 | 0 | No interruption
|  |  | Total : | 23:55 |  | Unserved Energy: |  | 0
Page: 5/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Rajshahi(N) | Rajshahi(N)-C.nawabganj 132 kV line | 2021-03-01 08:43 | 2021-03-01 16:55 | 8:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | Amnura-Rajshahi (N) 132 kV line | 2021-03-03 12:12 | 2021-03-03 15:33 | 3:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | Sherpur-Sirajganj 132 kV line-2 | 2021-03-03 16:09 | 2021-03-03 18:05 | 1:56 | S/O | Due to protection test | 0 | 0 | No interruption
| Sherpur-Sirajganj 132 kV line-1 | 2021-03-03 18:50 | 2021-03-03 21:08 | 2:18 | S/O |  | 0 | 0 | No interruption
Rajshahi | Rajshahi-Amnura 132 kV line-2 | 2021-03-04 08:34 | 2021-03-04 16:30 | 7:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | Naogaon-Bogura 132 k line-2 | 2021-03-04 09:53 | 2021-03-04 09:53 | 0:00 | S/O | Due to A/M work | 0 | 0 | No interruption
Mahastanghor | Mahastanghor-Bogura 132 kV line-1 | 2021-03-06 09:29 | 2021-03-06 17:07 | 7:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| Mahastanghor-Palashbari 132 kV line-1 | 2021-03-06 09:49 | 2021-03-06 17:11 | 7:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura -Sherpur 132 kV line-1 | 2021-03-07 13:23 | 2021-03-07 15:34 | 2:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura New | Bogura New-Sherpur 132 kV line-2 | 2021-03-07 15:39 | 2021-03-07 17:10 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur | Rangpur-Confidence-Palshbari 132 kV line-1 & 2 | 2021-03-08 07:48 | 2021-03-08 11:05 | 3:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| Rangpur-Confidence-Palshbari 132 kV line-1 | 2021-03-08 16:41 | 2021-03-08 19:18 | 2:37 | S/O | Due to D/W work | 0 | 0 | No interruption
Joldhaka | Joldhaka-Saidpur 132 kV line-2 | 2021-03-08 16:08 | 2021-03-08 17:22 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur Confience 132 kV line-1 |  | 2021-03-08 19:18 |  |  | new connection | 0 | 0 | No interruption
| Mithapukur-Palashbari 132 kV line-1 |  | 2021-03-08 19:40 |  |  |  | 0 | 0 | No interruption
| Mithapukur-Rangpur Confience 132 kV line-2 |  | 2021-03-08 16:08 |  |  |  | 0 | 0 | No interruption
| Mithapukur-Palashbari 132 kV line-2 |  | 2021-03-08 16:02 |  |  |  | 0 | 0 | No interruption
Bogura | Bogura -Sherpur 132 kV line-1 | 2021-03-10 10:30 | 2021-03-10 12:39 | 2:09 | S/O | Due to A/M work | 0 | 0 | No interruption
Bogura | Bogura -Sirajganj 230 kV line-1 | 2021-03-18 10:26 | 2021-03-18 13:47 | 3:21 | S/O | Due to A/M work | 0 | 0 | No interruption
Natore | Natore-Bogura 132 kV line-2 |  | 2021-03-18 15:40 |  |  | After maintenance work | 0 | 0 | No interruption
Rajshahi | Rajshahi-Natore 132 lV line-1 | 2021-03-22 09:03 | 2021-03-22 11:48 | 2:45 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rajshahi-Natore 132 lV line-2 | 2021-03-22 11:51 | 2021-03-22 13:34 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | Rampur-Saidpur 132 kV line-1 | 2021-03-30 09:44 | 2021-03-30 15:46 | 6:02 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 65:33 |  | Unserved Energy: |  | 0
Others :
Bangabhaban | Bangabhaban-Motijiheel-Maniknagar 132 kV line | 2021-03-17 14:59 | 2021-03-17 15:49 | 0:50 | S/O | Due to fire at Motijiheel S/S | 0 | 0 | No interruption
|  |  | Total : | 0:50 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 1723:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:March' 2021
| Area | Previous Month (February2021 |  |  |  | Current Month (March 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 12 | 8 | 159 | 179 | 24 | 5 | 105 | 134
2 | Dhaka (South) Grid Circle. | 16 | 5 | 60 | 81 | 7 | 8 | 47 | 62
3 | Chattogram Grid Circle. | 9 | 5 | 100 | 114 | 6 | 9 | 84 | 99
4 | Cumilla Grid Circle. | 24 | 16 | 147 | 187 | 24 | 10 | 67 | 101
5 | Khulna Grid Circle. | 2 | 4 | 26 | 32 | 7 | 6 | 21 | 34
6 | HVDC Grid Circle | 5 | 3 | 30 | 38 | 5 | 2 | 15 | 22
7 | Bogura Grid Circle. | 4 | 6 | 43 | 53 | 7 | 12 | 42 | 61
8 | Others | 1 | 2 | 5 | 8 | 1 | 0 | 1 | 2
9 | Total | 73 | 49 | 570 | 692 | 81 | 52 | 382 | 515
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:March' 2021
| Area | Previous Month (February 2021) |  |  |  | Current Month (March 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 192.44 | 60.5 | 631.7 | 884.64 | 1161 | 213 | 587.5 | 1961.5
2 | Dhaka (South) Grid Circle. | 66.67 | 61.17 | 77.33 | 205.17 | 205.83 | 16.43 | 253 | 475.26
3 | Chattogram Grid Circle. | 127.7 | 155.32 | 117 | 400.02 | 58.6 | 29.5 | 0 | 88.1
4 | Cumilla Grid Circle. | 290.02 | 90.24 | 683.67 | 1063.93 | 133.15 | 222.43 | 90.17 | 445.75
5 | Khulna Grid Circle. | 27.73 | 21 | 165.18 | 213.91 | 0 | 167.68 | 14.17 | 181.85
6 | HVDC Grid Circle | 8.9 | 33.33 |  | 42.23 | 129 | 15.83 | 18.33 | 163.16
7 | Bogura Grid Circle. | 39.42 | 93.42 | 418.33 | 551.17 | 22.87 | 622.73 | 167.83 | 813.43
8 | Others |  | 288.92 |  | 288.92 | 0 | 0 | 0 | 0
9 | Total | 752.88 | 803.9 | 2093.21 | 3649.99 | 1710.45 | 1287.6 | 1131 | 4129.05
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:March2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 11 | 7 | 19 | 5 | 2 | 12 | 1742.6
2 | Dhaka (South) | 5031.6 | - | 2 | 2 | - | - | 2 | 129
3 | Chattogram | 2042 | 5 |  | 5 | 4 | 1 |  | 88.1
4 | Khulna | 2434 | 4 | 2 | 6 | 3 |  | 3 | 181.85
5 | HVDC | 5954.3 | 1 | 1 | 2 |  |  | 2 | 34.16
6 | Bogura | 3145.6 | 4 | 2 | 6 | - | 1 | 5 | 651.73
7 | Cumilla | 2981 | 8 | 2 | 10 | 4 |  | 6 | 342.65
8 | Others | - | - | - | - | - | - | - | -
| Total | 30390.1 | [6 empty] | 3170.09
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.96%
4 | Khulna | 99.93%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.85% | [6 empty] | Information Management Division
7 | Cumilla | 99.9% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:March' 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 2 |  | 2 | 2 | - | - | 218.9
2 | Dhaka (South) | 990.29 |  | 4 | 1 | 5 | 2 |  | 2 | 346.27
3 | Chattogram | 917 | - | - | - | - | - | - | - | -
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | 501 | 1 | - | 1 | 1 | - | - | 129
6 | Bogura | 1803.3 | - | 2 |  | 2 | - | 1 | 1 | 161.7
7 | Cumilla | 1648.16 | - | 5 |  | 5 | 4 | 1 |  | 103.1
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 958.97
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.99%
2 | Dhaka (South) | 99.97%
3 | Chattogram | 99.98%
4 | Khulna | 99.98%
5 | Bheramara (HVDC) | 99.98% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.97% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:March' 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-03-18 | 21 | - | 5 | 06hr11 min | 2 | 01hr55 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March' 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Sherpur | 1 | 0:12 | 50 | 10 | Due to tripping of 132/33 kV Transformers-T1 & T2
Bhaluka | 1 | 8:07 | 73 | 592.5167 | Due to tripping of 132/33 kV Transformer-T2
Kishoreganj |  | 0:55 | 75 | 68.75 | Due to tripping of 132/33 kV Transformers-T1 & T2
Rajendrapur | 1 | 1:48 | 76 | 136.8
Kishoreganj | 2 | 0:08 | 15 | 2
|  | 0:11 | 80 | 14.6667
Kodda | 1 | 0:22 | 64 | 23.4667 | Due to tripping of 132/33 kV Transformers-T1 & T2
Kabirpur | 2 | 2:12 | 45 | 99 | Due to red-hot maintenance of 132/33 kV Trasformer T2
|  | 1:54 | 60 | 114
Kishoreganj | 2 | 0:09 | 126 | 18.9 | Due to 33 kV Feeder fault
|  | 0:45 | 100 | 75
Tongi | 2 | 0:13 | 300 | 65 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2
|  | 0:27 | 342 | 153.9
Kaliakoir | 1 | 1:08 | 50 | 56.6667 | Due to S/D of 400/132 kV Transformer T2
Manikganj | 1 | 6:20 | 14 | 88.6667 | Due to S/D of 132/33 kV Transformer T3
Kabirpur | 1 | 2:06 | 40 | 84 | Due to S/D of 132/33 kV Transformer T2
Tangail | 1 | 1:36 | 35 | 67.6667 | Due to S/D of 132/33 kV Transformer T4
Bhaluka | 3 | 8:46 | 15 | 131.5 | Due to S/D of 132/33 kV Transformer T2
|  | 8:00 | 10 | 80
|  | 4:22 | 10 | 43.6667
Kishoreganj | 1 | 1:46 | 20 | 35.3333 | Due to S/D of 132/33 kV Transformer T2
Siddhirganj | 1 | 0:10 | 95 | 15.8333 | Due to tripping of Haripur-Matuail 132 kV line
Rampura | 2 | 0:24 | 100 | 40 | Due to tripping of Rampura-Gulshahn 132 kV line-1 & 2
|  | 0:17 | 58 | 16.4333
Shyampur(N) | 1 | 0:50 | 180 | 150 | Due to tripping of Shyampur(N)-Shyampur(O) 132 kV line-1 & 2
Keraniganj | 1 | 2:10 | 42 | 91 | Due to S/D of 132/33 kV Transformer T2
Sonargaon | 1 | 1:16 | 30 | 38
Meghnaghat | 1 | 6:12 | 20 | 124 | Due to S/D of Meghnaghat-Shyampur 230 kV line-1
Cox'sbazar | 2 | 0:12 | 42 | 8.4 | Due to of tripping of 132/33 kV Transformer-T3
|  | 0:27 | 36 | 16.2
Halishahar | 1 | 0:59 | 30 | 29.5 | Due to emergency maintenance work
Madunaghat | 2 | 0:19 | 35 | 11.0833 | Due to tripping of 132/33 kV Transformers-T1 & T2
|  | 0:25 | 55 | 22.9167
Chandpur | 1 | 0:15 | 27 | 6.75 | Due to tripping of 132/33 kV Transformers-T1,T2 & T3
Chowmuhani | 1 | 0:13 | 100 | 21.6667 | Due to 33 kV feeder fault
Sreemongal | 1 | 0:07 | 14 | 1.6333 | Due to tripping of 132/33 kV Transformers-T2 & T3
Sylhet | 1 | 1:22 | 43 | 58.7667 | Due to red-hot maintenance of 132/33 kV Trasformer T2
Sreemongal | 1 | 1:52 | 20 | 37.3333 | Due to red-hot maintenance of 33 kV Bus
Chowmuhani | 1 | 1:40 | 30 | 50
Cumilla(N) | 1 | 0:17 | 100 | 28.3333 | Due to cable bursting of 33 kV Transformer T3
Ramganj | 1 | 1:12 | 40 | 48 | Due to red-hot maintenance of 132/33 kV Transformer T2
Sylhet | 1 | 0:54 | 26 | 23.4 | Due to tripping of Sylhet-Fenchuganj S/S 132 kV line
Cumilla(S) |  | 0:27 | 110 | 49.5 | Due to tripping of Cumilla(S)-Tripura 132 kV line-1 & 2
Sylhet |  | 0:19 | 28 | 8.8667 | Due to tripping of Sylhet-Fenchuganj S/S 132 kV line
Sunamganj | 1 | 0:26 | 20 | 8.6667 | Due to tripping of Sunamganj-Chatak 132 kV line
Sylhet | 1 | 0:19 | 40 | 12.6667 | Due to tripping of Sylhet-Fenchuganj S/S 132 kV line
Cumilla(N) | 1 | 4:04 | 10 | 40.6667 | Due to S/D of 132/33 kV Transformer T4
Sylhet | 1 | 1:30 | 33 | 49.5 | Due to S/D of 132/33 kV Transformer T1
Norail |  | 2:35 | 5 | 12.9167 | Due to Oil leakage of 132/33 kV Transformer T2
Khulna© | 1 | 0':62 | 144 | 148.8 | Due to flashing at sectionalizer isolator Bus-1
Barishal(N) | 1 | 0:19 | 10 | 3.1667 | Due to Oil leakage of 33 kV side
Faridpur | 1 | 0:24 | 7 | 2.8 | Due to red-hot maintenance of 132/33 kV Trasformer T3
Barishal | 1 | 1:22 | 5 | 6.8333 | Due to S/D of 132/33 kV Transformer T1
Barishal(S) | 1 | 0:22 | 20 | 7.3333 | Due to S/D of 132/33 kV Transformer T2
Ishurdi | 1 | 1:35 | 10 | 15.8333 | Due to red-hot maintenance of 132/33 kV Trasformer T1
Bheramara | 1 | 0:30 | 258 | 129 | Due to tripping of Bheramara-Bottail 132 kV line-1 & 2
Ishurdi | 1 | 1:50 | 10 | 18.3333 | Due to S/D of 132/33 kV Transformer T1
Rajshahi | 1 | 5:21 | 70 | 374.5 | Due to 33 kV Feeder fault of 132/33 kV TransformersT1 & T2
Mahasthangar | 1 | 0:56 | 20 | 18.6667 | Due to red-hot maintenance of 33 kV Bus
Niyamatpur | 1 | 0:56 | 24 | 22.4
Rangpur | 1 | 1:23 | 10 | 13.8333 | Due flashing at Rangpur S/S at 132/33 kV Transformer
Sirajganj | 2 | 1:49 | 30 | 54.5 | Due to red-hot maintenance of 132/33 kV Trasformer T1
|  | 0:49 | 28 | 22.8667 | Due to tripping of Sirajganj-Ashuganj 230 kV line-1
Bogura | 1 | 2:26 | 85 | 138.8333 | Due to red-hot maintenance of Bogura-Sirajganj 230 kV line-2
Purbasadipur | 2 | 2:38 | 25 | 65.8333 | Due to S/D of 132/33 kV Transformer T2
|  | 6:48 | 15 | 102 | Due to S/D of 132/33 kV Transformer T3
| Total Unserved energy : |  |  | 4129.0667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 140 | 24 | 2021-03-01 | 15:00
2 | Munsiganj | 136 | 31 | 2021-03-01 | 22:00
3 | Sonargaon | 89 | 28 | 2021-03-01 | 18:30
4 | Shyampur | 210 | 25 | 2021-03-01 | 1:00
5 | Bhulta | 222 | 31 | 2021-03-01 | 17:00
6 | Madanganj | 65 | 31 | 2021-03-01 | 18:00
7 | Shitalakhya | 129 | 29 | 2021-03-01 | 12:00
8 | Rahim steel | 33 | 29 | 2021-03-01 | 10:00
9 | Matuail | 88 | 8 | 2021-03-01 | 10:00
10 | Ghorasal | 86 | 24 | 2021-03-01 | 19:00
11 | Narsingdi | 170 | 24 | 2021-03-01 | 19:30
12 | Haripur (SBU) | 133 | 28 | 2021-03-01 | 15:00
13 | Sreenagar | - | - | - | -
14 | Ullon | 99 | 20 | 2021-03-01 | 11:00
15 | Hasnabad | 110 | 31 | 2021-03-01 | 22:00
16 | Magbazar | 104 | 31 | 2021-03-01 | 15:00
17 | Maniknagar | 94 | 23 | 2021-03-01 | 11:00
18 | Bangabhaban | 26 | 31 | 2021-03-01 | 11:00
19 | Narinda | 102 | 21 | 2021-03-01 | 18:00
20 | Dhanmondi | 201 | 21 | 2021-03-01 | 14:00
21 | Lalbag | 97 | 10 | 2021-03-01 | 13:00
22 | Madartek | 76 | 31 | 2021-03-01 | 22:00
23 | Dhaka University | - | - | - | -
24 | Aftabnagar | 38 | 24 | 2021-03-01 | 13:00
25 | Fatullah | 65 | 23 | 2021-03-01 | 23:00
26 | Nawabganj | 52 | 30 | 2021-03-01 | 20:00
27 | Mirpur | 119 | 31 | 2021-03-01 | 18:30
28 | Kalyanpur | 102 | 7 | 2021-03-01 | 19:00
29 | Gulshan | 150 | 31 | 2021-03-01 | 13:00
30 | Uttara | 97 | 28 | 2021-03-01 | 19:00
31 | Uttara(new) | 37 | 22 | 2021-03-01 | 13:00
32 | Kamrangirchar | 96 | 23 | 2021-03-01 | 19:00
33 | Savar | 196 | 31 | 2021-03-01 | 16:00
34 | Bhasantec | 174 | 31 | 2021-03-01 | 13:00
35 | Agargaon | 75 | 31 | 2021-03-01 | 17:00
36 | Satmosjid | 103 | 31 | 2021-03-01 | 13:00
37 | Tongi | 131 | 15 | 2021-03-01 | 11:00
38 | Kabirpur | 267 | 25 | 2021-03-01 | 16:00
39 | Basundhara | 194 | 23 | 2021-03-01 | 18:30
40 | Manikganj | 76 | 31 | 2021-03-01 | 22:00
41 | Joydevpur | 175 | 23 | 2021-03-01 | 18:30
42 | New Tongi | 112 | 31 | 2021-03-01 | 12:00
43 | Kodda | 269 | 23 | 2021-03-01 | 12:00
44 | Dhamrai | 128 | 24 | 2021-03-01 | 19:30
45 | Rajendrapur | 106 | 11 | 2021-03-01 | 19:00
46 | Valuka | 130 | 13 | 2021-03-01 | 15:00
47 | Tangail | 233 | 31 | 2021-03-01 | 21:00
48 | Mymensing | 227 | 22 | 2021-03-01 | 18:30
49 | Kishorganj | 136 | 24 | 2021-03-01 | 18:30
50 | Netrokona | 128 | 27 | 2021-03-01 | 20:00
51 | Jamalpur | 148 | 24 | 2021-03-01 | 19:30
52 | Sherpur | 134 | 27 | 2021-03-01 | 19:00
53 | Srimongal | 53 | 24 | 2021-03-01 | 22:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 127 | 23 | 2021-03-01 | 20:00
56 | Fenchuganj | 39 | 29 | 2021-03-01 | 18:30
57 | Kulawara | 38 | 29 | 2021-03-01 | 19:00
58 | Sylhet | 120 | 25 | 2021-03-01 | 19:30
59 | Chatak | 31 | 22 | 2021-03-01 | 18:30
60 | Sunamganj | 38 | 29 | 2021-03-01 | 19:30
61 | Bianibazar | 54 | 23 | 2021-03-01 | 18:30
62 | Cumilla (S) | 186 | 27 | 2021-03-01 | 18:30
63 | Cumilla(N) | 135 | 29 | 2021-03-01 | 21:00
64 | Chandpur | 79 | 31 | 2021-03-01 | 19:00
65 | Feni | 126 | 29 | 2021-03-01 | 18:30
66 | Chowmuhani | 187 | 22 | 2021-03-01 | 19:00
67 | Ashuganj | 57 | 21 | 2021-03-01 | 22:00
68 | Daudkandi | 152 | 31 | 2021-03-01 | 21:00
69 | B.Baria | 165 | 29 | 2021-03-01 | 20:00
70 | Ramganj | 86 | 21 | 2021-03-01 | 19:30
71 | Chaddagram | 55 | 29 | 2021-03-01 | 21:00
72 | PHP | 12 | 24 | 2021-03-01 | 15:00
73 | Kochua | 70 | 30 | 2021-03-01 | 20:00
74 | Madanhat | 73 | 25 | 2021-03-01 | 18:30
75 | Hathazari | 96 | 23 | 2021-03-01 | 18:30
76 | Khulshi | 212 | 25 | 2021-03-01 | 12:00
77 | Halishahar | 139 | 25 | 2021-03-01 | 15:00
78 | Baraulia | 166 | 24 | 2021-03-01 | 1:00
79 | Sikalbaha | 34 | 25 | 2021-03-01 | 19:00
80 | Dohazari | 102 | 31 | 2021-03-01 | 19:30
81 | Cox'sbazar | 110 | 21 | 2021-03-01 | 19:00
82 | Chandraghona | 32 | 5 | 2021-03-01 | 18:30
83 | Kaptai | 4 | 30 | 2021-03-01 | 21:00
84 | A. Khaer Stl. | 14 | 20 | 2021-03-01 | 9:00
85 | Bakulia | 116 | 24 | 2021-03-01 | 19:00
86 | Julda | 26 | 19 | 2021-03-01 | 1:00
87 | TK chemical | 28 | 22 | 2021-03-01 | 19:00
88 | Modern Steel | 0 | 1 | 2021-03-01 | 1:00
89 | Shahmirpur | 34 | 24 | 2021-03-01 | 23:00
90 | Khagrachhari | 24 | 11 | 2021-03-01 | 19:30
91 | Matarbari | 39 | 23 | 2021-03-01 | 19:00
92 | Baroiar Hat | 46 | 1 | 2021-03-01 | 18:30
93 | Rangamati | 12 | 14 | 2021-03-01 | 18:30
94 | Abul Khair 230 | 185 | 5 | 2021-03-01 | 2:00
95 | BSRM | 158 | 27 | 2021-03-01 | 12:00
96 | GPH Ispat | 93 | 17 | 2021-03-01 | 16:00
97 | Goalpara | 33 | 29 | 2021-03-01 | 13:00
98 | Central s/s | 105 | 7 | 2021-03-01 | 19:00
99 | Noapara | 65 | 8 | 2021-03-01 | 20:00
100 | Jashore | 134 | 30 | 2021-03-01 | 21:00
101 | Benapol | 72 | 11 | 2021-03-01 | 19:30
101 | Jhenidah | 120 | 30 | 2021-03-01 | 20:00
102 | Bottail | 124 | 31 | 2021-03-01 | 19:00
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:March'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 55 | 2 | 2021-03-01 | 19:00
104 | Faridpur | 200 | 31 | 2021-03-01 | 22:00
105 | Madaripur | 105 | 31 | 2021-03-01 | 22:00
106 | Sariatpur | 66 | 31 | 2021-03-01 | 21:00
107 | Gopalganj | 92 | 31 | 2021-03-01 | 19:30
108 | Bagerhat | 113 | 23 | 2021-03-01 | 19:00
109 | Mongla | 44 | 4 | 2021-03-01 | 18:00
110 | Satkhira | 110 | 31 | 2021-03-01 | 21:00
111 | Gallamari | 41 | 23 | 2021-03-01 | 13:00
112 | Magura | 56 | 30 | 2021-03-01 | 19:00
113 | Norail | 42 | 29 | 2021-03-01 | 19:00
114 | Chuadanga | 93 | 30 | 2021-03-01 | 19:00
115 | Borguna | 16 | 23 | 2021-03-01 | 19:00
116 | Barsal(N) | 48 | 30 | 2021-03-01 | 24:00
117 | Barsal(S) | 108 | 31 | 2021-03-01 | 19:00
118 | Patuakhali | 104 | 24 | 2021-03-01 | 20:00
119 | Bhandaria | 50 | 24 | 2021-03-01 | 20:00
120 | Borhan Uddin | 44 | 6 | 2021-03-01 | 18:30
121 | Ishurdi | 63 | 31 | 2021-03-01 | 19:00
122 | Ruppur Paromanobik | 3 | 1 | 2021-03-01 | 12:00
123 | Natore | 134 | 25 | 2021-03-01 | 20:00
124 | Bogura | 166 | 28 | 2021-03-01 | 19:00
125 | Naogaon | 115 | 29 | 2021-03-01 | 19:00
126 | Rajshahi | 149 | 24 | 2021-03-01 | 20:00
127 | Rajshahi New | 24 | 10 | 2021-03-01 | 19:00
128 | C.Nawabganj | 80 | 28 | 2021-03-01 | 20:00
129 | Amnura | 60 | 29 | 2021-03-01 | 20:00
130 | Pabna | 107 | 23 | 2021-03-01 | 20:00
131 | Shahjadpur | 121 | 23 | 2021-03-01 | 20:00
132 | Serajganj | 118 | 31 | 2021-03-01 | 19:30
133 | Niyamatpur | 93 | 28 | 2021-03-01 | 19:00
134 | Joypurhat | 65 | 24 | 2021-03-01 | 19:00
135 | Sherpur(Bogura) | 56 | 21 | 2021-03-01 | 18:30
136 | Mohastangar | 58 | 6 | 2021-03-01 | 20:00
137 | Bangura | 30 | 11 | 2021-03-01 | 19:00
138 | Rangpur | 133 | 23 | 2021-03-01 | 19:00
139 | Lalmonirhat | 49 | 23 | 2021-03-01 | 19:00
140 | Saidpur | 108 | 22 | 2021-03-01 | 19:00
141 | Purbasadipur | 101 | 23 | 2021-03-01 | 13:00
142 | Thakurgaon | 81 | 28 | 2021-03-01 | 20:00
143 | Palshbari | 120 | 17 | 2021-03-01 | 19:00
144 | Barapukuria | 55 | 25 | 2021-03-01 | 19:00
145 | Panchugar | 49 | 10 | 2021-03-01 | 19:30
146 | Joldhaka | 60 | 25 | 2021-03-01 | 19:30
147 | Kurigram | 56 | 27 | 2021-03-01 | 20:00
148 | Mitha Pukur | 31 | 18 | 2021-03-01 | 19:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:March' 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4527 | 31.03.2021 | 18:30
Chattogram | 1399 | 27.03.2021 | 21:00
Khulna | 1573 | 31.03.2021 | 21:00
Rajshahi | 1333 | 23.03.2021 | 20:00
Cumilla | 1190 | 24.03.2021 | 21:00
Mymensingh | 1046 | 27.03.2021 | 19:00
Sylhet | 488 | 23.03.2021 | 18:00
Barisal | 350 | 24.03.2021 | 20:00
Rangpur | 982 | 28.03.2021 | 14:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 413 | 4 | 2021-03-01 | 21:00 | 396 | 13 | 2021-03-01 | 13:00
2 | Bheramara | 400 | 408 | 26 | 2021-03-01 | 19:00 | 389 | 22 | 2021-03-01 | 12:00
3 | Ashuganj(N) | 400 | 398 | 1 | 2021-03-01 | 6:00 | 366 | 10 | 2021-03-01 | 15:00
4 | Payra | 400 | 413 | 13 | 2021-03-01 | 17:00 | 394 | 25 | 2021-03-01 | 1:00
5 | Kaliakoir | 400 | 404 | 1 | 2021-03-01 | 7:00 | 371 | 16 | 2021-03-01 | 12:00
6 | Bhulta | 400 | 398 | 1 | 2021-03-01 | 6:00 | 360 | 13 | 2021-03-01 | 11:00
7 | Gopalganj | 400 | 416 | 13 | 2021-03-01 | 15:00 | 379 | 25 | 2021-03-01 | 19:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 240 | 2 | 2021-03-01 | 1:00 | 222 | 15 | 2021-03-01 | 15:00
2 | Ishurdi | 230 | 242 | 4 | 2021-03-01 | 18:00 | 221 | 15 | 2021-03-01 | 19:00
3 | Ashuganj | 230 | 243 | 1 | 2021-03-01 | 6:00 | 225 | 6 | 2021-03-01 | 12:00
4 | Serajganj | 230 | 238 | 1 | 2021-03-01 | 6:00 | 224 | 18 | 2021-03-01 | 7:00
5 | Baghabari | 230 | 238 | 2 | 2021-03-01 | 3:00 | 225 | 20 | 2021-03-01 | 7:00
6 | Barapukuria | 230 | 240 | 13 | 2021-03-01 | 14:00 | 221 | 21 | 2021-03-01 | 19:00
7 | Bogura | 230 | 245 | 1 | 2021-03-01 | 20:00 | 213 | 30 | 2021-03-01 | 12:00
8 | Rajshahi | 230 | 246 | 0 | 2021-03-01 | 1:00 | 212 | 30 | 2021-03-01 | 8:00
9 | Khulna South | 230 | 248 | 14 | 2021-03-01 | 12:00 | 209 | 31 | 2021-03-01 | 20:00
10 | Rampura | 230 | 233 | 2 | 2021-03-01 | 20:00 | 215 | 13 | 2021-03-01 | 12:00
11 | Haripur | 230 | 243 | 1 | 2021-03-01 | 9:00 | 213 | 13 | 2021-03-01 | 11:00
12 | Hasnabad | 230 | 239 | 1 | 2021-03-01 | 20:00 | 208 | 14 | 2021-03-01 | 12:00
13 | Shyampur | 230 | 229 | 11 | 2021-03-01 | 6:00 | 220 | 2 | 2021-03-01 | 3:00
14 | Aminbazar | 230 | 237 | 2 | 2021-03-01 | 19:30 | 211 | 13 | 2021-03-01 | 2:00
15 | Tongi | 230 | 233 | 2 | 2021-03-01 | 19:30 | 202 | 14 | 2021-03-01 | 12:00
16 | Comilla (N) | 230 | 236 | 1 | 2021-03-01 | 19:00 | 216 | 6 | 2021-03-01 | 12:00
17 | Hathazari | 230 | 233 | 30 | 2021-03-01 | 19:00 | 210 | 6 | 2021-03-01 | 12:00
18 | Megnaghat | 230 | 243 | 30 | 2021-03-01 | 19:30 | 217 | 13 | 2021-03-01 | 14:00
19 | Fenchuganj | 230 | 244 | 13 | 2021-03-01 | 6:00 | 222 | 30 | 2021-03-01 | 15:00
20 | Siddhirganj | 230 | 238 | 1 | 2021-03-01 | 6:00 | 214 | 13 | 2021-03-01 | 11:00
21 | Maniknagar | 230 | 236 | 1 | 2021-03-01 | 6:00 | 212 | 13 | 2021-03-01 | 11:00
22 | Old Airport | 230 | 238 | 2 | 2021-03-01 | 9:00 | 209 | 13 | 2021-03-01 | 12:00
23 | Barisal | 230 | 251 | 23 | 2021-03-01 | 2:00 | 230 | 20 | 2021-03-01 | 19:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-03-01 | 3:00 | 225 | 15 | 2021-03-01 | 22:00
25 | AKSML | 230 | 234 | 1 | 2021-03-01 | 20:00 | 206 | 6 | 2021-03-01 | 13:00
26 | BSRM | 230 | 233 | 2 | 2021-03-01 | 19:30 | 206 | 6 | 2021-03-01 | 12:00
27 | Bibiyana | 230 | 243 | 1 | 2021-03-01 | 9:00 | 232 | 21 | 2021-03-01 | 17:00
28 | Bhulta | 230 | 239 | 1 | 2021-03-01 | 20:00 | 214 | 13 | 2021-03-01 | 15:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-03-01 | 10:00 | 222 | 6 | 2021-03-01 | 12:00
30 | Kaliakoir | 230 | 236 | 1 | 2021-03-01 | 6:00 | 212 | 13 | 2021-03-01 | 14:00
31 | GPH | 230 | 232 | 1 | 2021-03-01 | 20:00 | 206 | 6 | 2021-03-01 | 13:00
132 kV Substation
1 | Siddhirganj | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 113 | 25 | 2021-03-01 | 0.125
2 | Munsiganj | 132 | 141 | 22 | 2021-03-01 | 0.91667 | 119 | 13 | 2021-03-01 | 0.45833
3 | Sonargaon | 132 | 140 | 17 | 2021-03-01 | 0.79167 | 121 | 13 | 2021-03-01 | 0.45833
4 | Shyampur | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 129 | 1 | 2021-03-01 | 0.083333
5 | Bhulta | 132 | 137 | 2 | 2021-03-01 | 0.54167 | 115 | 13 | 2021-03-01 | 0.41667
6 | Madanganj | 132 | 140 | 3 | 2021-03-01 | 0.8125 | 118 | 13 | 2021-03-01 | 0.45833
7 | Shitalakhya | 132 | 143 | 21 | 2021-03-01 | 0.79167 | 120 | 7 | 2021-03-01 | 0.41667
8 | Rahim Steal | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 122 | 13 | 2021-03-01 | 0.45833
9 | Matuail | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 113 | 25 | 2021-03-01 | 0.125
10 | Ghorasal | 132 | 140 | 1 | 2021-03-01 | 0.29167 | 132 | 10 | 2021-03-01 | 0.625
11 | Narsinghdi | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 118 | 11 | 2021-03-01 | 0.45833
12 | Haripur (SBU) | 132 | 139 | 22 | 2021-03-01 | 0.45833 | 122 | 13 | 2021-03-01 | 0.45833
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 121 | 11 | 2021-03-01 | 0.5
15 | Hasnabad | 132 | 140 | 21 | 2021-03-01 | 0.83333 | 123 | 6 | 2021-03-01 | 0.41667
16 | Magbazar | 132 | 135 | 15 | 2021-03-01 | 0.20833 | 120 | 13 | 2021-03-01 | 0.45833
17 | Maniknagar | 132 | 136 | 1 | 2021-03-01 | 0.91667 | 122 | 17 | 2021-03-01 | 0.45833
18 | Bangabhaban | 132 | 136 | 1 | 2021-03-01 | 0.91667 | 122 | 17 | 2021-03-01 | 0.45833
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 138 | 22 | 2021-03-01 | 0.83333 | 122 | 17 | 2021-03-01 | 0.45833
20 | Dhanmondi | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 121 | 11 | 2021-03-01 | 0.5
21 | Lalbag | 132 | 141 | 13 | 2021-03-01 | 0.70833 | 117 | 7 | 2021-03-01 | 0.41667
22 | Madartek | 132 | 138 | 13 | 2021-03-01 | 0.70833 | 121 | 6 | 2021-03-01 | 0.5
23 | Dhaka University | 132 | - | - | - | - | - | - | - | -
24 | Aftabnagar | 132 | 136 | 25 | 2021-03-01 | 0.25 | 122 | 9 | 2021-03-01 | 0.5
25 | Fatullah | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 124 | 10 | 2021-03-01 | 0.45833
26 | Nawabganj | 133 | 135 | 13 | 2021-03-01 | 0.70833 | 119 | 6 | 2021-03-01 | 0.5
27 | Mirpur | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 120 | 9 | 2021-03-01 | 0.5
28 | Kalyanpur | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 121 | 13 | 2021-03-01 | 0.45833
29 | Gulshan | 132 | 137 | 13 | 2021-03-01 | 0.70833 | 121 | 11 | 2021-03-01 | 0.5
30 | Uttara | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 123 | 14 | 2021-03-01 | 0.5
31 | Uttara(New) | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 120 | 12 | 2021-03-01 | 0.5
32 | Kamrangirchar | 132 | 138 | 13 | 2021-03-01 | 0.70833 | 117 | 9 | 2021-03-01 | 0.5
33 | Savar | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 119 | 12 | 2021-03-01 | 0.5
34 | Bhasantec | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 121 | 13 | 2021-03-01 | 0.45833
35 | Agargaon | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 122 | 13 | 2021-03-01 | 0.45833
36 | Satmosjid | 132 | 141 | 13 | 2021-03-01 | 0.70833 | 122 | 6 | 2021-03-01 | 0.5
37 | Tongi | 132 | 142 | 13 | 2021-03-01 | 0.70833 | 126 | 16 | 2021-03-01 | 0.45833
38 | Kabirpur | 132 | 145 | 13 | 2021-03-01 | 0.70833 | 121 | 16 | 2021-03-01 | 0.5
39 | Basundhara | 132 | 139 | 13 | 2021-03-01 | 0.70833 | 120 | 19 | 2021-03-01 | 0.45833
40 | Manikganj | 132 | 145 | 13 | 2021-03-01 | 0.70833 | 126 | 7 | 2021-03-01 | 0.66667
41 | Joydevpur | 132 | 139 | 1 | 2021-03-01 | 20:00 | 126 | 13 | 2021-03-01 | 0.5
42 | New Tongi | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 124 | 15 | 2021-03-01 | 0.625
43 | Kodda | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 116 | 15 | 2021-03-01 | 0.625
44 | Dhamrai | 132 | 145 | 13 | 2021-03-01 | 0.70833 | 122 | 6 | 2021-03-01 | 0.5
45 | Rajendrapur | 132 | 141 | 13 | 2021-03-01 | 0.70833 | 117 | 6 | 2021-03-01 | 0.54167
46 | Valuka | 132 | 138 | 13 | 2021-03-01 | 0.70833 | 107 | 28 | 2021-03-01 | 0.77083
47 | Tangail | 132 | 140 | 13 | 2021-03-01 | 0.66667 | 120 | 6 | 2021-03-01 | 0.5
48 | Mymensing | 132 | 141 | 13 | 2021-03-01 | 0.70833 | 113 | 1 | 2021-03-01 | 0.77083
49 | Kishorganj | 132 | 137 | 13 | 2021-03-01 | 0.70833 | 116 | 7 | 2021-03-01 | 0.77083
50 | Netrokona | 132 | 140 | 13 | 2021-03-01 | 0.70833 | 108 | 19 | 2021-03-01 | 0.33333
51 | Jamalpur | 132 | 141 | 3 | 2021-03-01 | 0.79167 | 112 | 19 | 2021-03-01 | 0.29167
52 | Sherpur | 132 | 140 | 3 | 2021-03-01 | 0.875 | 111 | 19 | 2021-03-01 | 0.33333
53 | Srimongal | 132 | 140 | 13 | 2021-03-01 | 0.79167 | 131 | 21 | 2021-03-01 | 0.625
54 | Shahjibazar | 132 | 139 | 13 | 2021-03-01 | 0.77083 | 127 | 21 | 2021-03-01 | 0.77083
55 | Fenchuganj | 132 | 140 | 30 | 2021-03-01 | 0.91667 | 130 | 21 | 2021-03-01 | 0.77083
56 | Khulawara | 132 | 140 | 30 | 2021-03-01 | 0.91667 | 130 | 20 | 2021-03-01 | 0.8125
57 | Sylhet | 132 | 138 | 30 | 2021-03-01 | 0.20833 | 126 | 21 | 2021-03-01 | 0.625
58 | Chattak | 132 | 138 | 30 | 2021-03-01 | 0.125 | 121 | 21 | 2021-03-01 | 0.77083
59 | Sunamganj | 132 | 138 | 30 | 2021-03-01 | 0.125 | 122 | 20 | 2021-03-01 | 0.77083
60 | Biani Bazar | 132 | 140 | 30 | 2021-03-01 | 0.16667 | 123 | 21 | 2021-03-01 | 0.77083
61 | Comilla(South) | 132 | 132 | 3 | 2021-03-01 | 0.5 | 114 | 14 | 2021-03-01 | 0.79167
62 | Comilla (North) | 132 | 143 | 1 | 2021-03-01 | 0.83333 | 129 | 13 | 2021-03-01 | 0.625
63 | Chandpur | 132 | 144 | 1 | 2021-03-01 | 0.79167 | 124 | 17 | 2021-03-01 | 0.16667
64 | Feni | 132 | 140 | 25 | 2021-03-01 | 0.875 | 122 | 13 | 2021-03-01 | 0.45833
65 | Chowmuhani | 132 | 138 | 1 | 2021-03-01 | 0.625 | 122 | 16 | 2021-03-01 | 0.625
66 | Ashuganj | 132 | 141 | 31 | 2021-03-01 | 0.83333 | 130 | 6 | 2021-03-01 | 0.625
67 | Daudkandi | 132 | 141 | 23 | 2021-03-01 | 0.79167 | 124 | 7 | 2021-03-01 | 0.5
68 | Brahminbaria | 132 | 138 | 31 | 2021-03-01 | 0.83333 | 124 | 18 | 2021-03-01 | 0.79167
69 | Ramganj | 132 | 140 | 1 | 2021-03-01 | 0.70833 | 121 | 19 | 2021-03-01 | 0.41667
70 | Chaddagram | 132 | 142 | 25 | 2021-03-01 | 0.875 | 125 | 14 | 2021-03-01 | 0.625
71 | PHP | 132 | 137 | 1 | 2021-03-01 | 0.79167 | 122 | 7 | 2021-03-01 | 0.66667
72 | Kochua | 132 | 144 | 25 | 2021-03-01 | 0.45833 | 126 | 17 | 2021-03-01 | 0.41667
73 | Madanhat | 132 | 139 | 25 | 2021-03-01 | 0.875 | 125 | 6 | 2021-03-01 | 0.5
74 | Hathazari | 132 | 137 | 1 | 2021-03-01 | 0.79167 | 126 | 5 | 2021-03-01 | 0.66667
75 | Khulshi | 132 | 138 | 31 | 2021-03-01 | 0.5 | 122 | 6 | 2021-03-01 | 0.54167
76 | Halishahar | 132 | 138 | 1 | 2021-03-01 | 0.8125 | 124 | 6 | 2021-03-01 | 0.041667
77 | Baraulia | 132 | 137 | 2 | 2021-03-01 | 0.41667 | 121 | 13 | 2021-03-01 | 0.75
78 | Sikalbaha | 132 | 140 | 31 | 2021-03-01 | 0.83333 | 125 | 6 | 2021-03-01 | 0.54167
79 | Dohazari | 132 | 139 | 3 | 2021-03-01 | 0.8125 | 122 | 6 | 2021-03-01 | 0.58333
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: March'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 131 | 9 | 2021-03-01 | 0.75 | 107 | 8 | 2021-03-01 | 0.625
81 | Chandraghona | 132 | 138 | 3 | 2021-03-01 | 0.79167 | 121 | 6 | 2021-03-01 | 0.5
82 | Kaptai | 132 | 138 | 31 | 2021-03-01 | 0.29167 | 130 | 31 | 2021-03-01 | 0.375
83 | A. Khaer Stl. | 132 | 136 | 1 | 2021-03-01 | 0.83333 | 124 | 6 | 2021-03-01 | 0.45833
84 | Bakulia | 132 | 139 | 31 | 2021-03-01 | 0.8125 | 124 | 6 | 2021-03-01 | 0.5
85 | Julda | 132 | 139 | 1 | 2021-03-01 | 0.79167 | 125 | 6 | 2021-03-01 | 0.041667
86 | TK Chemical | 132 | 139 | 10 | 2021-03-01 | 0.875 | 124 | 6 | 2021-03-01 | 0.041667
87 | Modern Steel | - | - | - | - | - | - | - | - | -
88 | Shahmirpur | 132 | 140 | 31 | 2021-03-01 | 0.8125 | 125 | 6 | 2021-03-01 | 0.125
89 | Khagrachhari | 132 | 137 | 31 | 2021-03-01 | 0.54167 | 121 | 6 | 2021-03-01 | 0.5
90 | Matarbari | 132 | 135 | 3 | 2021-03-01 | 0.8125 | 115 | 8 | 2021-03-01 | 0.625
91 | Baroiar Hat | 132 | 138 | 1 | 2021-03-01 | 0.70833 | 123 | 6 | 2021-03-01 | 0.5
92 | Rangamati | 132 | 138 | 25 | 2021-03-01 | 0.875 | 122 | 6 | 2021-03-01 | 0.54167
93 | Goalpara | 132 | 140 | 13 | 2021-03-01 | 0.625 | 120 | 9 | 2021-03-01 | 0.29167
94 | Khulna Central | 132 | 139 | 1 | 2021-03-01 | 0.70833 | 121 | 8 | 2021-03-01 | 0.25
95 | Noapara | 132 | 139 | 13 | 2021-03-01 | 0.625 | 118 | 12 | 2021-03-01 | 0.33333
96 | Jessore | 132 | 135 | 13 | 2021-03-01 | 0.66667 | 110 | 8 | 2021-03-01 | 0.25
97 | Benapol | 132 | 136 | 14 | 2021-03-01 | 0.16667 | 110 | 30 | 2021-03-01 | 0.77083
98 | Jhenida | 132 | 135 | 13 | 2021-03-01 | 0.66667 | 105 | 31 | 2021-03-01 | 0.83333
99 | Bottail | 132 | 137 | 5 | 2021-03-01 | 0.75 | 112 | 25 | 2021-03-01 | 0.8125
100 | G.K Project | 132 | 142 | 4 | 2021-03-01 | 0.75 | 132 | 22 | 2021-03-01 | 0.8125
101 | Faridpur | 132 | 140 | 6 | 2021-03-01 | 0.20833 | 124 | 25 | 2021-03-01 | 0.79167
102 | Madaripur | 132 | 144 | 13 | 2021-03-01 | 0.70833 | 130 | 25 | 2021-03-01 | 0.79167
103 | Sariatpur | 132 | 146 | 13 | 2021-03-01 | 0.70833 | 128 | 25 | 2021-03-01 | 0.79167
104 | Gopalganj | 132 | 148 | 13 | 2021-03-01 | 0.70833 | 129 | 30 | 2021-03-01 | 0.83333
105 | Bagerhat | 132 | 140 | 12 | 2021-03-01 | 0.375 | 117 | 16 | 2021-03-01 | 0.29167
106 | Mongla | 132 | 142 | 12 | 2021-03-01 | 0.375 | 114 | 9 | 2021-03-01 | 0.29167
107 | Satkhira | 132 | 141 | 13 | 2021-03-01 | 0.625 | 118 | 9 | 2021-03-01 | 0.29167
108 | Gallamari | 132 | 140 | 1 | 2021-03-01 | 0.70833 | 117 | 12 | 2021-03-01 | 0.33333
109 | Magura | 132 | 135 | 1 | 2021-03-01 | 0.16667 | 104 | 31 | 2021-03-01 | 0.875
110 | Norail | 132 | 138 | 6 | 2021-03-01 | 0.5 | 103 | 30 | 2021-03-01 | 1900-01-07 20:00
111 | Chuadanga | 132 | 132 | 13 | 2021-03-01 | 0.625 | 94 | 31 | 2021-03-01 | 0.83333
112 | Borguna | 132 | 144 | 6 | 2021-03-01 | 0.375 | 127 | 30 | 2021-03-01 | 0.77083
113 | Barisal(N) | 132 | 145 | 17 | 2021-03-01 | 0.25 | 128 | 20 | 2021-03-01 | 0.79167
114 | Barisal(S) | 132 | 143 | 17 | 2021-03-01 | 0.75 | 127 | 23 | 2021-03-01 | 0.77083
115 | Patuakhali | 132 | 142 | 13 | 2021-03-01 | 0.70833 | 125 | 30 | 2021-03-01 | 0.77083
116 | Bhandaria | 132 | 143 | 13 | 2021-03-01 | 0.70833 | 125 | 20 | 2021-03-01 | 0.77083
117 | Ishurdi | 132 | 140 | 4 | 2021-03-01 | 0.75 | 130 | 23 | 2021-03-01 | 0.79167
118 | Ruppur paromanobik | 132 | 140 | 4 | 2021-03-01 | 0.75 | 130 | 22 | 2021-03-01 | 0.79167
118 | Natore | 132 | 139 | 4 | 2021-03-01 | 0.75 | 127 | 9 | 2021-03-01 | 0.29167
119 | Bogra | 132 | 141 | 13 | 2021-03-01 | 0.58333 | 119 | 9 | 2021-03-01 | 0.29167
120 | Noagaon | 132 | 139 | 13 | 2021-03-01 | 0.58333 | 114 | 30 | 2021-03-01 | 0.54167
121 | Rajshahi | 132 | 138 | 1 | 2021-03-01 | 0.83333 | 126 | 8 | 2021-03-01 | 0.5
122 | Rajshahi New | 132 | 138 | 1 | 2021-03-01 | 0.83333 | 125 | 9 | 2021-03-01 | 0.29167
123 | C.Nawabganj | 132 | 136 | 1 | 2021-03-01 | 0.83333 | 121 | 1 | 2021-03-01 | 0.41667
124 | Amnura | 132 | 138 | 4 | 2021-03-01 | 0.75 | 121 | 13 | 2021-03-01 | 0.29167
125 | Pabna | 132 | 139 | 4 | 2021-03-01 | 0.75 | 128 | 23 | 2021-03-01 | 0.83333
126 | Shahjadpur | 132 | 143 | 1 | 2021-03-01 | 0.125 | 131 | 30 | 2021-03-01 | 0.375
127 | Serajganj | 132 | 137 | 13 | 2021-03-01 | 0.625 | 124 | 30 | 2021-03-01 | 0.5
128 | Niyamatpur | 132 | 139 | 13 | 2021-03-01 | 0.625 | 109 | 30 | 2021-03-01 | 0.5
129 | Joypurhat | 132 | 140 | 13 | 2021-03-01 | 0.625 | 113 | 30 | 2021-03-01 | 0.54167
130 | Sherpur(Bogura) | 132 | 141 | 13 | 2021-03-01 | 0.625 | 124 | 30 | 2021-03-01 | 0.54167
132 | Mohastangor | 132 | 140 | 13 | 2021-03-01 | 0.625 | 122 | 7 | 2021-03-01 | 0.33333
133 | Bangura | 132 | 140 | 2 | 2021-03-01 | 0.041667 | 130 | 16 | 2021-03-01 | 0.58333
134 | Rangpur | 132 | 137 | 13 | 2021-03-01 | 0.58333 | 114 | 22 | 2021-03-01 | 0.79167
135 | Lalmonirhat | 132 | 137 | 2 | 2021-03-01 | 0.083333 | 115 | 7 | 2021-03-01 | 0.33333
136 | Saidpur | 132 | 137 | 13 | 2021-03-01 | 0.58333 | 112 | 20 | 2021-03-01 | 0.79167
137 | Purbasadipur | 132 | 138 | 13 | 2021-03-01 | 0.58333 | 101 | 22 | 2021-03-01 | 0.77083
138 | Thakurgaon | 132 | 138 | 13 | 2021-03-01 | 0.58333 | 106 | 23 | 2021-03-01 | 0.79167
139 | Palashbari | 132 | 138 | 13 | 2021-03-01 | 0.625 | 116 | 9 | 2021-03-01 | 0.29167
140 | Barapukuria | 132 | 140 | 13 | 2021-03-01 | 0.58333 | 121 | 21 | 2021-03-01 | 0.79167
141 | Panchagar | 132 | 136 | 13 | 2021-03-01 | 0.58333 | 101 | 22 | 2021-03-01 | 0.79167
142 | Joldhaka | 132 | 137 | 13 | 2021-03-01 | 0.58333 | 106 | 22 | 2021-03-01 | 0.79167
143 | Kurigram | 132 | 136 | 13 | 2021-03-01 | 0.625 | 110 | 20 | 2021-03-01 | 0.29167
144 | Mithapukur | 132 | 138 | 13 | 2021-03-01 | 0.58333 | 117 | 22 | 2021-03-01 | 0.79167
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:March' 2021
Name of the | Auto transformer |  | Recorded maximum load in the month
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 120 | 300
Hasnabad | TR2 | 225 | 115 | 300 | 2021-07-03 | 9:00
| TR3 | 225 | 115 | 300
| TR1 | 225 | 195 | 560
Tongi | TR2 | 225 | 195 | 560 | 23/03/21 | 12:00
| TR3 | 225 | 195 | 560
Haripur | TR1 | 225 | 118 | 375
| TR2 | 225 | 118 | 375 | 15/03/2021 | 11:00
| TR3 | 225 | 118 | 375
| TR1 | 225 | 196 | 535 | 24/03/21 | 10:00
Rampura | TR2 | 225 | 196 | 535
| TR3 | 225 | 196 | 535
Keraniganj | ATR1 | 300 | 58 | 160 | 2021-03-31 | 22:00
| ATR2 | 300 | 58 | 160
| ATR3 | 300 | 58 | 160
| TR1 | 225 | 135 | 385
Aminbazar | TR2 | 225 | 135 | 385 | 21/03/21 | 10:00 | S/D
| TR3 | 225 | 143 | 402
Agargaon | TR1 | 300 | 281 | 832 | 2021-03-31 | 9:00 | TR-2 S/D
| TR2 | 300 | 269 | 804 | 2021-03-29 | 9:00 | TR-1 S/D
Maniknagar | TR1 | 300 | 110 | 330 | 31/03/21 | 15:00
| TR2 | 300 | 110 | 330
Cumilla (N) | TR1 | 225 | 174 | 486 | 13/03/2021
| TR2 | 225 | 173 | 480 |  | 17:00
Fenchuganj | AT2 | 300 | 270 | 740 | 21/03/21 | 18:30
| MT1 | 150 | 83 | 230 | 13/03/21
Hathazari | MT2 | 150 | 83 | 230
| MT3 | 150 | 83 | 230 |  | 17:00
| MT4 | 150 | 83 | 230
| TR1 | 225 | 91 | 232
Ishurdi | TR2 | 225 | 91 | 232 | 30/03/21
| TR3 | 225 | 91 | 232 |  | 19:00
Khulna(S) | TR1 | 225 | 133 | 353
| TR2 | 225 | 133 | 353 | 2021-08-03 | 20:00
| TR3 | 300 | 169 | 450
Bogura | TR1 | 225 | 121 | 365
| TR2 | 225 | 121 | 365 | 30/03/21 | 3:00
| TR3 | 225 | 166 | 488
Baghabari | TR1 | 300 | 157 | 440
| TR2 | 225 | 110 | 310 | 28/03/21 | 20:00
Rajshahi | ATR-01 | 300 | 122 | 345 | 2021-03-30 | 13:00
| ATR-02 | 300 | 122 | 345
Barapukuria | TR1 | 225 | 144 | 700 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 159 | 810 | 28/03/21 | 19:00 | 132 kV current is being provided
| TR3 | 300 | 205 | 1020
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:March' 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 277.8 | 432 | 2021-12-03 | 14:45
| TR2(400/230 kV) | 520 | 281.3 | 435
| TR1(400/132 kV) | 325 | 277 | 465 | 2021-01-03 | 18:15
| TR2(400/132 kV) | 325 | 277 | 468
Bibiyana | ICT1(400/230 kV) | 520 | 161 | 239 | 21/03/21 | 18:00
| ICT2(400/230kV) | 520 | 157 | 232
Bhulta | ATR1(400/230 kV) | 520 | 213 | 397 | 2021-11-03 | 3:15
| ATR2(400/230kV) | 520 | 213 | 397
Ashuganj(N) | GSUT1 | 567 | 380.6 | 636 | 2021-11-03 | 3:16
Gopalganj | ATR1(400/138 kV) | 325 | 309 | 466 | 29/03/21 | 21:00
| ATR2(400/138kV) | 325 | 309 | 466
Payra | GSUT1 | 270 | 208 | 305 | 29/03/21 | 21:00
| GSUT2 | 270 | 208 | 305
| GSUT3 | 270 | 208 | 305
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
270

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:March' 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:March' 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
01-03-21 | 10988 | 10988 | - | - | - | - | - | - | - | - | - | - | - | - | 01-03-21 | 9520 | 9520 | - | - | - | - | - | - | - | - | - | - | - | -
02-03-21 | 10798 | 10798 | - | - | - | - | - | - | - | - | - | - | - | - | 02-03-21 | 9540 | 9540 | - | - | - | - | - | - | - | - | - | - | - | -
03-04-21 | 10755 | 10755 | - | - | - | - | - | - | - | - | - | - | - | - | 03-04-21 | 9209 | 9209 | - | - | - | - | - | - | - | - | - | - | - | -
04-05-21 | 10640 | 10640 | - | - | - | - | - | - | - | - | - | - | - | - | 04-05-21 | 9014 | 9014 | - | - | - | - | - | - | - | - | - | - | - | -
05-03-21 | 9947 | 9947 | - | - | - | - | - | - | - | - | - | - | - | - | 05-03-21 | 7951 | 7951 | - | - | - | - | - | - | - | - | - | - | - | -
06-03-21 | 10781 | 10781 | - | - | - | - | - | - | - | - | - | - | - | - | 06-03-21 | 8314 | 8314 | - | - | - | - | - | - | - | - | - | - | - | -
07-03-21 | 10951 | 10951 | - | - | - | - | - | - | - | - | - | - | - | - | 07-03-21 | 9720 | 9720 | - | - | - | - | - | - | - | - | - | - | - | -
08-03-21 | 11416 | 11416 | - | - | - | - | - | - | - | - | - | - | - | - | 08-03-21 | 9652 | 9652 | - | - | - | - | - | - | - | - | - | - | - | -
09-03-21 | 11147 | 11147 | - | - | - | - | - | - | - | - | - | - | - | - | 09-03-21 | 9091 | 9091 | - | - | - | - | - | - | - | - | - | - | - | -
10-03-21 | 11397 | 11397 | - | - | - | - | - | - | - | - | - | - | - | - | 10-03-21 | 9260 | 9260 | - | - | - | - | - | - | - | - | - | - | - | -
11-03-21 | 11615 | 11615 | - | - | - | - | - | - | - | - | - | - | - | - | 11-03-21 | 9693 | 9693 | - | - | - | - | - | - | - | - | - | - | - | -
12-03-21 | 10869 | 10869 | - | - | - | - | - | - | - | - | - | - | - | - | 12-03-21 | 8639 | 8639 | - | - | - | - | - | - | - | - | - | - | - | -
13-03-21 | 9432 | 9432 | - | - | - | - | - | - | - | - | - | - | - | - | 13-03-21 | 9212 | 9212 | - | - | - | - | - | - | - | - | - | - | - | -
14-03-21 | 10957 | 10957 | - | - | - | - | - | - | - | - | - | - | - | - | 14-03-21 | 9132 | 9132 | - | - | - | - | - | - | - | - | - | - | - | -
15-03-21 | 11505 | 11505 | - | - | - | - | - | - | - | - | - | - | - | - | 15-03-21 | 9445 | 9445 | - | - | - | - | - | - | - | - | - | - | - | -
16-03-21 | 11595 | 11595 | - | - | - | - | - | - | - | - | - | - | - | - | 16-03-21 | 9886 | 9886 | - | - | - | - | - | - | - | - | - | - | - | -
17-03-21 | 10952 | 10952 | - | - | - | - | - | - | - | - | - | - | - | - | 17-03-21 | 9616 | 9616 | - | - | - | - | - | - | - | - | - | - | - | -
18-03-21 | 11701 | 11701 | - | - | - | - | - | - | - | - | - | - | - | - | 18-03-21 | 10120 | 10120 | - | - | - | - | - | - | - | - | - | - | - | -
19-03-21 | 10846 | 10846 | - | - | - | - | - | - | - | - | - | - | - | - | 19-03-21 | 8737 | 8737 | - | - | - | - | - | - | - | - | - | - | - | -
20-03-21 | 12176 | 12176 | - | - | - | - | - | - | - | - | - | - | - | - | 20-03-21 | 9578 | 9578 | - | - | - | - | - | - | - | - | - | - | - | -
21-03-21 | 12525 | 12525 | - | - | - | - | - | - | - | - | - | - | - | - | 21-03-21 | 10584 | 10584 | - | - | - | - | - | - | - | - | - | - | - | -
22-03-21 | 12565 | 12565 | - | - | - | - | - | - | - | - | - | - | - | - | 22-03-21 | 10862 | 10862 | - | - | - | - | - | - | - | - | - | - | - | -
23-03-21 | 12643 | 12643 | - | - | - | - | - | - | - | - | - | - | - | - | 23-03-21 | 11146 | 11146 | - | - | - | - | - | - | - | - | - | - | - | -
24-03-21 | 12790 | 12790 | - | - | - | - | - | - | - | - | - | - | - | - | 24-03-21 | 11126 | 11126 | - | - | - | - | - | - | - | - | - | - | - | -
25-03-21 | 12717 | 12717 | - | - | - | - | - | - | - | - | - | - | - | - | 25-03-21 | 11023 | 11023 | - | - | - | - | - | - | - | - | - | - | - | -
26-03-21 | 11129 | 11129 | - | - | - | - | - | - | - | - | - | - | - | - | 26-03-21 | 9413 | 9413 | - | - | - | - | - | - | - | - | - | - | - | -
27-03-21 | 12446 | 12446 | - | - | - | - | - | - | - | - | - | - | - | - | 27-03-21 | 10425 | 10425 | - | - | - | - | - | - | - | - | - | - | - | -
28-03-21 | 12634 | 10603 | - | - | - | - | - | - | - | - | - | - | - | - | 28-03-21 | 10542 | 10542 | - | - | - | - | - | - | - | - | - | - | - | -
29-02-21 | 12050 | 12050 | - | - | - | - | - | - | - | - | - | - | - | - | 29-02-21 | 11016 | 11016 | - | - | - | - | - | - | - | - | - | - | - | -
30-02-21 | 11407 | 11407 | - | - | - | - | - | - | - | - | - | - | - | - | 30-02-21 | 8688 | 8688 | - | - | - | - | - | - | - | - | - | - | - | -
31-02-21 | 12403 | 12403 | - | - | - | - | - | - | - | - | - | - | - | - | 31-02-21 | 9878 | 9878 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:March' 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 12790 | 24-03-2021 | 21:00
2 | Maximum Day Peak Genaration | MW | 11146 | 23-03-2021 | 12:00
3 | Maximum Evening Peak Demand | MW | 12790 | 24-03-2021 | 19:00
4 | Minimum Generation | MW | 6990 | 2021-03-04 | 5:00
5 | Average of the daily evening peak Genaration | MW | 11476.6774
6 | Average of the daily day peak Genaration | MW | 9678.4516
7 | Maximum load shed | MW | - | - | -
8 | Minimum load shed | MW | - | - | -
9 | Total nos. of load shed days | Day | -
10 | Average load shed ( Avg. of the 31 days in the month) | MW | -
11 | Total Generation | MKWH | 6493.0942
12 | Total Generation by BPDB | MKWH | 1525.7498 | % of total Gen. | 23.5%
13 | Total Generation by IPP | MKWH | 1871.41 | '' | 28.82%
14 | A) Total Generation by Generation Companies | MKWH | 2029.1999 | '' | 31.25%
| B) Total Generation by REB | MKWH | 123.4508 | " | 1.901%
| C) Total Generation by RENTAL | MKWH | 358.3773 | " | 5.519%
| D) Total Imported from India (BIPTC) | MKWH | 497.3927 | " | 7.66%
| E) Total Imported from Tripura, India (A.C) | MKWH | 87.5136 | " | 1.348%
15 | Fuel wise Generation.
| A) Gas | MKWH | 3953.2485 | % of total Gen. | 60.88%
| B) Oil | MKWH | 1447.7817 | '' | 22.3%
| C) Hydro | MKWH | 45.441 | '' | 0.6998%
| D) Solar | MKWH | 18.2866 | '' | 0.2816%
| E) Coal | MKWH | 443.4301 | '' | 6.829%
| F) BIPTC (Import from India) | MKWH | 497.3927 | '' | 7.66%
| G) A.C (Import from Tripura, India) | MKWH | 87.5136 | '' | 1.348%
16 | Maximun of the daily total Generation . | MKWH | 266.7615 | 24-03-2021
17 | Monthly Load factor | % | 68.2352
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 22124.1575
| A) Gas | M.Taka | 4661.5017
| B) Liquid fuel | M.Taka | 11974.0516
| C) Coal | M.Taka | 2295.5493
| D) BIPTC (Import from India) | M.Taka | 2536.7029
| E) Tripura(Import from India) | M.Taka | 656.352
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 963.6625 | 24/03/2021
| A) Gas | M.Taka | 171.9048 | 28/03/2021
| B) Liquid fuel | M.Taka | 742.3088 | 24/03/2021
| C) Coal | M.Taka | 85.4666 | 02/03/2021
| D) BIPTC (Import from India) | M.Taka | 103.1201 | 08-03-2021
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/KWHR | 3.3826
| B) Excluding Hydro & Solar | Taka/KWHR | 3.4157
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 88.17 | 31/03/2021 | 06:00
b) | Actual | FT (MSL) | 85 | 31/03/2021 | 06:00
22 | Peak Genaration of March 2020 | MW | 10790 | 18/03/20 | 19:30
23 | Peak Demand of March 2020 | MW | 10790 | 18/03/20 | 19:30
24 | Maximum peak Generation recorded upto 31/03/2021 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2021 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/03/2021 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.