## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-06 | Thursday
|  |  | Date (day): | 2021-05-06 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14668.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15467 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-05 | 2021-05-06 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 102 | 98 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  | 412 | Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 280 | 276 | 300 | 300 |  |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 280 | 300 | 300 | 150 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 16 | 91 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 250 | 300 | 300
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 150 | 115 | 130 | 150 | 60 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 15 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 216 | 170 | 200 | 220 |  | 115 | ST under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 93 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 54 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 2 | 205 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 81 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2121 | 2755 | 3421 | 3731 | 369 | 1612
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 90 | 90 | 90 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 19 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 22 | 23 | 23 | 23 | 207 |  | Unit 4 & 5 Under S/D due to Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 204 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 140 | 140 | 140
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 70 | 90 | 90 | 90 |  | 15 | Engine problem
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 34 | 10 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 23 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 42 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 60 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 22 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 829 | 1116 | 1623 | 1608 | 577 | 180
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 100 | 100 |  |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 182 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 310 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 295 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 36 | 150 | 100 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 93 | 95 | 95 | 68 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 102 | 144 | 160 | 160 |  | 40 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 162 | 156 | 178
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 74 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 36 | 36 |  | 18 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1520 | 1813 | 2150 | 2372 | 501 | 82
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 153 | 151 | 160 | 160
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 14 | 19 | 19 | 19
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 65 | 65 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 110 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 45 | 85 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 23 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 21 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 322 | 454 | 641.6 | 590 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 272 | 275 | 275 |  |  | Machine problem
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 32 | 32 | 32
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 75 | 76 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 184 | 223 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 373 | 367 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 371 | 370 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1790 | 1939 | 2103 | 2105 | 0 | 192
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 16
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 830 | 829 | 852 | 852
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 21 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 360 | 350 | 320 | 320 | 90 |  | Gas shortage
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 53 | 92 | 92 |  | 13 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 50 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1277 | 1402 | 1625 | 1912 | 90 | 119
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 34 | 35 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 60 | 65 | 65 |  | 129 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 94 | 100 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 280 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 80 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 611 | 570 | 1007 | 1007 | 0 | 129
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 34 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 24 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 22 | 22 |  | 28 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 131 | 105 | 144 | 144 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 199 | 158 | 200 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 198 | 150 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 419 | 377 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 0 | 32 |  |  | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 18 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 0 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 997 | 1235 | 1752 | 1784 | 171 | 43
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 73 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 266 | 336 | 346 | 358 | 124 | 105
|  | Total |  |  |  |  | 21967 | 21219 | 9733 | 11620 | 14668.6 | 15467 | 1832 | 2483
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9315.0338 | 11121 | 14038.6834 | 14802.7975
| A. |  | 2021-05-05 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11620 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7825 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11620 | MW
| 3 | Day peak Generation : |  |  | 9733 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11121 | MW
| 4 | Evening peak Generation : |  |  | 11620 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 240.5223 | MKWHr | By Solar | 0.65834 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 151.3592 | MKWHr |  | By Oil: | 49.2385 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.6363 | MKWHr |  | By Hydro: | 0.48174 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1832 | MW | Dhaka | 4161 | 4161 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2483 | MW | Chittagong | 1312 | 1312 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4315 | MW | Khulna | 1112 | 1112 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1259.47 | MMCFD |  |  | Rajshahi | 904 | 904 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 165772840.412 | ii) Oil : | Taka | 340562232.71 | Comilla | 1174 | 1174 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 75293937.81 | Total | Taka | 581629010.932 | Mymensingh | 958 | 958 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.0825 | MKWHr. | Sylhet | 486 | 486 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 280 | MW (E to W) at | 21:00 | hrs | Barisal | 367 | 367 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 60 | MW at | 19:00 | hrs | Rangpur | 647 | 647 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.5° C |  |  | Total | 11121 | 11121 |  | 0
| B. |  | 2021-05-06 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15467 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3267 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 252.5278 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8254 | MW at | 6:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.0436 | MKWHr. | ii) HVDC Flow at Peak Time |  | 829 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1046 | MKWHr. | iii) Maximum HVDC Flow : |  | 830 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76.3 |  | (b) Today: | 76.2 |  | (c) Rule Curve: |  | 81.24
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-05
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 292 |  | 0 | 260 | 240 | 0 | 0 | 30 | 221 | 0 | 120 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 17 | 203 | 0 | 140 | 0 |  | 24 | 0 | 34 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 100 | 310 | 300 | 181 | 36 | 87 | 26 | 57 | 0 | 43 | 0 | 0 | 43 | 11 | 11 | 33 | 20 | 120 | 159 | 57 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 162 | 34 | 75 | 0 | 223 | 18 | 0 | 7 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 148 | 0 | 100 | 102 | 0 | 366 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 370 | 17 | 0 | 17 | 71 | 0 | 17 | 0 |  | 830 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 29 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 121 | 0 | 176 | 0 | 97 | 0 | 184 | 0 | 397 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 6646 | 3138 | 9784 | 4556 | 830 | 1928 | 1597 | 693 | 22 | 38 | 120 | 0 | 0 | 76.32
2:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 292 |  | 0 | 260 | 250 | 0 | 0 | 30 | 180 | 0 | 125 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 17 | 203 | 0 | 140 | 0 |  | 22 | 0 | 34 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 100 | 280 | 265 | 181 | 36 | 86 | 26 | 57 | 0 | 51 | 0 | 0 | 43 | 11 | 8 | 33 | 20 | 116 | 159 | 49 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 162 | 34 | 75 | 0 | 223 | 18 | 0 | 7 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 0 | 100 | 102 | 0 | 366 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 370 | 17 | 0 | 17 | 35 | 0 | 17 | 0 |  | 830 | 0 | 355 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 120 | 0 | 176 | 0 | 97 | 0 | 182 | 0 | 318 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 6510 | 3055 | 9565 | 4448 | 830 | 1856 | 1562 | 693 | 22 | 38 | 116 | 0 | 0 | 76.32
3:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 292 |  | 0 | 260 | 240 | 0 | 0 | 30 | 180 | 0 | 120 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 17 | 215 | 0 | 140 | 0 |  | 22 | 0 | 34 | 0 | 0 | 0 | 21 | 16 | 0 | 0 | 100 | 280 | 290 | 193 | 36 | 86 | 26 | 57 | 0 | 51 | 0 | 0 | 43 | 11 | 8 | 33 | 20 | 116 | 159 | 49 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 161 | 33 | 75 | 0 | 223 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 149 | 0 | 100 | 102 | 0 | 375 | 115 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 381 | 17 | 0 | 17 | 35 | 0 | 17 | 0 |  | 830 | 0 | 385 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 28 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 112 | 0 | 166 | 0 | 97 | 0 | 170 | 0 | 352 | 0 | 0 | 35 | 0 | 34 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 6588 | 3089 | 9677 | 4510 | 830 | 1915 | 1552 | 693 | 23 | 38 | 116 | 0 | 0 | 76.31
4:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 312 |  | 0 | 260 | 245 | 0 | 0 | 30 | 180 | 0 | 120 | 7 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 17 | 203 | 0 | 140 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 21 | 32 | 0 | 0 | 100 | 260 | 265 | 181 | 36 | 86 | 26 | 57 | 0 | 51 | 0 | 0 | 43 | 11 | 8 | 33 | 20 | 116 | 159 | 65 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 161 | 33 | 75 | 0 | 223 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 102 | 0 | 367 | 95 | 34 | 105 | 0 | 0 | 54 | 0 | 0 | 26 | 100 | 370 | 17 | 0 | 17 | 35 | 0 | 17 | 0 |  | 830 | 0 | 350 | 0 | 32 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 110 | 0 | 157 | 0 | 97 | 0 | 160 | 0 | 313 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 6442 | 2926 | 9368 | 4360 | 830 | 1895 | 1447 | 693 | 23 | 4 | 116 | 0 | 0 | 76.31
5:00 | 0 | 0 | 0 | 180 | 0 | 54 | 0 | 0 | 313 |  | 0 | 260 | 245 | 0 | 0 | 30 | 160 | 0 | 97 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 24 | 0 | 90 | 0 | 17 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 100 | 260 | 265 | 181 | 36 | 86 | 26 | 30 | 0 | 10 | 0 | 0 | 8 | 11 | 8 | 33 | 20 | 100 | 159 | 65 | 17 | 0 | 43 | 42 | 11 | 0 | 110 | 161 | 33 | 20 | 0 | 190 | 18 | 0 | 7 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 70 | 102 | 0 | 329 | 35 | 17 | 68 | 0 | 0 | 54 | 0 | 0 | 0 | 30 | 340 | 0 | 0 | 17 | 17 | 0 | 17 | 0 |  | 830 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 106 | 0 | 153 | 0 | 62 | 0 | 156 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 410 | 0 | 0 | 0 |  | 5604 | 2766 | 8370 | 4202 | 830 | 1604 | 973 | 633 | 24 | 4 | 100 | 0 | 0 | 76.31
6:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 0 | 273 |  | 0 | 260 | 240 | 0 | 0 | 30 | 140 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 16 | 0 | 0 | 24 | 0 | 90 | 0 | 17 | 213 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 32 | 0 | 0 | 80 | 260 | 265 | 181 | 8 | 86 | 26 | 10 | 0 | 10 | 0 | 0 | 8 | 11 | 5 | 33 | 15 | 96 | 160 | 73 | 17 | 0 | 43 | 42 | 11 | 0 | 110 | 163 | 20 | 10 | 0 | 162 | 18 | 0 | 7 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 1 | 70 | 102 | 0 | 316 | 16 | 17 | 51 | 0 | 0 | 54 | 0 | 0 | 0 | 30 | 320 | 0 | 2 | 17 | 17 | 0 | 17 | 2 |  | 830 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 80 | 0 | 152 | 0 | 33 | 0 | 155 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0 | 0 |  | 5249 | 2576 | 7825 | 3936 | 830 | 1419 | 908 | 603 | 24 | 4 | 96 | 5 | 0 | 76.3
7:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 0 | 272 |  | 0 | 260 | 255 | 0 | 0 | 30 | 140 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 25 | 0 | 0 | 24 | 0 | 90 | 0 | 17 | 217 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 15 | 0 | 0 | 80 | 310 | 255 | 206 | 8 | 87 | 26 | 10 | 0 | 10 | 0 | 0 | 8 | 11 | 5 | 33 | 15 | 94 | 159 | 73 | 17 | 0 | 43 | 42 | 11 | 0 | 110 | 163 | 20 | 10 | 0 | 162 | 17 | 0 | 7 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 1 | 70 | 102 | 0 | 353 | 16 | 17 | 51 | 1 | 0 | 54 | 0 | 0 | 0 | 30 | 365 | 0 | 7 | 17 | 17 | 0 | 17 | 7 |  | 830 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 80 | 0 | 139 | 0 | 32 | 0 | 140 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 380 | 0 | 0 | 0 |  | 5431 | 2561 | 7992 | 4039 | 830 | 1457 | 923 | 604 | 24 | 4 | 94 | 17 | 0 | 76.3
8:00 | 0 | 0 | 0 | 180 | 0 | 51 | 0 | 0 | 322 |  | 0 | 260 | 255 | 0 | 0 | 30 | 170 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 24 | 33 | 25 | 0 | 0 | 24 | 0 | 90 | 0 | 8 | 203 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 21 | 10 | 0 | 0 | 80 | 260 | 255 | 182 | 8 | 87 | 26 | 10 | 0 | 10 | 0 | 0 | 8 | 11 | 5 | 33 | 15 | 94 | 158 | 73 | 17 | 0 | 43 | 42 | 11 | 0 | 110 | 161 | 33 | 70 | 0 | 162 | 17 | 0 | 7 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 2 | 70 | 102 | 0 | 320 | 16 | 30 | 51 | 3 | 0 | 54 | 0 | 0 | 0 | 30 | 320 | 0 | 23 | 17 | 17 | 0 | 17 | 15 |  | 830 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 104 | 0 | 149 | 0 | 32 | 0 | 158 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 380 | 0 | 0 | 0 |  | 5486 | 2707 | 8193 | 4060 | 830 | 1588 | 945 | 604 | 24 | 4 | 94 | 44 | 0 | 76.3
9:00 | 0 | 0 | 0 | 180 | 0 | 52 | 0 | 0 | 310 |  | 0 | 260 | 250 | 0 | 0 | 30 | 222 | 0 | 73 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 205 | 0 | 140 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 5 | 0 | 0 | 80 | 360 | 265 | 216 | 8 | 88 | 26 | 30 | 0 | 20 | 0 | 0 | 8 | 11 | 5 | 33 | 15 | 108 | 156 | 73 | 17 | 1 | 43 | 42 | 11 | 0 | 110 | 161 | 32 | 70 | 0 | 162 | 17 | 0 | 7 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 5 | 70 | 102 | 0 | 376 | 16 | 50 | 51 | 4 | 0 | 54 | 0 | 0 | 0 | 30 | 377 | 0 | 40 | 17 | 17 | 0 | 17 | 11 |  | 830 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 109 | 0 | 155 | 0 | 32 | 0 | 164 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 380 | 0 | 0 | 0 |  | 5897 | 2785 | 8682 | 4403 | 830 | 1656 | 989 | 605 | 22 | 4 | 108 | 65 | 0 | 76.29
10:00 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 0 | 300 |  | 0 | 270 | 260 | 4 | 0 | 30 | 219 | 0 | 120 | 4 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 205 | 0 | 140 | 0 |  | 18 | 0 | 0 | 0 | 0 | 19 | 21 | 5 | 0 | 0 | 80 | 320 | 310 | 191 | 8 | 89 | 26 | 30 | 0 | 40 | 0 | 0 | 8 | 10 | 5 | 33 | 15 | 114 | 155 | 73 | 17 | 1 | 43 | 42 | 11 | 0 | 163 | 161 | 32 | 73 | 0 | 163 | 17 | 0 | 7 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 70 | 102 | 1 | 376 | 23 | 60 | 51 | 5 | 0 | 54 | 0 | 0 | 30 | 30 | 378 | 7 | 32 | 17 | 17 | 0 | 17 | 28 |  | 830 | 0 | 360 | 0 | 49 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 15 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 128 | 0 | 172 | 0 | 88 | 0 | 181 | 0 | 425 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 380 | 0 | 0 | 0 |  | 6154 | 3000 | 9154 | 4466 | 830 | 1860 | 1184 | 604 | 22 | 4 | 114 | 70 | 0 | 76.29
11:00 | 0 | 0 | 0 | 180 | 0 | 99 | 0 | 0 | 290 |  | 0 | 270 | 275 | 16 | 0 | 30 | 221 | 0 | 120 | 15 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 43 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 211 | 0 | 140 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 21 | 6 | 0 | 0 | 80 | 325 | 310 | 197 | 8 | 90 | 26 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 15 | 128 | 154 | 65 | 14 | 1 | 44 | 42 | 11 | 0 | 163 | 163 | 31 | 73 | 0 | 163 | 17 | 0 | 7 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 18 | 70 | 102 | 16 | 396 | 45 | 70 | 51 | 5 | 0 | 54 | 0 | 0 | 55 | 30 | 390 | 17 | 27 | 70 | 17 | 0 | 17 | 34 |  | 829 | 0 | 385 | 0 | 49 | 0 | 0 | 0 | 7 | 0 | 0 | 64 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 135 | 0 | 199 | 0 | 96 | 0 | 202 | 0 | 422 | 0 | 0 | 0 | 0 | 39 | 0 | 5 | 0 | 400 | 0 | 0 | 0 |  | 6433 | 3117 | 9550 | 4588 | 829 | 1874 | 1389 | 623 | 22 | 7 | 128 | 90 | 0 | 76.29
12:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 280 |  | 0 | 270 | 265 | 16 | 0 | 30 | 216 | 0 | 150 | 15 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 204 | 0 | 140 | 0 |  | 21 | 0 | 0 | 0 | 0 | 19 | 21 | 6 | 0 | 0 | 80 | 310 | 310 | 187 | 8 | 90 | 26 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 18 | 132 | 153 | 65 | 14 | 1 | 44 | 42 | 11 | 0 | 163 | 162 | 31 | 75 | 0 | 184 | 17 | 0 | 7 | 310 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 149 | 20 | 100 | 102 | 36 | 373 | 45 | 90 | 70 | 5 | 0 | 42 | 0 | 0 | 74 | 60 | 371 | 17 | 23 | 81 | 22 | 0 | 17 | 33 |  | 830 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 131 | 0 | 199 | 0 | 94 | 0 | 198 | 0 | 419 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 430 | 0 | 0 | 0 |  | 6582 | 3151 | 9733 | 4528 | 830 | 1870 | 1604 | 655 | 22 | 4 | 132 | 88 | 0 | 76.28
13:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 274 |  | 0 | 270 | 245 | 16 | 0 | 55 | 216 | 0 | 75 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 205 | 0 | 130 | 0 |  | 17 | 0 | 0 | 0 | 0 | 19 | 21 | 13 | 0 | 0 | 80 | 310 | 305 | 183 | 8 | 89 | 26 | 48 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 20 | 128 | 152 | 65 | 14 | 1 | 44 | 42 | 50 | 0 | 163 | 163 | 31 | 75 | 0 | 190 | 17 | 0 | 7 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 149 | 19 | 100 | 102 | 98 | 368 | 48 | 105 | 81 | 5 | 0 | 54 | 0 | 0 | 113 | 80 | 376 | 17 | 14 | 108 | 53 | 0 | 17 | 29 |  | 830 | 0 | 370 | 0 | 94 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 21 | 0 | 11 | 74 | 0 | 149 | 0 | 0 | 125 | 0 | 189 | 0 | 95 | 0 | 190 | 0 | 418 | 0 | 0 | 33 | 0 | 35 | 0 | 6 | 0 | 490 | 0 | 0 | 0 |  | 6824 | 3258 | 10082 | 4471 | 830 | 1915 | 1925 | 713 | 22 | 4 | 128 | 74 | 0 | 76.28
14:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 270 |  | 0 | 270 | 260 | 16 | 0 | 55 | 160 | 0 | 120 | 80 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 29 | 19 | 25 | 28 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 15 | 205 | 0 | 130 | 0 |  | 18 | 0 | 0 | 0 | 0 | 17 | 21 | 7 | 0 | 0 | 80 | 315 | 305 | 190 | 8 | 90 | 26 | 49 | 0 | 51 | 0 | 0 | 8 | 0 | 11 | 33 | 20 | 144 | 149 | 65 | 14 | 2 | 44 | 42 | 53 | 0 | 130 | 163 | 31 | 75 | 0 | 203 | 17 | 0 | 7 | 300 | 16 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 149 | 17 | 100 | 102 | 142 | 373 | 66 | 105 | 82 | 4 | 0 | 54 | 0 | 0 | 113 | 100 | 376 | 20 | 24 | 115 | 56 | 0 | 17 | 23 |  | 829 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 127 | 0 | 193 | 0 | 95 | 0 | 194 | 0 | 418 | 0 | 0 | 38 | 0 | 50 | 0 | 5 | 0 | 490 | 0 | 0 | 0 |  | 6999 | 3299 | 10298 | 4498 | 829 | 1876 | 2137 | 712 | 23 | 4 | 144 | 75 | 0 | 76.28
15:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 268 |  | 0 | 270 | 250 | 42 | 0 | 55 | 160 | 0 | 115 | 50 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 30 | 19 | 25 | 28 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 16 | 205 | 0 | 130 | 0 |  | 18 | 0 | 0 | 0 | 0 | 16 | 21 | 5 | 0 | 0 | 80 | 310 | 295 | 183 | 8 | 84 | 26 | 50 | 0 | 51 | 0 | 0 | 8 | 20 | 8 | 33 | 20 | 150 | 150 | 64 | 14 | 1 | 44 | 42 | 53 | 0 | 130 | 273 | 31 | 75 | 0 | 217 | 17 | 0 | 7 | 285 | 16 | 5 | 0 | 76 | 0 | 0 | 0 | 0 | 149 | 13 | 100 | 102 | 100 | 368 | 115 | 105 | 77 | 3 | 0 | 54 | 0 | 0 | 111 | 100 | 370 | 68 | 15 | 148 | 72 | 0 | 35 | 8 |  | 829 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 121 | 0 | 173 | 0 | 94 | 0 | 182 | 0 | 404 | 35 | 0 | 70 | 0 | 70 | 0 | 3 | 0 | 490 | 0 | 0 | 0 |  | 7231 | 3292 | 10523 | 4543 | 829 | 1843 | 2373 | 715 | 23 | 4 | 150 | 43 | 0 | 76.27
16:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 264 |  | 0 | 270 | 240 | 40 | 0 | 55 | 160 | 0 | 120 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 30 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 16 | 205 | 0 | 130 | 0 |  | 21 | 0 | 0 | 0 | 0 | 19 | 21 | 8 | 0 | 0 | 80 | 310 | 295 | 182 | 26 | 94 | 26 | 53 | 0 | 51 | 0 | 0 | 8 | 20 | 8 | 33 | 20 | 146 | 146 | 64 | 14 | 1 | 44 | 42 | 53 | 0 | 130 | 273 | 31 | 75 | 0 | 217 | 17 | 0 | 7 | 290 | 16 | 5 | 0 | 65 | 0 | 0 | 0 | 0 | 149 | 8 | 100 | 102 | 70 | 366 | 115 | 105 | 82 | 2 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 60 | 22 | 108 | 72 | 0 | 35 | 11 |  | 829 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 11 | 69 | 0 | 150 | 0 | 0 | 122 | 0 | 159 | 0 | 96 | 0 | 175 | 0 | 400 | 17 | 0 | 35 | 0 | 70 | 0 | 4 | 0 | 490 | 0 | 0 | 0 |  | 7129 | 3263 | 10392 | 4533 | 829 | 1866 | 2184 | 709 | 23 | 54 | 146 | 48 | 0 | 76.27
17:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 264 |  | 0 | 280 | 240 | 16 | 0 | 55 | 160 | 0 | 120 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 19 | 21 | 15 | 0 | 0 | 80 | 315 | 295 | 182 | 26 | 94 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 20 | 8 | 33 | 20 | 144 | 142 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 272 | 31 | 75 | 0 | 216 | 17 | 0 | 7 | 280 | 16 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 149 | 3 | 100 | 112 | 70 | 368 | 115 | 105 | 90 | 1 | 0 | 54 | 0 | 0 | 113 | 100 | 370 | 20 | 8 | 108 | 60 | 0 | 35 | 6 |  | 830 | 0 | 355 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 6 | 16 | 0 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 115 | 0 | 158 | 0 | 96 | 0 | 173 | 0 | 398 | 17 | 0 | 35 | 0 | 70 | 0 | 2 | 0 | 460 | 0 | 0 | 0 |  | 7070 | 3198 | 10268 | 4528 | 830 | 1877 | 2102 | 684 | 23 | 60 | 144 | 20 | 0 | 76.26
18:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 254 |  | 0 | 280 | 275 | 16 | 0 | 55 | 160 | 0 | 145 | 24 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 29 | 33 | 25 | 0 | 0 | 23 | 0 | 90 | 0 | 16 | 218 | 0 | 130 | 0 |  | 24 | 0 | 1 | 0 | 0 | 19 | 21 | 18 | 0 | 0 | 80 | 310 | 305 | 206 | 26 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 20 | 8 | 33 | 20 | 134 | 136 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 271 | 31 | 75 | 0 | 196 | 17 | 0 | 7 | 280 | 16 | 5 | 0 | 52 | 0 | 0 | 5 | 0 | 149 | 0 | 100 | 131 | 70 | 365 | 115 | 105 | 86 | 0 | 0 | 54 | 0 | 5 | 113 | 100 | 393 | 17 | 1 | 108 | 35 | 0 | 35 | 1 |  | 829 | 0 | 365 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 16 | 0 | 0 | 0 | 50 | 10 | 15 | 0 | 0 | 15 | 16 | 20 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 104 | 0 | 162 | 0 | 92 | 0 | 176 | 0 | 394 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 7153 | 2761 | 9914 | 4596 | 829 | 1858 | 2123 | 222 | 23 | 127 | 134 | 2 | 0 | 76.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 270 |  | 0 | 280 | 250 | 53 | 0 | 55 | 170 | 0 | 120 | 50 | 70 | 16 | 0 | 0 | 0 | 0 | 35 | 30 | 55 | 19 | 25 | 14 | 33 | 25 | 20 | 0 | 29 | 0 | 90 | 0 | 17 | 204 | 0 | 130 | 0 |  | 15 | 0 | 34 | 0 | 5 | 19 | 21 | 24 | 0 | 0 | 80 | 290 | 295 | 182 | 26 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 8 | 21 | 8 | 33 | 20 | 152 | 148 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 273 | 32 | 75 | 0 | 203 | 17 | 0 | 7 | 250 | 16 | 11 | 0 | 122 | 0 | 0 | 16 | 0 | 149 | 0 | 100 | 138 | 112 | 365 | 115 | 105 | 89 | 0 | 0 | 54 | 0 | 17 | 113 | 100 | 370 | 66 | 0 | 130 | 55 | 0 | 35 | 0 |  | 829 | 0 | 320 | 0 | 68 | 0 | 0 | 0 | 5 | 0 | 24 | 65 | 34 | 64 | 0 | 0 | 0 | 50 | 10 | 100 | 42 | 0 | 30 | 52 | 40 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 110 | 0 | 176 | 0 | 96 | 0 | 166 | 0 | 335 | 17 | 0 | 66 | 50 | 113 | 0 | 0 | 95 | 100 | 0 | 0 | 10 |  | 7479 | 3321 | 10800 | 4464 | 829 | 1805 | 2864 | 322 | 29 | 335 | 152 | 0 | 0 | 76.25
19:30 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 270 |  | 0 | 280 | 255 | 89 | 0 | 55 | 170 | 0 | 120 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 14 | 33 | 25 | 51 | 0 | 23 | 0 | 90 | 0 | 17 | 204 | 0 | 100 | 0 |  | 23 | 0 | 68 | 0 | 37 | 19 | 21 | 25 | 0 | 0 | 80 | 310 | 295 | 181 | 26 | 91 | 26 | 56 | 0 | 51 | 0 | 50 | 8 | 21 | 8 | 33 | 20 | 154 | 152 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 271 | 32 | 75 | 0 | 223 | 17 | 0 | 7 | 275 | 16 | 11 | 0 | 185 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 138 | 125 | 366 | 115 | 105 | 85 | 0 | 0 | 54 | 17 | 17 | 113 | 100 | 370 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 829 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 18 | 0 | 24 | 58 | 34 | 75 | 0 | 0 | 0 | 50 | 24 | 100 | 42 | 0 | 30 | 52 | 40 | 21 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 108 | 0 | 158 | 0 | 97 | 0 | 150 | 0 | 366 | 35 | 0 | 85 | 50 | 113 | 0 | 0 | 109 | 240 | 0 | 0 | 0 |  | 8009 | 3599 | 11608 | 4474 | 829 | 1864 | 3407 | 461 | 23 | 396 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 273 |  | 0 | 280 | 250 | 84 | 0 | 55 | 170 | 0 | 115 | 100 | 93 | 16 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 25 | 25 | 0 | 23 | 0 | 90 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 68 | 0 | 40 | 19 | 21 | 29 | 0 | 0 | 80 | 310 | 295 | 182 | 26 | 91 | 26 | 55 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 20 | 156 | 152 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 272 | 32 | 75 | 0 | 223 | 17 | 0 | 7 | 270 | 16 | 11 | 0 | 203 | 0 | 0 | 62 | 0 | 149 | 0 | 100 | 138 | 145 | 367 | 85 | 105 | 90 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 370 | 90 | 0 | 162 | 116 | 0 | 36 | 0 |  | 830 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 22 | 0 | 0 | 62 | 34 | 110 | 0 | 0 | 0 | 50 | 34 | 50 | 24 | 0 | 31 | 43 | 40 | 22 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 107 | 0 | 159 | 0 | 97 | 0 | 150 | 0 | 367 | 52 | 0 | 113 | 50 | 113 | 0 | 0 | 70 | 260 | 0 | 0 | 0 |  | 7944 | 3591 | 11535 | 4503 | 830 | 1867 | 3364 | 481 | 23 | 311 | 156 | 0 | 0 | 76.25
21:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 276 |  | 0 | 280 | 250 | 91 | 0 | 55 | 170 | 0 | 115 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 33 | 25 | 25 | 0 | 23 | 0 | 90 | 0 | 17 | 204 | 0 | 140 | 0 |  | 24 | 0 | 68 | 0 | 23 | 19 | 21 | 34 | 0 | 0 | 80 | 310 | 295 | 182 | 26 | 93 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 20 | 162 | 151 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 272 | 32 | 75 | 0 | 223 | 17 | 0 | 7 | 280 | 16 | 11 | 0 | 205 | 0 | 0 | 110 | 0 | 149 | 0 | 100 | 144 | 150 | 367 | 85 | 105 | 90 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 370 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 21 | 0 | 0 | 60 | 34 | 96 | 0 | 0 | 0 | 50 | 34 | 0 | 24 | 0 | 30 | 52 | 39 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 105 | 0 | 158 | 0 | 100 | 0 | 150 | 0 | 377 | 53 | 0 | 113 | 50 | 113 | 0 | 0 | 70 | 280 | 0 | 0 | 0 |  | 8077 | 3543 | 11620 | 4520 | 829 | 1899 | 3410 | 503 | 23 | 274 | 162 | 0 | 0 | 76.25
22:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 0 | 278 |  | 0 | 280 | 255 | 88 | 0 | 55 | 170 | 0 | 118 | 100 | 64 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 29 | 33 | 25 | 25 | 0 | 23 | 0 | 90 | 0 | 17 | 204 | 0 | 140 | 0 |  | 24 | 0 | 68 | 0 | 0 | 19 | 21 | 33 | 0 | 0 | 80 | 310 | 295 | 181 | 26 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 30 | 21 | 10 | 33 | 20 | 158 | 150 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 270 | 32 | 75 | 0 | 223 | 17 | 0 | 7 | 300 | 16 | 11 | 0 | 110 | 0 | 0 | 110 | 0 | 149 | 0 | 100 | 155 | 150 | 367 | 85 | 105 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 370 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 830 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 34 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 39 | 22 | 0 | 0 | 72 | 0 | 150 | 0 | 0 | 107 | 0 | 159 | 0 | 97 | 0 | 150 | 0 | 391 | 17 | 0 | 70 | 50 | 113 | 0 | 0 | 35 | 280 | 0 | 0 | 0 |  | 7940 | 3285 | 11225 | 4519 | 830 | 1929 | 3121 | 502 | 23 | 143 | 158 | 0 | 0 | 76.24
23:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 278 |  | 0 | 280 | 240 | 65 | 0 | 55 | 170 | 0 | 118 | 100 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 21 | 0 | 90 | 0 | 17 | 209 | 0 | 140 | 0 |  | 24 | 0 | 68 | 0 | 0 | 0 | 21 | 39 | 0 | 0 | 80 | 335 | 320 | 197 | 26 | 95 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 21 | 10 | 33 | 20 | 154 | 152 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 270 | 32 | 75 | 0 | 225 | 17 | 0 | 7 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 60 | 0 | 149 | 0 | 100 | 155 | 50 | 387 | 85 | 105 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 374 | 90 | 0 | 108 | 116 | 0 | 36 | 0 |  | 830 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 67 | 33 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 0 | 73 | 0 | 150 | 0 | 0 | 106 | 0 | 160 | 0 | 97 | 0 | 161 | 0 | 418 | 17 | 0 | 35 | 50 | 113 | 0 | 0 | 35 | 280 | 0 | 0 | 0 |  | 7610 | 3248 | 10858 | 4632 | 830 | 1943 | 2671 | 503 | 21 | 104 | 154 | 0 | 0 | 76.23
24:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 262 |  | 0 | 280 | 245 | 55 | 0 | 55 | 170 | 0 | 76 | 100 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 21 | 0 | 90 | 0 | 17 | 163 | 0 | 140 | 0 |  | 24 | 0 | 68 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 80 | 285 | 295 | 182 | 26 | 94 | 26 | 57 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 148 | 156 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 272 | 32 | 75 | 0 | 209 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 149 | 0 | 100 | 100 | 50 | 365 | 85 | 105 | 91 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 370 | 90 | 0 | 106 | 116 | 0 | 36 | 0 |  | 830 | 0 | 340 | 0 | 83 | 0 | 0 | 0 | 5 | 0 | 0 | 67 | 33 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 0 | 73 | 0 | 150 | 0 | 0 | 111 | 0 | 154 | 0 | 97 | 0 | 188 | 0 | 388 | 17 | 0 | 35 | 50 | 113 | 0 | 0 | 35 | 280 | 0 | 0 | 0 |  | 7295 | 3219 | 10514 | 4435 | 830 | 1929 | 2543 | 503 | 21 | 105 | 148 | 0 | 0 | 76.23
KWH | 0 | 0 | 0 | 4284000 | 0 | 2008318 | 0 | 0 | 6780000 |  | 0 | 6333500 | 5869265 | 643200 | 0 | 1056360 | 4426456 | 0 | 2932000 | 1000320 | 700128 | 165120 | 0 | 0 | 0 | 0 | 619920 | 373611 | 919122 | 311760 | 600000 | 645300 | 814000 | 598300 | 108960 | 0 | 481740 | 0 | 2100000 | 0 | 360541 | 4824825 | 0 | 3244154 | 0 |  | 419520 | 0 | 504521 | 0 | 69120 | 270720 | 507648 | 444480 | 0 | 0 | 2033654 | 7466800 | 7014000 | 4537000 | 518545 | 2123610 | 577872 | 1090560 | 0 | 1064403 | 0 | 67216 | 472890 | 305676 | 217980 | 817700 | 435360 | 3104640 | 3592800 | 1555200 | 376092 | 8350 | 1028000 | 1013880 | 924600 | 0 | 3441845 | 4766000 | 741696 | 1607040 | 0 | 4776810 | 413000 | 0 | 162900 | 7282000 | 370320 | 118000 | 0 | 1124072 | 0 | 0 | 520800 | 0 | 3602160 | 120015 | 2234880 | 2757600 | 1436872 | 8751000 | 1872000 | 1792800 | 1959599 | 38279 | 0 | 1287521 | 91163 | 28500 | 1805160 | 1842240 | 8806000 | 892800 | 243940 | 1942560 | 1326055 | 0 | 624960 | 206335 |  | 20043636 | 0 | 8708256 | 0 | 1311360 | 0 | 0 | 0 | 119520 | 0 | 38625 | 1544000 | 615548 | 679296 | 0 | 0 | 0 | 297808 | 90886 | 196672 | 105250 | 0 | 94237 | 608640 | 170160 | 402720 | 0 | 231786 | 1746327 | 0 | 3676200 | 0 | 0 | 2837900 | 0 | 4226909 | 0 | 2007825 | 0 | 4366882 | 0 | 9187454 | 295680 | 0 | 879552 | 309312 | 1301760 | 0 | 41421 | 392256 | 10213800 | 0 | 0 | 30000 |  | 163750659 | 76771678 | 240522337 | 107487426 | 20043636 | 43871738 | 47532350 | 15636327 | 481740 | 1706140 | 3104640 | 658340 | 0
Fuel Cost | 0 | 0 | 0 | 6297480 | 0 | 2650979.76 | 0 | 0 | 6983400 |  | 0 | 6903515 | 6514884.15 | 4881888 | 0 | 8936805.6 | 4603514.24 | 0 | 5072360 | 7532409.6 | 6385167.36 | 1624780.8 | 0 | 0 | 0 | 0 | 4525416 | 2888013.03 | 9062542.92 | 233820 | 450000 | 0 | 0 | 0 | 1053643.2 | 0 | 130069.8 | 0 | 3801000 | 0 | 3349425.89 | 5259059.25 | 0 | 5515061.8 | 0 |  | 0 | 0 | 4893853.7 | 0 | 601344 | 2144102.4 | 639636.48 | 1320105.6 | 0 | 0 | 2989471.38 | 5525432 | 7014000 | 4174040 | 668923.05 | 2442151.5 | 652995.36 | 1526784 | 0 | 1820129.13 | 0 | 678881.6 | 4516099.5 | 388208.52 | 163485 | 1430975 | 326520 | 23284800 | 3808368 | 14121216 | 477636.84 | 133099 | 1685920 | 1622208 | 1645788 | 0 | 3923703.3 | 4956640 | 1461141.12 | 3069446.4 | 0 | 8263881.3 | 904470 | 0 | 332316 | 7354820 | 277740 | 89680 | 0 | 8497984.32 | 0 | 0 | 2708160 | 0 | 35445254.4 | 1402975.35 | 18214272 | 29919960 | 10129947.6 | 8138430 | 17072640 | 16941960 | 17068107.29 | 0 | 0 | 11214307.91 | 801322.77 | 284430 | 15470221.2 | 12269318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115451343.36 | 0 | 9143668.8 | 0 | 10307289.6 | 0 | 0 | 0 | 1253764.8 | 0 | 402472.5 | 1744720 | 954099.4 | 6629928.96 | 0 | 0 | 0 | 2930430.72 | 923401.76 | 1740547.2 | 810425 | 0 | 913156.53 | 5897721.6 | 1650552 | 773222.4 | 0 | 175462.002 | 10530351.81 | 0 | 19925004 | 0 | 0 | 3320343 | 0 | 5579519.88 | 0 | 3011737.5 | 0 | 5109251.94 | 0 | 9095579.46 | 3086899.2 | 0 | 8346948.48 | 2919905.28 | 10101657.6 | 0 | 457702.05 | 2898771.84 | 44838582 | 0 | 0 | 0 |  | 431564539.82 | 290924460.672 | 722489000.492 | 113738291.412 | 115451343.36 | 52034549 | 323952863.6 | 75293937.81 | 130069.8 | 16609369.11 | 23284800 | 1993776.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 0 | 280 |  | 0 | 270 | 265 | 16 | 0 | 30 | 216 | 0 | 150 | 15 | 24 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 0 | 25 | 28 | 33 | 25 | 0 | 0 | 22 | 0 | 90 | 0 | 8 | 204 | 0 | 140 | 0 |  | 21 | 0 | 0 | 0 | 0 | 19 | 21 | 6 | 0 | 0 | 80 | 310 | 310 | 187 | 8 | 90 | 26 | 30 | 0 | 51 | 0 | 0 | 8 | 0 | 8 | 33 | 18 | 132 | 153 | 65 | 14 | 1 | 44 | 42 | 11 | 0 | 163 | 162 | 31 | 75 | 0 | 184 | 17 | 0 | 7 | 310 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 149 | 20 | 100 | 102 | 36 | 373 | 45 | 90 | 70 | 5 | 0 | 42 | 0 | 0 | 74 | 60 | 371 | 17 | 23 | 81 | 22 | 0 | 17 | 33 |  | 830 | 0 | 360 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 21 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 131 | 0 | 199 | 0 | 94 | 0 | 198 | 0 | 419 | 0 | 0 | 0 | 0 | 35 | 0 | 6 | 0 | 430 | 0 | 0 | 0 |  | 9733 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 0 | 276 | 0 | 0 | 280 | 250 | 91 | 0 | 55 | 170 | 0 | 115 | 100 | 93 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 33 | 25 | 25 | 0 | 23 | 0 | 90 | 0 | 17 | 204 | 0 | 140 | 0 | 0 | 24 | 0 | 68 | 0 | 23 | 19 | 21 | 34 | 0 | 0 | 80 | 310 | 295 | 182 | 26 | 93 | 26 | 56 | 0 | 51 | 0 | 0 | 8 | 21 | 8 | 33 | 20 | 162 | 151 | 65 | 19 | 0 | 44 | 42 | 53 | 0 | 130 | 272 | 32 | 75 | 0 | 223 | 17 | 0 | 7 | 280 | 16 | 11 | 0 | 205 | 0 | 0 | 110 | 0 | 149 | 0 | 100 | 144 | 150 | 367 | 85 | 105 | 90 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 370 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 21 | 0 | 0 | 60 | 34 | 96 | 0 | 0 | 0 | 50 | 34 | 0 | 24 | 0 | 30 | 52 | 39 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 105 | 0 | 158 | 0 | 100 | 0 | 150 | 0 | 377 | 53 | 0 | 113 | 50 | 113 | 0 | 0 | 70 | 280 | 0 | 0 | 0 |  | 11620 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 300 | 0 | 0 | 300 | 300 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 23 | 0 | 90 | 0 | 17 | 225 | 0 | 140 | 0 | 0 | 22 |  | 68 | 0 | 90 | 43 | 22 | 20 | 0 | 0 | 100 | 330 | 330 | 220 | 26 | 95 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 178 | 160 | 74 | 19 | 0 | 43 | 42 | 51 | 0 | 163 | 275 | 32 | 78 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 160 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 116 | 0 | 36 |  |  | 852 | 16 | 320 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 65 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 22 | 52 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 10 | 144 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 92 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 80
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 300 | 0 | 0 | 300 | 300 | 100 | 0 | 55 | 200 | 0 | 130 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 23 | 0 | 90 | 0 | 17 | 225 | 0 | 140 | 0 | 0 | 22 |  | 68 | 0 | 90 | 43 | 22 | 10 | 0 | 0 | 100 | 330 | 330 | 220 | 26 | 95 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 156 | 160 | 74 | 19 | 1.6 | 43 | 42 | 51 | 0 | 163 | 275 | 32 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 250 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 160 | 100 | 400 | 115 | 105 | 90 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 116 | 0 | 36 | 30 |  | 852 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 65 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 22 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 144 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 92 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 0 | 273 | 0 | 0 | 280 | 250 | 0 | 0 | 0 | 170 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 28 | 33 |  | 0 | 0 | 23 | 0 | 90 | 0 | 17 | 214 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 6 | 0 | 0 | 80 | 270 | 270 | 182 | 26 | 95 | 26 | 20 | 0 | 20 | 0 | 0 | 8 | 19 | 10 | 33 | 20 | 104 | 158 | 65 | 17 | 1 | 43 | 42 | 11 | 0 | 130 | 273 | 32 | 10 | 0 | 176 | 18 | 0 | 0 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 11 | 100 | 50 | 0 | 322 | 13 | 17 | 89 | 3 | 0 | 54 | 2 | 0 | 0 | 100 | 330 | 0 | 15 | 0 | 10 | 0 | 36 | 4 | 0 | 837 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 74 | 0 | 150 | 0 | 0 | 80 | 0 | 157 | 0 | 97 | 0 | 165 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7825 | 6:00
| Highest Generation |  | 11620 | 21:00
| Day Peak Generation |  | 9733 | 12:00
| Evening Peak Generation |  | 11620 | 21:00
| HVDC Max Flow |  | 830 | 1:00
| HVDC EvPeak Flow |  | 829 | 21:00
| Load factor L.F |  | 86.25%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-06
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-05 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9733 | MW Hour : | 12:00 | Min. Gen. at | 6:00 | 8254 | MW
Evening Peak Generation : |  | 11620 | MW Hour : | 21:00 | Available Max Generation : |  | 15467 | MW
E.P. Demand (at gen end) : |  | 11620 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12200 | MW
Maximum Generation : |  | 11620 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3267 | MW
Total Gen. (MKWH) : |  | 240.5223 | System Load Factor : | 86.25% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 60 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-06
Actual : | 76.2 | Ft.(MSL) , | Rule curve : | 81.24 | Ft.( MSL )
Gas Consumed : | Total = | 1259.47 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165772840.412
: |  | Coal : | 75293937.81 | Oil : | 340562232.71 | Total : | 581629010.932
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4341.8909 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1479.3393 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1325.9479 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1198.2865 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1082.7745 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 873.7679 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 484.8926 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 224.8745 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 673.9108 |  |  | 0 | 0%
Total | 0 |  | 11685.6851 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bogura-Sherpur 132 kV Ckt-1 was under shut down from 08:20 to 18:09 for D/W.
b) Bogura-Sherpur 132 kV Ckt-2 was under shut down from 08:30 to 18:14 for D/W.
c) Shahjibazar-Srimongal 132 kV Ckt-2 was under shut down from 08:17 to 12:04 for D/W.
d) Jaldhaka 132/33 kV T-2 transformer was under shut down from 08:17 to 12:04 for C/M. |  |  |  |  | About 10 MW power interruption occurred under Jaldhaka S/S area
from 11:43 17:50.
e) Sherpur 132/33 kV T-1 transformer was under shut down from 09:34 to 11:13 for C/M.
f) Fenchuganj 132 kV Bus-2 was under shut down from 08:24 to 23:13 for D/W.
g) Haripur 230/132 kV T1 transformer tripped at 14:02 showing L/O relay and was switched on at 14:28.
h) Rajshahi(New)-Rajshahi(Old) 132 kV Ckt-2 was switched on at 16:58.
i) Shahjibazar 330 MW GT-1 was synchronized at 14:13.
j) Payra unit-2 tripped at 17:49 due to Gopalganj 400/132 kV both transformer trip and was synchronized
at 18:24.
k) Gopalganj 400/132 kV both transformer tripped at 17:49 showing PRD at T1 transformer and was
switched on at 01:22(05-06-2021),18:09 respectively.
l) Chowmuhani 132/33 kV both transformer tripped at 14:17 due to 33 kV CB burst of PBS feeder and was |  |  |  |  | About 120 MW power interruption occurred under Chowmuhani S/S area
switched on at 14:26. |  |  |  |  | from 14:17 to 14:26.
m) Siddhirganj 210 MW Gt2 was shut down at 01:07(06/05/2021) due to gas shortage and was
synchronized at 08:28(06-05-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-05 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 2008318
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 276 | 6780000 | Gas Shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6333500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 91 | 643200 | Engine problem
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 250 | 5869265 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1056360
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 311760
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 115 | 2932000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1000320
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 170 | 4426456 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 93 | 700128 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 619920 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 165120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 373611
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 919122
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1245300 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 814000 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 598300 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 108960 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 205 | 1124072 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3602160
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1792800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 892800 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1942560
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 206335
| Dhaka area Total |  |  |  | 5829 | 2755 | 50750367
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2100000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 360541 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 120015
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 270720 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 23 | 481740 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4824825 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 3244154
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 90 | 1959599
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 504521 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2234880
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 507648
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 34 | 444480
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 23 | 69120 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 38279
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1287521
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 91163 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1842240
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1326055
| Chattogram area Total |  |  |  | 2382 | 1116 | 21707501
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2033654 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4537000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7466800 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7014000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 577872 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1090560
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 518545 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1064403
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1436872
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 67216 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 93 | 2123610 | Gas shortage
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 144 | 2757600 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 305676
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 217980
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 162 | 3104640
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817700
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 472890 | Low demand
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 435360 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 28500 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1805160
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 624960 | Engine problem
| Cumilla Area Total |  |  |  | 3034 | 1813 | 38500998
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 3592800 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 376092
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 65 | 1555200 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8350
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 110 | 520800 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 85 | 1872000 | Low demand
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 243940
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 419520
| Mymensingh Area Total |  |  |  | 709 | 454 | 8588702
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1028000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1013880 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3441845
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 272 | 4766000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 924600
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 118000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 32 | 741696
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1607040 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 223 | 4776810
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 413000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 370320 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7282000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8751000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 162900 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 370 | 8806000 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1939 | 44203091
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 829 | 20043636
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1311360 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 21 | 119520 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 8708256 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 38625 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 53 | 295680 | Engine problem
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 50 | 309312 | Low demand
| Khulna Area Total |  |  |  | 2284 | 1402 | 30826389
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 679296 | Engine problem
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 615548
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 60 | 1544000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 100 | 2007825
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 280 | 10213800 | Transformer O/L
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 30000 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 570 | 15090469
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 297808
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 34 | 90886 | Low demand
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 24 | 105250 | Low demand
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 94237 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 105 | 2837900 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 158 | 4226909 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 150 | 4366882 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 377 | 9187454 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 170160
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 402720
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231786
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 608640
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 0 | 196672 | Reserve.
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 879552
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 392256 | Low demand
| Rajshahi Area Total |  |  |  | 2173 | 1235 | 24089112
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1746327
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676200 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1301760
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41421
| Rangpur Area Total |  |  |  | 605 | 336 | 6765708
| Total |  |  |  | 21219 | 11620 | 240522337
| Eastern Grid Total |  |  |  | 14331 | 8077 | 163750659
| Western Grid Total |  |  |  | 6888 | 3543 | 76771678
| National Grid Total |  |  |  | 21219 | 11620 | 240522337
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-05
(a) ENTIRE EASTERN GRID : |  | 8091 | MW | (b) ENTIRE WESTERN GRID : |  | 3030 | MW
i) Dhaka area |  | 4161 | MW | i) Khulna area |  | 1112 | MW
ii) Chittagong area |  | 1312 | MW | ii) Rajshahi area |  | 904 | MW
iii) Comilla area |  | 1174 | MW | iii) Barisal area |  | 367 | MW
iv) Mymensingh area |  | 958 | MW | iv) Rangpur area |  | 647 | MW
v) Sylhet area |  | 486 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11121 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 10:00 | Netrokona | 106 | 22:00 | Benapol | 42 | 19:30
Munsiganj | 120 | 21:00 | Jamalpur | 124 | 21:00 | Jhenida | 100 | 19:30
Sonargaon | 64 | 0:00 | Sherpur | 94 | 22:00 | Bottail | 118 | 15:00
Shyampur | 224 | 13:00 | Srimongal | 44 | 21:00 | G.K Project | 52 | 19:30
Bhulta | 189 | 1:00 | Shahjibazar | 116 | 22:00 | Faridpur | 178 | 21:00
Madanganj | 54 | 12:00 | Fenchuganj | 38 | 23:00 | Madaripur | 76 | 15:00
Shitalakhya | 110 | 12:00 | Kulawara | 44 | 22:00 | Sariatpur | 44 | 14:00
Rahim steel | 26 | 12:00 | Sylhet | 111 | 23:00 | Gopalganj | 75 | 20:00
Matuail | 60 | 12:00 | Chatak | 30 | 21:00 | Bagerhat | 99 | 21:00
Ghorasal | 76 | 21:00 | Sunamganj | 43 | 21:00 | Mongla | 38 | 9:00
Narsingdi | 170 | 21:00 | Biani Bazar | 68 | 22:00 | Satkhira | 85 | 20:00
Haripur (SBU) | 104 | 21:00 | Comilla (S) | 162 | 21:00 | Gallamari | 34 | 20:00
Sreenagar | 35 | 22:00 | Comilla(N) | 143 | 21:00 | Magura | 52 | 21:00
Ullon | 66 | 19:00 | Chandpur | 61 | 23:00 | Norail | 28 | 22:00
Hasnabad | 78 | 20:00 | Feni | 128 | 22:00 | Chuadanga | 78 | 19:00
Magbazar | 87 | 13:00 | Chowmuhani | 174 | 22:00 | Borguna | 18 | 21:00
Maniknagar | 64 | 13:00 | Ashuganj | 38 | 1:00 | Barisal(N) | 34 | 22:00
Bangabhaban | 20 | 10:00 | Daudkandi | 150 | 20:00 | Barisal (S) | 110 | 19:30
Narinda | 70 | 12:00 | B.Baria | 159 | 21:00 | Patuakhali | 114 | 22:00
Dhanmondi | 184 | 13:00 | Ramganj | 94 | 21:00 | Bhandaria | 54 | 21:00
Lalbag | 85 | 13:00 | Chaddagram | 41 | 21:00 | Borhan Uddin | 41 | 21:00
Madartek | 69 | 22:00 | PHP | 11 | 19:00 | Ishurdi | 65 | 19:30
Dhaka University | 40 | 13:00 | Kochua | 68 | 21:00 | Ruppur Paromanobik | 4 | 12:00
Aftabnagar | 9 | 13:00 | Madunaghat | 63 | 12:00 | Natore | 122 | 20:00
Fatullah | 59 | 3:00 | Hathazari | 87 | 19:30 | Bogra | 142 | 21:00
Nawabganj | 48 | 21:00 | Khulshi | 207 | 21:00 | Noagaon | 108 | 21:00
Keraniganj | 70 | 19:30 | Halishahar | 132 | 13:00 | Rajshahi | 144 | 19:30
Mirpur | 107 | 20:00 | Baraulia | 164 | 3:00 | Rajshahi New | 15 | 3:00
Kalyanpur | 105 | 20:00 | Sikalbaha | 30 | 1:00 | C.Nawabganj | 62 | 3:00
Gulshan | 116 | 13:00 | Dohazari | 82 | 22:00 | Amnura | 39 | 19:00
Uttara | 82 | 19:30 | Cox'sbazar | 105 | 21:00 | Pabna | 100 | 19:30
Uttara New | 35 | 14:00 | Chandraghona | 32 | 19:00 | Shahjadpur | 99 | 20:00
Kamrangirchar | 83 | 13:00 | Kaptai | 4.1 | 19:30 | Serajganj | 98 | 20:00
Savar | 151 | 21:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 48 | 23:00
Bhasantec | 140 | 21:00 | Bakulia | 101 | 15:00 | Joypurhat | 52 | 21:00
Agargaon | 63 | 12:00 | Julda | 20 | 1:00 | Sherpur(Bogura) | 52 | 21:00
Satmosjid | 87 | 19:00 | TK chemical | 27 | 21:00 | Mohastangor | 48 | 20:00
Tongi | 116 | 11:00 | Modern Steel | 0 | #N/A | Bangura | 36 | 21:00
Kabirpur | 247 | 14:00 | Shahmirpur | 27.2 | 0:00 | Rangpur | 108 | 18:30
Basundhara | 149 | 19:30 | Khagrachhari | 28 | 2:00 | Lalmonirhat | 30 | 19:30
Manikganj | 68 | 19:30 | Matarbari | 38 | 20:00 | Saidpur | 82 | 19:30
Joydevpur | 158 | 21:00 | Baroiar Hat | 42 | 19:00 | Purbasadipur | 92 | 19:30
New Tongi | 100 | 14:00 | Rangamati | 12 | 19:00 | Thakurgaon | 70 | 19:30
Kodda | 248 | 15:00 | Abul Khair 230 | 143 | 11:00 | Palashbari | 88 | 19:30
Dhamrai | 98 | 18:00 | BSRM | 158 | 21:00 | Barapukuria | 47 | 21:00
Rajendrapur | 92 | 22:00 | GPH Ispat | 94 | 2:00 | Panchagar | 43 | 18:30
Valuka | 108 | 14:00 | Goalpara | 32 | 21:00 | Joldhaka | 45 | 20:00
Tangail | 212 | 19:30 | Central s/s | 84 | 21:00 | Kurigram | 43 | 19:30
Mymensing | 198 | 20:00 | Noapara | 58 | 20:00 | Mithapukur | 30 | 19:30
Kishoreganj | 138 | 21:00 | Jessore | 99 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-05 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 18:30 | 395 | 11:00 | Kaliakoir | 386 | 0.83333 | 370 | 0.45833
| Bheramara | 400 | 18:30 | 397 | 11:00 | Bhulta | 378 | 0.79167 | 358 | 0.45833
| Ashuganj(N) | 386 | 18:30 | 367 | 10:00 | Gopalganj | 409 | 0.625 | 0 | 0.75
| Payra | 412 | 17:00 | 0 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 19:00 | 225 | 7:00 | Hathazari | 218 | 18:30 | 206 | 11:00
| Ishurdi | 235 | 21:00 | 224 | 11:00 | Megnaghat | 225 | 14:00 | 214 | 11:00
| Ashuganj | 238 | 19:00 | 225 | 11:00 | Fenchuganj | 237 | 19:00 | 234 | 17:00
| Serajganj | 232 | 20:00 | 225 | 9:00 | Siddhirganj | 226 | 19:00 | 214 | 11:00
| Baghabari | 233 | 21:00 | 226 | 9:00 | Maniknagar | 224 | 19:00 | 212 | 11:00
| Barapukuria | 234 | 5:00 | 230 | 18:00 | Agargaon | 222 | 20:00 | 209 | 10:00
| Bogra | 228 | 18:30 | 221 | 3:00 | Barisal | 249 | 20:00 | 231 | 16:00
| Rajshahi | 237 | 18:30 | 222 | 12:00 | Bhola 225 MW | 251 | 18:30 | 230 | 18:00
| Khulna South | 230 | 18:30 | 211 | 9:00 | AKSML | 219 | 20:00 | 207 | 11:00
| Rampura | 224 | 18:30 | 214 | 11:00 | BSRM | 220 | 2:00 | 208 | 10:00
| Haripur | 223 | 19:30 | 212 | 12:00 | Bibiyana | 239 | 19:30 | 234 | 11:00
| Hasnabad | 221 | 18:30 | 210 | 9:00 | Bhulta | 228 | 18:30 | 214 | 11:00
| Shyampur | 224 | 17:00 | 220 | 10:00 | Ashuganj (S) | 234 | 18:30 | 223 | 10:00
| Aminbazar | 223 | 1:00 | 210 | 2:00 | Kaliakoir | 224 | 18:30 | 211 | 11:00
| Tongi | 224 | 19:30 | 207 | 11:00 | GPH | 220 | 18:30 | 208 | 10:00
| Comilla (N) | 224 | 18:30 | 214 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:00 | 125 | 10:00 | Madanhat | 130 | 0.041667 | 126 | 0.45833
| Munsiganj | 135 | 19:00 | 124 | 10:00 | Hathazari | 130 | 0.16667 | 125 | 0.45833
| Sonargaon | 135 | 19:00 | 124 | 11:00 | Khulshi | 128 | 0.041667 | 121 | 0.45833
| Shyampur | 133 | 18:30 | 124 | 10:00 | Halishahar | 130 | 0.083333 | 122 | 0.45833
| Bhulta | 126 | 18:30 | 116 | 11:00 | Baraulia | 129 | 0.083333 | 121 | 0.45833
| Madanganj | 133 | 19:00 | 121 | 12:00 | Sikalbaha | 130 | 0.041667 | 124 | 0.45833
| Shitalakhya | 136 | 18:30 | 122 | 10:00 | Dohazari | 126 | 0.083333 | 122 | 0.45833
| Rahim steal | 134 | 19:30 | 125 | 11:00 | Cox'sbazar | 118 | 0.25 | 112 | 0.77083
| Matuail | 134 | 19:00 | 125 | 10:00 | Chandraghona | 129 | 0.16667 | 123 | 0.41667
| Ghorasal | 137 | 1:00 | 133 | 11:00 | Kaptai | 130 | 0.75 | 125 | 0.54167
| Narsinghdi | 132 | 4:00 | 127 | 18:00 | A. Khaer Stl. | 127 | 0.20833 | 124 | 0.45833
| Haripur (SBU) | 134 | 19:00 | 125 | 10:00 | Bakulia | 129 | 0.041667 | 122 | 0.45833
| Sreenagar | 127 | 19:00 | 119 | 11:00 | Julda | 130 | 0.041667 | 124 | 0.41667
| Ullon | 133 | 19:00 | 125 | 10:00 | TK Chemical | 129 | 0.77083 | 124 | 0.45833
| Hasnabad | 135 | 18:30 | 124 | 11:00 | Modern Steel
| Magbazar | 132 | 5:00 | 124 | 11:00 | Shahmirpur | 131 | 0.125 | 123 | 0.5
| Maniknagar | 134 | 19:30 | 126 | 12:00 | Khagrachhari | 128 | 0.083333 | 122 | 0.45833
| Bangabhaban | 134 | 19:30 | 126 | 12:00 | Matarbari | 120 | 0.041667 | 115 | 0.77083
| Narinda | 134 | 19:30 | 126 | 12:00 | Baroiar Hat | 129 | 0.8125 | 123 | 0.375
| Dhanmondi | 133 | 19:00 | 125 | 10:00 | Rangamati | 128 | 0.041667 | 122 | 0.45833
| Lalbag | 133 | 18:30 | 121 | 11:00 | Goalpara S/S | 139 | 21:00 | 128 | 9:00
| Madartek | 132 | 2:00 | 124 | 11:00 | Khulna Central S/S | 138 | 21:00 | 126 | 9:00
| Dhaka University | 133 | 19:30 | 124 | 10:00 | Noapara | 135 | 18:30 | 123 | 0.54167
| Aftabnagar | 132 | 1:00 | 124 | 11:00 | Jessore | 131 | 18:30 | 119 | 0.54167
| Fatullah | 135 | 19:00 | 124 | 10:00 | Benapol | 134 | 5:00 | 119 | 0.54167
| Nawabganj | 126 | 18:30 | 119 | 12:00 | Jhenida | 131 | 6:00 | 117 | 0.54167
| Keraniganj | 127 | 6:00 | 120 | 10:00 | Bottail | 133 | 0.875 | 124 | 0.54167
| Mirpur | 134 | 18:30 | 124 | 11:00 | G.K Project | 140 | 21:00 | 133 | 0.5
| Kalyanpur | 135 | 19:00 | 126 | 11:00 | Faridpur | 135 | 0.20833 | 128 | 0.5
| Gulshan | 132 | 19:00 | 123 | 11:00 | Madaripur | 141 | 0.83333 | 131 | 0.54167
| Uttara | 134 | 19:00 | 124 | 11:00 | Shariyatpur S/S | 140 | 0.83333 | 122 | 0.75
| Uttara New | 133 | 19:00 | 124 | 11:00 | Gopalganj | 144 | 0.79167 | 123 | 0.75
| Kamrangirchar | 133 | 19:00 | 122 | 11:00 | Bagerhat | 135 | 16:00 | 123 | 0.45833
| Savar | 132 | 19:30 | 123 | 11:00 | Mongla | 133 | 0.70833 | 119 | 0.41667
| Bhasantec | 132 | 19:30 | 123 | 11:00 | Satkhira | 137 | 18:30 | 126 | 0.54167
| Agargaon | 133 | 19:00 | 125 | 11:00 | Gallamari | 139 | 18:30 | 129 | 0.45833
| Satmosjid | 132 | 19:00 | 125 | 11:00 | Magura | 130 | 6:00 | 115 | 13:00
| Tongi | 137 | 20:00 | 127 | 11:00 | Narail | 127 | 0.16667 | 115 | 13:00
| Kabirpur | 134 | 3:00 | 127 | 11:00 | Chuadanga | 127 | 6:00 | 110 | 0.58333
| Basundhara | 136 | 20:00 | 124 | 11:00 | Borguna | 137 | 0.25 | 126 | 0.66667
| Manikganj | 140 | 18:30 | 128 | 10:00 | Barisal(N) | 140 | 18:30 | 129 | 0.66667
| Joydevpur | 137 | 19:00 | 127 | 11:00 | Barisal (S) | 140 | 18:30 | 128 | 0.54167
| New Tongi | 138 | 18:30 | 125 | 10:00 | Patuakhali(S) | 138 | 18:30 | 124 | 15:00
| Kodda | 137 | 19:00 | 122 | 9:00 | Bhandaria | 135 | 0.25 | 121 | 0.75
| Dhamrai | 134 | 6:00 | 127 | 18:00 | Ishurdi | 138 | 0.875 | 130 | 0.45833
| Rajendrapur | 137 | 19:30 | 120 | 10:00 | Ruppur Paromanobik | 136 | 0.875 | 131 | 0.41667
| Valuka | 124 | 4:00 | 113 | 19:30 | Natore | 137 | 21:00 | 129 | 3:00
| Tangail | 131 | 4:00 | 122 | 19:30 | Bogra | 135 | 20:00 | 132 | 4:00
| Mymensing | 128 | 4:00 | 117 | 19:30 | Noagaon | 133 | 18:30 | 125 | 3:00
| Kishorganj | 131 | 5:00 | 121 | 21:00 | Rajshahi | 136 | 21:00 | 128 | 11:00
| Netrokona | 127 | 4:00 | 115 | 19:30 | Rajshahi New | 138 | 18:30 | 128 | 11:00
| Jamalpur | 135 | 19:30 | 127 | 12:00 | C.Nawabganj | 137 | 18:30 | 126 | 10:00
| Sherpur | 133 | 24:00 | 121 | 10:00 | Amnura | 139 | 18:30 | 127 | 10:00
| Srimongal | 138 | 4:00 | 133 | 21:00 | Pabna | 136 | 22:00 | 127 | 12:00
| Shahjibazar | 135 | 8:00 | 131 | 21:00 | Shahjadpur | 138 | 22:00 | 132 | 9:00
| Fenchuganj | 136 | 6:00 | 133 | 22:00 | Serajganj | 135 | 18:30 | 125 | 10:00
| Khulawara | 135 | 1:00 | 133 | 21:00 | Niyamatpur | 132 | 18:30 | 123 | 23:00
| Sylhet | 134 | 7:00 | 130 | 19:30 | Joypurhat | 132 | 6:00 | 124 | 3:00
| Chatak | 133 | 5:00 | 128 | 19:00 | Sherpur(Bogura) | 134 | 19:00 | 124 | 13:00
| Sunamganj | 133 | 6:00 | 126 | 21:00 | Mohastangor | 136 | 18:30 | 131 | 5:00
| Biani Bazar | 134 | 5:00 | 125 | 21:00 | Bangura | 137 | 22:00 | 130 | 11:00
| Comilla(s) | 129 | 5:00 | 121 | 12:00 | Rangpur | 130 | 7:00 | 126 | 18:00
| Comilla(n) | 134 | 2:00 | 128 | 11:00 | Lalmonirhat | 131 | 2:00 | 127 | 18:00
| Chandpur | 134 | 6:00 | 130 | 0:00 | Saidpur | 131 | 2:00 | 124 | 21:00
| Feni | 128 | 18:30 | 122 | 11:00 | Purbasadipur | 130 | 5:00 | 121 | 19:30
| Chowmuhani | 130 | 19:30 | 126 | 22:00 | Thakurgaon | 128 | 6:00 | 120 | 18:00
| Ashuganj | 138 | 20:00 | 135 | 17:00 | Palashbari | 132 | 19:00 | 126 | 18:00
| Daudkandi | 131 | 18:30 | 123 | 12:00 | Barapukuria | 134 | 5:00 | 130 | 18:00
| B.Baria | 134 | 17:00 | 128 | 21:00 | Panchagar | 127 | 5:00 | 117 | 19:30
| Ramganj | 131 | 19:30 | 127 | 23:00 | Joldhaka | 129 | 6:00 | 122 | 19:30
| Chaddagram | 132 | 3:00 | 126 | 10:00 | Kurigram | 130 | 5:00 | 125 | 18:00
| PHP | 130 | 18:30 | 122 | 11:00 | Mithapukur | 132 | 0.29167 | 128 | 0.125

## L-Curve
Date | 2021-05-05
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 270 | 7295 | 3219 | 10514 |  |  |  | QF-LDC-11
0:30 | 295 | 6970.5 | 3178.5 | 10149 | Date: | 2021-05-05
1:00 | 320 | 6646 | 3138 | 9784
1:30 | 285 | 6578 | 3096.5 | 9674.5
2:00 | 250 | 6510 | 3055 | 9565
2:30 | 209 | 6549 | 3072 | 9621 | [5 empty] | Gen. at Eve. Peak | 11620 | 11620 MW (21:00 )
3:00 | 168 | 6588 | 3089 | 9677 | [6 empty] | 21:00
3:30 | 219 | 6515 | 3007.5 | 9522.5 | [5 empty] | Gen. at Day Peak | 9733 | 9733 MW (12:00 )
4:00 | 270 | 6442 | 2926 | 9368 | [6 empty] | 12:00
4:30 | 335 | 6023 | 2846 | 8869 | [5 empty] | Highest Generation | 11620
5:00 | 400 | 5604 | 2766 | 8370 | [6 empty] | 21:00
5:30 | 420 | 5426.5 | 2671 | 8097.5
6:00 | 440 | 5249 | 2576 | 7825
6:30 | 442.5 | 5340 | 2568.5 | 7908.5
7:00 | 445 | 5431 | 2561 | 7992
7:30 | 462.5 | 5458.5 | 2634 | 8092.5
8:00 | 480 | 5486 | 2707 | 8193
8:30 | 495 | 5691.5 | 2746 | 8437.5
9:00 | 510 | 5897 | 2785 | 8682
9:30 | 575 | 6025.5 | 2892.5 | 8918
10:00 | 640 | 6154 | 3000 | 9154
10:30 | 639 | 6293.5 | 3058.5 | 9352
11:00 | 638 | 6433 | 3117 | 9550
11:30 | 643 | 6507.5 | 3134 | 9641.5
12:00 | 648 | 6582 | 3151 | 9733
12:30 | 574 | 6703 | 3204.5 | 9907.5
13:00 | 500 | 6824 | 3258 | 10082
13:30 | 482 | 6911.5 | 3278.5 | 10190
14:00 | 464 | 6999 | 3299 | 10298
14:30 | 446 | 7115 | 3295.5 | 10410.5
15:00 | 428 | 7231 | 3292 | 10523
15:30 | 445 | 7180 | 3277.5 | 10457.5
16:00 | 462 | 7129 | 3263 | 10392
16:30 | 443 | 7099.5 | 3230.5 | 10330
17:00 | 424 | 7070 | 3198 | 10268
17:30 | 278 | 7111.5 | 2979.5 | 10091
18:00 | 132 | 7153 | 2761 | 9914
18:30 | 96 | 7316 | 3041 | 10357
19:00 | 60 | 7479 | 3321 | 10800
19:30 | 72 | 8009 | 3599 | 11608
20:00 | 152 | 7944 | 3591 | 11535 |  |  |  | Executive Engineer
20:30 | 216 | 8010.5 | 3567 | 11577.5 |  |  |  | Network Operation Division
21:00 | 280 | 8077 | 3543 | 11620
21:30 | 288 | 8008.5 | 3414 | 11422.5
22:00 | 296 | 7940 | 3285 | 11225 |  |  |  |  | Page 6 of 7
22:30 | 303 | 7775 | 3266.5 | 11041.5
23:00 | 310 | 7610 | 3248 | 10858
23:30 | 290 | 7452.5 | 3233.5 | 10686
24:00 | 270 | 7295 | 3219 | 10514
11620 MW (21:00 )
9733 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-05 |  | Energy | 240522337
[11 empty] | 2021-05-05 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4435 | 830 | 1929 | 2671 | 503 | 21 | 105 | 0 | 148 | 0
0:30 | 4495.5 | 830 | 1928.5 | 2134 | 598 | 21.5 | 71.5 | 0 | 134 | 0 | Date: | 2021-05-05
1:00 | 4556 | 830 | 1928 | 1597 | 693 | 22 | 38 | 0 | 120 | 0
1:30 | 4502 | 830 | 1892 | 1579.5 | 693 | 22 | 38 | 0 | 118 | 0 | [7 empty] | Total Energy | 240.5223 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4448 | 830 | 1856 | 1562 | 693 | 22 | 38 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4479 | 830 | 1885.5 | 1557 | 693 | 22.5 | 38 | 0 | 116 | 0 | [7 empty] | Energy Requirement | 240.5223
3:00 | 4510 | 830 | 1915 | 1552 | 693 | 23 | 38 | 0 | 116 | 0
3:30 | 4435 | 830 | 1905 | 1499.5 | 693 | 23 | 21 | 0 | 116 | 0 | [6 empty] | Shortage
4:00 | 4360 | 830 | 1895 | 1447 | 693 | 23 | 4 | 0 | 116 | 0
4:30 | 4281 | 830 | 1749.5 | 1210 | 663 | 23.5 | 4 | 0 | 108 | 0
5:00 | 4202 | 830 | 1604 | 973 | 633 | 24 | 4 | 0 | 100 | 0
5:30 | 4069 | 830 | 1511.5 | 940.5 | 618 | 24 | 4 | 0 | 98 | 2.5
6:00 | 3936 | 830 | 1419 | 908 | 603 | 24 | 4 | 0 | 96 | 5
6:30 | 3987.5 | 830 | 1438 | 915.5 | 603.5 | 24 | 4 | 0 | 95 | 11 |  |  |  |  | Coal
7:00 | 4039 | 830 | 1457 | 923 | 604 | 24 | 4 | 0 | 94 | 17
7:30 | 4049.5 | 830 | 1522.5 | 934 | 604 | 24 | 4 | 0 | 94 | 30.5 |  |  |  | Oil
8:00 | 4060 | 830 | 1588 | 945 | 604 | 24 | 4 | 0 | 94 | 44
8:30 | 4231.5 | 830 | 1622 | 967 | 604.5 | 23 | 4 | 0 | 101 | 54.5
9:00 | 4403 | 830 | 1656 | 989 | 605 | 22 | 4 | 0 | 108 | 65
9:30 | 4434.5 | 830 | 1758 | 1086.5 | 604.5 | 22 | 4 | 0 | 111 | 67.5
10:00 | 4466 | 830 | 1860 | 1184 | 604 | 22 | 4 | 0 | 114 | 70
10:30 | 4527 | 829.5 | 1867 | 1286.5 | 613.5 | 22 | 5.5 | 0 | 121 | 80
11:00 | 4588 | 829 | 1874 | 1389 | 623 | 22 | 7 | 0 | 128 | 90
11:30 | 4558 | 829.5 | 1872 | 1496.5 | 639 | 22 | 5.5 | 0 | 130 | 89
12:00 | 4528 | 830 | 1870 | 1604 | 655 | 22 | 4 | 0 | 132 | 88
12:30 | 4499.5 | 830 | 1892.5 | 1764.5 | 684 | 22 | 4 | 0 | 130 | 81
13:00 | 4471 | 830 | 1915 | 1925 | 713 | 22 | 4 | 0 | 128 | 74
13:30 | 4471 | 830 | 1915 | 1925 | 713 | 22 | 4 | 0 | 128 | 74
14:00 | 4471 | 830 | 1915 | 1925 | 713 | 22 | 4 | 0 | 128 | 74
14:30 | 4507 | 829.5 | 1879 | 2149 | 714 | 22.5 | 4 | 0 | 139 | 58.5
15:00 | 4543 | 829 | 1843 | 2373 | 715 | 23 | 4 | 0 | 150 | 43
15:30 | 4538 | 829 | 1854.5 | 2278.5 | 712 | 23 | 29 | 0 | 148 | 45.5
16:00 | 4533 | 829 | 1866 | 2184 | 709 | 23 | 54 | 0 | 146 | 48
16:30 | 4530.5 | 829.5 | 1871.5 | 2143 | 696.5 | 23 | 57 | 0 | 145 | 34
17:00 | 4528 | 830 | 1877 | 2102 | 684 | 23 | 60 | 0 | 144 | 20
17:30 | 4562 | 829.5 | 1867.5 | 2112.5 | 453 | 23 | 93.5 | 0 | 139 | 11
18:00 | 4596 | 829 | 1858 | 2123 | 222 | 23 | 127 | 0 | 134 | 2
18:30 | 4530 | 829 | 1831.5 | 2493.5 | 272 | 26 | 231 | 0 | 143 | 1
19:00 | 4464 | 829 | 1805 | 2864 | 322 | 29 | 335 | 0 | 152 | 0
19:30 | 4474 | 829 | 1864 | 3407 | 461 | 23 | 396 | 0 | 154 | 0
20:00 | 4503 | 830 | 1867 | 3364 | 481 | 23 | 311 | 0 | 156 | 0
20:30 | 4511.5 | 829.5 | 1883 | 3387 | 492 | 23 | 292.5 | 0 | 159 | 0
21:00 | 4520 | 829 | 1899 | 3410 | 503 | 23 | 274 | 0 | 162 | 0
21:30 | 4519.5 | 829.5 | 1914 | 3265.5 | 502.5 | 23 | 208.5 | 0 | 160 | 0
22:00 | 4519 | 830 | 1929 | 3121 | 502 | 23 | 143 | 0 | 158 | 0
22:30 | 4575.5 | 830 | 1936 | 2896 | 502.5 | 22 | 123.5 | 0 | 156 | 0
23:00 | 4632 | 830 | 1943 | 2671 | 503 | 21 | 104 | 0 | 154 | 0
23:30 | 4533.5 | 830 | 1936 | 2671 | 503 | 21 | 104.5 | 0 | 151 | 0 | Max Temp. in Dhaka |  | 34.5° C
24:00 | 4435 | 830 | 1929 | 2671 | 503 | 21 | 105 | 0 | 148 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-05
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 22 | 22 | 23 | 23 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 |  | 29 | 23 | 23 | 23 | 23 | 21 | 21 | 481740
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 2100000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 16 | 16 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 360541
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 1 | 2 | 5 |  | 18 | 20 | 19 | 17 | 13 | 8 | 3 | 0 | [8 empty] | 120015
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 215 | 203 | 203 | 213 | 217 | 203 | 205 | 205 | 211 | 204 | 205 | 205 | 205 | 205 | 204 | 218 |  | 204 | 204 | 204 | 204 | 204 | 209 | 163 | 4824825
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 130 | 130 | 130 | 130 | 130 | 130 |  | 130 | 100 | 100 | 140 | 140 | 140 | 140 | 3244154
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | [14 empty] | 1 |  | 34 | 68 | 68 | 68 | 68 | 68 | 68 | 504521
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 68 | 51 | 51 | 51 | 51 | 51 | 51 | 70 | 81 | 82 | 77 | 82 | 90 | 86 |  | 89 | 85 | 90 | 90 | 89 | 89 | 91 | 1959599
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 |  |  |  |  | 0 | 67216
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 125 | 120 | 120 | 97 | 73 | 73 | 73 | 73 | 120 | 120 | 150 | 75 | 120 | 115 | 120 | 120 | 145 |  | 120 | 120 | 115 | 115 | 118 | 118 | 76 | 2932000
17 | Siddhirganj 335 MW CCPP | 221 | 180 | 180 | 180 | 160 | 140 | 140 | 170 | 222 | 219 | 221 | 216 | 216 | 160 | 160 | 160 | 160 | 160 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4426456
18 | Kodda 300 MW PP Unit-2 (Summit) | [11 empty] | 2 | 45 | 47 | 76 | 65 | 45 | 52 |  | 122 | 185 | 203 | 205 | 110 | 15 | 15 | 1124072
19 | Ashuganj 195MW PP (APSCL-United) | 36 | 36 | 36 | 36 | 36 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 518545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2033654
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 577872
33 | Ashuganj 225 MW CCPP | 181 | 181 | 193 | 181 | 181 | 181 | 206 | 182 | 216 | 191 | 197 | 187 | 183 | 190 | 183 | 182 | 182 | 206 |  | 182 | 181 | 182 | 182 | 181 | 197 | 182 | 4537000
34 | Ashuganj 450 MW CCPP(South) | 300 | 265 | 290 | 265 | 265 | 265 | 255 | 255 | 265 | 310 | 310 | 310 | 305 | 305 | 295 | 295 | 295 | 305 |  | 295 | 295 | 295 | 295 | 295 | 320 | 295 | 7014000
| Ashuganj 450 MW CCPP(North) | 310 | 280 | 280 | 260 | 260 | 260 | 310 | 260 | 360 | 320 | 325 | 310 | 310 | 315 | 310 | 310 | 315 | 310 |  | 290 | 310 | 310 | 310 | 310 | 335 | 285 | 7466800
35 | Ashuganj 55 MW PP (Precision) | 57 | 57 | 57 | 57 | 30 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 48 | 49 | 50 | 53 | 55 | 55 |  | 55 | 56 | 55 | 56 | 56 | 56 | 57 | 1090560
36 | Chandpur 150 MW CCPP | 87 | 86 | 86 | 86 | 86 | 86 | 87 | 87 | 88 | 89 | 90 | 90 | 89 | 90 | 84 | 94 | 94 | 95 |  | 90 | 91 | 91 | 93 | 91 | 95 | 94 | 2123610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6333500
41 | Haripur 360MW CCPP(HPL) | 292 | 292 | 292 | 312 | 313 | 273 | 272 | 322 | 310 | 300 | 290 | 280 | 274 | 270 | 268 | 264 | 264 | 254 |  | 270 | 270 | 273 | 276 | 278 | 278 | 262 | 6780000
42 | RPCL 210MW CCPP | 159 | 159 | 159 | 159 | 159 | 160 | 159 | 158 | 156 | 155 | 154 | 153 | 152 | 149 | 150 | 146 | 142 | 136 |  | 148 | 152 | 152 | 151 | 150 | 152 | 156 | 3592800
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 7 | 23 | 40 | 32 | 27 | 23 | 14 | 24 | 15 | 22 | 8 | 1 | [8 empty] | 243940
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 |  | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 1028000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1013880
46 | Shajibazar 330 MW CCPP | 162 | 162 | 161 | 161 | 161 | 163 | 163 | 161 | 161 | 161 | 163 | 162 | 163 | 163 | 273 | 273 | 272 | 271 |  | 273 | 271 | 272 | 272 | 270 | 270 | 272 | 4766000
47 | Shahjibazar GTPP Unit- 8 & 9 | 34 | 34 | 33 | 33 | 33 | 20 | 20 | 33 | 32 | 32 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 741696
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 20 | 10 | 10 | 70 | 70 | 73 | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1607040
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 223 | 223 | 223 | 223 | 190 | 162 | 162 | 162 | 162 | 163 | 163 | 184 | 190 | 203 | 217 | 217 | 216 | 196 |  | 203 | 223 | 223 | 223 | 223 | 225 | 209 | 4776810
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 413000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 162900
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | [7 empty] | 5 | 5 | 5 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 118000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 924600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | [7 empty] | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 370320
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 285 | 310 | 290 | 295 | 295 | 310 | 300 | 310 | 310 | 305 | 310 | 300 | 300 | 285 | 290 | 280 | 280 |  | 250 | 275 | 270 | 280 | 300 | 280 | 310 | 7282000
| Bibiyana South 400 MW | 370 | 370 | 381 | 370 | 340 | 320 | 365 | 320 | 377 | 378 | 390 | 371 | 376 | 376 | 370 | 370 | 370 | 393 |  | 370 | 370 | 370 | 370 | 370 | 374 | 370 | 8806000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 |  |  |  |  | 5 | 17 | 43 | 55 |  | 29 | 30 | 30 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 919122
59 | Tangail Palli Power Gen 22 MW | 24 | 22 | 22 | 23 | [5 empty] | 18 | 24 | 21 | 17 | 18 | 18 | 21 | 24 | 24 |  | 15 | 23 | 24 | 24 | 24 | 24 | 24 | 419520
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 507648
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | [7 empty] | 22 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 311760
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 14 | 14 | 14 | 14 | 14 | 14 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 376092
63 | Impoprt (Tripura) | 120 | 116 | 116 | 116 | 100 | 96 | 94 | 94 | 108 | 114 | 128 | 132 | 128 | 144 | 150 | 146 | 144 | 134 |  | 152 | 154 | 156 | 162 | 158 | 154 | 148 | 3104640
64 | Malancha, Ctg. EPZ (United) | 16 | 16 | 16 | 32 | 32 | 32 | 15 | 10 | 5 | 5 | 6 | 6 | 13 | 7 | 5 | 8 | 15 | 18 |  | 24 | 25 | 29 | 34 | 33 | 39 | 38 | 444480
65 | Feni 22MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 10 |  |  |  |  | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 305676
66 | Feni 11 MW PP (Doreen) | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 10 | 10 | 10 | 217980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817700
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 15 | 15 | 15 | 15 | 15 | 15 | 18 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 435360
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 29 | 29 | 29 |  | 14 | 14 | 28 | 29 | 29 | 29 | 29 | 645300
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 814000
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 598300
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 54 | 14 | 14 | 51 | 52 | 93 | 99 | 102 | 96 | 96 | 96 | 96 | 100 | 98 |  | 98 | 98 | 98 | 98 | 96 | 98 | 100 | 2008318
| Feni Lanka Power | [17 empty] | 5 |  | 17 | 17 |  |  |  |  | 0 | 28500
| Chowmuhani 113 MW | 46 | 46 | 46 | 26 | [5 empty] | 30 | 55 | 74 | 113 | 113 | 111 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1805160
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 70 | 81 | 108 | 115 | 148 | 108 | 108 | 108 |  | 130 | 162 | 162 | 162 | 162 | 108 | 106 | 1942560
77 | Siddhirganj 100 PP(Dutch Bangla) | 7 | 7 | 7 | 7 | [5 empty] | 4 | 15 | 15 | 50 | 80 | 50 | 24 | 24 | 24 |  | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 1000320
78 | Gazipur 52 MW PP | [19 empty] | 20 | 51 | 25 | 25 | 25 |  | 0 | 108960
79 | Kodda 150MW PP | [17 empty] | 16 |  | 16 | 16 | 16 | 32 | 32 | 32 | 32 | 165120
80 | Jamalpur 95 MW PP(Powerpac) | 57 | 49 | 49 | 65 | 65 | 73 | 73 | 73 | 73 | 73 | 65 | 65 | 65 | 65 | 64 | 64 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1555200
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 30 | 52 | 52 | 472890
| Gazipur 100 MW PP | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 30 | 50 | 60 | 70 | 90 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1792800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [9 empty] | 38279
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 42 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1287521
| Karnaphuli Power Ltd. | [19 empty] | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 91163
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 240 | 250 | 240 | 245 | 245 | 240 | 255 | 255 | 250 | 260 | 275 | 265 | 245 | 260 | 250 | 240 | 240 | 275 |  | 250 | 255 | 250 | 250 | 255 | 240 | 245 | 5869265
87 | Meghnaghat 100 MW(IEL) | [9 empty] | 4 | 16 | 16 | 16 | 16 | 42 | 40 | 16 | 16 |  | 53 | 89 | 84 | 91 | 88 | 65 | 55 | 643200
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | 17 | [5 empty] | 7 | 17 | 17 | 17 | 20 | 68 | 60 | 20 | 17 |  | 66 | 90 | 90 | 90 | 90 | 90 | 90 | 892800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 20 | 40 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1064403
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | 7 | 7 |  |  |  |  | 7 | 7 | 10 | 24 | 24 | 24 | 32 | 48 | 48 | 48 |  | 70 | 93 | 93 | 93 | 64 | 7 | 7 | 700128
95 | Patenga 50MW PP (Baraka) | [7 empty] | 1 | 18 | 19 | 19 | 19 | 19 | 17 | 16 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 270720
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 5 | 37 | 40 | 23 |  |  | 0 | 69120
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1056360
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 55 | 17 | 17 | 17 |  | 30 | 55 | 55 | 55 | 17 | 17 | 17 | 373611
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 3441845
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 8350
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 619920
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 16 | 16 | 16 | [14 empty] | 5 |  | 16 | 60 | 62 | 110 | 110 | 60 | 8 | 520800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3602160
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2234880
116 | Chandpur 200MW (Desh energy) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 112 | 131 |  | 138 | 138 | 138 | 144 | 155 | 155 | 100 | 2757600
117 | Ashuganj 150MW PP (Midland) | [9 empty] | 1 | 16 | 36 | 98 | 142 | 100 | 70 | 70 | 70 |  | 112 | 125 | 145 | 150 | 150 | 50 | 50 | 1436872
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 375 | 367 | 329 | 316 | 353 | 320 | 376 | 376 | 396 | 373 | 368 | 373 | 368 | 366 | 368 | 365 |  | 365 | 366 | 367 | 367 | 367 | 387 | 365 | 8751000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 95 | 35 | 16 | 16 | 16 | 16 | 23 | 45 | 45 | 48 | 66 | 115 | 115 | 115 | 115 |  | 115 | 115 | 85 | 85 | 85 | 85 | 85 | 1872000
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 80 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1842240
| Anlima Energy Ltd. | 71 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 22 | 53 | 56 | 72 | 72 | 60 | 35 |  | 55 | 116 | 116 | 116 | 116 | 116 | 116 | 1326055
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 35 | 35 | 36 | 35 | 35 | 36 | 36 | 624960
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 7 | 15 | 11 | 28 | 34 | 33 | 29 | 23 | 8 | 11 | 6 | 1 | [8 empty] | 206335
120 | Eastern Zone Total | 6646 | 6510 | 6588 | 6442 | 5604 | 5249 | 5431 | 5486 | 5897 | 6154 | 6433 | 6582 | 6824 | 6999 | 7231 | 7129 | 7070 | 7153 |  | 7479 | 8009 | 7944 | 8077 | 7940 | 7610 | 7295 | 163750659
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 32 | 32 | 32 | 32 | [5 empty] | 49 | 49 | 83 | 94 | 99 | 99 | 99 | 66 | 32 |  | 68 | 99 | 99 | 99 | 99 | 99 | 83 | 1311360
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 4 | 4 | 4 | 4 | 4 | 4 |  |  | 5 | 18 | 22 | 21 | 4 | 4 | 5 | 119520
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [14 empty] | 35 | 17 | 17 | 17 |  | 17 | 35 | 52 | 53 | 17 | 17 | 17 | 295680
130
131
132 | United Payra Power Ltd. | [19 empty] | 10 | [5 empty] | 0 | 30000
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 32 | 32 | 32 | [12 empty] | 16 |  | 64 | 75 | 110 | 96 | 96 | 96 | 96 | 679296
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 97 | 97 | 62 | 33 | 32 | 32 | 32 | 88 | 96 | 94 | 95 | 95 | 94 | 96 | 96 | 92 |  | 96 | 97 | 97 | 100 | 97 | 97 | 97 | 2007825
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 64 | 64 | 64 | 64 | 65 | 65 | 65 |  | 65 | 58 | 62 | 60 | 63 | 67 | 67 | 1544000
140 | Bhola 33 MW PP (Venture) | 29 | 28 | 28 | 27 | 25 | 23 | 22 | 11 | 14 | 22 | 22 | 23 | 26 | 26 | 26 | 26 | 26 | 24 |  | 34 | 34 | 34 | 34 | 34 | 33 | 33 | 615548
141 | Noapara 100 MW PP (Bangla Trac) | [25 empty] | 0 | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 24 | 24 |  |  |  |  | 0 | 38625
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 309312
146 | Bheramara HVDC | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 830 | 829 | 830 | 830 | 829 | 829 | 829 | 830 | 829 |  | 829 | 829 | 830 | 829 | 830 | 830 | 830 | 20043636
147 | Bheramara 410 MW CCPP | 355 | 355 | 385 | 350 | 350 | 300 | 270 | 365 | 375 | 360 | 385 | 360 | 370 | 370 | 355 | 355 | 355 | 365 |  | 320 | 360 | 370 | 350 | 355 | 350 | 340 | 8708256
148 | Payra 1320 MW | 470 | 470 | 470 | 470 | 410 | 380 | 380 | 380 | 380 | 380 | 400 | 430 | 490 | 490 | 490 | 490 | 460 | 0 |  | 100 | 240 | 260 | 280 | 280 | 280 | 280 | 10213800
149
150 | Barapukuria TPP Unit-1 | 73 | 73 | 73 | 73 | 73 | 73 | 74 | 74 | 75 | 74 | 73 | 75 | 74 | 72 | 75 | 69 | 74 | 72 |  | 72 | 71 | 71 | 73 | 72 | 73 | 73 | 1746327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3676200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [15 empty] | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 |  |  |  | 297808
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 121 | 120 | 112 | 110 | 106 | 80 | 80 | 104 | 109 | 128 | 135 | 131 | 125 | 127 | 121 | 122 | 115 | 104 |  | 110 | 108 | 107 | 105 | 107 | 106 | 111 | 2837900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 176 | 166 | 157 | 153 | 152 | 139 | 149 | 155 | 172 | 199 | 199 | 189 | 193 | 173 | 159 | 158 | 162 |  | 176 | 158 | 159 | 158 | 159 | 160 | 154 | 4226909
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 184 | 182 | 170 | 160 | 156 | 155 | 140 | 158 | 164 | 181 | 202 | 198 | 190 | 194 | 182 | 175 | 173 | 176 |  | 166 | 150 | 150 | 150 | 150 | 161 | 188 | 4366882
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 397 | 318 | 352 | 313 | 317 | 320 | 363 | 373 | 414 | 425 | 422 | 419 | 418 | 418 | 404 | 400 | 398 | 394 |  | 335 | 366 | 367 | 377 | 391 | 418 | 388 | 9187454
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 10 | 24 | 34 | 34 |  |  |  | 90886
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 22 | 22 | 3 | 3 | 3 | 3 | 15 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 402720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 |  |  | 0 | 231786
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 42 | 42 | 24 | 24 |  |  |  | 105250
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [16 empty] | 6 | 15 |  | 30 | 30 | 31 | 30 |  |  | 0 | 94237
168 | Santahar 50 MW Peaking PP | [17 empty] | 20 |  | 40 | 40 | 40 | 39 | 39 |  |  | 170160
169 | Natore 52 MW PP (Rajlanka) | 25 | 25 | 25 | 8 | [5 empty] | 8 | 8 | 18 | 34 | 43 | 16 | 16 | 16 | 16 |  | 52 | 52 | 43 | 52 | 52 | 52 | 52 | 608640
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 15 |  | 100 | 100 | 50 |  |  |  |  | 196672
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | [9 empty] | 33 | 38 | 70 | 35 | 35 | 35 |  | 66 | 85 | 113 | 113 | 70 | 35 | 35 | 879552
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 95 | 109 | 70 | 70 | 35 | 35 | 35 | 392256
173 | Rangpur 20 MW GTPP
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 34 | 34 | 34 | 15 | [5 empty] | 34 | 39 | 35 | 35 | 50 | 70 | 70 | 70 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1301760
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 4 | 4 | 5 | 6 | 6 | 5 | 3 | 4 | 2 | 0 | [8 empty] | 41421
178
178