## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-09 | Sunday
|  |  | Date (day): | 2021-05-09 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 15001.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15780 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-08 | 2021-05-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 100 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 217 | 383 | 360 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 202 | 180 | 250 | 250 | 110 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 280 | 280 | 170 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 235 | 240 | 240 | 55 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 30 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 155 | 120 | 150 | 60 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 2 | 100 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 214 | 217 | 220 | 220 |  | 115 | ST under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 72 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 52 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 42 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 88 | 245 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 132 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 90 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 94 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 17 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2180 | 3019 | 3681 | 4033 | 554 | 1180
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 80 | 90 | 80 | 80 | 100 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 4 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 22 | 20 | 22 | 22 | 208 |  | Unit 4 & 5 Under S/D due to Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 215 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 140 | 135 | 130 | 130
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 91 | 105 | 90 | 90 |  | 15 | Engine problem
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Fuel shortage
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 26 | 15 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 91 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 4 | 17 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 58 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 926 | 1226 | 1607 | 1587 | 588 | 180
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 189 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 335 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 305 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 150 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 127 | 133 | 130 | 130 | 33 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 161 | 160 | 160 |  | 40 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 158 | 157 | 188
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 3 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 19 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 52 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 17 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 36 | 36 | 36 |  | 18 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1379 | 1986 | 2198 | 2379 | 538 | 82
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 146 | 133 | 160 | 160 |  |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 14 | 19 | 19
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 65 | 73 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 100 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 0 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 5 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 252 | 459 | 641.6 | 590 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 250 | 271 | 275 | 275 |  |  | Machine problem
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 31 | 32 | 32
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 76 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 122 | 223 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 366 | 400 | 400 | 400 |  |  | FGMO
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 380 | 400 | 400 |  |  | FGMO
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1762 | 2032 | 2103 | 2105 | 0 | 192
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 836 | 835 | 857 | 857
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 85 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 5 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 240 | 350 | 350 | 60 |  | Gas shortage
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 74 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1278 | 1376 | 1673 | 1944 | 60 | 106
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 16 | 33 | 35 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 62 | 65 | 65 | 65 |  | 129 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 97 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 550 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 77 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 80 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 574 | 903 | 1007 | 1007 | 0 | 129
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 42 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 29 | 29 |  | 21 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 110 | 80 | 130 | 130 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 170 | 200 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 201 | 180 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 406 | 406 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 41 | 0 | 32 |  |  | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 100 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 929 | 1406 | 1745 | 1777 | 171 | 36
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 70 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 107 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 230 | 327 | 346 | 358 | 124 | 105
|  | Total |  |  |  |  | 21967 | 21219 | 9510 | 12734 | 15001.6 | 15780 | 2035 | 2031
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9069.3765 | 12144 | 14306.5361 | 15048.8707
| A. |  | 2021-05-08 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12734 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8185 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12734 | MW
| 3 | Day peak Generation : |  |  | 9510 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12144 | MW
| 4 | Evening peak Generation : |  |  | 12734 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 250.5588 | MKWHr | By Solar | 0.70805 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 156.1371 | MKWHr |  | By Oil: | 52.2354 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.8204 | MKWHr |  | By Hydro: | 0.44208 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2035 | MW | Dhaka | 4349 | 4349 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2031 | MW | Chittagong | 1353 | 1353 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4066 | MW | Khulna | 1594 | 1594 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1290.42 | MMCFD |  |  | Rajshahi | 1164 | 1164 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 169274834.836 | ii) Oil : | Taka | 369605889.77 | Comilla | 1244 | 1244 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 84884827.92 | Total | Taka | 623765552.526 | Mymensingh | 979 | 979 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.004 | MKWHr. | Sylhet | 486 | 486 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 30 | MW (E to W) at | 21:00 | hrs | Barisal | 355 | 355 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | 5 | MW at | 19:00 | hrs | Rangpur | 620 | 620 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.5° C |  |  | Total | 12144 | 12144 |  | 0
| B. |  | 2021-05-09 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15780 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 2780 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 255.7927 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8936 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.1716 | MKWHr. | ii) HVDC Flow at Peak Time |  | 835 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0442 | MKWHr. | iii) Maximum HVDC Flow : |  | 836 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 76 |  | (b) Today: | 75.98 |  | (c) Rule Curve: |  | 80.48
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 283 | 271 |  | 0 | 270 | 230 | 0 | 0 | 55 | 160 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 21 | 0 | 80 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 68 | 0 | 0 | 0 | 21 | 41 | 0 | 0 | 100 | 280 | 260 | 215 | 8 | 129 | 26 | 57 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 18 | 134 | 159 | 73 | 0 | 0 | 43 | 42 | 53 | 0 | 130 | 274 | 32 | 78 | 0 | 162 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 0 | 100 | 100 | 0 | 370 | 16 | 52 | 105 | 0 | 0 | 54 | 0 | 0 | 111 | 100 | 380 | 17 | 0 | 17 | 90 | 0 | 18 | 0 |  | 836 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 29 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 22 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 131 | 0 | 191 | 0 | 97 | 0 | 194 | 0 | 398 | 17 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 570 | 0 | 0 | 0 |  | 7032 | 3382 | 10414 | 4839 | 836 | 1914 | 1807 | 791 | 21 | 72 | 134 | 0 | 0 | 76.01
2:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 285 | 270 |  | 0 | 270 | 232 | 0 | 0 | 55 | 160 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 21 | 0 | 80 | 0 | 17 | 214 | 0 | 130 | 0 |  | 22 | 0 | 68 | 0 | 0 | 0 | 21 | 41 | 0 | 0 | 100 | 275 | 260 | 215 | 8 | 128 | 26 | 57 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 18 | 132 | 159 | 73 | 0 | 0 | 43 | 42 | 53 | 0 | 110 | 271 | 32 | 78 | 0 | 162 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 100 | 100 | 0 | 376 | 16 | 52 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 389 | 17 | 0 | 17 | 90 | 0 | 18 | 0 |  | 835 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 27 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 129 | 0 | 188 | 0 | 95 | 0 | 178 | 0 | 376 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 |  | 7041 | 3283 | 10324 | 4846 | 835 | 1877 | 1771 | 770 | 21 | 72 | 132 | 0 | 0 | 76.01
3:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 285 | 271 |  | 0 | 270 | 248 | 0 | 0 | 50 | 160 | 0 | 100 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 29 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 17 | 204 | 0 | 130 | 0 |  | 23 | 0 | 68 | 0 | 0 | 0 | 21 | 41 | 0 | 0 | 100 | 285 | 260 | 215 | 8 | 128 | 26 | 57 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 18 | 132 | 159 | 73 | 0 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 32 | 78 | 0 | 162 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 100 | 100 | 0 | 375 | 16 | 52 | 105 | 0 | 0 | 54 | 0 | 0 | 111 | 100 | 370 | 17 | 0 | 17 | 90 | 0 | 18 | 0 |  | 835 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 70 | 0 | 150 | 0 | 0 | 135 | 0 | 196 | 0 | 95 | 0 | 163 | 0 | 371 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 |  | 7032 | 3293 | 10325 | 4839 | 835 | 1874 | 1781 | 770 | 22 | 72 | 132 | 0 | 0 | 76
4:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 286 | 300 |  | 0 | 270 | 230 | 0 | 0 | 55 | 160 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 17 | 215 | 0 | 130 | 0 |  | 22 | 0 | 68 | 0 | 0 | 0 | 22 | 41 | 0 | 0 | 100 | 300 | 260 | 215 | 8 | 128 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 126 | 159 | 73 | 0 | 0 | 43 | 42 | 53 | 0 | 110 | 272 | 32 | 78 | 0 | 162 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 100 | 100 | 0 | 394 | 0 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 55 | 100 | 402 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 836 | 0 | 410 | 0 | 56 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 129 | 0 | 188 | 0 | 96 | 0 | 155 | 0 | 415 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 0 | 0 | 0 |  | 6603 | 3207 | 9810 | 4890 | 836 | 1936 | 1157 | 771 | 22 | 72 | 126 | 0 | 0 | 76
5:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 286 | 260 |  | 0 | 270 | 245 | 0 | 0 | 55 | 160 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 20 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 0 | 216 | 0 | 100 | 0 |  | 0 | 0 | 34 | 0 | 0 | 0 | 22 | 41 | 0 | 0 | 80 | 280 | 260 | 215 | 8 | 128 | 26 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 116 | 159 | 16 | 17 | 0 | 43 | 42 | 5 | 0 | 110 | 273 | 32 | 10 | 0 | 136 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 70 | 50 | 0 | 379 | 0 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 0 | 50 | 375 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 836 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 128 | 0 | 186 | 0 | 96 | 0 | 154 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 5884 | 2904 | 8788 | 4700 | 836 | 1628 | 776 | 672 | 22 | 38 | 116 | 0 | 0 | 76
6:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 286 | 260 |  | 0 | 270 | 235 | 0 | 0 | 40 | 160 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 0 | 216 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 38 | 0 | 0 | 80 | 290 | 260 | 161 | 8 | 128 | 26 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 98 | 159 | 0 | 17 | 0 | 43 | 42 | 5 | 0 | 110 | 248 | 33 | 10 | 0 | 136 | 18 | 0 | 7 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 1 | 50 | 34 | 0 | 318 | 0 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 0 | 30 | 375 | 0 | 3 | 0 | 35 | 0 | 18 | 0 |  | 836 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 70 | 0 | 140 | 0 | 53 | 0 | 155 | 0 | 311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5591 | 2607 | 8198 | 4396 | 836 | 1536 | 679 | 623 | 22 | 4 | 98 | 4 | 0 | 76
7:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 73 | 282 |  | 0 | 270 | 250 | 0 | 0 | 40 | 160 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 20 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 0 | 219 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 10 | 0 | 0 | 80 | 310 | 260 | 182 | 8 | 128 | 26 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 18 | 92 | 158 | 0 | 17 | 0 | 43 | 42 | 5 | 0 | 110 | 246 | 32 | 10 | 0 | 149 | 18 | 0 | 7 | 320 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 5 | 50 | 34 | 0 | 340 | 0 | 1 | 51 | 1 | 0 | 54 | 0 | 0 | 0 | 30 | 387 | 0 | 11 | 0 | 35 | 0 | 18 | 0 |  | 836 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 51 | 0 | 171 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 0 | 0 | 0 |  | 5497 | 2688 | 8185 | 4325 | 836 | 1569 | 695 | 624 | 22 | 4 | 92 | 18 | 0 | 0
8:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 28 | 281 |  | 0 | 270 | 235 | 0 | 0 | 40 | 228 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 0 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 0 | 0 | 9 | 22 | 6 | 0 | 0 | 80 | 260 | 240 | 218 | 8 | 125 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 15 | 98 | 159 | 13 | 17 | 1 | 43 | 42 | 5 | 0 | 110 | 247 | 20 | 10 | 0 | 123 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 11 | 100 | 43 | 0 | 365 | 0 | 38 | 51 | 2 | 0 | 54 | 0 | 0 | 0 | 30 | 340 | 0 | 8 | 0 | 36 | 0 | 18 | 14 |  | 835 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 62 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 81 | 0 | 156 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 0 | 0 | 0 |  | 5555 | 2672 | 8227 | 4264 | 835 | 1529 | 815 | 623 | 22 | 4 | 98 | 37 | 0 | 75.99
9:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 81 | 263 |  | 0 | 270 | 235 | 0 | 0 | 30 | 221 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 0 | 217 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 6 | 0 | 0 | 80 | 280 | 240 | 215 | 8 | 127 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 22 | 8 | 33 | 10 | 106 | 158 | 48 | 17 | 1 | 43 | 42 | 5 | 0 | 110 | 246 | 5 | 75 | 0 | 121 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 130 | 15 | 100 | 85 | 0 | 365 | 0 | 70 | 82 | 2 | 0 | 54 | 0 | 0 | 0 | 100 | 340 | 0 | 8 | 0 | 35 | 0 | 18 | 22 |  | 836 | 0 | 350 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 95 | 0 | 153 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 0 | 0 | 0 |  | 5895 | 2720 | 8615 | 4334 | 836 | 1615 | 1026 | 622 | 22 | 4 | 106 | 50 | 0 | 75.99
10:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 171 | 221 |  | 0 | 270 | 240 | 0 | 0 | 30 | 221 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 23 | 0 | 80 | 0 | 0 | 206 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 3 | 0 | 0 | 80 | 305 | 240 | 214 | 8 | 128 | 26 | 25 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 90 | 158 | 48 | 0 | 1 | 43 | 42 | 5 | 0 | 110 | 248 | 31 | 75 | 0 | 122 | 0 | 0 | 0 | 305 | 0 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 121 | 18 | 100 | 85 | 0 | 385 | 0 | 70 | 105 | 4 | 0 | 54 | 0 | 0 | 0 | 100 | 350 | 0 | 41 | 0 | 35 | 0 | 18 | 5 |  | 836 | 0 | 380 | 0 | 16 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 93 | 0 | 161 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 0 | 0 | 0 |  | 6108 | 2762 | 8870 | 4543 | 836 | 1593 | 1085 | 623 | 23 | 4 | 90 | 73 | 0 | 75.99
11:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 193 | 212 |  | 0 | 270 | 245 | 0 | 0 | 30 | 219 | 0 | 175 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 23 | 0 | 80 | 0 | 0 | 219 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 18 | 22 | 3 | 0 | 0 | 80 | 300 | 240 | 212 | 8 | 127 | 26 | 48 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 10 | 106 | 148 | 64 | 0 | 1 | 43 | 42 | 5 | 0 | 163 | 250 | 31 | 75 | 0 | 121 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 130 | 20 | 100 | 85 | 0 | 416 | 0 | 72 | 105 | 2 | 0 | 54 | 0 | 0 | 0 | 100 | 350 | 0 | 43 | 0 | 35 | 0 | 18 | 34 |  | 835 | 0 | 380 | 0 | 29 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 94 | 0 | 171 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 400 | 0 | 0 | 0 |  | 6354 | 2838 | 9192 | 4630 | 835 | 1720 | 1145 | 623 | 23 | 4 | 106 | 106 | 0 | 75.99
12:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 217 | 202 |  | 0 | 270 | 260 | 0 | 0 | 30 | 214 | 0 | 180 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 4 | 204 | 0 | 140 | 0 |  | 5 | 0 | 0 | 0 | 0 | 18 | 22 | 4 | 0 | 0 | 80 | 280 | 265 | 212 | 8 | 127 | 26 | 54 | 0 | 10 | 0 | 0 | 3 | 19 | 5 | 33 | 12 | 110 | 146 | 65 | 0 | 1 | 43 | 42 | 5 | 0 | 163 | 250 | 31 | 75 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 0 | 133 | 20 | 100 | 100 | 0 | 366 | 0 | 90 | 91 | 5 | 0 | 54 | 4 | 0 | 17 | 100 | 350 | 0 | 35 | 0 | 58 | 0 | 18 | 17 |  | 836 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 62 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 110 | 0 | 170 | 0 | 96 | 0 | 201 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 400 | 0 | 0 | 0 |  | 6499 | 3011 | 9510 | 4686 | 836 | 1737 | 1407 | 624 | 22 | 4 | 110 | 84 | 0 | 75.99
13:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 362 | 191 |  | 0 | 270 | 260 | 0 | 0 | 30 | 215 | 0 | 180 | 7 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 0 | 25 | 8 | 0 | 21 | 0 | 80 | 0 | 16 | 206 | 0 | 140 | 0 |  | 22 | 0 | 0 | 0 | 0 | 18 | 22 | 4 | 0 | 0 | 80 | 290 | 305 | 211 | 8 | 133 | 26 | 55 | 0 | 23 | 0 | 0 | 16 | 19 | 5 | 33 | 16 | 120 | 133 | 60 | 0 | 1 | 43 | 42 | 5 | 0 | 163 | 270 | 31 | 74 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 127 | 20 | 90 | 102 | 0 | 372 | 8 | 90 | 89 | 2 | 0 | 54 | 17 | 0 | 26 | 100 | 350 | 0 | 26 | 0 | 100 | 0 | 18 | 34 |  | 836 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 110 | 0 | 200 | 0 | 96 | 0 | 189 | 0 | 419 | 35 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 430 | 0 | 0 | 0 |  | 6802 | 3112 | 9914 | 4893 | 836 | 1742 | 1555 | 654 | 21 | 4 | 120 | 89 | 0 | 75.99
14:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 398 | 190 |  | 0 | 270 | 275 | 0 | 0 | 30 | 211 | 0 | 178 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 0 | 25 | 16 | 0 | 20 | 0 | 80 | 0 | 16 | 222 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 22 | 3 | 0 | 0 | 80 | 335 | 320 | 206 | 8 | 134 | 26 | 55 | 0 | 51 | 0 | 0 | 20 | 19 | 8 | 33 | 16 | 132 | 129 | 65 | 0 | 2 | 41 | 42 | 5 | 0 | 163 | 267 | 31 | 72 | 0 | 121 | 0 | 0 | 0 | 320 | 0 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 113 | 17 | 100 | 102 | 0 | 407 | 48 | 90 | 89 | 4 | 0 | 54 | 17 | 0 | 49 | 100 | 351 | 0 | 20 | 17 | 100 | 0 | 18 | 30 |  | 836 | 0 | 365 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 18 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 127 | 0 | 190 | 0 | 95 | 0 | 194 | 0 | 413 | 64 | 0 | 0 | 0 | 29 | 0 | 7 | 0 | 440 | 0 | 0 | 0 |  | 7081 | 3213 | 10294 | 5036 | 836 | 1779 | 1744 | 663 | 20 | 4 | 132 | 80 | 0 | 0
15:00 | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 367 | 191 |  | 0 | 270 | 235 | 0 | 0 | 50 | 213 | 0 | 150 | 60 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 4 | 35 | 22 | 25 | 24 | 25 | 25 | 22 | 0 | 20 | 0 | 50 | 0 | 16 | 204 | 0 | 130 | 0 |  | 23 | 0 | 0 | 0 | 0 | 20 | 22 | 4 | 0 | 0 | 80 | 295 | 290 | 212 | 8 | 133 | 26 | 55 | 0 | 51 | 0 | 0 | 50 | 19 | 8 | 33 | 16 | 132 | 94 | 65 | 0 | 2 | 44 | 42 | 5 | 0 | 163 | 270 | 31 | 76 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 123 | 14 | 90 | 102 | 2 | 367 | 100 | 90 | 89 | 3 | 0 | 54 | 17 | 17 | 113 | 100 | 350 | 50 | 40 | 78 | 100 | 0 | 20 | 23 |  | 836 | 0 | 330 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 58 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 130 | 0 | 170 | 0 | 80 | 0 | 201 | 0 | 353 | 105 | 0 | 27 | 0 | 102 | 0 | 7 | 25 | 480 | 0 | 0 | 0 |  | 7211 | 3320 | 10531 | 4771 | 836 | 1686 | 2273 | 704 | 20 | 20 | 132 | 89 | 0 | 0
16:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 365 | 182 |  | 0 | 270 | 240 | 0 | 0 | 30 | 180 | 0 | 100 | 60 | 58 | 16 | 10 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 24 | 25 | 25 | 42 | 0 | 20 | 0 | 100 | 0 | 16 | 203 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 48 | 40 | 21 | 7 | 0 | 0 | 80 | 295 | 300 | 208 | 8 | 133 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 16 | 122 | 106 | 73 | 0 | 1 | 44 | 42 | 8 | 0 | 130 | 270 | 31 | 75 | 0 | 122 | 0 | 0 | 0 | 290 | 0 | 5 | 0 | 105 | 0 | 0 | 0 | 0 | 126 | 8 | 100 | 102 | 73 | 315 | 85 | 90 | 102 | 1 | 0 | 54 | 11 | 17 | 75 | 100 | 350 | 90 | 26 | 90 | 101 | 0 | 36 | 11 |  | 835 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 62 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 100 | 0 | 167 | 0 | 32 | 0 | 197 | 0 | 401 | 53 | 0 | 35 | 0 | 50 | 0 | 6 | 35 | 500 | 0 | 0 | 0 |  | 7317 | 3204 | 10521 | 4655 | 835 | 1646 | 2447 | 723 | 20 | 20 | 122 | 53 | 0 | 0
17:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 362 | 162 |  | 0 | 270 | 235 | 0 | 0 | 30 | 210 | 0 | 123 | 50 | 58 | 32 | 10 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 24 | 25 | 25 | 42 | 0 | 20 | 0 | 100 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 36 | 0 | 51 | 50 | 21 | 16 | 0 | 0 | 80 | 295 | 295 | 208 | 8 | 134 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 16 | 122 | 125 | 73 | 0 | 1 | 44 | 42 | 7 | 0 | 163 | 272 | 31 | 50 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 105 | 0 | 0 | 3 | 0 | 132 | 3 | 100 | 115 | 145 | 316 | 85 | 90 | 105 | 1 | 0 | 54 | 17 | 17 | 55 | 50 | 350 | 66 | 11 | 90 | 116 | 0 | 36 | 6 |  | 835 | 0 | 295 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 100 | 0 | 167 | 0 | 32 | 0 | 171 | 0 | 392 | 35 | 0 | 35 | 0 | 37 | 0 | 4 | 35 | 480 | 0 | 0 | 0 |  | 7409 | 3071 | 10480 | 4680 | 835 | 1612 | 2411 | 702 | 20 | 72 | 122 | 26 | 0 | 0
18:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 325 | 151 |  | 0 | 270 | 275 | 0 | 0 | 30 | 180 | 0 | 75 | 50 | 58 | 32 | 10 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 24 | 25 | 25 | 25 | 0 | 20 | 0 | 100 | 0 | 16 | 205 | 0 | 80 | 0 |  | 24 | 0 | 68 | 0 | 51 | 50 | 21 | 19 | 0 | 0 | 80 | 260 | 260 | 190 | 8 | 134 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 16 | 136 | 113 | 73 | 0 | 0 | 44 | 43 | 8 | 0 | 130 | 272 | 31 | 50 | 0 | 122 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 135 | 0 | 0 | 24 | 0 | 132 | 0 | 60 | 145 | 150 | 316 | 85 | 90 | 100 | 0 | 0 | 54 | 17 | 17 | 55 | 50 | 350 | 55 | 2 | 90 | 116 | 0 | 36 | 1 |  | 836 | 0 | 270 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 25 | 11 | 18 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 80 | 0 | 153 | 0 | 33 | 0 | 170 | 0 | 362 | 35 | 0 | 35 | 0 | 38 | 0 | 2 | 35 | 480 | 0 | 0 | 0 |  | 7177 | 3037 | 10214 | 4359 | 836 | 1534 | 2497 | 702 | 20 | 125 | 136 | 5 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 80 | 0 | 305 | 162 |  | 0 | 270 | 235 | 0 | 0 | 40 | 210 | 0 | 150 | 70 | 58 | 64 | 10 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 13 | 25 | 25 | 25 | 0 | 20 | 0 | 100 | 0 | 17 | 210 | 0 | 80 | 0 |  | 23 | 0 | 68 | 0 | 61 | 50 | 21 | 22 | 0 | 0 | 80 | 340 | 330 | 208 | 8 | 134 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 154 | 121 | 73 | 14 | 0 | 44 | 42 | 8 | 0 | 130 | 272 | 31 | 60 | 0 | 162 | 18 | 0 | 0 | 310 | 16 | 5 | 0 | 178 | 0 | 0 | 70 | 0 | 132 | 0 | 100 | 161 | 150 | 420 | 85 | 90 | 105 | 0 | 0 | 54 | 17 | 52 | 61 | 80 | 380 | 70 | 0 | 122 | 116 | 0 | 36 | 0 |  | 835 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 32 | 65 | 33 | 80 | 0 | 0 | 0 | 50 | 0 | 74 | 24 | 0 | 18 | 25 | 38 | 18 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 87 | 0 | 159 | 0 | 92 | 0 | 171 | 0 | 379 | 37 | 0 | 50 | 0 | 106 | 0 | 0 | 35 | 480 | 65 | 0 | 10 |  | 8050 | 3532 | 11582 | 4832 | 835 | 1742 | 2982 | 701 | 20 | 316 | 154 | 0 | 0 | 76.02
19:30 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 390 | 172 |  | 0 | 270 | 235 | 0 | 0 | 55 | 212 | 0 | 150 | 100 | 64 | 100 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 13 | 25 | 25 | 35 | 0 | 20 | 0 | 90 | 0 | 17 | 203 | 0 | 135 | 0 |  | 24 | 0 | 68 | 0 | 80 | 50 | 21 | 16 | 0 | 0 | 80 | 305 | 290 | 215 | 8 | 133 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 19 | 148 | 124 | 73 | 14 | 0 | 44 | 42 | 40 | 0 | 163 | 270 | 32 | 77 | 0 | 203 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 161 | 150 | 367 | 108 | 90 | 105 | 0 | 0 | 54 | 17 | 91 | 113 | 100 | 380 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 835 | 0 | 245 | 0 | 83 | 0 | 0 | 0 | 7 | 0 | 32 | 50 | 34 | 80 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 31 | 52 | 42 | 18 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 95 | 0 | 164 | 0 | 96 | 50 | 178 | 0 | 352 | 105 | 0 | 51 | 0 | 113 | 0 | 0 | 109 | 540 | 79 | 0 | 17 |  | 8554 | 3882 | 12436 | 4884 | 835 | 1807 | 3583 | 761 | 20 | 398 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 371 | 182 |  | 0 | 270 | 230 | 0 | 0 | 55 | 180 | 0 | 115 | 100 | 72 | 64 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 24 | 25 | 25 | 36 | 0 | 20 | 0 | 90 | 0 | 17 | 203 | 0 | 135 | 0 |  | 24 | 0 | 68 | 0 | 85 | 50 | 22 | 20 | 0 | 0 | 80 | 305 | 275 | 211 | 8 | 134 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 148 | 138 | 73 | 14 | 0 | 43 | 42 | 50 | 0 | 163 | 272 | 32 | 77 | 0 | 223 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 216 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 161 | 150 | 367 | 108 | 90 | 105 | 0 | 0 | 54 | 17 | 114 | 113 | 100 | 380 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 835 | 0 | 245 | 0 | 83 | 0 | 0 | 0 | 6 | 0 | 32 | 54 | 33 | 80 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 31 | 52 | 41 | 18 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 93 | 0 | 164 | 0 | 97 | 50 | 180 | 0 | 353 | 105 | 0 | 108 | 0 | 113 | 0 | 0 | 113 | 540 | 78 | 0 | 17 |  | 8566 | 3945 | 12511 | 4832 | 835 | 1843 | 3712 | 761 | 20 | 360 | 148 | 0 | 0 | 76.03
21:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 383 | 180 |  | 0 | 270 | 235 | 0 | 0 | 55 | 217 | 0 | 155 | 100 | 72 | 48 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 25 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 17 | 215 | 0 | 135 | 0 |  | 24 | 0 | 68 | 0 | 91 | 50 | 22 | 26 | 0 | 0 | 80 | 335 | 305 | 189 | 8 | 133 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 158 | 133 | 73 | 14 | 0 | 44 | 42 | 53 | 0 | 163 | 271 | 31 | 78 | 0 | 223 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 161 | 150 | 400 | 115 | 90 | 105 | 0 | 0 | 54 | 17 | 52 | 113 | 100 | 380 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 835 | 0 | 240 | 0 | 85 | 0 | 0 | 0 | 5 | 0 | 32 | 65 | 33 | 64 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 30 | 52 | 41 | 18 | 0 | 11 | 70 | 0 | 150 | 0 | 0 | 80 | 0 | 170 | 0 | 97 | 74 | 180 | 0 | 406 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 550 | 77 | 0 | 17 |  | 8722 | 4012 | 12734 | 4999 | 835 | 1918 | 3692 | 770 | 20 | 342 | 158 | 0 | 0 | 76.02
22:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 394 | 140 |  | 0 | 270 | 230 | 0 | 0 | 55 | 219 | 0 | 155 | 100 | 72 | 48 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 25 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 17 | 208 | 0 | 135 | 0 |  | 24 | 0 | 68 | 0 | 91 | 50 | 22 | 28 | 0 | 0 | 80 | 310 | 295 | 174 | 8 | 134 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 158 | 134 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 274 | 31 | 77 | 0 | 223 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 160 | 150 | 384 | 115 | 90 | 105 | 0 | 0 | 54 | 17 | 52 | 113 | 100 | 380 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 836 | 0 | 225 | 0 | 90 | 0 | 0 | 0 | 5 | 0 | 32 | 65 | 34 | 64 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 30 | 52 | 41 | 22 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 80 | 0 | 167 | 0 | 97 | 98 | 180 | 0 | 408 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 550 | 71 | 0 | 17 |  | 8642 | 4026 | 12668 | 4928 | 836 | 1897 | 3716 | 771 | 20 | 342 | 158 | 0 | 0 | 75.98
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 381 | 140 |  | 0 | 270 | 225 | 0 | 0 | 55 | 219 | 0 | 150 | 100 | 72 | 48 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 25 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 17 | 204 | 0 | 135 | 0 |  | 23 | 0 | 68 | 0 | 91 | 50 | 22 | 29 | 0 | 0 | 80 | 265 | 265 | 175 | 8 | 132 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 162 | 135 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 273 | 32 | 77 | 0 | 189 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 160 | 150 | 365 | 115 | 90 | 105 | 0 | 0 | 54 | 17 | 52 | 113 | 100 | 380 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 836 | 0 | 215 | 0 | 96 | 0 | 0 | 0 | 5 | 0 | 32 | 60 | 33 | 80 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 30 | 52 | 41 | 22 | 0 | 11 | 71 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 97 | 98 | 180 | 0 | 373 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 9 | 0 | 35 |  | 8488 | 3951 | 12439 | 4757 | 836 | 1796 | 3756 | 770 | 20 | 342 | 162 | 0 | 0 | 75.98
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 365 | 140 |  | 0 | 270 | 225 | 0 | 0 | 55 | 224 | 0 | 95 | 100 | 72 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 25 | 25 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 68 | 0 | 91 | 50 | 22 | 29 | 0 | 0 | 80 | 260 | 265 | 185 | 8 | 132 | 26 | 57 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 19 | 156 | 140 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 270 | 33 | 77 | 0 | 190 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 120 | 0 | 100 | 100 | 150 | 367 | 115 | 90 | 90 | 0 | 0 | 54 | 17 | 52 | 111 | 100 | 380 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 836 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 32 | 50 | 33 | 64 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 71 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 70 | 180 | 0 | 280 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 37 | 0 | 17 |  | 8298 | 3695 | 11993 | 4685 | 836 | 1706 | 3599 | 720 | 20 | 271 | 156 | 0 | 0 | 75.98
KWH | 0 | 0 | 0 | 4315500 | 0 | 2232045 | 0 | 6963200 | 5188000 |  | 0 | 6383500 | 5628393 | 0 | 0 | 1074942 | 4889802 | 0 | 3213000 | 1246080 | 679824 | 415200 | 103733 | 0 | 0 | 0 | 505440 | 269149 | 863579 | 388764 | 600000 | 557100 | 661300 | 607900 | 391200 | 0 | 442080 | 0 | 2000000 | 0 | 277039 | 4908577 | 0 | 2993960 | 0 |  | 378720 | 0 | 821026 | 0 | 667200 | 585120 | 513600 | 502080 | 0 | 0 | 2013618 | 7236400 | 6630000 | 4943000 | 217454 | 3116950 | 579240 | 1080960 | 0 | 1009715 | 0 | 0 | 759571 | 470736 | 178560 | 818200 | 401390 | 3044160 | 3280200 | 1391040 | 167328 | 10500 | 1028000 | 1074480 | 571800 | 0 | 3451254 | 6013000 | 739680 | 1524480 | 0 | 3718480 | 249000 | 0 | 94140 | 7419000 | 207480 | 168000 | 0 | 2248145 | 0 | 0 | 614400 | 0 | 3119620 | 142020 | 2257920 | 2583360 | 1284654 | 8791000 | 1172400 | 1615200 | 2232254 | 26639 | 0 | 1298938 | 214945 | 422940 | 1570800 | 1977600 | 8668100 | 868080 | 273760 | 1478880 | 1999745 | 0 | 614520 | 207951 |  | 20171636 | 0 | 7929792 | 0 | 1529280 | 0 | 0 | 0 | 81600 | 0 | 164250 | 1519000 | 592182 | 642144 | 0 | 0 | 0 | 293072 | 0 | 538688 | 222500 | 0 | 150092 | 672480 | 230956 | 422160 | 0 | 215838 | 1756364 | 0 | 3663100 | 0 | 0 | 2545700 | 0 | 4187918 | 0 | 1971460 | 424320 | 4469527 | 0 | 9020600 | 1025760 | 0 | 776448 | 0 | 1001280 | 0 | 47185 | 728448 | 12400900 | 483000 | 0 | 122400 |  | 170558740 | 80000080 | 250558820 | 113973320 | 20171636 | 42163830 | 49704741 | 17820364 | 442080 | 2530634 | 3044160 | 708055 | 0
Fuel Cost | 0 | 0 | 0 | 6343785 | 0 | 2946299.4 | 0 | 7032832 | 5343640 |  | 0 | 6958015 | 6247516.23 | 0 | 0 | 9094009.32 | 5085394.08 | 0 | 5558490 | 9382982.4 | 6199994.88 | 4085568 | 956418.26 | 0 | 0 | 0 | 3689712 | 2080521.77 | 8514888.94 | 291573 | 450000 | 0 | 0 | 0 | 3782904 | 0 | 119361.6 | 0 | 3620000 | 0 | 2573692.31 | 5350348.93 | 0 | 5089732 | 0 |  | 0 | 0 | 7963952.2 | 0 | 5804640 | 4634150.4 | 647136 | 1491177.6 | 0 | 0 | 2960018.46 | 5354936 | 6630000 | 4547560 | 280515.66 | 3584492.5 | 654541.2 | 1513344 | 0 | 1726612.65 | 0 | 0 | 7253903.05 | 597834.72 | 133920 | 1431850 | 301042.5 | 22831200 | 3477012 | 12630643.2 | 212506.56 | 167370 | 1685920 | 1719168 | 1017804 | 0 | 3934429.56 | 6253520 | 1457169.6 | 2911756.8 | 0 | 6432970.4 | 545310 | 0 | 192045.6 | 7493190 | 155610 | 127680 | 0 | 16995976.2 | 0 | 0 | 3194880 | 0 | 30697060.8 | 1660213.8 | 18402048 | 28029456 | 9056810.7 | 8175630 | 10692288 | 15263640 | 19442932.34 | 0 | 0 | 11313749.98 | 1889366.55 | 4220941.2 | 13461756 | 13170816 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 116188623.36 | 0 | 8326281.6 | 0 | 12020140.8 | 0 | 0 | 0 | 855984 | 0 | 1711485 | 1716470 | 917882.1 | 6267325.44 | 0 | 0 | 0 | 2883828.48 | 0 | 4767388.8 | 1713250 | 0 | 1454391.48 | 6516331.2 | 2240273.2 | 810547.2 | 0 | 163389.366 | 10590874.92 | 0 | 19854002 | 0 | 0 | 2978469 | 0 | 5528051.76 | 0 | 2957190 | 7217683.2 | 5229346.59 | 0 | 8930394 | 10708934.4 | 0 | 7368491.52 | 0 | 7769932.8 | 0 | 521394.25 | 5383230.72 | 54439951 | 0 | 0 | 0 |  | 447222177.35 | 318031538.186 | 765253715.536 | 119849991.266 | 116188623.36 | 49424843.57 | 345354503.61 | 84884827.92 | 119361.6 | 24251386.16 | 22831200 | 2348978.05 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 217 | 202 |  | 0 | 270 | 260 | 0 | 0 | 30 | 214 | 0 | 180 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 4 | 204 | 0 | 140 | 0 |  | 5 | 0 | 0 | 0 | 0 | 18 | 22 | 4 | 0 | 0 | 80 | 280 | 265 | 212 | 8 | 127 | 26 | 54 | 0 | 10 | 0 | 0 | 3 | 19 | 5 | 33 | 12 | 110 | 146 | 65 | 0 | 1 | 43 | 42 | 5 | 0 | 163 | 250 | 31 | 75 | 0 | 122 | 0 | 0 | 0 | 310 | 0 | 5 | 0 | 88 | 0 | 0 | 0 | 0 | 133 | 20 | 100 | 100 | 0 | 366 | 0 | 90 | 91 | 5 | 0 | 54 | 4 | 0 | 17 | 100 | 350 | 0 | 35 | 0 | 58 | 0 | 18 | 17 |  | 836 | 0 | 355 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 62 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 110 | 0 | 170 | 0 | 96 | 0 | 201 | 0 | 406 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 400 | 0 | 0 | 0 |  | 9510 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 383 | 180 | 0 | 0 | 270 | 235 | 0 | 0 | 55 | 217 | 0 | 155 | 100 | 72 | 48 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 27 | 25 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 17 | 215 | 0 | 135 | 0 | 0 | 24 | 0 | 68 | 0 | 91 | 50 | 22 | 26 | 0 | 0 | 80 | 335 | 305 | 189 | 8 | 133 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 19 | 158 | 133 | 73 | 14 | 0 | 44 | 42 | 53 | 0 | 163 | 271 | 31 | 78 | 0 | 223 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 132 | 0 | 100 | 161 | 150 | 400 | 115 | 90 | 105 | 0 | 0 | 54 | 17 | 52 | 113 | 100 | 380 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 835 | 0 | 240 | 0 | 85 | 0 | 0 | 0 | 5 | 0 | 32 | 65 | 33 | 64 | 0 | 0 | 0 | 50 | 0 | 100 | 42 | 0 | 30 | 52 | 41 | 18 | 0 | 11 | 70 | 0 | 150 | 0 | 0 | 80 | 0 | 170 | 0 | 97 | 74 | 180 | 0 | 406 | 105 | 0 | 113 | 0 | 107 | 0 | 0 | 113 | 550 | 77 | 0 | 17 |  | 12734 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 412 | 250 | 0 | 0 | 280 | 240 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 22 | 0 | 80 | 0 | 17 | 225 | 0 | 130 | 0 | 0 | 22 |  | 68 | 0 | 90 | 43 | 22 | 20 | 0 | 0 | 80 | 330 | 330 | 220 | 8 | 130 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 188 | 160 | 74 | 19 | 0 | 43 | 42 | 51 | 0 | 163 | 275 | 32 | 78 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 160 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 116 | 0 | 36 |  |  | 857 | 0 | 350 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 65 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 29 | 52 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 10 | 130 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 80
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 360 | 250 | 0 | 0 | 280 | 240 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 22 | 0 | 80 | 0 | 17 | 225 | 0 | 130 | 0 | 0 | 22 |  | 68 | 0 | 90 | 43 | 22 | 15 | 0 | 0 | 80 | 330 | 330 | 220 | 8 | 130 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 160 | 74 | 19 | 1.6 | 43 | 42 | 51 | 0 | 163 | 275 | 32 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 250 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 160 | 150 | 400 | 115 | 105 | 90 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 116 | 0 | 36 | 30 |  | 857 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 65 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 29 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 130 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 339 | 153 | 0 | 0 | 270 | 235 | 0 | 0 | 40 | 219 | 0 | 94 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 |  | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 208 | 0 | 130 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 80 | 260 | 270 | 214 | 8 | 133 | 23 | 30 | 0 | 10 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 120 | 147 | 65 | 17 | 1 | 43 | 42 | 11 | 0 | 163 | 274 | 20 | 10 | 0 | 215 | 18 | 0 | 6 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 10 | 100 | 100 | 0 | 378 | 16 | 65 | 89 | 3 | 0 | 54 | 0 | 0 | 46 | 100 | 400 | 0 | 27 | 0 | 90 | 0 | 36 | 13 | 0 | 842 | 0 | 235 | 0 | 66 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 90 | 0 | 139 | 0 | 95 | 0 | 143 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 440 | 6 | 0 | 0 | 0
199
| Minimum Generation |  | 8185 | 7:00
| Highest Generation |  | 12734 | 21:00
| Day Peak Generation |  | 9510 | 12:00
| Evening Peak Generation |  | 12734 | 21:00
| HVDC Max Flow |  | 836 | 1:00
| HVDC EvPeak Flow |  | 835 | 21:00
| Load factor L.F |  | 81.98%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-09
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9510 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8936 | MW
Evening Peak Generation : |  | 12734 | MW Hour : | 21:00 | Available Max Generation : |  | 15780 | MW
E.P. Demand (at gen end) : |  | 12734 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12734 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2780 | MW
Total Gen. (MKWH) : |  | 250.5588 | System Load Factor : | 81.98% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | 5 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-09
Actual : | 75.98 | Ft.(MSL) , | Rule curve : | 80.48 | Ft.( MSL )
Gas Consumed : | Total = | 1290.42 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 169274834.836
: |  | Coal : | 84884827.92 | Oil : | 369605889.77 | Total : | 623765552.526
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4607.3116 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1571.5214 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1408.8829 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1273.347 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1150.5385 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 928.4559 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.9952 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.8896 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 716.1007 |  |  | 0 | 0%
Total | 0 |  | 12408.0428 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Agargaon 230 kV Ckt-1 was under shut down from 09:52 to 12:13 for D/W.
b) Bogura 230/132 kV T1 transformer tripped at 09:25 showing lockout and was switched on at 09:45.
c) Bogura 132/33 kV T3 transformer is under shut down since 10:20 for C/M.
d) Chowmuhuni 132/33 kV T2 transformer was under shut down from 08:48 to 10:48 for C/M.
e) Fenchuganj 132 kV Bus-1 was under shut down from 08:40 to 22:25 for D/W.
f) Gopalganj(N)-Madaripur 132 kV Ckt-1 was under shut down from 08:15 to 11:14 for C/M.
g) Hathazari-Baroiarhat 132 kV Ckt-2 was under shut down from 09:24 to 15:21 for C/M.
h) Rajshahi 132/33 kV T3 transformer was under shut down from 12:05 to 16:20 for protection test.
i) Rampura 132 kV Bus-1 is under shut down since 10:07 for D/W.
j) Sitalakha 132/33 kV GT1 transformer is under shut down since 09:38 for C/M.
k) Sreemangal-Fenchuganj 132 kV Ckt-1 was under shut down from 08:29 to 18:17 for D/W.
l) Keraniganj 230/132 kV ATR1 transformer was under shut down from 10:45 to 11:41 for oil leakage maintenance.
m) Narail 132/33 kV T2 transformer was under shut down from 14:15 to 15:38 for C/M.
n) Raozan Unit-1 was tripped at 14:15 due to Boiler trip and was synchronized at 14:53.
o) Barapukuria-Saidpur 132 kV Ckt-2 was under shut down from 00:02(09/05/2021) to 02:48(09/05/2021) for R/H.
p) Bogura 132/33 kV T1 transformer is under shut down since 07:01(09/05/2021) for C/M. |  |  |  |  | About 52 MW power interruption has been running under Bogura S/S area
since 07:01(09/05/2021).
q) Netrokona 132/33 kV T1 transformer is under shut down since 07:16(09/05/2021) for C/M.
r) Gopalganj-Madaripur 132 kV Ckt-2 is under shutdown since 07:19(09/05/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2232045
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 383 | 6963200 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 180 | 5188000 | Gas Shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6383500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 235 | 5628393 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1074942
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 103733 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 388764
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 155 | 3213000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1246080
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 217 | 4889802 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 679824 | High voltage
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 505440 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 415200 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 269149 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 863579
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1157100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 661300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 607900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 391200 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 2248145 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 3119620 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1615200 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 868080 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1478880
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 207951
| Dhaka area Total |  |  |  | 5829 | 3019 | 56715527
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2000000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 277039 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 142020
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 585120
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 442080 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 215 | 4908577 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 135 | 2993960
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2232254
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 821026 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2257920
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 513600
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 502080
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 91 | 667200 | Engine problem
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26639
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1298938
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 214945 | Transformer O/L
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1977600
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1999745
| Chattogram area Total |  |  |  | 2382 | 1226 | 23860743
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2013618 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 189 | 4943000 | Gas shortage
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7236400 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6630000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 579240 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1080960
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1009715
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 1284654
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 133 | 3116950 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 161 | 2583360 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 470736
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 178560
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 158 | 3044160
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 818200
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 759571
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 401390 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 422940 | Low demand
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1570800
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 614520 | 33 kV feeder fault
| Cumilla Area Total |  |  |  | 3034 | 1986 | 38976228
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 133 | 3280200 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 167328 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 73 | 1391040 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10500
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 100 | 614400 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1172400
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 273760
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 378720
| Mymensingh Area Total |  |  |  | 709 | 459 | 7288348
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1028000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1074480 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3451254
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 271 | 6013000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 571800
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 168000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 31 | 739680 | Engine problem
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1524480 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 223 | 3718480
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 249000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 207480 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7419000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 8791000
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 94140 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 380 | 8668100 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2032 | 43717894
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 835 | 20171636
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 85 | 1529280 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 5 | 81600 | Engine problem
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 240 | 7929792 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 164250 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 74 | 424320 | Low demand
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1025760
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1376 | 31326638
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 642144 | Line O/L
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 592182
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1519000 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1971460
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 12400900
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 77 | 483000 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 122400 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 903 | 17731086
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 293072
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 222500 | Engine problem
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 150092 | Engine problem
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 80 | 2545700 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4187918 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4469527 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 406 | 9020600 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 230956 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 422160 | Machine problem
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 215838
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 672480
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 100 | 538688
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 776448
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 728448
| Rajshahi Area Total |  |  |  | 2173 | 1406 | 24474427
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 70 | 1756364
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3663100 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 107 | 1001280
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47185
| Rangpur Area Total |  |  |  | 605 | 327 | 6467929
| Total |  |  |  | 21219 | 12734 | 250558820
| Eastern Grid Total |  |  |  | 14331 | 8722 | 170558740
| Western Grid Total |  |  |  | 6888 | 4012 | 80000080
| National Grid Total |  |  |  | 21219 | 12734 | 250558820
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-08
(a) ENTIRE EASTERN GRID : |  | 8411 | MW | (b) ENTIRE WESTERN GRID : |  | 3733 | MW
i) Dhaka area |  | 4349 | MW | i) Khulna area |  | 1594 | MW
ii) Chittagong area |  | 1353 | MW | ii) Rajshahi area |  | 1164 | MW
iii) Comilla area |  | 1244 | MW | iii) Barisal area |  | 355 | MW
iv) Mymensingh area |  | 979 | MW | iv) Rangpur area |  | 620 | MW
v) Sylhet area |  | 486 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12144 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 11:00 | Netrokona | 102 | 19:30 | Benapol | 54 | 21:00
Munsiganj | 108 | 21:00 | Jamalpur | 118 | 0:00 | Jhenida | 117 | 21:00
Sonargaon | 74 | 0:00 | Sherpur | 102 | 19:30 | Bottail | 128 | 20:00
Shyampur | 190 | 9:00 | Srimongal | 50 | 21:00 | G.K Project | 55 | 22:00
Bhulta | 193 | 22:00 | Shahjibazar | 120 | 23:00 | Faridpur | 202 | 21:00
Madanganj | 50 | 2:00 | Fenchuganj | 38 | 19:00 | Madaripur | 101 | 20:00
Shitalakhya | 114 | 15:00 | Kulawara | 43 | 19:00 | Sariatpur | 68 | 21:00
Rahim steel | 32 | 13:00 | Sylhet | 112 | 20:00 | Gopalganj | 92 | 21:00
Matuail | 58 | 15:00 | Chatak | 26 | 21:00 | Bagerhat | 107 | 22:00
Ghorasal | 72 | 23:00 | Sunamganj | 42 | 21:00 | Mongla | 40 | 14:00
Narsingdi | 172 | 23:00 | Biani Bazar | 65 | 21:00 | Satkhira | 128 | 22:00
Haripur (SBU) | 114 | 19:30 | Comilla (S) | 162 | 23:00 | Gallamari | 41 | 19:30
Sreenagar | 42 | 21:00 | Comilla(N) | 147 | 21:00 | Magura | 56 | 20:00
Ullon | 80 | 19:30 | Chandpur | 74 | 21:00 | Norail | 44 | 19:30
Hasnabad | 76 | 4:00 | Feni | 129 | 20:00 | Chuadanga | 92 | 23:00
Magbazar | 73 | 15:00 | Chowmuhani | 180 | 20:00 | Borguna | 16 | 19:30
Maniknagar | 62 | 20:00 | Ashuganj | 42 | 1:00 | Barisal(N) | 43 | 21:00
Bangabhaban | 10 | 11:00 | Daudkandi | 154 | 21:00 | Barisal (S) | 104 | 19:30
Narinda | 52 | 11:00 | B.Baria | 167 | 21:00 | Patuakhali | 104 | 22:00
Dhanmondi | 166 | 15:00 | Ramganj | 96 | 21:00 | Bhandaria | 52 | 19:30
Lalbag | 81 | 13:00 | Chaddagram | 42 | 19:30 | Borhan Uddin | 37 | 21:00
Madartek | 75 | 22:00 | PHP | 10 | 17:00 | Ishurdi | 65 | 1:00
Dhaka University | 36 | 13:00 | Kochua | 70 | 19:00 | Ruppur Paromanobik | 3 | 16:00
Aftabnagar | 10 | 19:00 | Madunaghat | 65 | 13:00 | Natore | 125 | 19:30
Fatullah | 60 | 10:00 | Hathazari | 94 | 19:00 | Bogra | 130 | 20:00
Nawabganj | 52 | 20:00 | Khulshi | 221 | 15:00 | Noagaon | 101 | 20:00
Keraniganj | 73 | 21:00 | Halishahar | 140 | 14:00 | Rajshahi | 125 | 21:00
Mirpur | 109 | 15:00 | Baraulia | 143 | 3:00 | Rajshahi New | 16 | 3:00
Kalyanpur | 114 | 21:00 | Sikalbaha | 35 | 23:00 | C.Nawabganj | 62 | 20:00
Gulshan | 104 | 14:00 | Dohazari | 88 | 21:00 | Amnura | 42 | 3:00
Uttara | 85 | 19:30 | Cox'sbazar | 104 | 21:00 | Pabna | 102 | 21:00
Uttara New | 28 | 19:30 | Chandraghona | 30 | 19:00 | Shahjadpur | 103 | 19:30
Kamrangirchar | 83 | 15:00 | Kaptai | 4 | 19:00 | Serajganj | 77 | 21:00
Savar | 165 | 15:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 49 | 21:00
Bhasantec | 140 | 20:00 | Bakulia | 105 | 19:30 | Joypurhat | 48 | 21:00
Agargaon | 64 | 15:00 | Julda | 22 | 11:00 | Sherpur(Bogura) | 52 | 20:00
Satmosjid | 95 | 19:30 | TK chemical | 30.5 | 1:00 | Mohastangor | 64 | 20:00
Tongi | 117 | 24:00 | Modern Steel |  |  | Bangura | 32 | 19:30
Kabirpur | 232 | 15:00 | Shahmirpur | 28 | 0:00 | Rangpur | 107 | 20:00
Basundhara | 159 | 19:30 | Khagrachhari | 26 | 18:30 | Lalmonirhat | 33 | 19:30
Manikganj | 76 | 24:00 | Matarbari | 40 | 19:30 | Saidpur | 89 | 20:00
Joydevpur | 163 | 22:00 | Baroiar Hat | 44 | 21:00 | Purbasadipur | 94 | 20:00
New Tongi | 99 | 12:00 | Rangamati | 12 | 19:00 | Thakurgaon | 73 | 19:30
Kodda | 254 | 11:00 | Abul Khair 230 | 140 | 4:00 | Palashbari | 96 | 19:30
Dhamrai | 98 | 24:00 | BSRM | 159 | 19:00 | Barapukuria | 50 | 19:30
Rajendrapur | 104 | 22:00 | GPH Ispat | 89 | 16:00 | Panchagar | 43 | 19:30
Valuka | 120 | 15:00 | Goalpara | 27 | 1:00 | Joldhaka | 42 | 19:30
Tangail | 229 | 21:00 | Central s/s | 93 | 19:30 | Kurigram | 46 | 20:00
Mymensing | 198 | 21:00 | Noapara | 56 | 19:30 | Mithapukur | 32 | 21:00
Kishoreganj | 132 | 19:30 | Jessore | 121 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 20:00 | 396 | 11:00 | Kaliakoir | 384 | 0.20833 | 370 | 0.58333
| Bheramara | 399 | 18:30 | 392 | 24:00 | Bhulta | 378 | 0.8125 | 360 | 0.45833
| Ashuganj(N) | 384 | 18:30 | 367 | 12:00 | Gopalganj | 408 | 0.625 | 384 | 0.66667
| Payra | 409 | 24:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 220 | 9:00 | Hathazari | 218 | 22:00 | 208 | 15:00
| Ishurdi | 235 | 18:30 | 225 | 11:00 | Megnaghat | 224 | 19:00 | 220 | 8:00
| Ashuganj | 235 | 19:00 | 225 | 12:00 | Fenchuganj | 238 | 3:00 | 234 | 11:00
| Serajganj | 231 | 24:00 | 225 | 12:00 | Siddhirganj | 224 | 18:30 | 214 | 13:00
| Baghabari | 233 | 23:00 | 226 | 11:00 | Maniknagar | 223 | 18:30 | 213 | 11:00
| Barapukuria | 236 | 7:00 | 230 | 13:00 | Agargaon | 220 | 9:00 | 208 | 11:00
| Bogra | 229 | 24:00 | 220 | 13:00 | Barisal | 245 | 20:00 | 232 | 16:00
| Rajshahi | 234 | 23:00 | 222 | 3:00 | Bhola 225 MW | 249 | 5:00 | 235 | 15:00
| Khulna South | 225 | 24:00 | 208 | 11:00 | AKSML | 219 | 20:00 | 209 | 5:00
| Rampura | 222 | 22:00 | 214 | 11:00 | BSRM | 219 | 18:30 | 207 | 7:00
| Haripur | 221 | 19:00 | 212 | 11:00 | Bibiyana | 238 | 18:30 | 234 | 14:00
| Hasnabad | 220 | 1:00 | 212 | 13:00 | Bhulta | 226 | 20:00 | 214 | 11:00
| Shyampur | 220 | 24:00 | 220 | 11:00 | Ashuganj (S) | 233 | 18:30 | 223 | 12:00
| Aminbazar | 221 | 1:00 | 210 | 2:00 | Kaliakoir | 224 | 18:30 | 212 | 10:00
| Tongi | 221 | 23:00 | 207 | 12:00 | GPH | 218 | 5:00 | 206 | 7:00
| Comilla (N) | 225 | 20:00 | 216 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 18:30 | 126 | 11:00 | Madanhat | 130 | 0.83333 | 124 | 0.25
| Munsiganj | 134 | 18:30 | 124 | 10:00 | Hathazari | 130 | 0.83333 | 125 | 0.625
| Sonargaon | 134 | 18:30 | 124 | 10:00 | Khulshi | 127 | 0.8125 | 122 | 0.25
| Shyampur | 133 | 18:30 | 126 | 10:00 | Halishahar | 129 | 0.8125 | 120 | 0.29167
| Bhulta | 125 | 18:30 | 117 | 11:00 | Baraulia | 128 | 0.8125 | 122 | 0.25
| Madanganj | 132 | 5:00 | 122 | 10:00 | Sikalbaha | 130 | 0.5 | 124 | 0.20833
| Shitalakhya | 140 | 18:30 | 127 | 14:00 | Dohazari | 125 | 0.75 | 120 | 0.25
| Rahim steal | 133 | 19:00 | 126 | 11:00 | Cox'sbazar | 116 | 0.45833 | 108 | 0.041667
| Matuail | 134 | 18:30 | 126 | 11:00 | Chandraghona | 128 | 0.77083 | 123 | 0.29167
| Ghorasal | 136 | 1:00 | 130 | 13:00 | Kaptai | 127 | 0.375 | 126 | 0.041667
| Narsinghdi | 132 | 5:00 | 126 | 21:00 | A. Khaer Stl. | 126 | 0.8125 | 122 | 0.54167
| Haripur (SBU) | 132 | 3:00 | 126 | 11:00 | Bakulia | 128 | 0 | 122 | 0.29167
| Sreenagar | 127 | 18:30 | 118 | 11:00 | Julda | 128 | 0.041667 | 122 | 0.29167
| Ullon | 132 | 24:00 | 123 | 14:00 | TK Chemical | 129 | 0 | 123 | 0.25
| Hasnabad | 137 | 19:00 | 128 | 9:00 | Modern Steel
| Magbazar | 131 | 1:00 | 122 | 14:00 | Shahmirpur | 130 | 0.83333 | 124 | 0.45833
| Maniknagar | 133 | 1:00 | 127 | 14:00 | Khagrachhari | 127 | 0.77083 | 122 | 0.29167
| Bangabhaban | 133 | 1:00 | 127 | 14:00 | Matarbari | 122 | 0.91667 | 112 | 0.875
| Narinda | 133 | 1:00 | 127 | 14:00 | Baroiar Hat | 130 | 0.83333 | 122 | 0.20833
| Dhanmondi | 132 | 24:00 | 123 | 14:00 | Rangamati | 128 | 0.77083 | 123 | 0.29167
| Lalbag | 137 | 18:30 | 127 | 12:00 | Goalpara S/S | 134 | 1:00 | 124 | 11:00
| Madartek | 131 | 2:00 | 123 | 13:00 | Khulna Central S/S | 134 | 15:00 | 124 | 11:00
| Dhaka University | 131 | 1:00 | 123 | 13:00 | Noapara | 131 | 14:00 | 121 | 0.45833
| Aftabnagar | 131 | 1:00 | 124 | 11:00 | Jessore | 123 | 3:00 | 117 | 0.45833
| Fatullah | 134 | 18:30 | 126 | 11:00 | Benapol | 124 | 5:00 | 115 | 0.875
| Nawabganj | 126 | 18:30 | 119 | 10:00 | Jhenida | 121 | 9:00 | 106 | 0.875
| Keraniganj | 127 | 19:30 | 120 | 11:00 | Bottail | 128 | 0.29167 | 119 | 0.875
| Mirpur | 133 | 24:00 | 123 | 11:00 | G.K Project | 137 | 18:30 | 133 | 0.875
| Kalyanpur | 134 | 18:30 | 124 | 11:00 | Faridpur | 136 | 0.91667 | 126 | 0.875
| Gulshan | 131 | 24:00 | 123 | 11:00 | Madaripur | 139 | 0.25 | 130 | 0.58333
| Uttara | 132 | 18:30 | 123 | 10:00 | Shariyatpur S/S | 137 | 0.20833 | 130 | 0.66667
| Uttara New | 133 | 24:00 | 124 | 10:00 | Gopalganj | 142 | 0.20833 | 134 | 0.58333
| Kamrangirchar | 136 | 20:00 | 127 | 12:00 | Bagerhat | 131 | 1:00 | 118 | 0.45833
| Savar | 135 | 19:30 | 122 | 10:00 | Mongla | 131 | 0.58333 | 119 | 0.45833
| Bhasantec | 131 | 24:00 | 123 | 11:00 | Satkhira | 132 | 15:00 | 122 | 0.45833
| Agargaon | 132 | 24:00 | 124 | 12:00 | Gallamari | 135 | 15:00 | 125 | 0.45833
| Satmosjid | 132 | 24:00 | 124 | 12:00 | Magura | 120 | 6:00 | 103 | 21:00
| Tongi | 135 | 20:00 | 125 | 12:00 | Narail | 120 | 0.25 | 104 | 21:00
| Kabirpur | 135 | 1:00 | 129 | 14:00 | Chuadanga | 118 | 6:00 | 94 | 0.875
| Basundhara | 134 | 24:00 | 123 | 14:00 | Borguna | 137 | 0.5 | 127 | 0.70833
| Manikganj | 136 | 18:00 | 127 | 11:00 | Barisal(N) | 138 | 3:00 | 130 | 0.66667
| Joydevpur | 138 | 19:30 | 127 | 10:00 | Barisal (S) | 138 | 4:00 | 129 | 0.625
| New Tongi | 135 | 18:30 | 124 | 11:00 | Patuakhali(S) | 137 | 12:00 | 129 | 17:00
| Kodda | 134 | 20:00 | 120 | 11:00 | Bhandaria | 135 | 0.375 | 127 | 0.875
| Dhamrai | 134 | 5:00 | 127 | 14:00 | Ishurdi | 136 | 0.77083 | 130 | 0.45833
| Rajendrapur | 131 | 19:00 | 119 | 12:00 | Ruppur Paromanobik | 134 | 0.25 | 130 | 0.54167
| Valuka | 125 | 6:00 | 115 | 14:00 | Natore | 135 | 18:30 | 129 | 13:00
| Tangail | 132 | 5:00 | 122 | 21:00 | Bogra | 136 | 7:00 | 129 | 13:00
| Mymensing | 127 | 3:00 | 119 | 21:00 | Noagaon | 133 | 7:00 | 124 | 13:00
| Kishorganj | 130 | 1:00 | 122 | 21:00 | Rajshahi | 133 | 18:30 | 127 | 13:00
| Netrokona | 129 | 7:00 | 116 | 21:00 | Rajshahi New | 133 | 19:00 | 127 | 1:00
| Jamalpur | 134 | 0:00 | 125 | 7:00 | C.Nawabganj | 135 | 18:30 | 126 | 1:00
| Sherpur | 135 | 18:30 | 122 | 12:00 | Amnura | 136 | 20:00 | 123 | 1:00
| Srimongal | 137 | 4:00 | 133 | 21:00 | Pabna | 134 | 18:30 | 127 | 14:00
| Shahjibazar | 136 | 8:00 | 131 | 21:00 | Shahjadpur | 137 | 18:30 | 132 | 10:00
| Fenchuganj | 137 | 5:00 | 130 | 10:00 | Serajganj | 134 | 19:30 | 129 | 14:00
| Khulawara | 136 | 6:00 | 133 | 14:00 | Niyamatpur | 134 | 6:00 | 123 | 13:00
| Sylhet | 134 | 7:00 | 131 | 19:00 | Joypurhat | 135 | 7:00 | 125 | 13:00
| Chatak | 136 | 7:00 | 129 | 21:00 | Sherpur(Bogura) | 134 | 7:00 | 129 | 13:00
| Sunamganj | 136 | 6:00 | 127 | 21:00 | Mohastangor | 135 | 8:00 | 128 | 13:00
| Biani Bazar | 136 | 6:00 | 128 | 18:30 | Bangura | 135 | 15:00 | 132 | 1:00
| Comilla(s) | 127 | 5:00 | 121 | 21:00 | Rangpur | 134 | 7:00 | 124 | 13:00
| Comilla(n) | 134 | 19:30 | 128 | 13:00 | Lalmonirhat | 135 | 6:00 | 125 | 18:00
| Chandpur | 133 | 19:30 | 128 | 23:00 | Saidpur | 134 | 6:00 | 124 | 14:00
| Feni | 130 | 19:30 | 128 | 23:00 | Purbasadipur | 133 | 6:00 | 118 | 19:30
| Chowmuhani | 130 | 20:00 | 122 | 7:00 | Thakurgaon | 132 | 5:00 | 116 | 19:30
| Ashuganj | 137 | 18:30 | 135 | 21:00 | Palashbari | 134 | 8:00 | 120 | 21:00
| Daudkandi | 128 | 18:00 | 127 | 19:00 | Barapukuria | 136 | 7:00 | 130 | 13:00
| B.Baria | 134 | 9:00 | 128 | 21:00 | Panchagar | 132 | 6:00 | 113 | 19:30
| Ramganj | 130 | 20:00 | 123 | 6:00 | Joldhaka | 133 | 6:00 | 120 | 19:00
| Chaddagram | 132 | 20:00 | 123 | 11:00 | Kurigram | 133 | 7:00 | 122 | 18:00
| PHP | 130 | 20:00 | 120 | 7:00 | Mithapukur | 134 | 0.33333 | 126 | 0.54167

## L-Curve
Date | 2021-05-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 150 | 8298 | 3695 | 11993 |  |  |  | QF-LDC-11
0:30 | 255 | 7665 | 3538.5 | 11203.5 | Date: | 2021-05-08
1:00 | 360 | 7032 | 3382 | 10414
1:30 | 310 | 7036.5 | 3332.5 | 10369
2:00 | 260 | 7041 | 3283 | 10324
2:30 | 270 | 7036.5 | 3288 | 10324.5 | [5 empty] | Gen. at Eve. Peak | 12734 | 12734 MW (21:00 )
3:00 | 280 | 7032 | 3293 | 10325 | [6 empty] | 21:00
3:30 | 395 | 6817.5 | 3250 | 10067.5 | [5 empty] | Gen. at Day Peak | 9510 | 9510 MW (12:00 )
4:00 | 510 | 6603 | 3207 | 9810 | [6 empty] | 12:00
4:30 | 515 | 6243.5 | 3055.5 | 9299 | [5 empty] | Highest Generation | 12734
5:00 | 520 | 5884 | 2904 | 8788 | [6 empty] | 21:00
5:30 | 520 | 5737.5 | 2755.5 | 8493
6:00 | 520 | 5591 | 2607 | 8198
6:30 | 580 | 5544 | 2647.5 | 8191.5
7:00 | 640 | 5497 | 2688 | 8185
7:30 | 636 | 5526 | 2680 | 8206
8:00 | 632 | 5555 | 2672 | 8227
8:30 | 596 | 5725 | 2696 | 8421
9:00 | 560 | 5895 | 2720 | 8615
9:30 | 556 | 6001.5 | 2741 | 8742.5
10:00 | 552 | 6108 | 2762 | 8870
10:30 | 542 | 6231 | 2800 | 9031
11:00 | 532 | 6354 | 2838 | 9192
11:30 | 556 | 6426.5 | 2924.5 | 9351
12:00 | 580 | 6499 | 3011 | 9510
12:30 | 490 | 6650.5 | 3061.5 | 9712
13:00 | 400 | 6802 | 3112 | 9914
13:30 | 464 | 6941.5 | 3162.5 | 10104
14:00 | 528 | 7081 | 3213 | 10294
14:30 | 504 | 7146 | 3266.5 | 10412.5
15:00 | 480 | 7211 | 3320 | 10531
15:30 | 410 | 7264 | 3262 | 10526
16:00 | 340 | 7317 | 3204 | 10521
16:30 | 295 | 7363 | 3137.5 | 10500.5
17:00 | 250 | 7409 | 3071 | 10480
17:30 | 200 | 7293 | 3054 | 10347
18:00 | 150 | 7177 | 3037 | 10214
18:30 | 77.5 | 7613.5 | 3284.5 | 10898
19:00 | 5 | 8050 | 3532 | 11582
19:30 | 16 | 8554 | 3882 | 12436
20:00 | 21 | 8566 | 3945 | 12511 |  |  |  | Executive Engineer
20:30 | 25.5 | 8644 | 3978.5 | 12622.5 |  |  |  | Network Operation Division
21:00 | 30 | 8722 | 4012 | 12734
21:30 | 71 | 8682 | 4019 | 12701
22:00 | 112 | 8642 | 4026 | 12668 |  |  |  |  | Page 6 of 7
22:30 | 151 | 8565 | 3988.5 | 12553.5
23:00 | 190 | 8488 | 3951 | 12439
23:30 | 170 | 8393 | 3823 | 12216
24:00 | 150 | 8298 | 3695 | 11993
12734 MW (21:00 )
9510 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-08 |  | Energy | 250558820
[11 empty] | 2021-05-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4685 | 836 | 1706 | 3756 | 720 | 20 | 271 | 0 | 156 | 0
0:30 | 4762 | 836 | 1810 | 2781.5 | 755.5 | 20.5 | 171.5 | 0 | 145 | 0 | Date: | 2021-05-08
1:00 | 4839 | 836 | 1914 | 1807 | 791 | 21 | 72 | 0 | 134 | 0
1:30 | 4842.5 | 835.5 | 1895.5 | 1789 | 780.5 | 21 | 72 | 0 | 133 | 0 | [7 empty] | Total Energy | 250.5588 | Total Energy Gen 250.559 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 250.559 MKWHr
2:00 | 4846 | 835 | 1877 | 1771 | 770 | 21 | 72 | 0 | 132 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4842.5 | 835 | 1875.5 | 1776 | 770 | 21.5 | 72 | 0 | 132 | 0 | [7 empty] | Energy Requirement | 250.5588
3:00 | 4839 | 835 | 1874 | 1781 | 770 | 22 | 72 | 0 | 132 | 0
3:30 | 4864.5 | 835.5 | 1905 | 1469 | 770.5 | 22 | 72 | 0 | 129 | 0 | [6 empty] | Shortage
4:00 | 4890 | 836 | 1936 | 1157 | 771 | 22 | 72 | 0 | 126 | 0
4:30 | 4795 | 836 | 1782 | 966.5 | 721.5 | 22 | 55 | 0 | 121 | 0
5:00 | 4700 | 836 | 1628 | 776 | 672 | 22 | 38 | 0 | 116 | 0
5:30 | 4548 | 836 | 1582 | 727.5 | 647.5 | 22 | 21 | 0 | 107 | 2
6:00 | 4396 | 836 | 1536 | 679 | 623 | 22 | 4 | 0 | 98 | 4
6:30 | 4360.5 | 836 | 1552.5 | 687 | 623.5 | 22 | 4 | 0 | 95 | 11 |  |  |  |  | Coal
7:00 | 4325 | 836 | 1569 | 695 | 624 | 22 | 4 | 0 | 92 | 18
7:30 | 4294.5 | 835.5 | 1549 | 755 | 623.5 | 22 | 4 | 0 | 95 | 27.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4264 | 835 | 1529 | 815 | 623 | 22 | 4 | 0 | 98 | 37
8:30 | 4299 | 835.5 | 1572 | 920.5 | 622.5 | 22 | 4 | 0 | 102 | 43.5
9:00 | 4334 | 836 | 1615 | 1026 | 622 | 22 | 4 | 0 | 106 | 50
9:30 | 4438.5 | 836 | 1604 | 1055.5 | 622.5 | 22.5 | 4 | 0 | 98 | 61.5
10:00 | 4543 | 836 | 1593 | 1085 | 623 | 23 | 4 | 0 | 90 | 73
10:30 | 4586.5 | 835.5 | 1656.5 | 1115 | 623 | 23 | 4 | 0 | 98 | 89.5
11:00 | 4630 | 835 | 1720 | 1145 | 623 | 23 | 4 | 0 | 106 | 106
11:30 | 4658 | 835.5 | 1728.5 | 1276 | 623.5 | 22.5 | 4 | 0 | 108 | 95
12:00 | 4686 | 836 | 1737 | 1407 | 624 | 22 | 4 | 0 | 110 | 84
12:30 | 4789.5 | 836 | 1739.5 | 1481 | 639 | 21.5 | 4 | 0 | 115 | 86.5
13:00 | 4893 | 836 | 1742 | 1555 | 654 | 21 | 4 | 0 | 120 | 89
13:30 | 4893 | 836 | 1742 | 1555 | 654 | 21 | 4 | 0 | 120 | 89
14:00 | 4893 | 836 | 1742 | 1555 | 654 | 21 | 4 | 0 | 120 | 89
14:30 | 4832 | 836 | 1714 | 1914 | 679 | 20.5 | 12 | 0 | 126 | 89
15:00 | 4771 | 836 | 1686 | 2273 | 704 | 20 | 20 | 0 | 132 | 89
15:30 | 4713 | 835.5 | 1666 | 2360 | 713.5 | 20 | 20 | 0 | 127 | 71
16:00 | 4655 | 835 | 1646 | 2447 | 723 | 20 | 20 | 0 | 122 | 53
16:30 | 4667.5 | 835 | 1629 | 2429 | 712.5 | 20 | 46 | 0 | 122 | 39.5
17:00 | 4680 | 835 | 1612 | 2411 | 702 | 20 | 72 | 0 | 122 | 26
17:30 | 4519.5 | 835.5 | 1573 | 2454 | 702 | 20 | 98.5 | 0 | 129 | 15.5
18:00 | 4359 | 836 | 1534 | 2497 | 702 | 20 | 125 | 0 | 136 | 5
18:30 | 4595.5 | 835.5 | 1638 | 2739.5 | 701.5 | 20 | 220.5 | 0 | 145 | 2.5
19:00 | 4832 | 835 | 1742 | 2982 | 701 | 20 | 316 | 0 | 154 | 0
19:30 | 4884 | 835 | 1807 | 3583 | 761 | 20 | 398 | 0 | 148 | 0
20:00 | 4832 | 835 | 1843 | 3712 | 761 | 20 | 360 | 0 | 148 | 0
20:30 | 4915.5 | 835 | 1880.5 | 3702 | 765.5 | 20 | 351 | 0 | 153 | 0
21:00 | 4999 | 835 | 1918 | 3692 | 770 | 20 | 342 | 0 | 158 | 0
21:30 | 4963.5 | 835.5 | 1907.5 | 3704 | 770.5 | 20 | 342 | 0 | 158 | 0
22:00 | 4928 | 836 | 1897 | 3716 | 771 | 20 | 342 | 0 | 158 | 0
22:30 | 4842.5 | 836 | 1846.5 | 3736 | 770.5 | 20 | 342 | 0 | 160 | 0
23:00 | 4757 | 836 | 1796 | 3756 | 770 | 20 | 342 | 0 | 162 | 0
23:30 | 4721 | 836 | 1751 | 3756 | 745 | 20 | 306.5 | 0 | 159 | 0 | Max Temp. in Dhaka |  | 35.5° C
24:00 | 4685 | 836 | 1706 | 3756 | 720 | 20 | 271 | 0 | 156 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 250.559 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 250.559 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 23 | 22 | 21 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 442080
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 50 | 100 | 100 | 100 |  | 100 | 90 | 90 | 90 | 90 | 90 | 90 | 2000000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | [7 empty] | 4 | 16 | 16 | 16 | 16 | 16 | 16 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 277039
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 11 | 15 | 18 | 20 | 20 | 20 | 17 | 14 | 8 | 3 | 0 | [8 empty] | 142020
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 214 | 204 | 215 | 216 | 216 | 219 | 204 | 217 | 206 | 219 | 204 | 206 | 222 | 204 | 203 | 204 | 205 |  | 210 | 203 | 203 | 215 | 208 | 204 | 204 | 4908577
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 140 | 140 | 130 | 130 | 130 | 130 | 80 |  | 80 | 135 | 135 | 135 | 135 | 135 | 130 | 2993960
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 34 | [11 empty] | 36 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 821026
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 82 | 105 | 105 | 91 | 89 | 89 | 89 | 102 | 105 | 100 |  | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 2232254
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 100 | 100 | 100 | 78 | 75 | 75 | 75 | 120 | 120 | 145 | 175 | 180 | 180 | 178 | 150 | 100 | 123 | 75 |  | 150 | 150 | 115 | 155 | 155 | 150 | 95 | 3213000
17 | Siddhirganj 335 MW CCPP | 160 | 160 | 160 | 160 | 160 | 160 | 160 | 228 | 221 | 221 | 219 | 214 | 215 | 211 | 213 | 180 | 210 | 180 |  | 210 | 212 | 180 | 217 | 219 | 219 | 224 | 4889802
18 | Kodda 300 MW PP Unit-2 (Summit) | [8 empty] | 5 | 45 | 45 | 88 | 95 | 95 | 95 | 105 | 105 | 135 |  | 178 | 200 | 216 | 245 | 245 | 245 | 245 | 2248145
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2013618
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 579240
33 | Ashuganj 225 MW CCPP | 215 | 215 | 215 | 215 | 215 | 161 | 182 | 218 | 215 | 214 | 212 | 212 | 211 | 206 | 212 | 208 | 208 | 190 |  | 208 | 215 | 211 | 189 | 174 | 175 | 185 | 4943000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 240 | 240 | 240 | 240 | 265 | 305 | 320 | 290 | 300 | 295 | 260 |  | 330 | 290 | 275 | 305 | 295 | 265 | 265 | 6630000
| Ashuganj 450 MW CCPP(North) | 280 | 275 | 285 | 300 | 280 | 290 | 310 | 260 | 280 | 305 | 300 | 280 | 290 | 335 | 295 | 295 | 295 | 260 |  | 340 | 305 | 305 | 335 | 310 | 265 | 260 | 7236400
35 | Ashuganj 55 MW PP (Precision) | 57 | 57 | 57 | 56 | 5 | 5 | 5 | 5 | 5 | 25 | 48 | 54 | 55 | 55 | 55 | 54 | 54 | 54 |  | 54 | 54 | 56 | 56 | 56 | 56 | 57 | 1080960
36 | Chandpur 150 MW CCPP | 129 | 128 | 128 | 128 | 128 | 128 | 128 | 125 | 127 | 128 | 127 | 127 | 133 | 134 | 133 | 133 | 134 | 134 |  | 134 | 133 | 134 | 133 | 134 | 132 | 132 | 3116950
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 283 | 285 | 285 | 286 | 286 | 286 | 73 | 28 | 81 | 171 | 193 | 217 | 362 | 398 | 367 | 365 | 362 | 325 |  | 305 | 390 | 371 | 383 | 394 | 381 | 365 | 6963200
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6383500
41 | Haripur 360MW CCPP(HPL) | 271 | 270 | 271 | 300 | 260 | 260 | 282 | 281 | 263 | 221 | 212 | 202 | 191 | 190 | 191 | 182 | 162 | 151 |  | 162 | 172 | 182 | 180 | 140 | 140 | 140 | 5188000
42 | RPCL 210MW CCPP | 159 | 159 | 159 | 159 | 159 | 159 | 158 | 159 | 158 | 158 | 148 | 146 | 133 | 129 | 94 | 106 | 125 | 113 |  | 121 | 124 | 138 | 133 | 134 | 135 | 140 | 3280200
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 11 | 8 | 8 | 41 | 43 | 35 | 26 | 20 | 40 | 26 | 11 | 2 | [8 empty] | 273760
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 41 | 44 | 44 | 44 | 44 |  | 44 | 44 | 43 | 44 | 43 | 43 | 43 | 1028000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1074480
46 | Shajibazar 330 MW CCPP | 274 | 271 | 270 | 272 | 273 | 248 | 246 | 247 | 246 | 248 | 250 | 250 | 270 | 267 | 270 | 270 | 272 | 272 |  | 272 | 270 | 272 | 271 | 274 | 273 | 270 | 6013000
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 32 | 32 | 32 | 33 | 32 | 20 | 5 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 |  | 31 | 32 | 32 | 31 | 31 | 32 | 33 | 739680
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 10 | 10 | 10 | 10 | 75 | 75 | 75 | 75 | 74 | 72 | 76 | 75 | 50 | 50 |  | 60 | 77 | 77 | 78 | 77 | 77 | 77 | 1524480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 162 | 162 | 162 | 162 | 136 | 136 | 149 | 123 | 121 | 122 | 121 | 122 | 122 | 121 | 122 | 122 | 122 | 122 |  | 162 | 203 | 223 | 223 | 223 | 189 | 190 | 3718480
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [11 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 249000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | [12 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 94140
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 168000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 7 | 8 |  | 8 | 40 | 50 | 53 | 53 | 53 | 53 | 571800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | [11 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 207480
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 310 | 310 | 300 | 300 | 305 | 320 | 300 | 300 | 305 | 310 | 310 | 300 | 320 | 300 | 290 | 310 | 300 |  | 310 | 270 | 280 | 295 | 310 | 305 | 280 | 7419000
| Bibiyana South 400 MW | 380 | 389 | 370 | 402 | 375 | 375 | 387 | 340 | 340 | 350 | 350 | 350 | 350 | 351 | 350 | 350 | 350 | 350 |  | 380 | 380 | 380 | 380 | 380 | 380 | 380 | 8668100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 17 | [6 empty] | 8 | 35 | 35 | 35 | 35 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 863579
59 | Tangail Palli Power Gen 22 MW | 24 | 22 | 23 | 22 | [7 empty] | 5 | 22 | 24 | 23 | 24 | 24 | 24 |  | 23 | 24 | 24 | 24 | 24 | 23 | 24 | 378720
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 513600
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 388764
62 | Tangail 22 MW PP (Doreen) |  |  |  |  | 17 | 17 | 17 | 17 | 17 | [10 empty] | 14 | 14 | 14 | 14 | 17 | 17 | 17 | 167328
63 | Impoprt (Tripura) | 134 | 132 | 132 | 126 | 116 | 98 | 92 | 98 | 106 | 90 | 106 | 110 | 120 | 132 | 132 | 122 | 122 | 136 |  | 154 | 148 | 148 | 158 | 158 | 162 | 156 | 3044160
64 | Malancha, Ctg. EPZ (United) | 41 | 41 | 41 | 41 | 41 | 38 | 10 | 6 | 6 | 3 | 3 | 4 | 4 | 3 | 4 | 7 | 16 | 19 |  | 22 | 16 | 20 | 26 | 28 | 29 | 29 | 502080
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 |  | 20 | 20 | 21 | 21 | 21 | 22 | 22 | 470736
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 178560
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 818200
68 | Cumilla 25 MW PP (Summit) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 10 | 10 | 10 | 12 | 16 | 16 | 16 | 16 | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 401390
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 24 | 20 | 20 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 13 | 13 | 24 | 27 | 27 | 27 | 25 | 557100
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 661300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 607900
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 101 | 102 | 102 | 100 | 97 | 95 | 97 | 100 | 97 | 97 | 85 | 95 | 53 | 53 |  | 80 | 100 | 100 | 100 | 102 | 103 | 103 | 2232045
| Feni Lanka Power | [14 empty] | 17 | 17 | 17 | 17 |  | 52 | 91 | 114 | 52 | 52 | 52 | 52 | 422940
| Chowmuhani 113 MW | 111 | 113 | 111 | 55 | [7 empty] | 17 | 26 | 49 | 113 | 75 | 55 | 55 |  | 61 | 113 | 113 | 113 | 113 | 113 | 111 | 1570800
| Manikgonj 162MW PP(MPGL) | 17 | 17 | 17 | [10 empty] | 17 | 78 | 90 | 90 | 90 |  | 122 | 162 | 162 | 162 | 162 | 162 | 162 | 1478880
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | [8 empty] | 2 | 7 | 10 | 60 | 60 | 50 | 50 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 1246080
78 | Gazipur 52 MW PP | [12 empty] | 8 | 16 | 22 | 42 | 42 | 25 |  | 25 | 35 | 36 | 42 | 42 | 42 | 42 | 391200
79 | Kodda 150MW PP | [14 empty] | 16 | 16 | 32 | 32 |  | 64 | 100 | 64 | 48 | 48 | 48 | 48 | 415200
80 | Jamalpur 95 MW PP(Powerpac) | 73 | 73 | 73 | 73 | 16 |  |  | 13 | 48 | 48 | 64 | 65 | 60 | 65 | 65 | 73 | 73 | 73 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1391040
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | [8 empty] | 3 | 16 | 20 | 50 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 759571
| Gazipur 100 MW PP | 52 | 52 | 52 |  |  |  | 1 | 38 | 70 | 70 | 72 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1615200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 2 | 4 | 2 | 5 | 2 | 4 | 3 | 1 | 1 | [9 empty] | 26639
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1298938
| Karnaphuli Power Ltd. | [11 empty] | 4 | 17 | 17 | 17 | 11 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 214945
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [15 empty] | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 103733
86 | Meghnaghat CCPP ( Summit) | 230 | 232 | 248 | 230 | 245 | 235 | 250 | 235 | 235 | 240 | 245 | 260 | 260 | 275 | 235 | 240 | 235 | 275 |  | 235 | 235 | 230 | 235 | 230 | 225 | 225 | 5628393
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 17 | 17 | 17 | [11 empty] | 50 | 90 | 66 | 55 |  | 70 | 94 | 94 | 94 | 95 | 95 | 95 | 868080
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 23 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1009715
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 7 | 16 | 16 | 16 | 24 | 58 | 58 | 58 |  | 58 | 64 | 72 | 72 | 72 | 72 | 72 | 679824
95 | Patenga 50MW PP (Baraka) | [7 empty] | 9 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 40 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 585120
96 | Chattogram 108 MW PP (ECPV) | [15 empty] | 48 | 51 | 51 |  | 61 | 80 | 85 | 91 | 91 | 91 | 91 | 667200
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 50 | 55 | 55 | 40 | 40 | 40 | 30 | 30 | 30 | 30 | 30 | 30 | 50 | 30 | 30 | 30 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 1074942
100 | Manikganj 55 MW PP (Northern) | [14 empty] | 4 | 17 | 17 | 17 |  | 17 | 35 | 55 | 35 | 35 | 35 | 35 | 269149
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 130 | 163 | 130 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3451254
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 10500
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 17 | [7 empty] | 17 | 17 | 17 | 35 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 505440
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [16 empty] | 3 | 24 |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 614400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 130 | 132 | 132 | 132 | 132 | 132 | 132 | 132 | 130 | 121 | 130 | 133 | 127 | 113 | 123 | 126 | 132 | 132 |  | 132 | 132 | 132 | 132 | 132 | 132 | 120 | 3119620
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 70 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 90 | 100 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2257920
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 100 | 50 | 34 | 34 | 43 | 85 | 85 | 85 | 100 | 102 | 102 | 102 | 102 | 115 | 145 |  | 161 | 161 | 161 | 161 | 160 | 160 | 100 | 2583360
117 | Ashuganj 150MW PP (Midland) | [14 empty] | 2 | 73 | 145 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1284654
118 | Bibiyana-III 400 MW CCPP | 370 | 376 | 375 | 394 | 379 | 318 | 340 | 365 | 365 | 385 | 416 | 366 | 372 | 407 | 367 | 315 | 316 | 316 |  | 420 | 367 | 367 | 400 | 384 | 365 | 367 | 8791000
| Jamalpur 115 MW PP (United) | 16 | 16 | 16 | [9 empty] | 8 | 48 | 100 | 85 | 85 | 85 |  | 85 | 108 | 108 | 115 | 115 | 115 | 115 | 1172400
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 50 | 30 | 30 | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 1977600
| Anlima Energy Ltd. | 90 | 90 | 90 | 35 | 35 | 35 | 35 | 36 | 35 | 35 | 35 | 58 | 100 | 100 | 100 | 101 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 1999745
| Bhairob 54.5 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 614520
| Spectra Solar Plant Ltd. | [7 empty] | 14 | 22 | 5 | 34 | 17 | 34 | 30 | 23 | 11 | 6 | 1 | [8 empty] | 207951
120 | Eastern Zone Total | 7032 | 7041 | 7032 | 6603 | 5884 | 5591 | 5497 | 5555 | 5895 | 6108 | 6354 | 6499 | 6802 | 7081 | 7211 | 7317 | 7409 | 7177 |  | 8050 | 8554 | 8566 | 8722 | 8642 | 8488 | 8298 | 170558740
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 56 |  |  |  | 16 | 16 | 16 | 29 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 83 | 83 | 85 | 90 | 96 | 99 | 1529280
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 |  | 4 | 7 | 6 | 5 | 5 | 5 | 5 | 81600
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 17 | 17 | [9 empty] | 35 | 64 | 105 | 53 | 35 | 35 |  | 37 | 105 | 105 | 105 | 105 | 105 | 105 | 1025760
130
131
132 | United Payra Power Ltd. | [19 empty] | 10 | 17 | 17 | 17 | 17 | 35 | 17 | 122400
133 | Bhola Nutan Biddut BD LTD (GAS) | [19 empty] | 65 | 79 | 78 | 77 | 71 | 9 | 37 | 483000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 48 | 48 | 48 | [14 empty] | 32 |  | 80 | 80 | 80 | 64 | 64 | 80 | 64 | 642144
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 95 | 95 | 96 | 96 | 53 | 51 | 81 | 95 | 93 | 94 | 96 | 96 | 95 | 80 | 32 | 32 | 33 |  | 92 | 96 | 97 | 97 | 97 | 97 | 96 | 1971460
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 64 | 62 | 63 | 64 | 63 | 62 | 64 | 64 | 58 | 62 | 64 | 65 |  | 65 | 50 | 54 | 65 | 65 | 60 | 50 | 1519000
140 | Bhola 33 MW PP (Venture) | 29 | 27 | 28 | 27 | 23 | 20 | 17 | 17 | 20 | 19 | 17 | 16 | 19 | 19 | 27 | 25 | 26 | 27 |  | 33 | 34 | 33 | 33 | 34 | 33 | 33 | 592182
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 50 | 50 | 74 | 98 | 98 | 70 | 424320
142 | Noapara 40 MW PP (Khanjahan Ali) | [19 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 164250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 836 | 835 | 835 | 836 | 836 | 836 | 836 | 835 | 836 | 836 | 835 | 836 | 836 | 836 | 836 | 835 | 835 | 836 |  | 835 | 835 | 835 | 835 | 836 | 836 | 836 | 20171636
147 | Bheramara 410 MW CCPP | 360 | 370 | 385 | 410 | 350 | 300 | 350 | 350 | 350 | 380 | 380 | 355 | 355 | 365 | 330 | 315 | 295 | 270 |  | 250 | 245 | 245 | 240 | 225 | 215 | 215 | 7929792
148 | Payra 1320 MW | 570 | 550 | 550 | 550 | 450 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 430 | 440 | 480 | 500 | 480 | 480 |  | 480 | 540 | 540 | 550 | 550 | 550 | 500 | 12400900
149
150 | Barapukuria TPP Unit-1 | 71 | 70 | 70 | 71 | 72 | 73 | 74 | 73 | 72 | 73 | 73 | 74 | 74 | 73 | 74 | 73 | 72 | 72 |  | 71 | 71 | 71 | 70 | 71 | 71 | 71 | 1756364
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3663100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 293072
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 131 | 129 | 135 | 129 | 128 | 70 | 70 | 70 | 70 | 70 | 70 | 110 | 110 | 127 | 130 | 100 | 100 | 80 |  | 87 | 95 | 93 | 80 | 80 | 80 | 80 | 2545700
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 191 | 188 | 196 | 188 | 186 | 140 | 130 | 130 | 130 | 130 | 130 | 170 | 200 | 190 | 170 | 167 | 167 | 153 |  | 159 | 164 | 164 | 170 | 167 | 160 | 160 | 4187918
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 194 | 178 | 163 | 155 | 154 | 155 | 171 | 156 | 153 | 161 | 171 | 201 | 189 | 194 | 201 | 197 | 171 | 170 |  | 171 | 178 | 180 | 180 | 180 | 180 | 180 | 4469527
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 398 | 376 | 371 | 415 | 360 | 311 | 362 | 305 | 335 | 336 | 390 | 406 | 419 | 413 | 353 | 401 | 392 | 362 |  | 379 | 352 | 353 | 406 | 408 | 373 | 280 | 9020600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 |  | 14 | 16 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 22 | 22 | 22 | 422160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 215838
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 24 | 42 | 42 | 42 | 42 | 42 | 42 | 222500
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 18 | 31 | 31 | 30 | 30 | 30 | 0 | 150092
168 | Santahar 50 MW Peaking PP | [17 empty] | 11 |  | 38 | 42 | 41 | 41 | 41 | 41 | 0 | 230956
169 | Natore 52 MW PP (Rajlanka) | 45 | 52 | 52 | 25 | [7 empty] | 16 | 16 | 34 | 52 | 52 | 25 | 25 |  | 25 | 52 | 52 | 52 | 52 | 52 | 52 | 672480
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 10 |  | 74 | 100 | 100 | 100 | 100 | 100 | 100 | 538688
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [14 empty] | 27 | 35 | 35 | 35 |  | 50 | 51 | 108 | 113 | 113 | 113 | 113 | 776448
172 | Confidence Power Bogura Unit-1 113 MW | [14 empty] | 25 | 35 | 35 | 35 |  | 35 | 109 | 113 | 113 | 113 | 113 | 113 | 728448
173 | Rangpur 20 MW GTPP | [20 empty] | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 47 | [12 empty] | 29 | 102 | 50 | 37 | 38 |  | 106 | 113 | 113 | 107 | 107 | 113 | 113 | 1001280
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 4 | 6 | 6 | 6 | 7 | 7 | 6 | 4 | 2 | [8 empty] | 47185
178
178