## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-10 | Monday
|  |  | Date (day): | 2021-05-10 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14828.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15724 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-09 | 2021-05-10 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 102 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 356 | 329 | 350 | 360 |  |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 137 | 110 | 163 | 163 | 197 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 270 | 270 | 280 | 280 | 170 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 225 | 225 | 225 | 55 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 50 | 40 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 147 | 150 | 120 | 150 | 60 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 40 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 211 | 221 | 220 | 220 |  | 115 | ST under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 0 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 38 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 163 | 0 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 131 | 133 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 88 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 72 | 53 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 72 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 18 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 2707 | 2229 | 3569 | 3879 | 641 | 1180
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 80 | 80 | 80 | 80 | 100 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 16 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 22 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 23 | 23 | 22 | 22 | 208 |  | Unit 4 & 5 Under S/D due to Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 215 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 140 | 130 | 140
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 89 | 90 | 90 |  | 15 | Engine problem
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 40 | 15 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 50 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 17 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 967 | 1202 | 1707 | 1697 | 488 | 180
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 100 | 80 | 80 | 54 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 195 | 220 | 220 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 335 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 320 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 45 | 8 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 68 | 50 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 132 | 134 | 130 | 130 | 33 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 135 | 140 | 140 |  | 40 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 132 | 134 | 157 | 188
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 45 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 15 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | Engine problem
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1681 | 1826 | 2178 | 2396 | 501 | 82
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 118 | 131 | 160 | 160 |  |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 19 | 19
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 65 | 73 | 74 | 74 |  | 21 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 0 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 108 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 388 | 360 | 641.6 | 590 | 0 | 21
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 272 | 273 | 163 | 275 |  |  | Machine problem
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 31 | 33 | 32 | 32
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 71 | 76 | 76 | 78 |  | 8 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 177 | 215 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 310 | 341 | 341 |  |  | FGMO
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 368 | 390 | 400 | 400 |  |  | FGMO
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 10 | 10
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400 |  |  | FGMO
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1909 | 2050 | 1991 | 2105 | 0 | 192
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 842 | 842 | 855 | 855
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 99 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 225 | 215 | 210 | 210 | 200 |  | Gas shortage
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 32 | 33 |  | 7 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 35 | 17 | 105 | 105
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1201 | 1173 | 1531 | 1802 | 200 | 106
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 64 | 0 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 28 | 35 | 35
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 88 | 88 | 88 |  | 106 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 96 | 62 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 480 | 480 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 2 | 73 | 90 | 90 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 80 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 681 | 731 | 1120 | 1120 | 0 | 106
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 29 | 29 |  | 21 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 100 | 88 | 130 | 130 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 135 | 150 | 200 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 160 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 343 | 420 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 41 | 0 | 32 |  |  | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 50 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 35 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 35 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 847 | 1114 | 1745 | 1777 | 171 | 36
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 72 | 73 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 110 | 70 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 333 | 293 | 346 | 358 | 124 | 105
|  | Total |  |  |  |  | 21967 | 21219 | 10714 | 10978 | 14828.6 | 15724 | 2125 | 2008
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10333.3788 | 10588 | 14301.8051 | 15165.3955
| A. |  | 2021-05-09 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 11358 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8936 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10978 | MW
| 3 | Day peak Generation : |  |  | 10714 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10588 | MW
| 4 | Evening peak Generation : |  |  | 10978 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 247.4231 | MKWHr | By Solar | 0.6609 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 152.0891 | MKWHr |  | By Oil: | 53.5812 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.1795 | MKWHr |  | By Hydro: | 0.4266 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2125 | MW | Dhaka | 3817 | 3817 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2008 | MW | Chittagong | 1227 | 1227 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4133 | MW | Khulna | 1270 | 1270 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1243.48 | MMCFD |  |  | Rajshahi | 1115 | 1115 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 165173540.27 | ii) Oil : | Taka | 367976877.78 | Comilla | 1034 | 1034 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 81960788.27 | Total | Taka | 615111206.32 | Mymensingh | 792 | 792 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.1385 | MKWHr. | Sylhet | 441 | 441 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -48 | MW (E to W) at | 21:00 | hrs | Barisal | 273 | 273 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -48 | MW at | 21:00 | hrs | Rangpur | 619 | 619 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.7° C |  |  | Total | 10588 | 10588 |  | 0
| B. |  | 2021-05-10 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 32.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15724 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9900 | MW
| 4 | Reserve(Generation end) |  |  |  | 3924 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 257.0516 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7793 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 20.3542 | MKWHr. | ii) HVDC Flow at Peak Time |  | 842 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1315 | MKWHr. | iii) Maximum HVDC Flow : |  | 843 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.98 |  | (b) Today: | 75.98 |  | (c) Rule Curve: |  | 80.48
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-09
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 359 | 141 |  | 0 | 270 | 230 | 0 | 0 | 55 | 223 | 0 | 95 | 100 | 48 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 33 | 25 | 24 | 0 | 20 | 0 | 90 | 0 | 17 | 204 | 0 | 130 | 0 |  | 22 | 0 | 68 | 0 | 72 | 19 | 22 | 29 | 0 | 0 | 80 | 260 | 265 | 196 | 8 | 132 | 26 | 56 | 0 | 51 | 0 | 0 | 46 | 22 | 8 | 33 | 19 | 152 | 139 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 274 | 32 | 75 | 0 | 190 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 40 | 0 | 122 | 0 | 100 | 100 | 120 | 366 | 115 | 90 | 90 | 0 | 0 | 54 | 17 | 17 | 111 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 842 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 32 | 60 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 45 | 0 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 0 | 180 | 0 | 297 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 500 | 38 | 0 | 17 |  | 7840 | 3518 | 11358 | 4729 | 842 | 1721 | 2984 | 721 | 20 | 189 | 152 | 0 | 0 | 75.98
2:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 349 | 141 |  | 0 | 270 | 235 | 0 | 0 | 55 | 155 | 0 | 73 | 100 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 33 | 25 | 8 | 0 | 20 | 0 | 90 | 0 | 17 | 213 | 0 | 130 | 0 |  | 22 | 0 | 68 | 0 | 48 | 0 | 22 | 34 | 0 | 0 | 80 | 280 | 290 | 197 | 8 | 134 | 26 | 56 | 0 | 51 | 0 | 0 | 46 | 22 | 8 | 33 | 19 | 152 | 152 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 274 | 32 | 75 | 0 | 190 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 120 | 0 | 100 | 100 | 120 | 366 | 115 | 90 | 89 | 0 | 0 | 54 | 17 | 0 | 111 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 842 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 32 | 64 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 0 | 180 | 0 | 334 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 500 | 0 | 0 | 17 |  | 7652 | 3445 | 11097 | 4703 | 842 | 1740 | 2730 | 721 | 20 | 189 | 152 | 0 | 0 | 75.98
3:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 340 | 150 |  | 0 | 270 | 230 | 0 | 0 | 55 | 220 | 0 | 115 | 100 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 33 | 25 | 8 | 0 | 20 | 0 | 90 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 68 | 0 | 43 | 0 | 22 | 40 | 0 | 0 | 80 | 310 | 300 | 185 | 8 | 132 | 26 | 56 | 0 | 51 | 0 | 0 | 44 | 22 | 8 | 33 | 20 | 144 | 152 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 272 | 32 | 75 | 0 | 190 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 129 | 0 | 100 | 100 | 120 | 367 | 115 | 90 | 89 | 0 | 0 | 54 | 17 | 0 | 111 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 36 | 0 |  | 842 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 32 | 55 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 0 | 185 | 0 | 363 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 500 | 0 | 0 | 17 |  | 7767 | 3476 | 11243 | 4818 | 842 | 1780 | 2729 | 721 | 20 | 189 | 144 | 0 | 0 | 75.98
4:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 330 | 161 |  | 0 | 270 | 240 | 0 | 0 | 55 | 217 | 0 | 115 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 226 | 0 | 130 | 0 |  | 24 | 0 | 68 | 0 | 23 | 0 | 22 | 40 | 0 | 0 | 80 | 305 | 310 | 195 | 8 | 133 | 26 | 30 | 0 | 43 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 140 | 150 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 270 | 33 | 75 | 0 | 190 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 100 | 100 | 0 | 333 | 115 | 70 | 89 | 0 | 0 | 54 | 0 | 0 | 111 | 100 | 350 | 55 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 220 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 0 | 180 | 0 | 417 | 70 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 7305 | 3167 | 10472 | 4760 | 842 | 1773 | 2143 | 721 | 20 | 73 | 140 | 0 | 0 | 75.98
5:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 330 | 160 |  | 0 | 270 | 220 | 0 | 0 | 55 | 221 | 0 | 145 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 22 | 25 | 24 | 33 | 25 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 203 | 0 | 130 | 0 |  | 0 | 0 | 68 | 0 | 0 | 0 | 22 | 40 | 0 | 0 | 80 | 265 | 265 | 217 | 8 | 132 | 23 | 30 | 0 | 10 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 130 | 152 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 272 | 33 | 75 | 0 | 190 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 100 | 100 | 0 | 319 | 35 | 35 | 89 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 350 | 0 | 0 | 0 | 116 | 0 | 36 | 0 |  | 843 | 0 | 220 | 0 | 90 | 0 | 0 | 0 | 5 | 0 | 0 | 63 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 80 | 0 | 160 | 0 | 96 | 0 | 180 | 0 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 500 | 0 | 0 | 0 |  | 6659 | 2901 | 9560 | 4689 | 843 | 1679 | 1404 | 722 | 20 | 73 | 130 | 0 | 0 | 75.98
6:00 | 0 | 0 | 0 | 180 | 0 | 22 | 0 | 330 | 160 |  | 0 | 270 | 235 | 0 | 0 | 40 | 170 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 208 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 33 | 0 | 0 | 80 | 275 | 280 | 215 | 8 | 133 | 23 | 30 | 0 | 10 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 120 | 153 | 73 | 17 | 0 | 43 | 42 | 11 | 0 | 130 | 272 | 20 | 10 | 0 | 189 | 18 | 0 | 7 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 1 | 100 | 100 | 0 | 322 | 16 | 17 | 89 | 0 | 0 | 54 | 0 | 0 | 46 | 100 | 350 | 0 | 4 | 0 | 90 | 0 | 36 | 1 |  | 842 | 0 | 220 | 0 | 49 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 68 | 0 | 150 | 0 | 0 | 80 | 0 | 160 | 0 | 95 | 0 | 180 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 |  | 6158 | 2789 | 8947 | 4567 | 842 | 1447 | 1262 | 678 | 20 | 5 | 120 | 6 | 0 | 75.98
7:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 330 | 160 |  | 0 | 270 | 255 | 0 | 0 | 40 | 170 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 205 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 14 | 0 | 0 | 80 | 275 | 275 | 215 | 8 | 134 | 23 | 30 | 0 | 10 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 108 | 150 | 73 | 17 | 1 | 43 | 42 | 11 | 0 | 130 | 271 | 20 | 10 | 0 | 190 | 18 | 0 | 6 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 5 | 100 | 100 | 0 | 360 | 16 | 30 | 89 | 1 | 0 | 54 | 0 | 0 | 46 | 100 | 350 | 0 | 13 | 0 | 90 | 0 | 36 | 6 |  | 842 | 0 | 225 | 0 | 49 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 22 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 68 | 0 | 150 | 0 | 0 | 80 | 0 | 130 | 0 | 95 | 0 | 130 | 0 | 357 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 0 | 0 | 0 |  | 6248 | 2688 | 8936 | 4520 | 842 | 1461 | 1295 | 658 | 20 | 5 | 108 | 27 | 0 | 75.98
8:00 | 0 | 0 | 0 | 180 | 0 | 23 | 0 | 339 | 153 |  | 0 | 270 | 235 | 0 | 0 | 40 | 219 | 0 | 94 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 208 | 0 | 130 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 8 | 0 | 0 | 80 | 260 | 270 | 214 | 8 | 133 | 23 | 30 | 0 | 10 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 120 | 147 | 65 | 17 | 1 | 43 | 42 | 11 | 0 | 163 | 274 | 20 | 10 | 0 | 215 | 18 | 0 | 6 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 10 | 100 | 100 | 0 | 378 | 16 | 65 | 89 | 3 | 0 | 54 | 0 | 0 | 46 | 100 | 400 | 0 | 27 | 0 | 90 | 0 | 36 | 13 |  | 842 | 0 | 235 | 0 | 66 | 0 | 0 | 0 | 5 | 0 | 0 | 65 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 90 | 0 | 139 | 0 | 95 | 0 | 143 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 440 | 6 | 0 | 0 |  | 6443 | 2768 | 9211 | 4694 | 842 | 1491 | 1320 | 663 | 20 | 5 | 120 | 56 | 0 | 75.98
9:00 | 0 | 0 | 0 | 180 | 0 | 72 | 0 | 339 | 192 |  | 0 | 270 | 240 | 0 | 0 | 40 | 218 | 0 | 145 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 10 | 55 | 15 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 20 | 0 | 90 | 0 | 17 | 203 | 0 | 130 | 0 |  | 3 | 0 | 0 | 0 | 0 | 4 | 22 | 5 | 0 | 0 | 80 | 315 | 265 | 188 | 8 | 133 | 20 | 30 | 0 | 30 | 0 | 0 | 52 | 22 | 8 | 33 | 16 | 126 | 133 | 65 | 17 | 1 | 44 | 42 | 47 | 0 | 163 | 272 | 31 | 69 | 0 | 216 | 18 | 0 | 6 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 15 | 100 | 100 | 0 | 367 | 36 | 90 | 89 | 4 | 0 | 54 | 0 | 0 | 69 | 100 | 400 | 0 | 33 | 0 | 100 | 0 | 36 | 17 |  | 842 | 0 | 230 | 0 | 83 | 0 | 0 | 0 | 5 | 0 | 0 | 15 | 24 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 0 | 21 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 102 | 0 | 152 | 0 | 95 | 0 | 191 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 450 | 3 | 0 | 0 |  | 6925 | 2938 | 9863 | 4781 | 842 | 1749 | 1593 | 673 | 20 | 5 | 126 | 74 | 0 | 75.97
10:00 | 0 | 0 | 0 | 180 | 0 | 92 | 0 | 342 | 192 |  | 0 | 270 | 240 | 0 | 0 | 55 | 217 | 0 | 150 | 50 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 9 | 22 | 25 | 25 | 33 | 33 | 26 | 0 | 20 | 0 | 90 | 0 | 17 | 206 | 0 | 130 | 0 |  | 21 | 0 | 0 | 0 | 0 | 13 | 22 | 4 | 0 | 0 | 80 | 310 | 265 | 184 | 26 | 134 | 20 | 30 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 16 | 136 | 118 | 65 | 17 | 1 | 44 | 42 | 53 | 0 | 163 | 272 | 31 | 69 | 0 | 217 | 18 | 0 | 6 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 18 | 100 | 100 | 3 | 367 | 90 | 90 | 89 | 5 | 0 | 54 | 0 | 0 | 108 | 100 | 390 | 8 | 37 | 1 | 116 | 0 | 36 | 18 |  | 842 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 5 | 0 | 0 | 15 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 100 | 0 | 143 | 0 | 96 | 0 | 150 | 0 | 366 | 5 | 0 | 8 | 0 | 50 | 0 | 1 | 0 | 480 | 3 | 0 | 0 |  | 7260 | 2980 | 10240 | 4728 | 842 | 1768 | 1958 | 703 | 20 | 5 | 136 | 80 | 0 | 75.97
11:00 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 348 | 141 |  | 0 | 270 | 235 | 0 | 0 | 55 | 215 | 0 | 150 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 33 | 22 | 25 | 25 | 33 | 25 | 42 | 0 | 20 | 0 | 90 | 0 | 16 | 205 | 0 | 130 | 0 |  | 23 | 0 | 0 | 0 | 0 | 18 | 22 | 4 | 0 | 0 | 80 | 310 | 265 | 186 | 26 | 134 | 20 | 30 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 16 | 134 | 118 | 65 | 17 | 1 | 43 | 42 | 5 | 0 | 163 | 268 | 31 | 69 | 0 | 177 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 58 | 0 | 0 | 0 | 0 | 131 | 7 | 100 | 100 | 55 | 368 | 115 | 90 | 89 | 5 | 0 | 54 | 0 | 0 | 111 | 100 | 395 | 53 | 57 | 50 | 116 | 0 | 36 | 35 |  | 842 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 100 | 0 | 138 | 0 | 95 | 0 | 150 | 0 | 366 | 35 | 0 | 35 | 0 | 54 | 0 | 1 | 0 | 480 | 3 | 0 | 0 |  | 7487 | 3032 | 10519 | 4681 | 842 | 1660 | 2374 | 702 | 20 | 0 | 134 | 106 | 0 | 75.97
12:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 356 | 137 |  | 0 | 270 | 230 | 0 | 0 | 50 | 211 | 0 | 147 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 42 | 0 | 23 | 0 | 80 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 22 | 3 | 0 | 0 | 80 | 310 | 265 | 186 | 26 | 132 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 16 | 132 | 118 | 65 | 17 | 2 | 44 | 42 | 5 | 0 | 163 | 272 | 31 | 71 | 0 | 177 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 163 | 0 | 0 | 0 | 0 | 131 | 17 | 90 | 100 | 68 | 368 | 108 | 90 | 89 | 5 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 72 | 54 | 108 | 116 | 0 | 36 | 18 |  | 842 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 100 | 0 | 135 | 0 | 96 | 0 | 150 | 0 | 343 | 35 | 0 | 35 | 0 | 110 | 0 | 1 | 0 | 480 | 2 | 0 | 0 |  | 7652 | 3062 | 10714 | 4676 | 842 | 1639 | 2603 | 702 | 23 | 0 | 132 | 97 | 0 | 75.97
13:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 338 | 139 |  | 0 | 270 | 230 | 0 | 0 | 40 | 209 | 0 | 115 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 42 | 0 | 22 | 0 | 80 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 18 | 19 | 21 | 3 | 0 | 0 | 80 | 300 | 265 | 182 | 26 | 132 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 16 | 138 | 119 | 73 | 17 | 0 | 44 | 42 | 5 | 0 | 163 | 271 | 31 | 71 | 0 | 176 | 18 | 0 | 7 | 275 | 16 | 5 | 0 | 218 | 0 | 0 | 0 | 0 | 130 | 19 | 100 | 100 | 70 | 368 | 108 | 90 | 89 | 5 | 0 | 54 | 14 | 0 | 113 | 100 | 370 | 94 | 40 | 162 | 116 | 0 | 36 | 2 |  | 842 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 100 | 0 | 138 | 0 | 95 | 0 | 150 | 0 | 287 | 35 | 0 | 35 | 0 | 113 | 0 | 3 | 0 | 470 | 2 | 0 | 0 |  | 7689 | 3007 | 10696 | 4581 | 842 | 1572 | 2779 | 693 | 22 | 0 | 138 | 69 | 0 | 75.97
14:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 304 | 138 |  | 0 | 270 | 230 | 0 | 0 | 55 | 160 | 0 | 195 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 22 | 25 | 24 | 0 | 25 | 42 | 0 | 21 | 0 | 80 | 0 | 16 | 204 | 0 | 80 | 0 |  | 24 | 0 | 0 | 0 | 50 | 34 | 21 | 5 | 0 | 0 | 80 | 260 | 260 | 160 | 26 | 133 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 18 | 156 | 119 | 72 | 17 | 0 | 43 | 42 | 15 | 0 | 110 | 267 | 31 | 50 | 0 | 176 | 18 | 0 | 7 | 270 | 16 | 8 | 0 | 195 | 0 | 0 | 0 | 0 | 133 | 15 | 100 | 100 | 30 | 310 | 75 | 90 | 89 | 5 | 0 | 54 | 17 | 0 | 113 | 100 | 393 | 94 | 0 | 108 | 116 | 0 | 36 | 25 |  | 842 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 148 | 0 | 43 | 0 | 150 | 0 | 313 | 0 | 0 | 0 | 0 | 5 | 0 | 6 | 0 | 400 | 3 | 0 | 0 |  | 7312 | 2580 | 9892 | 4393 | 842 | 1458 | 2347 | 624 | 21 | 0 | 156 | 51 | 0 | 75.97
15:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 301 | 136 |  | 0 | 270 | 230 | 0 | 0 | 40 | 160 | 0 | 93 | 70 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 25 | 21 | 0 | 33 | 0 | 0 | 20 | 0 | 80 | 0 | 16 | 204 | 0 | 80 | 0 |  | 23 | 0 | 0 | 0 | 50 | 39 | 21 | 6 | 0 | 0 | 80 | 260 | 260 | 160 | 26 | 135 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 17 | 154 | 120 | 65 | 0 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 33 | 50 | 0 | 176 | 18 | 0 | 7 | 290 | 16 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 121 | 13 | 90 | 100 | 10 | 309 | 8 | 50 | 89 | 3 | 0 | 54 | 17 | 0 | 111 | 100 | 350 | 76 | 3 | 72 | 116 | 0 | 36 | 24 |  | 841 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 148 | 0 | 32 | 0 | 150 | 0 | 306 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 350 | 9 | 0 | 0 |  | 6673 | 2555 | 9228 | 4248 | 841 | 1464 | 1879 | 574 | 20 | 0 | 154 | 48 | 0 | 75.97
16:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 300 | 131 |  | 0 | 270 | 230 | 0 | 0 | 15 | 160 | 0 | 95 | 24 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 21 | 25 | 33 | 0 | 0 | 21 | 0 | 80 | 0 | 16 | 204 | 0 | 80 | 0 |  | 10 | 0 | 0 | 0 | 50 | 40 | 21 | 6 | 0 | 0 | 80 | 260 | 260 | 160 | 26 | 133 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 0 | 8 | 33 | 17 | 74 | 106 | 44 | 17 | 1 | 43 | 42 | 53 | 0 | 110 | 269 | 33 | 20 | 0 | 176 | 18 | 0 | 7 | 295 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130 | 9 | 100 | 100 | 10 | 309 | 8 | 50 | 89 | 1 | 0 | 37 | 17 | 0 | 113 | 100 | 349 | 35 | 10 | 35 | 116 | 0 | 0 | 8 |  | 843 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 148 | 0 | 31 | 0 | 150 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 350 | 15 | 0 | 0 |  | 6221 | 2603 | 8824 | 4291 | 843 | 1444 | 1545 | 574 | 21 | 0 | 74 | 32 | 0 | 75.96
17:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 303 | 123 |  | 0 | 270 | 230 | 0 | 0 | 15 | 200 | 0 | 150 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 25 | 0 | 33 | 33 | 0 | 0 | 22 | 0 | 80 | 0 | 16 | 221 | 0 | 80 | 0 |  | 12 | 0 | 0 | 0 | 50 | 50 | 21 | 14 | 0 | 0 | 80 | 310 | 315 | 190 | 26 | 134 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 0 | 0 | 33 | 7 | 72 | 105 | 24 | 17 | 1 | 43 | 42 | 14 | 0 | 110 | 269 | 32 | 20 | 0 | 176 | 18 | 0 | 7 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 3 | 100 | 100 | 10 | 231 | 8 | 50 | 89 | 1 | 0 | 54 | 17 | 0 | 113 | 100 | 150 | 17 | 10 | 35 | 116 | 0 | 0 | 3 |  | 842 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 74 | 0 | 150 | 0 | 0 | 100 | 0 | 147 | 0 | 32 | 0 | 150 | 0 | 390 | 0 | 0 | 0 | 0 | 5 | 0 | 2 | 0 | 350 | 22 | 0 | 0 |  | 6102 | 2692 | 8794 | 4232 | 842 | 1506 | 1526 | 574 | 22 | 0 | 72 | 20 | 0 | 75.96
18:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 331 | 118 |  | 0 | 270 | 225 | 0 | 0 | 15 | 220 | 0 | 120 | 7 | 24 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 22 | 25 | 7 | 33 | 33 | 0 | 0 | 22 | 0 | 80 | 0 | 17 | 216 | 0 | 80 | 0 |  | 9 | 0 | 0 | 0 | 50 | 50 | 21 | 27 | 0 | 0 | 80 | 275 | 275 | 190 | 26 | 135 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 0 | 0 | 33 | 8 | 88 | 105 | 29 | 0 | 0 | 43 | 42 | 14 | 0 | 130 | 271 | 32 | 20 | 0 | 176 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 100 | 123 | 10 | 233 | 9 | 78 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 250 | 17 | 2 | 35 | 116 | 0 | 30 | 2 |  | 842 | 0 | 225 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 97 | 0 | 145 | 0 | 32 | 0 | 150 | 0 | 385 | 0 | 0 | 32 | 0 | 37 | 0 | 1 | 25 | 350 | 35 | 0 | 0 |  | 6272 | 2805 | 9077 | 4288 | 842 | 1545 | 1694 | 575 | 22 | 18 | 88 | 5 | 0 | 75.96
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 43 | 0 | 326 | 122 |  | 0 | 270 | 230 | 0 | 0 | 20 | 160 | 0 | 73 | 20 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 22 | 25 | 10 | 33 | 25 | 0 | 0 | 22 | 0 | 80 | 0 | 17 | 215 | 0 | 80 | 0 |  | 16 | 0 | 68 | 0 | 52 | 50 | 21 | 33 | 0 | 0 | 80 | 295 | 300 | 199 | 26 | 134 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 0 | 10 | 33 | 18 | 120 | 111 | 73 | 17 | 0 | 43 | 42 | 14 | 0 | 110 | 274 | 32 | 20 | 0 | 176 | 18 | 0 | 7 | 295 | 16 | 5 | 0 | 3 | 0 | 0 | 7 | 0 | 133 | 0 | 100 | 125 | 33 | 335 | 66 | 90 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 350 | 37 | 0 | 52 | 116 | 0 | 36 | 0 |  | 842 | 0 | 215 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 49 | 0 | 0 | 0 | 24 | 40 | 21 | 0 | 11 | 73 | 0 | 150 | 12 | 0 | 92 | 0 | 145 | 0 | 50 | 0 | 150 | 0 | 380 | 10 | 0 | 35 | 0 | 69 | 0 | 0 | 35 | 380 | 59 | 0 | 0 |  | 6785 | 3091 | 9876 | 4462 | 842 | 1560 | 2032 | 603 | 22 | 235 | 120 | 0 | 0 | 75.96
19:30 | 0 | 0 | 0 | 180 | 0 | 93 | 0 | 326 | 131 |  | 0 | 270 | 225 | 0 | 0 | 30 | 220 | 0 | 150 | 40 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 10 | 33 | 33 | 0 | 0 | 22 | 0 | 80 | 0 | 17 | 204 | 0 | 140 | 0 |  | 23 | 0 | 68 | 0 | 52 | 50 | 21 | 37 | 0 | 0 | 80 | 260 | 295 | 185 | 26 | 134 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 116 | 128 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 270 | 33 | 75 | 0 | 195 | 18 | 0 | 7 | 305 | 16 | 8 | 0 | 15 | 0 | 0 | 8 | 0 | 133 | 0 | 100 | 125 | 50 | 373 | 115 | 88 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 350 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 220 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 24 | 42 | 22 | 0 | 11 | 75 | 0 | 150 | 12 | 0 | 92 | 0 | 145 | 0 | 62 | 0 | 160 | 0 | 410 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 450 | 72 | 0 | 0 |  | 7406 | 3245 | 10651 | 4715 | 842 | 1803 | 2240 | 675 | 22 | 238 | 116 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 322 | 117 |  | 0 | 270 | 225 | 0 | 0 | 20 | 220 | 0 | 150 | 40 | 24 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 23 | 0 | 80 | 0 | 17 | 204 | 0 | 140 | 0 |  | 22 | 0 | 68 | 0 | 50 | 50 | 21 | 37 | 0 | 0 | 80 | 285 | 300 | 183 | 26 | 135 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 126 | 128 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 130 | 274 | 33 | 76 | 0 | 215 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 132 | 0 | 100 | 125 | 50 | 374 | 115 | 88 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 350 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 841 | 0 | 220 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 24 | 42 | 22 | 0 | 11 | 76 | 0 | 150 | 18 | 0 | 90 | 0 | 145 | 0 | 62 | 0 | 159 | 0 | 421 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 460 | 72 | 0 | 0 |  | 7458 | 3278 | 10736 | 4768 | 841 | 1813 | 2235 | 686 | 23 | 244 | 126 | 0 | 0 | 75.96
21:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 329 | 110 |  | 0 | 270 | 225 | 0 | 0 | 40 | 221 | 0 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 23 | 0 | 80 | 0 | 17 | 215 | 0 | 140 | 0 |  | 24 | 0 | 68 | 50 | 50 | 22 | 21 | 40 | 0 | 0 | 100 | 335 | 320 | 195 | 45 | 134 | 23 | 30 | 0 | 51 | 0 | 0 | 45 | 22 | 10 | 33 | 15 | 134 | 131 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 273 | 33 | 76 | 0 | 215 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 100 | 135 | 50 | 390 | 115 | 88 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 400 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 52 | 41 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 88 | 0 | 150 | 0 | 62 | 0 | 160 | 0 | 420 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 480 | 73 | 0 | 0 |  | 7667 | 3311 | 10978 | 4950 | 842 | 1862 | 2255 | 703 | 23 | 209 | 134 | 0 | 0 | 75.96
22:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 328 | 110 |  | 0 | 270 | 225 | 0 | 0 | 55 | 220 | 0 | 185 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 13 | 25 | 33 | 0 | 0 | 23 | 0 | 80 | 0 | 17 | 204 | 0 | 140 | 0 |  | 24 | 0 | 68 | 82 | 50 | 12 | 21 | 33 | 0 | 0 | 90 | 290 | 305 | 162 | 45 | 135 | 23 | 15 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 136 | 131 | 73 | 14 | 0 | 43 | 42 | 53 | 0 | 163 | 274 | 33 | 76 | 0 | 223 | 18 | 0 | 7 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 0 | 100 | 140 | 50 | 370 | 115 | 88 | 85 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 400 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 205 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 52 | 41 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 87 | 0 | 142 | 0 | 62 | 0 | 150 | 0 | 422 | 20 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 500 | 108 | 0 | 0 |  | 7615 | 3345 | 10960 | 4824 | 842 | 1885 | 2317 | 724 | 23 | 209 | 136 | 0 | 0 | 75.96
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 331 | 110 |  | 0 | 270 | 225 | 0 | 0 | 55 | 220 | 0 | 140 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 13 | 25 | 33 | 0 | 0 | 24 | 0 | 80 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 68 | 100 | 51 | 5 | 22 | 34 | 0 | 0 | 80 | 265 | 265 | 177 | 45 | 134 | 23 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 136 | 131 | 73 | 14 | 0 | 43 | 42 | 53 | 0 | 130 | 273 | 33 | 76 | 0 | 224 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 140 | 10 | 367 | 115 | 88 | 79 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 400 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 29 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 84 | 0 | 140 | 0 | 62 | 0 | 150 | 0 | 399 | 53 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 510 | 108 | 0 | 0 |  | 7406 | 3289 | 10695 | 4709 | 842 | 1799 | 2283 | 734 | 24 | 168 | 136 | 0 | 0 | 75.96
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 330 | 110 |  | 0 | 270 | 225 | 0 | 0 | 55 | 221 | 0 | 140 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 13 | 25 | 33 | 0 | 0 | 24 | 0 | 80 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 68 | 100 | 55 | 0 | 22 | 40 | 0 | 0 | 80 | 260 | 265 | 199 | 45 | 132 | 23 | 5 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 132 | 129 | 73 | 16 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 34 | 76 | 0 | 223 | 18 | 0 | 7 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 100 | 10 | 366 | 115 | 88 | 89 | 0 | 0 | 54 | 17 | 0 | 111 | 100 | 400 | 53 | 0 | 54 | 116 | 0 | 36 | 0 |  | 842 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 84 | 0 | 140 | 0 | 42 | 0 | 150 | 0 | 376 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 470 | 108 | 0 | 0 |  | 7412 | 3117 | 10529 | 4718 | 842 | 1804 | 2196 | 695 | 24 | 118 | 132 | 0 | 0 | 75.96
KWH | 0 | 0 | 0 | 4315500 | 0 | 1850454 | 0 | 8077310 | 3438000 |  | 0 | 6393300 | 5415622 | 0 | 0 | 1082710 | 4982220 | 0 | 3184000 | 1279680 | 497520 | 94560 | 0 | 0 | 0 | 0 | 636120 | 353420 | 853730 | 310860 | 600000 | 475920 | 692300 | 743700 | 259680 | 0 | 426600 | 0 | 2000000 | 0 | 404550 | 4958307 | 0 | 2877678 | 0 |  | 428880 | 0 | 749617 | 278160 | 779520 | 476160 | 514608 | 533760 | 0 | 0 | 1943492 | 7217000 | 6838000 | 4545000 | 535272 | 3186520 | 505944 | 813600 | 0 | 1106391 | 0 | 0 | 1227355 | 425808 | 183240 | 810000 | 432760 | 3131520 | 3042560 | 1549440 | 326772 | 9000 | 1026000 | 1003680 | 832200 | 0 | 3569809 | 6189000 | 726432 | 1360320 | 0 | 4661330 | 412000 | 0 | 154620 | 7288500 | 237072 | 146048 | 0 | 1038763 | 0 | 0 | 110400 | 0 | 3191040 | 141066 | 2413440 | 2640000 | 1032072 | 8259000 | 1891200 | 1878000 | 2144436 | 35160 | 0 | 1282390 | 285199 | 37620 | 2504040 | 2436480 | 8834600 | 1182720 | 281490 | 1791360 | 2723618 | 0 | 825120 | 163465 |  | 20354182 | 0 | 5441184 | 0 | 1994880 | 0 | 0 | 0 | 0 | 0 | 120000 | 1243843 | 616939 | 739392 | 0 | 0 | 0 | 244793 | 0 | 627928 | 9910 | 0 | 0 | 727200 | 182618 | 441840 | 0 | 206550 | 1686109 | 0 | 3667500 | 0 | 0 | 2307100 | 0 | 3781082 | 0 | 1780727 | 37440 | 4153936 | 0 | 8829900 | 766080 | 0 | 690048 | 0 | 1224000 | 0 | 30716 | 385920 | 11825900 | 725127 | 0 | 56400 |  | 172523810 | 74899244 | 247423054 | 111818356 | 20354182 | 40270759 | 51681715 | 17179509 | 426600 | 1899516 | 3131520 | 660897 | 0
Fuel Cost | 0 | 0 | 0 | 6343785 | 0 | 2442599.28 | 0 | 8158083.1 | 3541140 |  | 0 | 6968697 | 6011340.42 | 0 | 0 | 9159726.6 | 5181508.8 | 0 | 5508320 | 9635990.4 | 4537382.4 | 930470.4 | 0 | 0 | 0 | 0 | 4643676 | 2731936.6 | 8417777.8 | 233145 | 450000 | 0 | 0 | 0 | 2511105.6 | 0 | 115182 | 0 | 3620000 | 0 | 3758269.5 | 5404554.63 | 0 | 4892052.6 | 0 |  | 0 | 0 | 7271284.9 | 2656428 | 6781824 | 3771187.2 | 648406.08 | 1585267.2 | 0 | 0 | 2856933.24 | 5340580 | 6838000 | 4181400 | 690500.88 | 3664498 | 571716.72 | 1139040 | 0 | 1891928.61 | 0 | 0 | 11721240.25 | 540776.16 | 137430 | 1417500 | 324570 | 23486400 | 3225113.6 | 14068915.2 | 415000.44 | 143460 | 1682640 | 1605888 | 1481316 | 0 | 4069582.26 | 6436560 | 1431071.04 | 2598211.2 | 0 | 8064100.9 | 902280 | 0 | 315424.8 | 7361385 | 177804 | 110996.48 | 0 | 7853048.28 | 0 | 0 | 574080 | 0 | 31399833.6 | 1649061.54 | 19669536 | 28644000 | 7276107.6 | 7680870 | 17247744 | 17747100 | 18678037.56 | 0 | 0 | 11169616.9 | 2506899.21 | 375447.6 | 21459622.8 | 16226956.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 117240088.32 | 0 | 5713243.2 | 0 | 15679756.8 | 0 | 0 | 0 | 0 | 0 | 1250400 | 1405542.59 | 956255.45 | 7216465.92 | 0 | 0 | 0 | 2408763.12 | 0 | 5557162.8 | 76307 | 0 | 0 | 7046568 | 1771394.6 | 848332.8 | 0 | 156358.35 | 10167237.27 | 0 | 19877850 | 0 | 0 | 2699307 | 0 | 4991028.24 | 0 | 2671090.5 | 636854.4 | 4860105.12 | 0 | 8741601 | 7997875.2 | 0 | 6548555.52 | 0 | 9498240 | 0 | 339411.8 | 2851948.8 | 51915701 | 0 | 0 | 0 |  | 456961365.18 | 301123444.8 | 758084809.98 | 117871168.29 | 117240088.32 | 47302371.98 | 350037801.96 | 81960788.27 | 115182 | 17939075.82 | 23486400 | 2131933.34 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 356 | 137 |  | 0 | 270 | 230 | 0 | 0 | 50 | 211 | 0 | 147 | 100 | 48 | 0 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 22 | 25 | 24 | 33 | 25 | 42 | 0 | 23 | 0 | 80 | 0 | 16 | 204 | 0 | 130 | 0 |  | 24 | 0 | 0 | 0 | 0 | 18 | 22 | 3 | 0 | 0 | 80 | 310 | 265 | 186 | 26 | 132 | 23 | 30 | 0 | 51 | 0 | 0 | 52 | 20 | 8 | 33 | 16 | 132 | 118 | 65 | 17 | 2 | 44 | 42 | 5 | 0 | 163 | 272 | 31 | 71 | 0 | 177 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 163 | 0 | 0 | 0 | 0 | 131 | 17 | 90 | 100 | 68 | 368 | 108 | 90 | 89 | 5 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 72 | 54 | 108 | 116 | 0 | 36 | 18 |  | 842 | 0 | 225 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 24 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 100 | 0 | 135 | 0 | 96 | 0 | 150 | 0 | 343 | 35 | 0 | 35 | 0 | 110 | 0 | 1 | 0 | 480 | 2 | 0 | 0 |  | 10714 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 329 | 110 | 0 | 0 | 270 | 225 | 0 | 0 | 40 | 221 | 0 | 150 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 13 | 33 | 33 | 0 | 0 | 23 | 0 | 80 | 0 | 17 | 215 | 0 | 140 | 0 | 0 | 24 | 0 | 68 | 50 | 50 | 22 | 21 | 40 | 0 | 0 | 100 | 335 | 320 | 195 | 45 | 134 | 23 | 30 | 0 | 51 | 0 | 0 | 45 | 22 | 10 | 33 | 15 | 134 | 131 | 73 | 17 | 0 | 43 | 42 | 53 | 0 | 163 | 273 | 33 | 76 | 0 | 215 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 0 | 100 | 135 | 50 | 390 | 115 | 88 | 89 | 0 | 0 | 54 | 17 | 0 | 113 | 100 | 400 | 53 | 0 | 72 | 116 | 0 | 36 | 0 |  | 842 | 0 | 215 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 50 | 0 | 0 | 0 | 52 | 41 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 88 | 0 | 150 | 0 | 62 | 0 | 160 | 0 | 420 | 17 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 480 | 73 | 0 | 0 |  | 10978 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 360 | 163 | 0 | 0 | 280 | 225 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 22 | 0 | 80 | 0 | 17 | 225 | 0 | 140 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 20 | 0 | 0 | 80 | 330 | 330 | 220 | 45 | 130 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 188 | 160 | 74 | 19 | 0 | 43 | 42 | 51 | 0 | 163 | 275 | 32 | 78 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 140 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 116 | 0 | 36 |  |  | 855 | 0 | 210 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 33 | 88 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 29 | 52 | 32 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 10 | 130 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 90 |  | 80
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 350 | 163 | 0 | 0 | 280 | 225 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 52 | 0 | 22 | 0 | 80 | 0 | 17 | 225 | 0 | 130 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 15 | 0 | 0 | 80 | 330 | 330 | 220 | 8 | 130 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 160 | 74 | 19 | 1.6 | 43 | 42 | 51 | 0 | 163 | 163 | 32 | 76 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 250 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 140 | 150 | 400 | 115 | 105 | 90 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 116 | 0 | 36 | 30 |  | 855 | 0 | 210 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 35 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 29 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 130 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 90 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 331 | 163 | 0 | 0 | 270 | 225 | 0 | 0 | 15 | 160 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 25 | 18 | 25 |  | 0 | 0 | 23 | 0 | 80 | 0 | 0 | 208 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 3 | 0 | 0 | 80 | 280 | 285 | 161 | 8 | 85 | 23 | 5 | 0 | 5 | 0 | 0 | 0 | 0 | 10 | 21 | 15 | 98 | 130 | 57 | 0 | 1 | 43 | 42 | 5 | 0 | 110 | 163 | 20 | 10 | 0 | 217 | 0 | 0 | 0 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 10 | 50 | 19 | 0 | 379 | 16 | 28 | 17 | 3 | 0 | 54 | 0 | 0 | 0 | 50 | 350 | 0 | 26 | 0 | 0 | 0 | 36 | 17 | 0 | 842 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 76 | 0 | 150 | 0 | 0 | 110 | 0 | 140 | 0 | 31 | 0 | 163 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 87 | 0 | 0 | 0
199
| Minimum Generation |  | 8936 | 7:00
| Highest Generation |  | 11358 | 1:00
| Day Peak Generation |  | 10714 | 12:00
| Evening Peak Generation |  | 10978 | 21:00
| HVDC Max Flow |  | 843 | 5:00
| HVDC EvPeak Flow |  | 842 | 21:00
| Load factor L.F |  | 90.77%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-10
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-09 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10714 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7793 | MW
Evening Peak Generation : |  | 10978 | MW Hour : | 21:00 | Available Max Generation : |  | 15724 | MW
E.P. Demand (at gen end) : |  | 10978 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 11358 | MW Hour : | 1:00 | Reserve(Generation end) |  | 3924 | MW
Total Gen. (MKWH) : |  | 247.4231 | System Load Factor : | 90.77% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -48 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-10
Actual : | 75.98 | Ft.(MSL) , | Rule curve : | 80.48 | Ft.( MSL )
Gas Consumed : | Total = | 1243.48 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165173540.27
: |  | Coal : | 81960788.27 | Oil : | 367976877.78 | Total : | 615111206.32
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4232.7182 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1441.4231 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1291.8352 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1167.4127 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1054.9019 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 851.2737 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 473.3335 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 219.1098 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 656.5573 |  |  | 0 | 0%
Total | 0 |  | 11388.5654 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sirajganj-Bogura 230 kV Ckt-2 was under shut down from 09:48 to 11:28 for C/M.
b) Tongi-Ghorasal 230 kV Ckt-1 was under shut down from 11:34 to 14:54 for kite removing at Tongi end.
c) Aminbazar-Manikganj P/P 132 kV Ckt was under shut down from 11:40 to 13:18 for C/M.
d) Rampura-Bashundhara 132 kV Ckt-1 tripped at 11:20 from both end showing Dist. Z1 B-phase relay
and was switched on at 11:33.
e) Aminbazar-Agargaon 230 kV Ckt-2 was under shut down from 13:52 to 15:31 for D/W.
f) Shahjadpur 132/33 kV T2 transformer was under shut down from 12:09 to 12:58 for C/M.
g) Sirajganj-Sherpur(Bogura) 132 kV Ckt-1 was switched on at 13:02 and tripped at 14:16 from Sirajganj end
h) Narshingdi 132 kV Bus-2 was under shut down from 17:06 to 18:22 due to red hot maintenance at
bus-DS.
i) Comilla(N)-Daudkandi 132 kV Ckt-2 tripped at 16:04 showing Dist. O/C, B-phase relay and was
switched on at 16:09.
j) Barishal(N)-Madaripur 132 kV Ckt-2 tripped at 15:40 from both end showing Dist. BC-phase relays and
was switched on at 16:24.
k) Bhola 225 MW STG was synchronized at 14:32.
l) Chandpur CCPP STG tripped at 06:48(10-05-2021) due to ECH LEO pump problem.
m) Shahjibazar 330 MW GT-1 tripped at 06:48(10-05-2021) showing high exhaust temperature.
n) Chattak 132/33 kV T-2 transformer is shut down since 06:48(10/05/2021) for C/M.
o) Bogura 132/33 kV T-1 transformer along with 33 kV Bus were shut down from 07:04(10/05/2021) to |  |  |  |  | About 45 MW power interruption occurred under Bogura S/S area
08:07(10/05/2021) due to PBS work. |  |  |  |  | from 07:04(10/05/2021) to 08:07(10-05-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-09 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 1850454
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8077310 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 110 | 3438000 | Gas Shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6393300 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 225 | 5415622 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 1082710 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 310860
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3184000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 40 | 1279680 | Low demand
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 221 | 4982220 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 497520 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 636120 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 94560 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 353420 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 853730
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 38 | 1075920 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 692300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 743700
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 259680 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 1038763 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 133 | 3191040 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1878000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 53 | 1182720 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 1791360 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 163465
| Dhaka area Total |  |  |  | 5829 | 2229 | 54781954
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 80 | 2000000 | Gas shortage.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 404550 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 141066
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 22 | 476160 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 23 | 426600 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 215 | 4958307 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 140 | 2877678
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 89 | 2144436 | Engine problem
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 749617 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 278160 | Fuel shortage
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2413440
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 514608
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 40 | 533760
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 779520 | Low demand
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35160
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1282390
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 285199 | Low demand
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2436480
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2723618
| Chattogram area Total |  |  |  | 2382 | 1202 | 25460749
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 100 | 1943492 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 195 | 4545000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 335 | 7217000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 320 | 6838000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 505944 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 813600 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 535272 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1106391
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1032072 | Low demand
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 134 | 3186520 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 135 | 2640000 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 425808
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 183240
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 3131520
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 810000
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 45 | 1227355 | Engine problem
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 432760 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 37620 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 2504040
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 825120 | 33 kV feeder fault
| Cumilla Area Total |  |  |  | 3034 | 1826 | 39940754
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 3042560 | Gas shortage
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 326772 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 73 | 1549440 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9000
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 0 | 110400 | Reserve.
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1891200
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 281490
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 428880
| Mymensingh Area Total |  |  |  | 709 | 360 | 7639742
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1026000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1003680 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3569809
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 273 | 6189000 | Machine problem
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 832200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 146048
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 33 | 726432 | Engine problem
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1360320 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 215 | 4661330
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 412000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 237072 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7288500 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 390 | 8259000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 154620 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8834600
| Sylhet Area Total |  |  |  | 2377 | 2050 | 44700611
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 842 | 20354182
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1994880 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 215 | 5441184 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 120000 | Reserve.
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 37440 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 17 | 766080 | Low demand
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1173 | 28713766
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 739392 | Reserve.
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 616939
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 1243843 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 62 | 1780727 | Low demand
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 11825900
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 73 | 725127 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 56400 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 731 | 16988328
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 244793
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 9910 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 88 | 2307100 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 150 | 3781082 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4153936 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 8829900 | Gas shortage
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 182618 | Engine problem
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 441840
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 206550
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 727200
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 627928 | Low demand
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 690048 | Low demand
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 385920 | Low demand
| Rajshahi Area Total |  |  |  | 2173 | 1114 | 22588825
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 73 | 1686109
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3667500 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 70 | 1224000 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 30716
| Rangpur Area Total |  |  |  | 605 | 293 | 6608325
| Total |  |  |  | 21219 | 10978 | 247423054
| Eastern Grid Total |  |  |  | 14331 | 7667 | 172523810
| Western Grid Total |  |  |  | 6888 | 3311 | 74899244
| National Grid Total |  |  |  | 21219 | 10978 | 247423054
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-09
(a) ENTIRE EASTERN GRID : |  | 7311 | MW | (b) ENTIRE WESTERN GRID : |  | 3277 | MW
i) Dhaka area |  | 3817 | MW | i) Khulna area |  | 1270 | MW
ii) Chittagong area |  | 1227 | MW | ii) Rajshahi area |  | 1115 | MW
iii) Comilla area |  | 1034 | MW | iii) Barisal area |  | 273 | MW
iv) Mymensingh area |  | 792 | MW | iv) Rangpur area |  | 619 | MW
v) Sylhet area |  | 441 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10588 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 9:00 | Netrokona | 87 | 24:00 | Benapol | 48 | 12:00
Munsiganj | 98 | 1:00 | Jamalpur | 118 | 1:00 | Jhenida | 101 | 1:00
Sonargaon | 69 | 15:00 | Sherpur | 94 | 23:00 | Bottail | 120 | 19:30
Shyampur | 198 | 5:00 | Srimongal | 44 | 15:00 | G.K Project | 52 | 21:00
Bhulta | 193 | 1:00 | Shahjibazar | 111 | 1:00 | Faridpur | 170 | 21:00
Madanganj | 43 | 2:00 | Fenchuganj | 31 | 1:00 | Madaripur | 84 | 20:00
Shitalakhya | 122 | 12:00 | Kulawara | 39 | 20:00 | Sariatpur | 60 | 1:00
Rahim steel | 36 | 13:00 | Sylhet | 113 | 14:00 | Gopalganj | 77 | 1:00
Matuail | 60 | 10:00 | Chatak | 26 | 22:00 | Bagerhat | 82 | 1:00
Ghorasal | 65 | 1:00 | Sunamganj | 40 | 21:00 | Mongla | 40 | 10:00
Narsingdi | 160 | 1:00 | Biani Bazar | 66 | 21:00 | Satkhira | 116 | 1:00
Haripur (SBU) | 115 | 11:00 | Comilla (S) | 156 | 14:00 | Gallamari | 39 | 1:00
Sreenagar | 38 | 1:00 | Comilla(N) | 129 | 1:00 | Magura | 46 | 1:00
Ullon | 73 | 21:00 | Chandpur | 74 | 22:00 | Norail | 37 | 1:00
Hasnabad | 86 | 21:00 | Feni | 116 | 22:00 | Chuadanga | 89 | 2:00
Magbazar | 82 | 12:00 | Chowmuhani | 160 | 1:00 | Borguna | 16 | 1:00
Maniknagar | 68 | 11:00 | Ashuganj | 29 | 1:00 | Barisal(N) | 33 | 1:00
Bangabhaban | 22 | 11:00 | Daudkandi | 144 | 21:00 | Barisal (S) | 94 | 13:00
Narinda | 54 | 11:00 | B.Baria | 156 | 1:00 | Patuakhali | 95 | 22:00
Dhanmondi | 190 | 11:00 | Ramganj | 88 | 1:00 | Bhandaria | 42 | 1:00
Lalbag | 87 | 13:00 | Chaddagram | 37 | 1:00 | Borhan Uddin | 39 | 22:00
Madartek | 70 | 1:00 | PHP | 10 | 18:30 | Ishurdi | 58 | 21:00
Dhaka University | 43 | 11:00 | Kochua | 60 | 1:00 | Ruppur Paromanobik | 2 | 18:00
Aftabnagar | 9 | 9:00 | Madunaghat | 62 | 14:00 | Natore | 113 | 21:00
Fatullah | 60 | 11:00 | Hathazari | 89 | 18:30 | Bogra | 130 | 21:00
Nawabganj | 45 | 1:00 | Khulshi | 211 | 11:00 | Noagaon | 99 | 22:00
Keraniganj | 66 | 1:00 | Halishahar | 140 | 13:00 | Rajshahi | 131 | 21:00
Mirpur | 107 | 13:00 | Baraulia | 145 | 12:00 | Rajshahi New | 14 | 3:00
Kalyanpur | 111 | 1:00 | Sikalbaha | 33 | 1:00 | C.Nawabganj | 60 | 22:00
Gulshan | 132 | 12:00 | Dohazari | 104 | 21:00 | Amnura | 38 | 20:00
Uttara | 89 | 13:00 | Cox'sbazar | 105 | 1:00 | Pabna | 91 | 20:00
Uttara New | 28 | 11:00 | Chandraghona | 30 | 19:30 | Shahjadpur | 90 | 9:00
Kamrangirchar | 84 | 12:00 | Kaptai | 4 | 19:00 | Serajganj | 77 | 12:00
Savar | 154 | 10:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 49 | 21:00
Bhasantec | 147 | 13:00 | Bakulia | 110 | 14:00 | Joypurhat | 48 | 22:00
Agargaon | 73 | 12:00 | Julda | 24 | 13:00 | Sherpur(Bogura) | 50 | 19:30
Satmosjid | 85 | 14:00 | TK chemical | 29.5 | 21:00 | Mohastangor | 60 | 19:30
Tongi | 126 | 12:00 | Modern Steel | 0 | #N/A | Bangura | 28 | 21:00
Kabirpur | 256 | 12:00 | Shahmirpur | 27.2 | 15:00 | Rangpur | 98 | 19:30
Basundhara | 161 | 14:00 | Khagrachhari | 22 | 18:30 | Lalmonirhat | 30 | 19:30
Manikganj | 67 | 14:00 | Matarbari | 43 | 22:00 | Saidpur | 73 | 17:00
Joydevpur | 162 | 11:00 | Baroiar Hat | 42 | 21:00 | Purbasadipur | 84 | 20:00
New Tongi | 101 | 12:00 | Rangamati | 12 | 19:00 | Thakurgaon | 69 | 19:30
Kodda | 260 | 11:00 | Abul Khair 230 | 139 | 4:00 | Palashbari | 86 | 19:30
Dhamrai | 126 | 11:00 | BSRM | 149 | 4:00 | Barapukuria | 44 | 21:00
Rajendrapur | 96 | 11:00 | GPH Ispat | 75 | 6:00 | Panchagar | 44 | 21:00
Valuka | 112 | 11:00 | Goalpara | 28 | 1:00 | Joldhaka | 50 | 19:00
Tangail | 190 | 1:00 | Central s/s | 84 | 22:00 | Kurigram | 43 | 20:00
Mymensing | 176 | 19:30 | Noapara | 46 | 1:00 | Mithapukur | 30 | 4:00
Kishoreganj | 120 | 1:00 | Jessore | 103 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-09 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 404 | 18:30 | 396 | 10:00 | Kaliakoir | 384 | 0.58333 | 370 | 0.33333
| Bheramara | 398 | 13:00 | 393 | 1:00 | Bhulta | 376 | 0.125 | 364 | 0.45833
| Ashuganj(N) | 384 | 3:00 | 373 | 9:00 | Gopalganj | 405 | 0.625 | 385 | 0.875
| Payra | 408 | 3:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 220 | 13:00 | Hathazari | 219 | 19:00 | 211 | 9:00
| Ishurdi | 234 | 13:00 | 224 | 20:00 | Megnaghat | 224 | 2:00 | 220 | 9:00
| Ashuganj | 235 | 3:00 | 228 | 9:00 | Fenchuganj | 238 | 18:30 | 235 | 10:00
| Serajganj | 230 | 1:00 | 225 | 8:00 | Siddhirganj | 226 | 3:00 | 218 | 8:00
| Baghabari | 232 | 18:30 | 226 | 8:00 | Maniknagar | 224 | 3:00 | 216 | 9:00
| Barapukuria | 236 | 13:00 | 230 | 9:00 | Agargaon | 221 | 14:00 | 211 | 10:00
| Bogra | 230 | 14:00 | 219 | 10:00 | Barisal | 251 | 16:00 | 238 | 21:00
| Rajshahi | 232 | 13:00 | 221 | 19:30 | Bhola 225 MW | 253 | 3:00 | 241 | 20:00
| Khulna South | 232 | 18:30 | 213 | 7:00 | AKSML | 219 | 16:00 | 212 | 4:00
| Rampura | 222 | 3:00 | 218 | 10:00 | BSRM | 224 | 18:30 | 213 | 4:00
| Haripur | 222 | 3:00 | 215 | 10:00 | Bibiyana | 238 | 1:00 | 234 | 9:00
| Hasnabad | 220 | 1:00 | 215 | 7:00 | Bhulta | 226 | 3:00 | 217 | 10:00
| Shyampur | 220 | 3:00 | 220 | 10:00 | Ashuganj (S) | 232 | 3:00 | 225 | 9:00
| Aminbazar | 221 | 1:00 | 213 | 2:00 | Kaliakoir | 222 | 3:00 | 212 | 9:00
| Tongi | 220 | 1:00 | 209 | 9:00 | GPH | 220 | 23:00 | 211 | 1:00
| Comilla (N) | 225 | 18:30 | 219 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 19:00 | 128 | 9:00 | Madanhat | 131 | 0.77083 | 127 | 0.25
| Munsiganj | 133 | 19:00 | 128 | 7:00 | Hathazari | 131 | 0 | 127 | 0.54167
| Sonargaon | 132 | 19:30 | 127 | 9:00 | Khulshi | 129 | 0.77083 | 123 | 0.45833
| Shyampur | 133 | 3:00 | 128 | 9:00 | Halishahar | 131 | 0.77083 | 124 | 0.45833
| Bhulta | 126 | 4:00 | 121 | 9:00 | Baraulia | 130 | 0.77083 | 124 | 0.45833
| Madanganj | 132 | 1:00 | 126 | 7:00 | Sikalbaha | 131 | 0.77083 | 126 | 0.45833
| Shitalakhya | 139 | 18:30 | 131 | 10:00 | Dohazari | 127 | 0.77083 | 122 | 0.5
| Rahim steal | 133 | 18:00 | 128 | 9:00 | Cox'sbazar | 119 | 0.75 | 111 | 0.041667
| Matuail | 133 | 19:00 | 128 | 9:00 | Chandraghona | 130 | 0.75 | 125 | 0.5
| Ghorasal | 136 | 1:00 | 133 | 8:00 | Kaptai | 130 | 0.95833 | 125 | 0.375
| Narsinghdi | 132 | 19:30 | 127 | 1:00 | A. Khaer Stl. | 128 | 0.91667 | 124 | 0.29167
| Haripur (SBU) | 134 | 18:30 | 128 | 8:00 | Bakulia | 131 | 0.77083 | 126 | 0.16667
| Sreenagar | 127 | 19:00 | 121 | 11:00 | Julda | 133 | 0.77083 | 126 | 0.5
| Ullon | 132 | 3:00 | 124 | 11:00 | TK Chemical | 130 | 0.66667 | 125 | 0.41667
| Hasnabad | 136 | 1:00 | 130 | 9:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 133 | 1:00 | 123 | 11:00 | Shahmirpur | 130 | 0.16667 | 126 | 0.5
| Maniknagar | 134 | 2:00 | 129 | 9:00 | Khagrachhari | 130 | 0.77083 | 123 | 0.5
| Bangabhaban | 134 | 2:00 | 129 | 9:00 | Matarbari | 120 | 0.66667 | 114 | 0
| Narinda | 134 | 2:00 | 129 | 9:00 | Baroiar Hat | 132 | 0.77083 | 124 | 0.54167
| Dhanmondi | 132 | 3:00 | 124 | 11:00 | Rangamati | 130 | 0.77083 | 124 | 0.45833
| Lalbag | 138 | 3:00 | 130 | 10:00 | Goalpara S/S | 140 | 18:30 | 128 | 7:00
| Madartek | 133 | 3:00 | 124 | 11:00 | Khulna Central S/S | 137 | 13:00 | 127 | 8:00
| Dhaka University | 132 | 3:00 | 125 | 10:00 | Noapara | 138 | 18:30 | 125 | 0.625
| Aftabnagar | 133 | 3:00 | 125 | 11:00 | Jessore | 133 | 18:30 | 119 | 0.875
| Fatullah | 133 | 3:00 | 128 | 9:00 | Benapol | 134 | 18:30 | 120 | 0.625
| Nawabganj | 125 | 1:00 | 121 | 10:00 | Jhenida | 128 | 18:00 | 115 | 0.875
| Keraniganj | 127 | 3:00 | 122 | 10:00 | Bottail | 131 | 0.75 | 124 | 0.875
| Mirpur | 133 | 1:00 | 125 | 9:00 | G.K Project | 139 | 18:00 | 133 | 0.83333
| Kalyanpur | 135 | 2:00 | 125 | 10:00 | Faridpur | 135 | 0.54167 | 127 | 0.875
| Gulshan | 132 | 2:00 | 124 | 11:00 | Madaripur | 140 | 0.125 | 131 | 0.875
| Uttara | 131 | 2:00 | 125 | 9:00 | Shariyatpur S/S | 141 | 0.58333 | 130 | 0.875
| Uttara New | 132 | 3:00 | 124 | 9:00 | Gopalganj | 146 | 0.58333 | 131 | 0.875
| Kamrangirchar | 136 | 1:00 | 128 | 10:00 | Bagerhat | 136 | 18:30 | 121 | 0.29167
| Savar | 132 | 3:00 | 124 | 9:00 | Mongla | 137 | 0.77083 | 121 | 0.29167
| Bhasantec | 135 | 3:00 | 125 | 10:00 | Satkhira | 137 | 18:00 | 125 | 0.29167
| Agargaon | 133 | 3:00 | 126 | 10:00 | Gallamari | 140 | 18:00 | 128 | 0.29167
| Satmosjid | 132 | 3:00 | 126 | 10:00 | Magura | 126 | 18:30 | 113 | 1:00
| Tongi | 135 | 1:00 | 127 | 9:00 | Narail | 126 | 0.54167 | 112 | 21:00
| Kabirpur | 137 | 15:00 | 129 | 9:00 | Chuadanga | 119 | 13:00 | 106 | 0.041667
| Basundhara | 133 | 3:00 | 123 | 11:00 | Borguna | 141 | 0.58333 | 130 | 0.875
| Manikganj | 138 | 18:30 | 130 | 17:00 | Barisal(N) | 142 | 13:00 | 133 | 0.875
| Joydevpur | 134 | 18:30 | 127 | 10:00 | Barisal (S) | 141 | 14:00 | 131 | 0.875
| New Tongi | 136 | 18:30 | 126 | 8:00 | Patuakhali(S) | 138 | 13:00 | 128 | 21:00
| Kodda | 135 | 18:30 | 122 | 17:00 | Bhandaria | 143 | 0.58333 | 130 | 0.875
| Dhamrai | 135 | 15:00 | 128 | 9:00 | Ishurdi | 136 | 0.54167 | 131 | 0.875
| Rajendrapur | 134 | 14:00 | 119 | 10:00 | Ruppur Paromanobik | 136 | 0.79167 | 130 | 0.83333
| Valuka | 132 | 15:00 | 116 | 2:00 | Natore | 136 | 13:00 | 130 | 7:00
| Tangail | 138 | 15:00 | 126 | 8:00 | Bogra | 136 | 14:00 | 129 | 17:00
| Mymensing | 134 | 15:00 | 121 | 2:00 | Noagaon | 133 | 14:00 | 124 | 9:00
| Kishorganj | 135 | 15:00 | 125 | 1:00 | Rajshahi | 133 | 13:00 | 128 | 8:00
| Netrokona | 134 | 15:00 | 119 | 3:00 | Rajshahi New | 133 | 18:00 | 128 | 8:00
| Jamalpur | 137 | 15:00 | 124 | 7:00 | C.Nawabganj | 134 | 1:00 | 127 | 21:00
| Sherpur | 138 | 15:00 | 122 | 17:00 | Amnura | 133 | 18:30 | 127 | 15:00
| Srimongal | 137 | 15:00 | 134 | 8:00 | Pabna | 134 | 18:00 | 129 | 21:00
| Shahjibazar | 137 | 15:00 | 131 | 8:00 | Shahjadpur | 136 | 3:00 | 134 | 9:00
| Fenchuganj | 137 | 15:00 | 134 | 2:00 | Serajganj | 134 | 13:00 | 127 | 8:00
| Khulawara | 136 | 16:00 | 133 | 11:00 | Niyamatpur | 131 | 14:00 | 123 | 21:00
| Sylhet | 133 | 2:00 | 131 | 14:00 | Joypurhat | 137 | 15:00 | 125 | 9:00
| Chatak | 132 | 3:00 | 130 | 1:00 | Sherpur(Bogura) | 135 | 13:00 | 129 | 7:00
| Sunamganj | 132 | 7:00 | 128 | 12:00 | Mohastangor | 135 | 13:00 | 128 | 9:00
| Biani Bazar | 132 | 5:00 | 128 | 14:00 | Bangura | 136 | 13:00 | 131 | 8:00
| Comilla(s) | 129 | 16:00 | 122 | 14:00 | Rangpur | 135 | 13:00 | 124 | 9:00
| Comilla(n) | 136 | 18:30 | 131 | 10:00 | Lalmonirhat | 133 | 14:00 | 125 | 9:00
| Chandpur | 136 | 16:00 | 128 | 1:00 | Saidpur | 133 | 13:00 | 123 | 9:00
| Feni | 130 | 18:00 | 124 | 16:00 | Purbasadipur | 133 | 13:00 | 118 | 17:00
| Chowmuhani | 134 | 16:00 | 126 | 1:00 | Thakurgaon | 132 | 13:00 | 119 | 19:30
| Ashuganj | 139 | 19:00 | 135 | 1:00 | Palashbari | 133 | 13:00 | 125 | 9:00
| Daudkandi | 132 | 16:00 | 126 | 8:00 | Barapukuria | 136 | 13:00 | 130 | 9:00
| B.Baria | 135 | 18:00 | 129 | 8:00 | Panchagar | 131 | 13:00 | 115 | 20:00
| Ramganj | 134 | 17:00 | 125 | 1:00 | Joldhaka | 132 | 13:00 | 120 | 19:30
| Chaddagram | 134 | 16:00 | 128 | 14:00 | Kurigram | 133 | 13:00 | 120 | 17:00
| PHP | 131 | 18:30 | 125 | 14:00 | Mithapukur | 135 | 0.54167 | 126 | 0.70833

## L-Curve
Date | 2021-05-09
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 12 | 7412 | 3117 | 10529 |  |  |  | QF-LDC-11
0:30 | 71 | 7626 | 3317.5 | 10943.5 | Date: | 2021-05-09
1:00 | 130 | 7840 | 3518 | 11358
1:30 | 160 | 7746 | 3481.5 | 11227.5
2:00 | 190 | 7652 | 3445 | 11097
2:30 | 135 | 7709.5 | 3460.5 | 11170 | [5 empty] | Gen. at Eve. Peak | 10978 | 10978 MW (21:00 )
3:00 | 80 | 7767 | 3476 | 11243 | [6 empty] | 21:00
3:30 | 135 | 7536 | 3321.5 | 10857.5 | [5 empty] | Gen. at Day Peak | 10714 | 10714 MW (12:00 )
4:00 | 190 | 7305 | 3167 | 10472 | [6 empty] | 12:00
4:30 | 211 | 6982 | 3034 | 10016 | [5 empty] | Highest Generation | 11358
5:00 | 232 | 6659 | 2901 | 9560 | [6 empty] | 1:00
5:30 | 256 | 6408.5 | 2845 | 9253.5
6:00 | 280 | 6158 | 2789 | 8947
6:30 | 270 | 6203 | 2738.5 | 8941.5
7:00 | 260 | 6248 | 2688 | 8936
7:30 | 280 | 6345.5 | 2728 | 9073.5
8:00 | 300 | 6443 | 2768 | 9211
8:30 | 293 | 6684 | 2853 | 9537
9:00 | 286 | 6925 | 2938 | 9863
9:30 | 266 | 7092.5 | 2959 | 10051.5
10:00 | 246 | 7260 | 2980 | 10240
10:30 | 280 | 7373.5 | 3006 | 10379.5
11:00 | 314 | 7487 | 3032 | 10519
11:30 | 318 | 7569.5 | 3047 | 10616.5
12:00 | 322 | 7652 | 3062 | 10714
12:30 | 345 | 7670.5 | 3034.5 | 10705
13:00 | 368 | 7689 | 3007 | 10696
13:30 | 375 | 7500.5 | 2793.5 | 10294
14:00 | 382 | 7312 | 2580 | 9892
14:30 | 280 | 6992.5 | 2567.5 | 9560
15:00 | 178 | 6673 | 2555 | 9228
15:30 | 149 | 6447 | 2579 | 9026
16:00 | 120 | 6221 | 2603 | 8824
16:30 | 129 | 6161.5 | 2647.5 | 8809
17:00 | 138 | 6102 | 2692 | 8794
17:30 | 188 | 6187 | 2748.5 | 8935.5
18:00 | 238 | 6272 | 2805 | 9077
18:30 | 178 | 6528.5 | 2948 | 9476.5
19:00 | 118 | 6785 | 3091 | 9876
19:30 | 30 | 7406 | 3245 | 10651
20:00 | 2 | 7458 | 3278 | 10736 |  |  |  | Executive Engineer
20:30 | 25 | 7562.5 | 3294.5 | 10857 |  |  |  | Network Operation Division
21:00 | 48 | 7667 | 3311 | 10978
21:30 | 40 | 7641 | 3328 | 10969
22:00 | 32 | 7615 | 3345 | 10960 |  |  |  |  | Page 6 of 7
22:30 | 20 | 7510.5 | 3317 | 10827.5
23:00 | 8 | 7406 | 3289 | 10695
23:30 | 10 | 7409 | 3203 | 10612
24:00 | 12 | 7412 | 3117 | 10529
10978 MW (21:00 )
10714 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-09 |  | Energy | 247423054
[11 empty] | 2021-05-09 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4718 | 842 | 1804 | 2283 | 695 | 24 | 118 | 0 | 132 | 0
0:30 | 4723.5 | 842 | 1762.5 | 2633.5 | 708 | 22 | 153.5 | 0 | 142 | 0 | Date: | 2021-05-09
1:00 | 4729 | 842 | 1721 | 2984 | 721 | 20 | 189 | 0 | 152 | 0
1:30 | 4716 | 842 | 1730.5 | 2857 | 721 | 20 | 189 | 0 | 152 | 0 | [7 empty] | Total Energy | 247.4231 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4703 | 842 | 1740 | 2730 | 721 | 20 | 189 | 0 | 152 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4760.5 | 842 | 1760 | 2729.5 | 721 | 20 | 189 | 0 | 148 | 0 | [7 empty] | Energy Requirement | 247.4231
3:00 | 4818 | 842 | 1780 | 2729 | 721 | 20 | 189 | 0 | 144 | 0
3:30 | 4789 | 842 | 1776.5 | 2436 | 721 | 20 | 131 | 0 | 142 | 0 | [6 empty] | Shortage
4:00 | 4760 | 842 | 1773 | 2143 | 721 | 20 | 73 | 0 | 140 | 0
4:30 | 4724.5 | 842.5 | 1726 | 1773.5 | 721.5 | 20 | 73 | 0 | 135 | 0
5:00 | 4689 | 843 | 1679 | 1404 | 722 | 20 | 73 | 0 | 130 | 0
5:30 | 4628 | 842.5 | 1563 | 1333 | 700 | 20 | 39 | 0 | 125 | 3
6:00 | 4567 | 842 | 1447 | 1262 | 678 | 20 | 5 | 0 | 120 | 6
6:30 | 4543.5 | 842 | 1454 | 1278.5 | 668 | 20 | 5 | 0 | 114 | 16.5 |  |  |  |  | Coal
7:00 | 4520 | 842 | 1461 | 1295 | 658 | 20 | 5 | 0 | 108 | 27
7:30 | 4607 | 842 | 1476 | 1307.5 | 660.5 | 20 | 5 | 0 | 114 | 41.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4694 | 842 | 1491 | 1320 | 663 | 20 | 5 | 0 | 120 | 56
8:30 | 4737.5 | 842 | 1620 | 1456.5 | 668 | 20 | 5 | 0 | 123 | 65
9:00 | 4781 | 842 | 1749 | 1593 | 673 | 20 | 5 | 0 | 126 | 74
9:30 | 4754.5 | 842 | 1758.5 | 1775.5 | 688 | 20 | 5 | 0 | 131 | 77
10:00 | 4728 | 842 | 1768 | 1958 | 703 | 20 | 5 | 0 | 136 | 80
10:30 | 4704.5 | 842 | 1714 | 2166 | 702.5 | 20 | 2.5 | 0 | 135 | 93
11:00 | 4681 | 842 | 1660 | 2374 | 702 | 20 | 0 | 0 | 134 | 106
11:30 | 4678.5 | 842 | 1649.5 | 2488.5 | 702 | 21.5 | 0 | 0 | 133 | 101.5
12:00 | 4676 | 842 | 1639 | 2603 | 702 | 23 | 0 | 0 | 132 | 97
12:30 | 4628.5 | 842 | 1605.5 | 2691 | 697.5 | 22.5 | 0 | 0 | 135 | 83
13:00 | 4581 | 842 | 1572 | 2779 | 693 | 22 | 0 | 0 | 138 | 69
13:30 | 4581 | 842 | 1572 | 2779 | 693 | 22 | 0 | 0 | 138 | 69
14:00 | 4581 | 842 | 1572 | 2779 | 693 | 22 | 0 | 0 | 138 | 69
14:30 | 4414.5 | 841.5 | 1518 | 2329 | 633.5 | 21 | 0 | 0 | 146 | 58.5
15:00 | 4248 | 841 | 1464 | 1879 | 574 | 20 | 0 | 0 | 154 | 48
15:30 | 4269.5 | 842 | 1454 | 1712 | 574 | 20.5 | 0 | 0 | 114 | 40
16:00 | 4291 | 843 | 1444 | 1545 | 574 | 21 | 0 | 0 | 74 | 32
16:30 | 4261.5 | 842.5 | 1475 | 1535.5 | 574 | 21.5 | 0 | 0 | 73 | 26
17:00 | 4232 | 842 | 1506 | 1526 | 574 | 22 | 0 | 0 | 72 | 20
17:30 | 4260 | 842 | 1525.5 | 1610 | 574.5 | 22 | 9 | 0 | 80 | 12.5
18:00 | 4288 | 842 | 1545 | 1694 | 575 | 22 | 18 | 0 | 88 | 5
18:30 | 4375 | 842 | 1552.5 | 1863 | 589 | 22 | 126.5 | 0 | 104 | 2.5
19:00 | 4462 | 842 | 1560 | 2032 | 603 | 22 | 235 | 0 | 120 | 0
19:30 | 4715 | 842 | 1803 | 2240 | 675 | 22 | 238 | 0 | 116 | 0
20:00 | 4768 | 841 | 1813 | 2235 | 686 | 23 | 244 | 0 | 126 | 0
20:30 | 4859 | 841.5 | 1837.5 | 2245 | 694.5 | 23 | 226.5 | 0 | 130 | 0
21:00 | 4950 | 842 | 1862 | 2255 | 703 | 23 | 209 | 0 | 134 | 0
21:30 | 4887 | 842 | 1873.5 | 2286 | 713.5 | 23 | 209 | 0 | 135 | 0
22:00 | 4824 | 842 | 1885 | 2317 | 724 | 23 | 209 | 0 | 136 | 0
22:30 | 4766.5 | 842 | 1842 | 2300 | 729 | 23.5 | 188.5 | 0 | 136 | 0
23:00 | 4709 | 842 | 1799 | 2283 | 734 | 24 | 168 | 0 | 136 | 0
23:30 | 4713.5 | 842 | 1801.5 | 2283 | 714.5 | 24 | 143 | 0 | 134 | 0 | Max Temp. in Dhaka |  | 34.7° C
24:00 | 4718 | 842 | 1804 | 2283 | 695 | 24 | 118 | 0 | 132 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-09
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 22 | 21 | 20 | 21 | 22 | 22 |  | 22 | 22 | 23 | 23 | 23 | 24 | 24 | 426600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2000000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 404550
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 15 | 18 | 7 | 17 | 19 | 15 | 13 | 9 | 3 | 0 | [8 empty] | 141066
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 213 | 203 | 226 | 203 | 208 | 205 | 208 | 203 | 206 | 205 | 204 | 204 | 204 | 204 | 204 | 221 | 216 |  | 215 | 204 | 204 | 215 | 204 | 203 | 203 | 4958307
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 | 80 | 80 | 80 |  | 80 | 140 | 140 | 140 | 140 | 130 | 130 | 2877678
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | [14 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 749617
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 90 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 |  | 89 | 89 | 89 | 89 | 85 | 79 | 89 | 2144436
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 95 | 73 | 115 | 115 | 145 | 94 | 94 | 94 | 145 | 150 | 150 | 147 | 115 | 195 | 93 | 95 | 150 | 120 |  | 73 | 150 | 150 | 150 | 185 | 140 | 140 | 3184000
17 | Siddhirganj 335 MW CCPP | 223 | 155 | 220 | 217 | 221 | 170 | 170 | 219 | 218 | 217 | 215 | 211 | 209 | 160 | 160 | 160 | 200 | 220 |  | 160 | 220 | 220 | 221 | 220 | 220 | 221 | 4982220
18 | Kodda 300 MW PP Unit-2 (Summit) | 45 | [9 empty] | 58 | 163 | 218 | 195 | 120 |  |  |  |  | 3 | 15 | 15 |  |  |  |  | 1038763
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 45 | 45 | 45 | 45 | 535272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 100 | 90 | 80 | 80 | 1943492
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 505944
33 | Ashuganj 225 MW CCPP | 196 | 197 | 185 | 195 | 217 | 215 | 215 | 214 | 188 | 184 | 186 | 186 | 182 | 160 | 160 | 160 | 190 | 190 |  | 199 | 185 | 183 | 195 | 162 | 177 | 199 | 4545000
34 | Ashuganj 450 MW CCPP(South) | 265 | 290 | 300 | 310 | 265 | 280 | 275 | 270 | 265 | 265 | 265 | 265 | 265 | 260 | 260 | 260 | 315 | 275 |  | 300 | 295 | 300 | 320 | 305 | 265 | 265 | 6838000
| Ashuganj 450 MW CCPP(North) | 260 | 280 | 310 | 305 | 265 | 275 | 275 | 260 | 315 | 310 | 310 | 310 | 300 | 260 | 260 | 260 | 310 | 275 |  | 295 | 260 | 285 | 335 | 290 | 265 | 260 | 7217000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 15 | 5 | 5 | 813600
36 | Chandpur 150 MW CCPP | 132 | 134 | 132 | 133 | 132 | 133 | 134 | 133 | 133 | 134 | 134 | 132 | 132 | 133 | 135 | 133 | 134 | 135 |  | 134 | 134 | 135 | 134 | 135 | 134 | 132 | 3186520
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 359 | 349 | 340 | 330 | 330 | 330 | 330 | 339 | 339 | 342 | 348 | 356 | 338 | 304 | 301 | 300 | 303 | 331 |  | 326 | 326 | 322 | 329 | 328 | 331 | 330 | 8077310
40 | Meghnaghat 450 MW CCPP(MPL) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6393300
41 | Haripur 360MW CCPP(HPL) | 141 | 141 | 150 | 161 | 160 | 160 | 160 | 153 | 192 | 192 | 141 | 137 | 139 | 138 | 136 | 131 | 123 | 118 |  | 122 | 131 | 117 | 110 | 110 | 110 | 110 | 3438000
42 | RPCL 210MW CCPP | 139 | 152 | 152 | 150 | 152 | 153 | 150 | 147 | 133 | 118 | 118 | 118 | 119 | 119 | 120 | 106 | 105 | 105 |  | 111 | 128 | 128 | 131 | 131 | 131 | 129 | 3042560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 4 | 13 | 27 | 33 | 37 | 57 | 54 | 40 | 0 | 3 | 10 | 10 | 2 | [8 empty] | 281490
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1026000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1003680
46 | Shajibazar 330 MW CCPP | 274 | 274 | 272 | 270 | 272 | 272 | 271 | 274 | 272 | 272 | 268 | 272 | 271 | 267 | 270 | 269 | 269 | 271 |  | 274 | 270 | 274 | 273 | 274 | 273 | 271 | 6189000
47 | Shahjibazar GTPP Unit- 8 & 9 | 32 | 32 | 32 | 33 | 33 | 20 | 20 | 20 | 31 | 31 | 31 | 31 | 31 | 31 | 33 | 33 | 32 | 32 |  | 32 | 33 | 33 | 33 | 33 | 33 | 34 | 726432
48 | Shahjibazar 86MW PP (Shahjibazar) | 75 | 75 | 75 | 75 | 75 | 10 | 10 | 10 | 69 | 69 | 69 | 71 | 71 | 50 | 50 | 20 | 20 | 20 |  | 20 | 75 | 76 | 76 | 76 | 76 | 76 | 1360320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 190 | 190 | 190 | 190 | 189 | 190 | 215 | 216 | 217 | 177 | 177 | 176 | 176 | 176 | 176 | 176 | 176 |  | 176 | 195 | 215 | 215 | 223 | 224 | 223 | 4661330
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 412000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 154620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 0 |  |  | 5 | 5 | 5 | 5 | 5 | 8 |  |  |  | 5 |  | 5 | 8 | 11 | 11 | 11 | 11 | 11 | 146048
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 47 | 53 | 5 | 5 | 5 | 15 | 53 | 53 | 14 | 14 |  | 14 | 53 | 53 | 53 | 53 | 53 | 53 | 832200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 0 |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 237072
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 300 | 295 | 290 | 280 | 270 | 310 | 305 | 310 | 305 | 290 | 290 | 275 | 270 | 290 | 295 | 310 | 310 |  | 295 | 305 | 310 | 310 | 315 | 295 | 305 | 7288500
| Bibiyana South 400 MW | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 400 | 400 | 390 | 395 | 400 | 370 | 393 | 350 | 349 | 150 | 250 |  | 350 | 350 | 350 | 400 | 400 | 400 | 400 | 8834600
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 17 | 0 |  |  | 15 | 9 | 33 | 35 | 35 | 35 |  | 17 | 17 | 17 |  |  | 55 | 55 | 55 | 55 | 55 | 55 | 853730
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 24 | 24 | 0 |  |  |  | 3 | 21 | 23 | 24 | 24 | 24 | 23 | 10 | 12 | 9 |  | 16 | 23 | 22 | 24 | 24 | 24 | 24 | 428880
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 514608
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 0 |  |  |  | 22 | 22 | 22 | 22 | 22 |  |  |  | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 310860
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  |  | 17 | 17 | 17 | 17 | 14 | 14 | 16 | 326772
63 | Impoprt (Tripura) | 152 | 152 | 144 | 140 | 130 | 120 | 108 | 120 | 126 | 136 | 134 | 132 | 138 | 156 | 154 | 74 | 72 | 88 |  | 120 | 116 | 126 | 134 | 136 | 136 | 132 | 3131520
64 | Malancha, Ctg. EPZ (United) | 29 | 34 | 40 | 40 | 40 | 33 | 14 | 8 | 5 | 4 | 4 | 3 | 3 | 5 | 6 | 6 | 14 | 27 |  | 33 | 37 | 37 | 40 | 33 | 34 | 40 | 533760
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | [5 empty] | 22 | 22 | 22 | 22 | 22 | 22 | 425808
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 183240
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 810000
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 16 | 16 | 16 | 16 | 16 | 18 | 17 | 17 | 7 | 8 |  | 18 | 20 | 20 | 15 | 20 | 20 | 20 | 432760
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 26 | 26 | 26 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 25 | 24 | 24 | 24 | 21 | 21 | 0 | 7 |  | 10 | 10 | 13 | 13 | 13 | 13 | 13 | 475920
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 0 | 0 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 692300
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 743700
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 22 | 23 | 23 | 72 | 92 | 95 | 100 | 100 | 103 | 43 | 43 | 43 | 43 |  | 43 | 93 | 100 | 102 | 103 | 103 | 103 | 1850454
| Feni Lanka Power | 17 | 0 | [24 empty] | 37620
| Chowmuhani 113 MW | 111 | 111 | 111 | 111 | 46 | 46 | 46 | 46 | 69 | 108 | 111 | 113 | 113 | 113 | 111 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 111 | 2504040
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 72 | 0 |  |  |  |  | 1 | 50 | 108 | 162 | 108 | 72 | 35 | 35 | 35 |  | 52 | 72 | 72 | 72 | 72 | 72 | 54 | 1791360
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 20 | 0 |  |  | 2 | 50 | 100 | 100 | 100 | 100 | 70 | 24 | 7 | 7 |  | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 1279680
78 | Gazipur 52 MW PP | 24 | 8 | 8 | 0 | [5 empty] | 26 | 42 | 42 | 42 | 42 | [12 empty] | 259680
79 | Kodda 150MW PP | 16 | 16 | 16 | 0 | [15 empty] | 16 | 16 | 16 |  |  |  |  | 94560
80 | Jamalpur 95 MW PP(Powerpac) | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 65 | 65 | 65 | 65 | 65 | 73 | 72 | 65 | 44 | 24 | 29 |  | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 1549440
81 | Jangalia 52 MW PP (Lakdanavi) | 46 | 46 | 44 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 45 | 52 | 52 | 52 | 1227355
| Gazipur 100 MW PP | 90 | 90 | 90 | 70 | 35 | 17 | 30 | 65 | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 50 | 50 | 78 |  | 90 | 88 | 88 | 88 | 88 | 88 | 88 | 1878000
| Kaptai 7 MW Solar PP | [6 empty] | 1 | 3 | 4 | 5 | 5 | 5 | 5 | 5 | 3 | 1 | 1 | [9 empty] | 35160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 37 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1282390
| Karnaphuli Power Ltd. | 17 | 17 | 17 | 0 | [8 empty] | 14 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 285199
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 230 | 235 | 230 | 240 | 220 | 235 | 255 | 235 | 240 | 240 | 235 | 230 | 230 | 230 | 230 | 230 | 230 | 225 |  | 230 | 225 | 225 | 225 | 225 | 225 | 225 | 5415622
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 95 | 95 | 95 | 55 | 0 |  |  |  |  | 8 | 53 | 72 | 94 | 94 | 76 | 35 | 17 | 17 |  | 37 | 53 | 53 | 53 | 53 | 53 | 53 | 1182720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [22 empty] | 50 | 82 | 100 | 100 | 278160
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 43 | 10 | 10 | 10 | 10 | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1106391
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 16 | 16 | 0 |  |  |  | 2 | 16 | 16 | 48 | 48 | 48 | 48 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 |  |  |  |  | 497520
95 | Patenga 50MW PP (Baraka) | 19 | 0 | [6 empty] | 4 | 13 | 18 | 18 | 19 | 34 | 39 | 40 | 50 | 50 |  | 50 | 50 | 50 | 22 | 12 | 5 |  | 476160
96 | Chattogram 108 MW PP (ECPV) | 72 | 48 | 43 | 23 | 0 | [7 empty] | 18 | 50 | 50 | 50 | 50 | 50 |  | 52 | 52 | 50 | 50 | 50 | 51 | 55 | 779520
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 40 | 40 | 55 | 55 | 50 | 40 | 55 | 40 | 15 | 15 | 15 |  | 20 | 30 | 20 | 40 | 55 | 55 | 55 | 1082710
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 55 | 55 | 55 | 55 | 55 | 17 | 17 |  |  |  |  | 17 | 17 | 17 |  |  |  |  | 353420
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 | 130 |  | 110 | 130 | 130 | 163 | 163 | 130 | 163 | 3569809
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 0 |  |  | 1 | 1 | 0 | [8 empty] | 9000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 0 |  |  |  | 10 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 636120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 40 | 8 | 8 | 0 | [15 empty] | 7 | 8 | 8 |  |  |  |  | 110400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 122 | 120 | 129 | 132 | 133 | 132 | 132 | 131 | 131 | 131 | 131 | 131 | 130 | 133 | 121 | 130 | 132 | 131 |  | 133 | 133 | 132 | 133 | 147 | 149 | 149 | 3191040
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 90 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2413440
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 123 |  | 125 | 125 | 125 | 135 | 140 | 140 | 100 | 2640000
117 | Ashuganj 150MW PP (Midland) | 120 | 120 | 120 | 0 | [5 empty] | 3 | 55 | 68 | 70 | 30 | 10 | 10 | 10 | 10 |  | 33 | 50 | 50 | 50 | 50 | 10 | 10 | 1032072
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 367 | 333 | 319 | 322 | 360 | 378 | 367 | 367 | 368 | 368 | 368 | 310 | 309 | 309 | 231 | 233 |  | 335 | 373 | 374 | 390 | 370 | 367 | 366 | 8259000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 35 | 16 | 16 | 16 | 36 | 90 | 115 | 108 | 108 | 75 | 8 | 8 | 8 | 9 |  | 66 | 115 | 115 | 115 | 115 | 115 | 115 | 1891200
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2436480
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 90 | 90 | 90 | 100 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2723618
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  |  | 30 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 825120
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 6 | 13 | 17 | 18 | 35 | 18 | 2 | 25 | 24 | 8 | 3 | 2 | [8 empty] | 163465
120 | Eastern Zone Total | 7840 | 7652 | 7767 | 7305 | 6659 | 6158 | 6248 | 6443 | 6925 | 7260 | 7487 | 7652 | 7689 | 7312 | 6673 | 6221 | 6102 | 6272 |  | 6785 | 7406 | 7458 | 7667 | 7615 | 7406 | 7412 | 172523810
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 90 | 49 | 49 | 66 | 83 | 99 | 99 | 99 | 99 | 66 | 66 | 66 | 66 | 66 |  | 66 | 66 | 75 | 99 | 99 | 99 | 99 | 1994880
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 0 |  |  |  |  | 5 | 35 | 35 | 35 | [6 empty] | 10 | 17 | 17 | 17 | 20 | 53 | 17 | 766080
130
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 0 | [22 empty] | 56400
133 | Bhola Nutan Biddut BD LTD (GAS) | 38 | 0 | [5 empty] | 6 | 3 | 3 | 3 | 2 | 2 | 3 | 9 | 15 | 22 | 35 |  | 59 | 72 | 72 | 73 | 108 | 108 | 108 | 725127
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 16 | 16 | 16 | 16 | 48 | 64 | 64 | 64 | 64 | 16 | [5 empty] | 16 | 16 | 16 |  |  |  |  | 739392
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 96 | 96 | 96 | 95 | 95 | 95 | 95 | 96 | 95 | 96 | 95 | 43 | 32 | 31 | 32 | 32 |  | 50 | 62 | 62 | 62 | 62 | 62 | 42 | 1780727
| Bhola 225 MW CCPP | 60 | 64 | 55 | 65 | 63 | 65 | 65 | 65 | 15 | 15 | 15 | 15 | 15 | 15 | 46 | 87 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 89 | 89 | 1243843
140 | Bhola 33 MW PP (Venture) | 33 | 28 | 29 | 29 | 27 | 26 | 22 | 23 | 24 | 22 | 24 | 24 | 27 | 24 | 24 | 17 | 23 | 26 |  | 29 | 29 | 29 | 28 | 30 | 29 | 28 | 616939
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 37440
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 0 | [22 empty] | 120000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 842 | 842 | 842 | 842 | 843 | 842 | 842 | 842 | 842 | 842 | 842 | 842 | 842 | 842 | 841 | 843 | 842 | 842 |  | 842 | 842 | 841 | 842 | 842 | 842 | 842 | 20354182
147 | Bheramara 410 MW CCPP | 215 | 215 | 220 | 220 | 220 | 220 | 225 | 235 | 230 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 225 |  | 215 | 220 | 220 | 215 | 205 | 210 | 210 | 5441184
148 | Payra 1320 MW | 500 | 500 | 500 | 500 | 500 | 460 | 440 | 440 | 450 | 480 | 480 | 480 | 470 | 400 | 350 | 350 | 350 | 350 |  | 380 | 450 | 460 | 480 | 500 | 510 | 470 | 11825900
149
150 | Barapukuria TPP Unit-1 | 72 | 72 | 72 | 72 | 72 | 68 | 68 | 73 | 73 | 73 | 72 | 72 | 73 | 74 | 74 | 74 | 74 | 75 |  | 73 | 75 | 76 | 73 | 74 | 74 | 75 | 1686109
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3667500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 |  | 244793
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 102 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 97 |  | 92 | 92 | 90 | 88 | 87 | 84 | 84 | 2307100
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 160 | 160 | 160 | 160 | 160 | 160 | 130 | 139 | 152 | 143 | 138 | 135 | 138 | 148 | 148 | 148 | 147 | 145 |  | 145 | 145 | 145 | 150 | 142 | 140 | 140 | 3781082
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 180 | 185 | 180 | 180 | 180 | 130 | 143 | 191 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 160 | 159 | 160 | 150 | 150 | 150 | 4153936
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 297 | 334 | 363 | 417 | 369 | 360 | 357 | 365 | 404 | 366 | 366 | 343 | 287 | 313 | 306 | 318 | 390 | 385 |  | 380 | 410 | 421 | 420 | 422 | 399 | 376 | 8829900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 5 | 5 | 5 | 21 | 20 | 21 | 21 | 21 | 0 | 21 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 441840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 8 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 206550
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 9910
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [17 empty] | 18 |  | 40 | 42 | 42 | 41 | 41 |  |  | 182618
169 | Natore 52 MW PP (Rajlanka) | 45 | 52 | 52 | 52 | 0 |  |  |  | 38 | 52 | 52 | 52 | 52 | [6 empty] | 24 | 24 | 24 | 52 | 52 | 52 | 52 | 727200
170 | Chapainawabganj 100 MW Peaking PP | 100 | 100 | 100 | 0 | [15 empty] | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 627928
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 70 | 70 | 0 | [5 empty] | 8 | 35 | 35 | 35 |  |  |  |  | 32 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 690048
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 35 | 35 | 0 | [13 empty] | 25 |  | 35 | 35 | 35 | 35 | 35 |  |  | 385920
173 | Rangpur 20 MW GTPP | [19 empty] | 12 | 12 | 18 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 34 | 0 |  |  |  |  | 50 | 54 | 110 | 113 | 5 |  |  | 5 | 37 |  | 69 | 70 | 70 | 70 | 70 | 70 | 70 | 1224000
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 1 | 1 | 1 | 3 | 6 | 5 | 3 | 2 | 1 | [8 empty] | 30716
178
178