## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-15 | Saturday
|  |  | Date (day): | 2021-05-15 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13776.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14686 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-14 | 2021-05-15 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 120 | 120 | 120 | 120
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 12 | 95 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 281 | 341 | 350 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 277 | 345 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 220 | 235 | 260 | 260 | 45 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 15 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 72 | 150 | 120 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 150 | 160 | 220 | 220 |  | 115 | ST under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 0 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 28 | 42 | 42 |  | 38 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 30 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 1515 | 1859 | 3730 | 4040 | 426 | 1191
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 8 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 23 | 22 | 22 | 23 | 207 |  | Unit 4 & 5 Under S/D due to Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 203 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 130 | 130 | 130 | 140
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 51 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 50 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 20 | 40
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 9 | 10 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 486 | 752 | 1647 | 1653 | 387 | 345
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 163 | 187 | 200 | 200 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 295 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 305 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 5 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 20 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 55 | 55 | 55 | 140 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 41 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 87 | 90 | 92 | 71 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 19 | 132 | 160 | 160 |  | 40 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 136 | 145 | 179
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 46 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 35 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 18 | 18 |  | 36 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1051 | 1547 | 2155 | 2341 | 529 | 100
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 205 | 205 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 17 | 17 |  | 5 | Engine problem
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 4 | 65 | 65 | 65 |  | 30 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 60 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 19 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 41 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 271 | 488 | 670.6 | 619 | 0 | 35
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 36 | 36 | 44 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 100 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 330 | 330 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 0 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 52 | 40 | 40 |  | 26
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 75 | 75 | 75 |  | 11 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 150 | 223 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 270 | 300 | 0 | 0 |  |  | under S/D due to gas line maint.
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 373 | 328 | 0 | 0 |  |  | under S/D due to gas line maint.
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 8 | 8
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 401 | 0 | 0 |  |  | under S/D due to gas line maint.
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1661 | 2055 | 1023 | 1023 | 0 | 220
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 575 | 910 | 780 | 925
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 280 | 365 | 390 | 390 | 20 |  | Gas shortage
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 35 | 105 | 105
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 855 | 1441 | 1636 | 2051 | 20 | 107
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 28 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 87 | 88 | 88 |  | 106 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 32 | 97 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 250 | 350 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 80 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 394 | 610 | 1028 | 1028 | 0 | 106
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 |  | 20 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 130 | 152 | 200 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 130 | 140 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 337 | 414 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 41 | 0 | 32 |  | 18 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 0 | 18 | 22 | 22
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 0 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 50 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 0 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 10 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 605 | 830 | 1616 | 1648 | 381 | 53
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 48 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 157 | 198 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 21967 | 21219 | 6995 | 9780 | 13776.6 | 14686 | 1952 | 2262
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6700.3231 | 9368 | 13196.2361 | 14067.326
| A. |  | 2021-05-14 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 9961 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 6470 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 9780 | MW
| 3 | Day peak Generation : |  |  | 6995 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9368 | MW
| 4 | Evening peak Generation : |  |  | 9780 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 191.6542 | MKWHr | By Solar | 0.74092 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 139.8372 | MKWHr |  | By Oil: | 17.1215 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.0946 | MKWHr |  | By Hydro: | 0.4626 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1952 | MW | Dhaka | 2625 | 2625 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2262 | MW | Chittagong | 799 | 799 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4214 | MW | Khulna | 1376 | 1376 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1144.2 | MMCFD |  |  | Rajshahi | 1066 | 1066 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 150337556.64 | ii) Oil : | Taka | 107088231.42 | Comilla | 1240 | 1240 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 56862622 | Total | Taka | 314288410.06 | Mymensingh | 915 | 915 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 4.092 | MKWHr. | Sylhet | 395 | 395 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -410 | MW (E to W) at | 21:00 | hrs | Barisal | 303 | 303 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -470 | MW at | 20:00 | hrs | Rangpur | 649 | 649 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.6° C |  |  | Total | 9368 | 9368 |  | 0
| B. |  | 2021-05-15 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 35.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14686 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3686 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 211.6451 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6568 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 18.7084 | MKWHr. | ii) HVDC Flow at Peak Time |  | 910 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.689 | MKWHr. | iii) Maximum HVDC Flow : |  | 912 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.51 |  | (b) Today: | 75.37 |  | (c) Rule Curve: |  | 79.34
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-14
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 342 | 300 |  | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 0 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 100 | 265 | 265 | 180 | 8 | 92 | 26 | 5 | 0 | 5 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 120 | 215 | 65 | 19 | 0 | 35 | 42 | 5 | 0 | 163 | 280 | 40 | 5 | 0 | 216 | 0 | 0 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 124 | 0 | 322 | 8 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 909 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 96 | 0 | 174 | 0 | 284 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5661 | 2823 | 8484 | 4435 | 909 | 1499 | 898 | 550 | 22 | 51 | 120 | 0 | 0 | 75.56
2:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 305 | 300 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 202 | 0 | 130 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 100 | 265 | 265 | 180 | 8 | 86 | 26 | 5 | 0 | 5 | 0 | 0 | 25 | 22 | 11 | 25 | 20 | 116 | 214 | 65 | 19 | 0 | 35 | 42 | 5 | 0 | 163 | 280 | 40 | 5 | 0 | 216 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 85 | 0 | 322 | 0 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 35 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 672 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 95 | 0 | 175 | 0 | 293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5562 | 2557 | 8119 | 4391 | 672 | 1523 | 811 | 550 | 22 | 34 | 116 | 0 | 0 | 75.55
3:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 305 | 300 |  | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 100 | 270 | 265 | 180 | 8 | 86 | 26 | 5 | 0 | 5 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 112 | 213 | 65 | 19 | 0 | 35 | 42 | 5 | 0 | 130 | 282 | 40 | 5 | 0 | 156 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 85 | 0 | 319 | 0 | 0 | 17 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 671 | 0 | 300 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 96 | 0 | 175 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5383 | 2424 | 7807 | 4255 | 671 | 1481 | 682 | 550 | 22 | 34 | 112 | 0 | 0 | 75.54
4:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 272 | 300 |  | 0 | 280 | 230 | 0 | 0 | 0 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 265 | 265 | 180 | 8 | 86 | 5 | 5 | 0 | 0 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 110 | 213 | 24 | 0 | 0 | 35 | 42 | 0 | 0 | 130 | 285 | 40 | 0 | 0 | 162 | 0 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68 | 0 | 319 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 672 | 0 | 300 | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 96 | 0 | 172 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 0 | 0 | 0 |  | 5111 | 2343 | 7454 | 4123 | 672 | 1461 | 547 | 520 | 21 | 0 | 110 | 0 | 0 | 75.53
5:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 270 | 300 |  | 0 | 280 | 245 | 0 | 0 | 0 | 150 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 265 | 265 | 180 | 8 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 0 | 102 | 213 | 8 | 0 | 0 | 35 | 42 | 0 | 0 | 130 | 285 | 40 | 0 | 0 | 163 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 68 | 0 | 318 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 671 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 72 | 0 | 130 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 5002 | 2209 | 7211 | 4014 | 671 | 1444 | 469 | 490 | 21 | 0 | 102 | 0 | 0 | 75.52
6:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 270 | 270 |  | 0 | 280 | 245 | 0 | 0 | 0 | 150 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 0 | 8 | 204 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 265 | 265 | 160 | 8 | 91 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 96 | 175 | 0 | 0 | 0 | 35 | 42 | 0 | 0 | 100 | 282 | 40 | 0 | 0 | 143 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 280 | 0 | 1 | 0 | 0 | 0 | 17 | 1 |  | 576 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 72 | 0 | 130 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 0 |  | 4705 | 2091 | 6796 | 3900 | 576 | 1438 | 313 | 450 | 21 | 0 | 96 | 2 | 0 | 75.51
7:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 270 | 270 |  | 0 | 280 | 260 | 0 | 0 | 0 | 150 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 260 | 265 | 161 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 100 | 174 | 0 | 0 | 0 | 35 | 42 | 0 | 0 | 100 | 285 | 40 | 0 | 0 | 156 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 319 | 0 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 0 | 280 | 0 | 5 | 0 | 0 | 0 | 17 | 7 |  | 576 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 72 | 0 | 130 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 0 | 0 | 0 |  | 4760 | 2090 | 6850 | 3902 | 576 | 1457 | 328 | 450 | 22 | 0 | 100 | 15 | 0 | 75.5
8:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 269 | 270 |  | 0 | 280 | 260 | 0 | 0 | 0 | 150 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 250 | 245 | 161 | 8 | 86 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 94 | 174 | 0 | 0 | 1 | 35 | 42 | 0 | 0 | 100 | 283 | 40 | 0 | 0 | 162 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 16 | 0 | 326 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 280 | 0 | 20 | 0 | 0 | 0 | 17 | 13 |  | 576 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 36 | 0 | 130 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 0 | 0 | 0 |  | 4736 | 1996 | 6732 | 3879 | 576 | 1333 | 328 | 450 | 22 | 0 | 94 | 50 | 0 | 75.49
9:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 251 | 248 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 216 | 0 | 100 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 245 | 230 | 162 | 8 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 94 | 155 | 0 | 0 | 1 | 36 | 43 | 0 | 0 | 100 | 284 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 16 | 0 | 240 | 0 | 0 | 0 | 4 | 0 | 17 | 0 | 0 | 0 | 0 | 260 | 0 | 17 | 0 | 0 | 0 | 17 | 17 |  | 576 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 32 | 0 | 130 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 0 | 0 | 0 |  | 4501 | 1969 | 6470 | 3691 | 576 | 1344 | 288 | 400 | 22 | 0 | 94 | 55 | 0 | 0
10:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 252 | 277 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 260 | 230 | 162 | 8 | 86 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 100 | 207 | 0 | 0 | 1 | 36 | 43 | 0 | 0 | 100 | 332 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 16 | 0 | 320 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 260 | 0 | 22 | 0 | 0 | 0 | 17 | 30 |  | 576 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 33 | 0 | 130 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 250 | 0 | 0 | 0 |  | 4692 | 1999 | 6691 | 3943 | 576 | 1291 | 288 | 400 | 23 | 0 | 100 | 70 | 0 | 0
11:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 252 | 278 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 260 | 230 | 163 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 9 | 25 | 20 | 100 | 207 | 0 | 0 | 1 | 36 | 42 | 0 | 0 | 100 | 331 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 16 | 0 | 321 | 0 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 5 | 260 | 0 | 54 | 0 | 0 | 0 | 17 | 33 |  | 576 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 31 | 0 | 130 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 250 | 0 | 0 | 0 |  | 4762 | 2001 | 6763 | 3944 | 576 | 1313 | 293 | 400 | 23 | 0 | 100 | 114 | 0 | 0
12:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 281 | 277 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 260 | 230 | 163 | 8 | 91 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 25 | 20 | 100 | 205 | 4 | 0 | 2 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 19 | 0 | 373 | 19 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 9 | 320 | 0 | 41 | 0 | 0 | 0 | 17 | 30 |  | 575 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 32 | 0 | 130 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 250 | 0 | 0 | 0 |  | 4984 | 2011 | 6995 | 4083 | 575 | 1389 | 323 | 400 | 23 | 0 | 100 | 102 | 0 | 0
13:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 302 | 277 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 210 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 285 | 255 | 162 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 16 | 20 | 106 | 202 | 49 | 0 | 2 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 60 | 0 | 379 | 32 | 0 | 0 | 6 | 0 | 17 | 0 | 0 | 0 | 10 | 320 | 0 | 50 | 0 | 0 | 0 | 17 | 32 |  | 786 | 0 | 280 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 31 | 0 | 197 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 250 | 0 | 0 | 0 |  | 5218 | 2321 | 7539 | 4220 | 786 | 1434 | 455 | 400 | 23 | 0 | 106 | 115 | 0 | 0
14:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 302 | 278 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 270 | 285 | 162 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 16 | 20 | 108 | 201 | 49 | 0 | 2 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 82 | 0 | 384 | 56 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 10 | 320 | 0 | 41 | 0 | 0 | 0 | 17 | 27 |  | 769 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 53 | 0 | 192 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 250 | 0 | 0 | 0 |  | 5252 | 2336 | 7588 | 4233 | 769 | 1441 | 518 | 400 | 23 | 0 | 108 | 96 | 0 | 75.43
15:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 302 | 278 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 285 | 285 | 161 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 19 | 108 | 200 | 49 | 0 | 2 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 300 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 117 | 0 | 367 | 65 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 320 | 0 | 33 | 0 | 0 | 0 | 17 | 22 |  | 768 | 0 | 280 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 72 | 0 | 188 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 0 | 0 | 0 |  | 5271 | 2318 | 7589 | 4221 | 768 | 1431 | 562 | 400 | 22 | 0 | 108 | 77 | 0 | 75.43
16:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 302 | 242 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 285 | 285 | 161 | 8 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 25 | 19 | 104 | 200 | 49 | 0 | 1 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 275 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 120 | 0 | 306 | 8 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 320 | 0 | 27 | 0 | 0 | 0 | 17 | 15 |  | 768 | 0 | 250 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 51 | 0 | 178 | 0 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 0 | 0 | 0 |  | 5073 | 2200 | 7273 | 4126 | 768 | 1327 | 475 | 400 | 22 | 0 | 104 | 51 | 0 | 75.43
17:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 292 | 243 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 285 | 285 | 161 | 8 | 90 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 16 | 20 | 100 | 200 | 64 | 0 | 1 | 36 | 42 | 0 | 0 | 100 | 308 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 260 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 68 | 0 | 250 | 8 | 0 | 0 | 1 | 0 | 17 | 0 | 0 | 0 | 10 | 260 | 0 | 11 | 0 | 0 | 0 | 17 | 7 |  | 768 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 52 | 0 | 130 | 0 | 322 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 0 | 0 | 0 |  | 4788 | 2162 | 6950 | 3877 | 768 | 1337 | 422 | 400 | 22 | 0 | 100 | 24 | 0 | 75.43
18:00 | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 253 | 243 |  | 0 | 280 | 220 | 0 | 0 | 0 | 90 | 0 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 8 | 203 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 270 | 235 | 162 | 8 | 85 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 21 | 10 | 33 | 20 | 98 | 202 | 32 | 0 | 0 | 35 | 42 | 0 | 0 | 100 | 308 | 40 | 0 | 0 | 122 | 0 | 0 | 0 | 270 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 0 | 241 | 8 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 10 | 260 | 0 | 2 | 0 | 0 | 0 | 17 | 1 |  | 767 | 0 | 210 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 10 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 51 | 0 | 130 | 0 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 250 | 0 | 0 | 0 |  | 4558 | 2105 | 6663 | 3651 | 767 | 1315 | 406 | 400 | 22 | 0 | 98 | 4 | 0 | 75.43
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 120 | 0 | 55 | 0 | 281 | 337 |  | 0 | 280 | 267 | 0 | 0 | 0 | 165 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 9 | 204 | 0 | 140 | 0 |  | 0 | 0 | 51 | 50 | 0 | 0 | 22 | 40 | 0 | 0 | 80 | 290 | 295 | 213 | 12 | 86 | 26 | 5 | 0 | 12 | 0 | 0 | 0 | 21 | 10 | 33 | 20 | 128 | 201 | 48 | 0 | 0 | 36 | 42 | 26 | 0 | 100 | 328 | 40 | 50 | 0 | 220 | 0 | 0 | 7 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 72 | 0 | 367 | 46 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 2 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 891 | 0 | 365 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 14 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 83 | 0 | 148 | 0 | 390 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 270 | 0 | 0 | 0 |  | 5852 | 2754 | 8606 | 4650 | 891 | 1739 | 641 | 420 | 22 | 115 | 128 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 120 | 0 | 85 | 0 | 339 | 346 |  | 0 | 280 | 230 | 0 | 0 | 5 | 162 | 0 | 115 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 140 | 0 |  | 3 | 0 | 51 | 70 | 0 | 0 | 22 | 30 | 0 | 0 | 80 | 290 | 295 | 186 | 45 | 86 | 26 | 5 | 0 | 30 | 0 | 0 | 12 | 21 | 10 | 33 | 20 | 130 | 205 | 65 | 0 | 0 | 36 | 42 | 53 | 0 | 163 | 329 | 52 | 75 | 0 | 215 | 18 | 0 | 7 | 275 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 0 | 50 | 120 | 0 | 326 | 115 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 911 | 0 | 355 | 0 | 94 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 32 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 206 | 0 | 96 | 0 | 160 | 0 | 365 | 35 | 0 | 30 | 0 | 34 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 6416 | 3093 | 9509 | 4685 | 911 | 1895 | 1243 | 490 | 22 | 133 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 120 | 0 | 91 | 0 | 340 | 346 |  | 0 | 280 | 235 | 0 | 0 | 7 | 160 | 0 | 114 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 3 | 20 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 10 | 0 | 51 | 100 | 0 | 0 | 22 | 40 | 0 | 0 | 80 | 295 | 295 | 182 | 55 | 86 | 26 | 5 | 0 | 38 | 0 | 0 | 32 | 22 | 10 | 33 | 20 | 132 | 205 | 65 | 19 | 0 | 36 | 42 | 50 | 0 | 163 | 334 | 52 | 75 | 0 | 216 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 48 | 0 | 25 | 0 | 50 | 114 | 0 | 329 | 115 | 12 | 34 | 0 | 0 | 49 | 0 | 0 | 35 | 10 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 912 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 23 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 16 | 38 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 97 | 0 | 140 | 0 | 363 | 35 | 0 | 31 | 0 | 34 | 0 | 0 | 0 | 340 | 0 | 0 | 0 |  | 6494 | 3060 | 9554 | 4639 | 912 | 1921 | 1299 | 490 | 22 | 139 | 132 | 0 | 0 | 75.42
21:00 | 0 | 0 | 0 | 120 | 0 | 95 | 0 | 341 | 345 |  | 0 | 280 | 235 | 0 | 0 | 15 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 295 | 305 | 187 | 55 | 87 | 26 | 20 | 0 | 41 | 0 | 0 | 46 | 22 | 10 | 33 | 20 | 136 | 205 | 65 | 19 | 0 | 36 | 42 | 53 | 0 | 163 | 330 | 52 | 75 | 0 | 223 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 0 | 50 | 132 | 0 | 328 | 115 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 910 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 41 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 97 | 0 | 140 | 0 | 414 | 35 | 0 | 0 | 0 | 48 | 0 | 0 | 10 | 350 | 0 | 0 | 0 |  | 6701 | 3079 | 9780 | 4709 | 910 | 2033 | 1328 | 500 | 22 | 142 | 136 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 328 | 346 |  | 0 | 280 | 230 | 0 | 0 | 15 | 160 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 41 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 290 | 300 | 181 | 55 | 86 | 26 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 140 | 207 | 65 | 19 | 0 | 36 | 42 | 53 | 0 | 163 | 330 | 52 | 75 | 0 | 223 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 0 | 50 | 124 | 0 | 328 | 115 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 912 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 87 | 29 | 64 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 41 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 97 | 0 | 194 | 0 | 369 | 35 | 0 | 31 | 0 | 63 | 0 | 0 | 35 | 440 | 0 | 0 | 0 |  | 6679 | 3282 | 9961 | 4744 | 912 | 2013 | 1409 | 590 | 22 | 131 | 140 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 320 | 346 |  | 0 | 280 | 230 | 0 | 0 | 15 | 160 | 0 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 290 | 300 | 181 | 55 | 86 | 26 | 56 | 0 | 43 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 140 | 209 | 65 | 19 | 0 | 35 | 42 | 53 | 0 | 130 | 330 | 52 | 75 | 0 | 223 | 18 | 0 | 7 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 0 | 50 | 126 | 0 | 303 | 115 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 912 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 0 | 41 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 95 | 0 | 214 | 0 | 365 | 35 | 0 | 35 | 0 | 74 | 0 | 0 | 35 | 450 | 0 | 0 | 0 |  | 6475 | 3332 | 9807 | 4614 | 912 | 1953 | 1425 | 600 | 22 | 141 | 140 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 120 | 0 | 104 | 0 | 322 | 346 |  | 0 | 280 | 230 | 0 | 0 | 15 | 160 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 0 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 290 | 300 | 181 | 55 | 86 | 26 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 138 | 208 | 65 | 19 | 0 | 35 | 42 | 53 | 0 | 130 | 330 | 52 | 75 | 0 | 183 | 18 | 0 | 7 | 230 | 16 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 30 | 0 | 30 | 140 | 0 | 304 | 115 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 300 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 912 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 96 | 0 | 215 | 0 | 382 | 35 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 450 | 0 | 0 | 0 |  | 6359 | 3175 | 9534 | 4582 | 912 | 1944 | 1260 | 600 | 23 | 75 | 138 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 2866500 | 0 | 722409 | 0 | 7162880 | 7032000 |  | 0 | 6638500 | 5625047 | 0 | 0 | 70968 | 3894947 | 0 | 2391000 | 13440 | 0 | 0 | 0 | 0 | 0 | 0 | 21600 | 0 | 0 | 53784 | 600000 | 113040 | 719600 | 605100 | 0 | 0 | 462600 | 0 | 0 | 0 | 292302 | 4827898 | 0 | 2854638 | 0 |  | 84240 | 0 | 422482 | 1105320 | 0 | 0 | 512736 | 1153920 | 0 | 0 | 1993582 | 6892000 | 6542000 | 4180000 | 418181 | 2077190 | 312984 | 319200 | 0 | 378626 | 0 | 0 | 318379 | 502524 | 232740 | 599500 | 452520 | 2688960 | 4664640 | 932160 | 151272 | 12450 | 844000 | 1003440 | 280200 | 0 | 3144518 | 7053000 | 1016448 | 452160 | 0 | 4163500 | 96000 | 0 | 34740 | 6652000 | 80496 | 144 | 0 | 0 | 0 | 0 | 297600 | 0 | 151632 | 122445 | 350400 | 1868640 | 0 | 7697000 | 859200 | 13200 | 329527 | 30602 | 0 | 803231 | 0 | 0 | 294840 | 150720 | 7399500 | 0 | 292670 | 0 | 0 | 0 | 444240 | 239853 |  | 18708364 | 0 | 7425504 | 0 | 925440 | 0 | 0 | 0 | 0 | 0 | 157875 | 2118270 | 607984 | 413090 | 0 | 0 | 0 | 0 | 0 | 252216 | 0 | 0 | 0 | 17280 | 174257 | 98160 | 0 | 176130 | 0 | 0 | 3657600 | 0 | 0 | 0 | 0 | 3779700 | 0 | 1656653 | 0 | 4245918 | 0 | 7945872 | 252000 | 0 | 124896 | 0 | 273600 | 0 | 42904 | 81696 | 8437000 | 0 | 0 | 0 |  | 130081805 | 61572409 | 191654214 | 102302125 | 18708364 | 37535123 | 16272563 | 12094600 | 462600 | 848955 | 2688960 | 740924 | 0
Fuel Cost | 0 | 0 | 0 | 4213755 | 0 | 953579.88 | 0 | 7234508.8 | 7242960 |  | 0 | 7235965 | 6243802.17 | 0 | 0 | 600389.28 | 4050744.88 | 0 | 4136430 | 101203.2 | 0 | 0 | 0 | 0 | 0 | 0 | 157680 | 0 | 0 | 40338 | 450000 | 0 | 0 | 0 | 0 | 0 | 124902 | 0 | 0 | 0 | 2715485.58 | 5262408.82 | 0 | 4852884.6 | 0 |  | 0 | 0 | 4098075.4 | 10555806 | 0 | 0 | 646047.36 | 3427142.4 | 0 | 0 | 2930565.54 | 5100080 | 6542000 | 3845600 | 539453.49 | 2388768.5 | 353671.92 | 446880 | 0 | 647450.46 | 0 | 0 | 3040519.45 | 638205.48 | 174555 | 1049125 | 339390 | 20167200 | 4944518.4 | 8464012.8 | 192115.44 | 198453 | 1384160 | 1605504 | 498756 | 0 | 3584750.52 | 7335120 | 2002402.56 | 863625.6 | 0 | 7202855 | 210240 | 0 | 70869.6 | 6718520 | 60372 | 109.44 | 0 | 0 | 0 | 0 | 1547520 | 0 | 1492058.88 | 1431382.05 | 2855760 | 20274744 | 0 | 7158210 | 7835904 | 124740 | 2870180.17 | 0 | 0 | 6996142.01 | 0 | 0 | 2526778.8 | 1003795.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 107760176.64 | 0 | 7796779.2 | 0 | 7273958.4 | 0 | 0 | 0 | 0 | 0 | 1645057.5 | 2393645.1 | 942375.2 | 4031758.4 | 0 | 0 | 0 | 0 | 0 | 2232111.6 | 0 | 0 | 0 | 167443.2 | 1690292.9 | 188467.2 | 0 | 133330.41 | 0 | 0 | 19824192 | 0 | 0 | 0 | 0 | 4989204 | 0 | 2484979.5 | 0 | 4967724.06 | 0 | 7866413.28 | 2630880 | 0 | 1185263.04 | 0 | 2123136 | 0 | 474089.2 | 603733.44 | 37038430 | 0 | 0 | 0 |  | 224001172.68 | 220443440.27 | 444444612.95 | 106625368.51 | 107760176.64 | 43712188.13 | 99067751.52 | 56862622 | 124902 | 8020479.9 | 20167200 | 2103924.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 281 | 277 |  | 0 | 280 | 220 | 0 | 0 | 0 | 150 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 8 | 203 | 0 | 130 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 260 | 230 | 163 | 8 | 91 | 5 | 5 | 0 | 0 | 0 | 0 | 0 | 20 | 8 | 25 | 20 | 100 | 205 | 4 | 0 | 2 | 36 | 42 | 0 | 0 | 100 | 330 | 40 | 0 | 0 | 150 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 19 | 0 | 373 | 19 | 0 | 0 | 2 | 0 | 17 | 0 | 0 | 0 | 9 | 320 | 0 | 41 | 0 | 0 | 0 | 17 | 30 |  | 575 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 32 | 0 | 130 | 0 | 337 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 250 | 0 | 0 | 0 |  | 6995 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 120 | 0 | 95 | 0 | 341 | 345 | 0 | 0 | 280 | 235 | 0 | 0 | 15 | 160 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 | 0 | 24 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 295 | 305 | 187 | 55 | 87 | 26 | 20 | 0 | 41 | 0 | 0 | 46 | 22 | 10 | 33 | 20 | 136 | 205 | 65 | 19 | 0 | 36 | 42 | 53 | 0 | 163 | 330 | 52 | 75 | 0 | 223 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 30 | 0 | 50 | 132 | 0 | 328 | 115 | 0 | 51 | 0 | 0 | 54 | 0 | 0 | 35 | 10 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 910 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 28 | 48 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 41 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 152 | 0 | 97 | 0 | 140 | 0 | 414 | 35 | 0 | 0 | 0 | 48 | 0 | 0 | 10 | 350 | 0 | 0 | 0 |  | 9780 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 360 | 360 | 0 | 0 | 280 | 260 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 33 | 52 | 0 | 23 | 0 | 0 | 0 | 17 | 225 | 0 | 140 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 40 | 0 | 0 | 80 | 330 | 330 | 200 | 55 | 92 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 179 | 200 | 65 | 17 | 0 | 44 | 42 | 51 | 0 | 163 | 330 | 40 | 75 | 0 | 225 | 18 | 0 | 8 | 0 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 160 | 150 | 0 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 0 | 162 | 116 | 0 | 18 |  |  | 925 | 0 | 390 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 80
Forecast for Day | 0 | 0 | 0 | 120 | 0 | 100 | 0 | 350 | 360 | 0 | 0 | 280 | 260 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 17 | 33 | 33 | 52 | 0 | 22 | 0 | 0 | 0 | 17 | 225 | 0 | 130 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 20 | 0 | 0 | 80 | 330 | 330 | 200 | 55 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 145 | 200 | 65 | 17 | 1.6 | 44 | 42 | 51 | 0 | 163 | 330 | 40 | 75 | 0 | 225 | 18 | 0 | 8 | 0 | 16 | 11 | 100 | 250 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 160 | 150 | 0 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 0 | 90 | 50 | 162 | 116 | 0 | 18 | 30 |  | 780 | 0 | 390 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 80
Generation at 08:00(Today) | 0 | 0 | 0 | 120 | 0 | 12 | 0 | 342 | 270 | 0 | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 3 | 20 |  | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 212 | 0 | 80 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 22 | 42 | 0 | 0 | 80 | 275 | 280 | 190 | 55 | 92 | 26 | 5 | 0 | 7 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 96 | 187 | 0 | 0 | 1 | 35 | 42 | 8 | 0 | 110 | 305 | 40 | 5 | 0 | 189 | 18 | 0 | 0 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 17 | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 0 | 0 | 0 | 17 | 12 | 0 | 696 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 23 | 0 | 186 | 0 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 250 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 6470 | 9:00
| Highest Generation |  | 9961 | 22:00
| Day Peak Generation |  | 6995 | 12:00
| Evening Peak Generation |  | 9780 | 21:00
| HVDC Max Flow |  | 912 | 20:00
| HVDC EvPeak Flow |  | 910 | 21:00
| Load factor L.F |  | 80.17%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-15
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-14 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 6995 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 6568 | MW
Evening Peak Generation : |  | 9780 | MW Hour : | 21:00 | Available Max Generation : |  | 14686 | MW
E.P. Demand (at gen end) : |  | 9780 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 9961 | MW Hour : | 22:00 | Reserve(Generation end) |  | 3686 | MW
Total Gen. (MKWH) : |  | 191.6542 | System Load Factor : | 80.17% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -470 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-15
Actual : | 75.37 | Ft.(MSL) , | Rule curve : | 79.34 | Ft.( MSL )
Gas Consumed : | Total = | 1144.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 150337556.64
: |  | Coal : | 56862622 | Oil : | 107088231.42 | Total : | 314288410.06
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3923.1681 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1333.9147 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1195.1113 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1079.8725 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 975.8715 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 787.4933 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 440.5586 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 202.7645 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 607.3528 |  |  | 0 | 0%
Total | 0 |  | 10546.1073 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #1,2
6) Sirajganj unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bheramara 230/132 kV T-2 transformer tripped at 10:47 showing PRD relay and was switched on at 12:50.
again tripped at 21:13 showing same relay and was switched on at 04:48(15-05-21).
b) Shajadpur 132/33 kV T-1 transformer was under shut down from 20:43 to 21:31 due to red hot maintenance
at R phase isolator.
c) Ghorasal(1)-Ishurdi(2) 230 kV line was shut down since at 20:50 due to red hot maint at R phase jumper
at tower #02 near Ghorasal S/S.
d) Haripur 230 kV CB 845 B(mid CB) was under shut down since 00:28(15-05-2021) due to red hot maintenance.
e) Bibiyana(S) STG & GT were under shut down since 02:15 & 02:52 hr respectively.
f) Bibiyana summit-2 was under shut down since 02:00.
g) Bibiyana -3 STG & GT were under shut down since 04:24 & 05:20 hr respectively.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-14 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 120 | 2866500 | Gas Shortage
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 722409
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 341 | 7162880 | Gas Shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7032000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6638500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 235 | 5625047 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 70968 | Low demand
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 53784 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 2391000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 13440 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 160 | 3894947 | ST under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 0 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 0 | 21600 | Reserve.
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 0 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 28 | 713040 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 719600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 605100 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 0 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 0 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 30 | 151632 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 13200 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 0 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 0 | Reserve.
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 239853
| Dhaka area Total |  |  |  | 5829 | 1859 | 38935500
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 292302 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122445
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve.
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 22 | 462600 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4827898 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2854638
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 51 | 329527 | Low demand
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 422482 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1105320
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 50 | 350400 | Low demand
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 512736
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1153920
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 30602
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 803231
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 150720 | Low demand
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Reserve.
| Chattogram area Total |  |  |  | 2382 | 752 | 13418821
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1993582 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 187 | 4180000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 6892000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6542000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 312984 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 319200 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 55 | 418181 | Gas shortage
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 41 | 378626 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 0 | Reserve.
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 87 | 2077190 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 132 | 1868640 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 502524
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 232740
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 136 | 2688960
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 599500
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 46 | 318379
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 452520 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 35 | 294840 | Low demand
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240
| Cumilla Area Total |  |  |  | 3034 | 1547 | 30516106
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4664640
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 151272 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 65 | 932160 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12450
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 60 | 297600 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 859200
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 292670
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 84240
| Mymensingh Area Total |  |  |  | 709 | 488 | 7294232
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 36 | 844000 | Machine problem
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1003440 | Machine problem
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3144518
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 330 | 7053000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 280200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 144 | Engine problem
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 1016448 | Frequency control
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 452160
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 223 | 4163500
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 96000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 80496 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 6652000 | FGMO
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 328 | 7697000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 34740 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 401 | 7399500 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 2055 | 39917146
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 910 | 18708364
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 925440 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 7425504 | Gas shortage
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 157875 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 0 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 35 | 252000 | Low demand
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1441 | 27469183
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 413090 | Low demand
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 607984
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2118270 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 1656653
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 350 | 8437000
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 610 | 13232997
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 152 | 3779700 | Gas shortage
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 140 | 4245918 | Gas shortage
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 7945872 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 41 | 174257 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 98160 | Engine problem
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 176130 | Engine problem
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 0 | 17280 | Reserve.
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 50 | 252216 | Low demand
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 0 | 124896 | Reserve.
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 10 | 81696 | Reserve.
| Rajshahi Area Total |  |  |  | 2173 | 830 | 16896125
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3657600 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 48 | 273600 | Low demand
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42904
| Rangpur Area Total |  |  |  | 605 | 198 | 3974104
| Total |  |  |  | 21219 | 9780 | 191654214
| Eastern Grid Total |  |  |  | 14331 | 6701 | 130081805
| Western Grid Total |  |  |  | 6888 | 3079 | 61572409
| National Grid Total |  |  |  | 21219 | 9780 | 191654214
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-14
(a) ENTIRE EASTERN GRID : |  | 5974 | MW | (b) ENTIRE WESTERN GRID : |  | 3394 | MW
i) Dhaka area |  | 2625 | MW | i) Khulna area |  | 1376 | MW
ii) Chittagong area |  | 799 | MW | ii) Rajshahi area |  | 1066 | MW
iii) Comilla area |  | 1240 | MW | iii) Barisal area |  | 303 | MW
iv) Mymensingh area |  | 915 | MW | iv) Rangpur area |  | 649 | MW
v) Sylhet area |  | 395 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9368 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 68 | 1:00 | Netrokona | 117 | 20:00 | Benapol | 46 | 20:00
Munsiganj | 84 | 22:00 | Jamalpur | 132 | 22:00 | Jhenida | 108 | 19:30
Sonargaon | 34 | 21:00 | Sherpur | 108 | 23:00 | Bottail | 100 | 19:30
Shyampur | 64 | 23:00 | Srimongal | 41 | 21:00 | G.K Project | 53 | 21:00
Bhulta | 88 | 22:00 | Shahjibazar | 81 | 22:00 | Faridpur | 176 | 21:00
Madanganj | 20 | 14:00 | Fenchuganj | 38 | 19:00 | Madaripur | 97 | 21:00
Shitalakhya | 48 | 23:00 | Kulawara | 36 | 19:00 | Sariatpur | 64 | 21:00
Rahim steel | 0 | 1:00 | Sylhet | 85 | 20:00 | Gopalganj | 84 | 21:00
Matuail | 30 | 23:00 | Chatak | 27 | 20:00 | Bagerhat | 95 | 21:00
Ghorasal | 46 | 21:00 | Sunamganj | 42 | 19:30 | Mongla | 12 | 1:00
Narsingdi | 122 | 21:00 | Biani Bazar | 53 | 21:00 | Satkhira | 112 | 21:00
Haripur (SBU) | 37 | 22:00 | Comilla (S) | 140 | 22:00 | Gallamari | 27 | 1:00
Sreenagar | 41 | 22:00 | Comilla(N) | 133 | 22:00 | Magura | 52 | 20:00
Ullon | 77 | 23:00 | Chandpur | 70 | 22:00 | Norail | 34 | 19:30
Hasnabad | 52 | 18:30 | Feni | 128 | 23:00 | Chuadanga | 87 | 19:30
Magbazar | 35 | 21:00 | Chowmuhani | 170 | 22:00 | Borguna | 16 | 21:00
Maniknagar | 44 | 19:30 | Ashuganj | 34 | 0:00 | Barisal(N) | 41 | 21:00
Bangabhaban | 6 | 3:00 | Daudkandi | 132 | 20:00 | Barisal (S) | 80 | 19:00
Narinda | 32 | 11:00 | B.Baria | 152 | 23:00 | Patuakhali | 98 | 1:00
Dhanmondi | 89 | 1:00 | Ramganj | 98 | 20:00 | Bhandaria | 52 | 21:00
Lalbag | 26 | 1:00 | Chaddagram | 40 | 22:00 | Borhan Uddin | 39 | 1:00
Madartek | 64 | 23:00 | PHP | 3 | 10:00 | Ishurdi | 52 | 21:00
Dhaka University | 14 | 19:00 | Kochua | 68 | 20:00 | Ruppur Paromanobik | 2 | 19:00
Aftabnagar | 8 | 22:00 | Madunaghat | 50 | 1:00 | Natore | 118 | 22:00
Fatullah | 32 | 22:00 | Hathazari | 76 | 1:00 | Bogra | 103 | 21:00
Nawabganj | 50 | 21:00 | Khulshi | 158 | 1:00 | Noagaon | 93 | 21:00
Keraniganj | 47 | 22:00 | Halishahar | 107 | 18:30 | Rajshahi | 126 | 23:00
Mirpur | 81 | 22:00 | Baraulia | 47 | 1:00 | Rajshahi New | 13 | 20:00
Kalyanpur | 90 | 23:00 | Sikalbaha | 25 | 21:00 | C.Nawabganj | 58 | 22:00
Gulshan | 74 | 19:30 | Dohazari | 92 | 19:00 | Amnura | 44 | 21:00
Uttara | 62 | 21:00 | Cox'sbazar | 100 | 1:00 | Pabna | 88 | 22:00
Uttara New | 17 | 21:00 | Chandraghona | 32 | 19:00 | Shahjadpur | 93 | 22:00
Kamrangirchar | 52 | 24:00 | Kaptai | 3.5 | 19:00 | Serajganj | 80 | 20:00
Savar | 102 | 23:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 54 | 21:00
Bhasantec | 106 | 22:00 | Bakulia | 79 | 1:00 | Joypurhat | 50 | 21:00
Agargaon | 58 | 23:00 | Julda | 21 | 16:00 | Sherpur(Bogura) | 44 | 19:30
Satmosjid | 73 | 24:00 | TK chemical | 25.2 | 1:00 | Mohastangor | 66 | 21:00
Tongi | 76 | 20:00 | Modern Steel | 0 | #N/A | Bangura | 32 | 21:00
Kabirpur | 118 | 19:30 | Shahmirpur | 20 | 22:00 | Rangpur | 99 | 20:00
Basundhara | 112 | 23:00 | Khagrachhari | 24 | 11:00 | Lalmonirhat | 35 | 20:00
Manikganj | 66 | 21:00 | Matarbari | 36 | 1:00 | Saidpur | 78 | 20:00
Joydevpur | 88 | 21:00 | Baroiar Hat | 40 | 19:30 | Purbasadipur | 79 | 21:00
New Tongi | 49 | 0:00 | Rangamati | 10 | 18:30 | Thakurgaon | 69 | 21:00
Kodda | 117 | 21:00 | Abul Khair 230 | 63 | 3:00 | Palashbari | 97 | 21:00
Dhamrai | 72 | 21:00 | BSRM | 2 | 18:00 | Barapukuria | 43 | 21:00
Rajendrapur | 74 | 20:00 | GPH Ispat | 3 | 2:00 | Panchagar | 41 | 20:00
Valuka | 90 | 20:00 | Goalpara | 17 | 1:00 | Joldhaka | 45 | 21:00
Tangail | 198 | 20:00 | Central s/s | 81 | 1:00 | Kurigram | 49 | 20:00
Mymensing | 168 | 21:00 | Noapara | 43 | 20:00 | Mithapukur | 25 | 20:00
Kishoreganj | 132 | 21:00 | Jessore | 98 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-14 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 408 | 3:00 | 401 | 23:00 | Kaliakoir | 394 | 0.75 | 383 | 0.95833
| Bheramara | 406 | 2:00 | 389 | 21:00 | Bhulta | 382 | 0.16667 | 375 | 0.625
| Ashuganj(N) | 388 | 2:00 | 382 | 13:00 | Gopalganj | 407 | 0.625 | 383 | 0.91667
| Payra | 411 | 5:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 217 | 11:00 | 210 | 1:00
| Ishurdi | 235 | 3:00 | 224 | 12:00 | Megnaghat | 232 | 19:30 | 228 | 1:00
| Ashuganj | 235 | 1:00 | 230 | 12:00 | Fenchuganj | 241 | 4:00 | 237 | 14:00
| Serajganj | 230 | 1:00 | 225 | 12:00 | Siddhirganj | 230 | 3:00 | 225 | 17:00
| Baghabari | 233 | 4:00 | 225 | 20:00 | Maniknagar | 228 | 3:00 | 225 | 12:00
| Barapukuria | 235 | 3:00 | 226 | 21:00 | Agargaon | 227 | 18:00 | 221 | 19:00
| Bogra | 228 | 6:00 | 214 | 21:00 | Barisal | 248 | 1:00 | 234 | 13:00
| Rajshahi | 235 | 18:00 | 223 | 12:00 | Bhola 225 MW | 248 | 18:00 | 235 | 13:00
| Khulna South | 229 | 18:00 | 210 | 19:00 | AKSML | 218 | 1:00 | 215 | 15:00
| Rampura | 228 | 1:00 | 223 | 20:00 | BSRM | 222 | 20:00 | 215 | 19:00
| Haripur | 228 | 1:00 | 225 | 11:00 | Bibiyana | 241 | 8:00 | 234 | 12:00
| Hasnabad | 232 | 6:00 | 225 | 8:00 | Bhulta | 232 | 5:00 | 224 | 22:00
| Shyampur | 227 | 5:00 | 220 | 19:00 | Ashuganj (S) | 234 | 8:00 | 230 | 14:00
| Aminbazar | 227 | 1:00 | 223 | 2:00 | Kaliakoir | 226 | 3:00 | 218 | 22:00
| Tongi | 225 | 7:00 | 219 | 21:00 | GPH | 220 | 20:00 | 212 | 19:00
| Comilla (N) | 225 | 5:00 | 220 | 19:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 3:00 | 134 | 12:00 | Madanhat | 130 | 0.45833 | 126 | 0.041667
| Munsiganj | 135 | 8:00 | 131 | 19:00 | Hathazari | 130 | 0.45833 | 125 | 0.041667
| Sonargaon | 133 | 4:00 | 131 | 14:00 | Khulshi | 127 | 0.45833 | 122 | 0.79167
| Shyampur | 135 | 4:00 | 131 | 19:00 | Halishahar | 128 | 0.83333 | 124 | 0.041667
| Bhulta | 130 | 4:00 | 128 | 1:00 | Baraulia | 128 | 0.45833 | 125 | 0.125
| Madanganj | 133 | 20:00 | 127 | 16:00 | Sikalbaha | 129 | 0.83333 | 125 | 0.041667
| Shitalakhya | 140 | 5:00 | 130 | 7:00 | Dohazari | 125 | 0.77083 | 121 | 0.041667
| Rahim steal | 136 | 4:00 | 134 | 11:00 | Cox'sbazar | 120 | 0.75 | 110 | 0.041667
| Matuail | 136 | 3:00 | 134 | 12:00 | Chandraghona | 129 | 0.83333 | 124 | 0.25
| Ghorasal | 138 | 1:00 | 136 | 9:00 | Kaptai | 127 | 0.75 | 125 | 0.041667
| Narsinghdi | 134 | 4:00 | 129 | 21:00 | A. Khaer Stl. | 128 | 0.83333 | 124 | 0.29167
| Haripur (SBU) | 135 | 5:00 | 133 | 19:00 | Bakulia | 128 | 0.83333 | 123 | 0.79167
| Sreenagar | 130 | 4:00 | 127 | 19:00 | Julda | 127 | 0.45833 | 125 | 0.16667
| Ullon | 137 | 4:00 | 131 | 19:00 | TK Chemical | 129 | 0.83333 | 124 | 0.041667
| Hasnabad | 138 | 8:00 | 136 | 1:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 136 | 8:00 | 131 | 13:00 | Shahmirpur | 129 | 0.83333 | 124 | 0.29167
| Maniknagar | 138 | 3:00 | 136 | 13:00 | Khagrachhari | 127 | 0.45833 | 123 | 0.25
| Bangabhaban | 138 | 3:00 | 136 | 13:00 | Matarbari | 120 | 0.66667 | 111 | 0.041667
| Narinda | 138 | 3:00 | 136 | 13:00 | Baroiar Hat | 126 | 0.77083 | 121 | 0.79167
| Dhanmondi | 137 | 4:00 | 131 | 19:00 | Rangamati | 128 | 0.45833 | 124 | 0.041667
| Lalbag | 141 | 8:00 | 137 | 19:00 | Goalpara S/S | 138 | 18:00 | 123 | 19:00
| Madartek | 137 | 4:00 | 131 | 13:00 | Khulna Central S/S | 137 | 16:00 | 121 | 19:00
| Dhaka University | 137 | 2:00 | 131 | 19:00 | Noapara | 135 | 16:00 | 120 | 0.79167
| Aftabnagar | 137 | 2:00 | 132 | 11:00 | Jessore | 133 | 18:00 | 116 | 0.79167
| Fatullah | 135 | 4:00 | 132 | 22:00 | Benapol | 133 | 18:00 | 115 | 0.79167
| Nawabganj | 132 | 8:00 | 127 | 14:00 | Jhenida | 130 | 18:00 | 110 | 0.875
| Keraniganj | 132 | 8:00 | 128 | 19:00 | Bottail | 133 | 0.75 | 122 | 0.875
| Mirpur | 135 | 8:00 | 132 | 13:00 | G.K Project | 139 | 18:00 | 132 | 0.875
| Kalyanpur | 136 | 8:00 | 132 | 19:00 | Faridpur | 137 | 0.33333 | 127 | 0.875
| Gulshan | 136 | 4:00 | 131 | 13:00 | Madaripur | 140 | 0.75 | 130 | 0.875
| Uttara | 136 | 18:00 | 131 | 22:00 | Shariyatpur S/S | 139 | 0.75 | 128 | 0.875
| Uttara New | 135 | 4:00 | 130 | 19:00 | Gopalganj | 142 | 0.75 | 130 | 0.875
| Kamrangirchar | 139 | 6:00 | 136 | 13:00 | Bagerhat | 135 | 15:00 | 120 | 0.77083
| Savar | 139 | 6:00 | 136 | 13:00 | Mongla | 135 | 0.66667 | 117 | 0.79167
| Bhasantec | 137 | 8:00 | 132 | 21:00 | Satkhira | 136 | 16:00 | 121 | 0.79167
| Agargaon | 137 | 3:00 | 134 | 13:00 | Gallamari | 139 | 16:00 | 125 | 0.79167
| Satmosjid | 137 | 4:00 | 133 | 19:00 | Magura | 128 | 18:00 | 108 | 21:00
| Tongi | 138 | 8:00 | 135 | 22:00 | Narail | 128 | 0.75 | 108 | 21:00
| Kabirpur | 136 | 18:00 | 132 | 21:00 | Chuadanga | 125 | 18:00 | 100 | 0.875
| Basundhara | 137 | 8:00 | 133 | 18:30 | Borguna | 139 | 0.75 | 128 | 0.54167
| Manikganj | 140 | 0:00 | 133 | 19:00 | Barisal(N) | 141 | 18:00 | 132 | 0.54167
| Joydevpur | 137 | 8:00 | 133 | 21:00 | Barisal (S) | 140 | 18:00 | 128 | 0.54167
| New Tongi | 137 | 8:00 | 133 | 19:00 | Patuakhali(S) | 141 | 18:00 | 127 | 13:00
| Kodda | 135 | 11:00 | 129 | 19:00 | Bhandaria | 136 | 0.75 | 125 | 0.54167
| Dhamrai | 135 | 9:00 | 129 | 19:00 | Ishurdi | 136 | 0.20833 | 130 | 0.79167
| Rajendrapur | 132 | 9:00 | 127 | 19:00 | Ruppur Paromanobik | 136 | 0.66667 | 130 | 0.77083
| Valuka | 125 | 2:00 | 118 | 21:00 | Natore | 136 | 18:00 | 128 | 21:00
| Tangail | 131 | 2:00 | 122 | 19:00 | Bogra | 134 | 6:00 | 125 | 21:00
| Mymensing | 128 | 8:00 | 119 | 19:00 | Noagaon | 132 | 6:00 | 123 | 21:00
| Kishorganj | 131 | 3:00 | 124 | 19:00 | Rajshahi | 134 | 5:00 | 127 | 21:00
| Netrokona | 127 | 18:00 | 118 | 19:00 | Rajshahi New | 136 | 18:00 | 127 | 21:00
| Jamalpur | 130 | 19:00 | 119 | 8:00 | C.Nawabganj | 135 | 9:00 | 125 | 21:00
| Sherpur | 129 | 18:30 | 113 | 11:00 | Amnura | 133 | 18:00 | 126 | 12:00
| Srimongal | 138 | 7:00 | 135 | 13:00 | Pabna | 135 | 7:00 | 128 | 21:00
| Shahjibazar | 136 | 7:00 | 133 | 12:00 | Shahjadpur | 139 | 17:00 | 134 | 20:00
| Fenchuganj | 137 | 6:00 | 134 | 13:00 | Serajganj | 134 | 9:00 | 127 | 21:00
| Khulawara | 137 | 4:00 | 134 | 13:00 | Niyamatpur | 131 | 8:00 | 121 | 21:00
| Sylhet | 134 | 5:00 | 132 | 12:00 | Joypurhat | 133 | 8:00 | 121 | 21:00
| Chatak | 134 | 5:00 | 131 | 18:30 | Sherpur(Bogura) | 135 | 6:00 | 127 | 21:00
| Sunamganj | 132 | 4:00 | 129 | 18:30 | Mohastangor | 134 | 9:00 | 124 | 21:00
| Biani Bazar | 134 | 4:00 | 131 | 14:00 | Bangura | 136 | 10:00 | 132 | 21:00
| Comilla(s) | 128 | 5:00 | 123 | 19:00 | Rangpur | 129 | 4:00 | 116 | 21:00
| Comilla(n) | 133 | 8:00 | 128 | 19:00 | Lalmonirhat | 130 | 4:00 | 120 | 19:30
| Chandpur | 127 | 23:00 | 124 | 19:00 | Saidpur | 130 | 9:00 | 116 | 21:00
| Feni | 125 | 8:00 | 120 | 18:30 | Purbasadipur | 129 | 5:00 | 116 | 21:00
| Chowmuhani | 125 | 8:00 | 112 | 0:00 | Thakurgaon | 127 | 10:00 | 115 | 20:00
| Ashuganj | 140 | 18:00 | 136 | 18:30 | Palashbari | 131 | 5:00 | 120 | 20:00
| Daudkandi | 131 | 5:00 | 126 | 22:00 | Barapukuria | 135 | 4:00 | 126 | 21:00
| B.Baria | 134 | 6:00 | 131 | 21:00 | Panchagar | 127 | 4:00 | 115 | 21:00
| Ramganj | 123 | 18:00 | 118 | 19:00 | Joldhaka | 131 | 4:00 | 115 | 21:00
| Chaddagram | 129 | 8:00 | 124 | 23:00 | Kurigram | 129 | 5:00 | 118 | 21:00
| PHP | 125 | 8:00 | 121 | 1:00 | Mithapukur | 131 | 0.375 | 123 | 0.83333

## L-Curve
Date | 2021-05-14
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 180 | 6359 | 3175 | 9534 |  |  |  | QF-LDC-11
0:30 | 160 | 6010 | 2999 | 9009 | Date: | 2021-05-14
1:00 | 140 | 5661 | 2823 | 8484
1:30 | 192.5 | 5611.5 | 2690 | 8301.5
2:00 | 245 | 5562 | 2557 | 8119
2:30 | 239.5 | 5472.5 | 2490.5 | 7963 | [5 empty] | Gen. at Eve. Peak | 9780 | 9780 MW (21:00 )
3:00 | 234 | 5383 | 2424 | 7807 | [6 empty] | 21:00
3:30 | 238 | 5247 | 2383.5 | 7630.5 | [5 empty] | Gen. at Day Peak | 6995 | 6995 MW (12:00 )
4:00 | 242 | 5111 | 2343 | 7454 | [6 empty] | 12:00
4:30 | 256 | 5056.5 | 2276 | 7332.5 | [5 empty] | Highest Generation | 9961
5:00 | 270 | 5002 | 2209 | 7211 | [6 empty] | 22:00
5:30 | 229 | 4853.5 | 2150 | 7003.5
6:00 | 188 | 4705 | 2091 | 6796
6:30 | 214 | 4732.5 | 2090.5 | 6823
7:00 | 240 | 4760 | 2090 | 6850
7:30 | 217 | 4748 | 2043 | 6791
8:00 | 194 | 4736 | 1996 | 6732
8:30 | 157 | 4618.5 | 1982.5 | 6601
9:00 | 120 | 4501 | 1969 | 6470
9:30 | 152 | 4596.5 | 1984 | 6580.5
10:00 | 184 | 4692 | 1999 | 6691
10:30 | 248 | 4727 | 2000 | 6727
11:00 | 312 | 4762 | 2001 | 6763
11:30 | 353.5 | 4873 | 2006 | 6879
12:00 | 395 | 4984 | 2011 | 6995
12:30 | 347.5 | 5101 | 2166 | 7267
13:00 | 300 | 5218 | 2321 | 7539
13:30 | 340 | 5235 | 2328.5 | 7563.5
14:00 | 380 | 5252 | 2336 | 7588
14:30 | 390 | 5261.5 | 2327 | 7588.5
15:00 | 400 | 5271 | 2318 | 7589
15:30 | 335 | 5172 | 2259 | 7431
16:00 | 270 | 5073 | 2200 | 7273
16:30 | 201 | 4930.5 | 2181 | 7111.5
17:00 | 132 | 4788 | 2162 | 6950
17:30 | 90 | 4673 | 2133.5 | 6806.5
18:00 | 48 | 4558 | 2105 | 6663
18:30 | 142 | 5205 | 2429.5 | 7634.5
19:00 | 236 | 5852 | 2754 | 8606
19:30 | 380 | 6416 | 3093 | 9509
20:00 | 470 | 6494 | 3060 | 9554 |  |  |  | Executive Engineer
20:30 | 440 | 6597.5 | 3069.5 | 9667 |  |  |  | Network Operation Division
21:00 | 410 | 6701 | 3079 | 9780
21:30 | 345 | 6690 | 3180.5 | 9870.5
22:00 | 280 | 6679 | 3282 | 9961 |  |  |  |  | Page 6 of 7
22:30 | 240 | 6577 | 3307 | 9884
23:00 | 200 | 6475 | 3332 | 9807
23:30 | 190 | 6417 | 3253.5 | 9670.5
24:00 | 180 | 6359 | 3175 | 9534
9780 MW (21:00 )
6995 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-14 |  | Energy | 191654214
[11 empty] | 2021-05-14 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4582 | 912 | 1944 | 1425 | 600 | 23 | 75 | 0 | 138 | 0
0:30 | 4508.5 | 910.5 | 1721.5 | 1161.5 | 575 | 22.5 | 63 | 0 | 129 | 0 | Date: | 2021-05-14
1:00 | 4435 | 909 | 1499 | 898 | 550 | 22 | 51 | 0 | 120 | 0
1:30 | 4413 | 790.5 | 1511 | 854.5 | 550 | 22 | 42.5 | 0 | 118 | 0 | [7 empty] | Total Energy | 191.6542 | Total Energy Gen 191.654 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.654 MKWHr
2:00 | 4391 | 672 | 1523 | 811 | 550 | 22 | 34 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4323 | 671.5 | 1502 | 746.5 | 550 | 22 | 34 | 0 | 114 | 0 | [7 empty] | Energy Requirement | 191.6542
3:00 | 4255 | 671 | 1481 | 682 | 550 | 22 | 34 | 0 | 112 | 0
3:30 | 4189 | 671.5 | 1471 | 614.5 | 535 | 21.5 | 17 | 0 | 111 | 0 | [6 empty] | Shortage
4:00 | 4123 | 672 | 1461 | 547 | 520 | 21 | 0 | 0 | 110 | 0
4:30 | 4068.5 | 671.5 | 1452.5 | 508 | 505 | 21 | 0 | 0 | 106 | 0
5:00 | 4014 | 671 | 1444 | 469 | 490 | 21 | 0 | 0 | 102 | 0
5:30 | 3957 | 623.5 | 1441 | 391 | 470 | 21 | 0 | 0 | 99 | 1
6:00 | 3900 | 576 | 1438 | 313 | 450 | 21 | 0 | 0 | 96 | 2
6:30 | 3901 | 576 | 1447.5 | 320.5 | 450 | 21.5 | 0 | 0 | 98 | 8.5 |  |  |  |  | Coal
7:00 | 3902 | 576 | 1457 | 328 | 450 | 22 | 0 | 0 | 100 | 15
7:30 | 3890.5 | 576 | 1395 | 328 | 450 | 22 | 0 | 0 | 97 | 32.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3879 | 576 | 1333 | 328 | 450 | 22 | 0 | 0 | 94 | 50
8:30 | 3785 | 576 | 1338.5 | 308 | 425 | 22 | 0 | 0 | 94 | 52.5
9:00 | 3691 | 576 | 1344 | 288 | 400 | 22 | 0 | 0 | 94 | 55
9:30 | 3817 | 576 | 1317.5 | 288 | 400 | 22.5 | 0 | 0 | 97 | 62.5
10:00 | 3943 | 576 | 1291 | 288 | 400 | 23 | 0 | 0 | 100 | 70
10:30 | 3943.5 | 576 | 1302 | 290.5 | 400 | 23 | 0 | 0 | 100 | 92
11:00 | 3944 | 576 | 1313 | 293 | 400 | 23 | 0 | 0 | 100 | 114
11:30 | 4013.5 | 575.5 | 1351 | 308 | 400 | 23 | 0 | 0 | 100 | 108
12:00 | 4083 | 575 | 1389 | 323 | 400 | 23 | 0 | 0 | 100 | 102
12:30 | 4151.5 | 680.5 | 1411.5 | 389 | 400 | 23 | 0 | 0 | 103 | 108.5
13:00 | 4220 | 786 | 1434 | 455 | 400 | 23 | 0 | 0 | 106 | 115
13:30 | 4220 | 786 | 1434 | 455 | 400 | 23 | 0 | 0 | 106 | 115
14:00 | 4220 | 786 | 1434 | 455 | 400 | 23 | 0 | 0 | 106 | 115
14:30 | 4220.5 | 777 | 1432.5 | 508.5 | 400 | 22.5 | 0 | 0 | 107 | 96
15:00 | 4221 | 768 | 1431 | 562 | 400 | 22 | 0 | 0 | 108 | 77
15:30 | 4173.5 | 768 | 1379 | 518.5 | 400 | 22 | 0 | 0 | 106 | 64
16:00 | 4126 | 768 | 1327 | 475 | 400 | 22 | 0 | 0 | 104 | 51
16:30 | 4001.5 | 768 | 1332 | 448.5 | 400 | 22 | 0 | 0 | 102 | 37.5
17:00 | 3877 | 768 | 1337 | 422 | 400 | 22 | 0 | 0 | 100 | 24
17:30 | 3764 | 767.5 | 1326 | 414 | 400 | 22 | 0 | 0 | 99 | 14
18:00 | 3651 | 767 | 1315 | 406 | 400 | 22 | 0 | 0 | 98 | 4
18:30 | 4150.5 | 829 | 1527 | 523.5 | 410 | 22 | 57.5 | 0 | 113 | 2
19:00 | 4650 | 891 | 1739 | 641 | 420 | 22 | 115 | 0 | 128 | 0
19:30 | 4685 | 911 | 1895 | 1243 | 490 | 22 | 133 | 0 | 130 | 0
20:00 | 4639 | 912 | 1921 | 1299 | 490 | 22 | 139 | 0 | 132 | 0
20:30 | 4674 | 911 | 1977 | 1313.5 | 495 | 22 | 140.5 | 0 | 134 | 0
21:00 | 4709 | 910 | 2033 | 1328 | 500 | 22 | 142 | 0 | 136 | 0
21:30 | 4726.5 | 911 | 2023 | 1368.5 | 545 | 22 | 136.5 | 0 | 138 | 0
22:00 | 4744 | 912 | 2013 | 1409 | 590 | 22 | 131 | 0 | 140 | 0
22:30 | 4679 | 912 | 1983 | 1417 | 595 | 22 | 136 | 0 | 140 | 0
23:00 | 4614 | 912 | 1953 | 1425 | 600 | 22 | 141 | 0 | 140 | 0
23:30 | 4598 | 912 | 1948.5 | 1425 | 600 | 22.5 | 108 | 0 | 139 | 0 | Max Temp. in Dhaka |  | 34.6° C
24:00 | 4582 | 912 | 1944 | 1425 | 600 | 23 | 75 | 0 | 138 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 191.654 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 191.654 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-14
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 22 | 22 | 22 | 21 | 21 | 21 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 23 | 462600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 9 | 17 | 17 | 17 | 17 | 17 | 17 | 292302
| Teknaf 20MW PP (Solartech) | [7 empty] | 12 | 13 | 10 | 20 | 20 | 18 | 18 | 14 | 4 | 3 | 0 | [8 empty] | 122445
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 202 | 204 | 203 | 203 | 204 | 203 | 203 | 216 | 203 | 203 | 203 | 210 | 203 | 203 | 203 | 203 | 203 |  | 204 | 203 | 203 | 203 | 203 | 203 | 203 | 4827898
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 130 | 130 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 80 | 80 |  | 140 | 140 | 130 | 130 | 130 | 130 | 130 | 2854638
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 34 | 34 | 0 | [15 empty] | 51 | 51 | 51 | 51 | 41 | 51 | 51 | 422482
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 17 | 17 | 17 | 0 | [16 empty] | 34 | 34 | 51 | 51 | 51 | 51 | 329527
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 95 | 70 | 73 | 73 | 73 | 69 | 72 | 72 | 72 | 72 | 72 | 73 | 72 | 71 | 72 | 71 |  | 145 | 115 | 114 | 150 | 145 | 115 | 120 | 2391000
17 | Siddhirganj 335 MW CCPP | 180 | 180 | 180 | 180 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 90 |  | 165 | 162 | 160 | 160 | 160 | 160 | 160 | 3894947
18 | Kodda 300 MW PP Unit-2 (Summit)
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 12 | 45 | 55 | 55 | 55 | 55 | 55 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2866500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1993582
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 312984
33 | Ashuganj 225 MW CCPP | 180 | 180 | 180 | 180 | 180 | 160 | 161 | 161 | 162 | 162 | 163 | 163 | 162 | 162 | 161 | 161 | 161 | 162 |  | 213 | 186 | 182 | 187 | 181 | 181 | 181 | 4180000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 265 | 245 | 230 | 230 | 230 | 230 | 255 | 285 | 285 | 285 | 285 | 235 |  | 295 | 295 | 295 | 305 | 300 | 300 | 300 | 6542000
| Ashuganj 450 MW CCPP(North) | 265 | 265 | 270 | 265 | 265 | 265 | 260 | 250 | 245 | 260 | 260 | 260 | 285 | 270 | 285 | 285 | 285 | 270 |  | 290 | 290 | 295 | 295 | 290 | 290 | 290 | 6892000
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 20 | 56 | 56 | 55 | 319200
36 | Chandpur 150 MW CCPP | 92 | 86 | 86 | 86 | 85 | 91 | 90 | 86 | 85 | 86 | 90 | 91 | 90 | 90 | 90 | 85 | 90 | 85 |  | 86 | 86 | 86 | 87 | 86 | 86 | 86 | 2077190
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 342 | 305 | 305 | 272 | 270 | 270 | 270 | 269 | 251 | 252 | 252 | 281 | 302 | 302 | 302 | 302 | 292 | 253 |  | 281 | 339 | 340 | 341 | 328 | 320 | 322 | 7162880
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6638500
41 | Haripur 360MW CCPP(HPL) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 270 | 248 | 277 | 278 | 277 | 277 | 278 | 278 | 242 | 243 | 243 |  | 337 | 346 | 346 | 345 | 346 | 346 | 346 | 7032000
42 | RPCL 210MW CCPP | 215 | 214 | 213 | 213 | 213 | 175 | 174 | 174 | 155 | 207 | 207 | 205 | 202 | 201 | 200 | 200 | 200 | 202 |  | 201 | 205 | 205 | 205 | 207 | 209 | 208 | 4664640
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 20 | 17 | 22 | 54 | 41 | 50 | 41 | 33 | 27 | 11 | 2 | [8 empty] | 292670
44 | Fenchugonj CCPP Phase-1 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 |  | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 844000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1003440
46 | Shajibazar 330 MW CCPP | 280 | 280 | 282 | 285 | 285 | 282 | 285 | 283 | 284 | 332 | 331 | 330 | 330 | 330 | 330 | 330 | 308 | 308 |  | 328 | 329 | 334 | 330 | 330 | 330 | 330 | 7053000
47 | Shahjibazar GTPP Unit- 8 & 9 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 52 | 52 | 52 | 52 | 52 | 52 | 1016448
48 | Shahjibazar 86MW PP (Shahjibazar) | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 75 | 75 | 75 | 75 | 75 | 75 | 452160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 216 | 216 | 156 | 162 | 163 | 143 | 156 | 162 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 122 |  | 220 | 215 | 216 | 223 | 223 | 223 | 183 | 4163500
51 | Sylhet 20 MW GTPP | [20 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 96000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [19 empty] | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 34740
54 | Hobiganj 11MW PP Cofidence-E | [13 empty] | 5 | 5 | 5 | 2 | 2 |  | 5 | 5 | 11 | 11 | 11 | 11 | 11 | 144
55 | Fenchugonj 51 MW PP (Barakatullah) | 5 | 5 | 5 | 0 | [15 empty] | 26 | 53 | 50 | 53 | 53 | 53 | 53 | 280200
56 | Shahjahanulla 25 MW PP | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 80496
57 | Bibiana-II 341 MW CCPP (Summit) | 260 | 280 | 265 | 265 | 275 | 280 | 300 | 270 | 250 | 180 | 200 | 270 | 315 | 300 | 300 | 275 | 260 | 270 |  | 300 | 275 | 270 | 300 | 280 | 260 | 230 | 6652000
| Bibiyana South 400 MW | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 260 | 260 | 260 | 320 | 320 | 320 | 320 | 320 | 260 | 260 |  | 400 | 400 | 401 | 401 | 401 | 300 | 300 | 7399500
58 | Nababganj 55 MW PP (Southern power ) | [26 empty] | 0
59 | Tangail Palli Power Gen 22 MW | [20 empty] | 3 | 10 | 24 | 24 | 24 |  | 84240
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 512736
61 | Narshingdi 22 MW PP (Doreen) | [22 empty] | 15 | 15 | 15 | 15 | 53784
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 0 | [17 empty] | 19 | 19 | 19 | 19 | 19 | 151272
63 | Impoprt (Tripura) | 120 | 116 | 112 | 110 | 102 | 96 | 100 | 94 | 94 | 100 | 100 | 100 | 106 | 108 | 108 | 104 | 100 | 98 |  | 128 | 130 | 132 | 136 | 140 | 140 | 138 | 2688960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 40 | 30 | 40 | 42 | 42 | 42 | 42 | 1153920
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 502524
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232740
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 25 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 599500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 0 | 20 | 15 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 452520
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 8 | 8 | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 3 | 3 | 3 | 3 | 3 | 0 | 3 | 3 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 113040
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 719600
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 605100
73 | Ghorashal 108MW PP (Regent) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 55 | 85 | 91 | 95 | 100 | 100 | 104 | 722409
| Feni Lanka Power | [26 empty] | 0
| Chowmuhani 113 MW | 35 | 35 | 0 | [16 empty] | 2 | 35 | 35 | 35 | 35 | 35 | 35 | 294840
| Manikgonj 162MW PP(MPGL) | [26 empty] | 0
77 | Siddhirganj 100 PP(Dutch Bangla) | [20 empty] | 10 | 12 |  |  |  |  | 13440
78 | Gazipur 52 MW PP | [26 empty] | 0
79 | Kodda 150MW PP | [26 empty] | 0
80 | Jamalpur 95 MW PP(Powerpac) | 65 | 65 | 65 | 24 | 8 | 0 | [5 empty] | 4 | 49 | 49 | 49 | 49 | 64 | 32 |  | 48 | 65 | 65 | 65 | 65 | 65 | 65 | 932160
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 8 | 8 | 0 | [15 empty] | 12 | 32 | 46 | 52 | 52 | 52 | 318379
| Gazipur 100 MW PP | [21 empty] | 12 |  |  |  |  | 13200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 3 | 1 | 2 | 6 | 2 | 3 | 3 | 1 | [9 empty] | 30602
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 54 | 49 | 54 | 54 | 54 | 54 | 803231
| Karnaphuli Power Ltd. | [26 empty] | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 240 | 235 | 240 | 230 | 245 | 245 | 260 | 260 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 267 | 230 | 235 | 235 | 230 | 230 | 230 | 5625047
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [26 empty] | 0
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 100 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 70 | 100 | 100 | 100 | 100 | 100 | 1105320
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 5 | 5 | 5 | 0 | 0 | 0 | [13 empty] | 12 | 30 | 38 | 41 | 43 | 43 | 43 | 378626
94 | Gagnagar 102 MW PP (Digital Power) | [26 empty] | 0
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [20 empty] | 5 | 7 | 15 | 15 | 15 | 15 | 70968
100 | Manikganj 55 MW PP (Northern)
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 163 | 163 | 163 | 163 | 130 | 130 | 3144518
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 12450
103 | Kamalaghat 54 MW PP(Banco Energy) | [20 empty] | 17 | 17 |  |  |  |  | 21600
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [20 empty] | 60 | 48 | 60 | 60 | 60 | 35 | 297600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [20 empty] | 30 | 25 | 30 | 30 | 30 | 30 | 151632
115 | Juldah 100 MW PP Unit-3 (Acorn) | 30 | 30 | 30 | 10 | 10 | 0 | [13 empty] | 10 | 50 | 50 | 50 | 50 | 50 | 30 | 350400
116 | Chandpur 200MW (Desh energy) | 124 | 85 | 85 | 68 | 68 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 60 | 82 | 117 | 120 | 68 | 68 |  | 72 | 120 | 114 | 132 | 124 | 126 | 140 | 1868640
117 | Ashuganj 150MW PP (Midland)
118 | Bibiyana-III 400 MW CCPP | 322 | 322 | 319 | 319 | 318 | 320 | 319 | 326 | 240 | 320 | 321 | 373 | 379 | 384 | 367 | 306 | 250 | 241 |  | 367 | 326 | 329 | 328 | 328 | 303 | 304 | 7697000
| Jamalpur 115 MW PP (United) | 8 | 0 | [9 empty] | 19 | 32 | 56 | 65 | 8 | 8 | 8 |  | 46 | 115 | 115 | 115 | 115 | 115 | 115 | 859200
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | [10 empty] | 5 | 9 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 150720
| Anlima Energy Ltd. | [26 empty] | 0
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 7 | 13 | 17 | 30 | 33 | 30 | 32 | 27 | 22 | 15 | 7 | 1 | [8 empty] | 239853
120 | Eastern Zone Total | 5661 | 5562 | 5383 | 5111 | 5002 | 4705 | 4760 | 4736 | 4501 | 4692 | 4762 | 4984 | 5218 | 5252 | 5271 | 5073 | 4788 | 4558 |  | 5852 | 6416 | 6494 | 6701 | 6679 | 6475 | 6359 | 130081805
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 49 | 19 | 0 | [7 empty] | 32 | 49 | 49 | 16 |  |  |  | 35 | 94 | 99 | 99 | 99 | 99 | 99 | 925440
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 | [18 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 252000
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 32 | 32 | 0 | [14 empty] | 16 |  | 48 | 48 | 48 | 48 | 64 | 64 | 64 | 413090
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 95 | 96 | 96 | 72 | 72 | 72 | 36 | 32 | 33 | 31 | 32 | 31 | 53 | 72 | 51 | 52 | 51 |  | 83 | 96 | 97 | 97 | 97 | 95 | 96 | 1656653
| Bhola 225 MW CCPP | 88 | 88 | 87 | 88 | 88 | 89 | 88 | 88 | 86 | 87 | 87 | 86 | 86 | 86 | 86 | 86 | 88 | 88 |  | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 2118270
140 | Bhola 33 MW PP (Venture) | 34 | 30 | 29 | 29 | 28 | 28 | 27 | 25 | 22 | 24 | 24 | 26 | 27 | 27 | 26 | 24 | 13 | 10 |  | 25 | 23 | 23 | 28 | 29 | 28 | 28 | 607984
141 | Noapara 100 MW PP (Bangla Trac) | [26 empty] | 0
142 | Noapara 40 MW PP (Khanjahan Ali) | [20 empty] | 32 | 32 | 32 | 33 | 32 | 32 | 157875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 909 | 672 | 671 | 672 | 671 | 576 | 576 | 576 | 576 | 576 | 576 | 575 | 786 | 769 | 768 | 768 | 768 | 767 |  | 891 | 911 | 912 | 910 | 912 | 912 | 912 | 18708364
147 | Bheramara 410 MW CCPP | 355 | 355 | 300 | 300 | 300 | 270 | 270 | 270 | 240 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 210 |  | 365 | 355 | 350 | 365 | 355 | 355 | 355 | 7425504
148 | Payra 1320 MW | 400 | 400 | 400 | 370 | 340 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 270 | 340 | 340 | 350 | 440 | 450 | 450 | 8437000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3657600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
Baghabari 50 MW Peaking PP
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 159 | 160 | 160 | 145 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 |  | 162 | 206 | 186 | 152 | 176 | 183 | 183 | 3779700
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 174 | 175 | 175 | 172 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 197 | 192 | 188 | 178 | 130 | 130 |  | 148 | 160 | 140 | 140 | 194 | 214 | 215 | 4245918
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 284 | 293 | 299 | 294 | 292 | 341 | 341 | 285 | 345 | 330 | 333 | 337 | 337 | 336 | 308 | 288 | 322 | 294 |  | 390 | 365 | 363 | 414 | 369 | 365 | 382 | 7945872
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 0 | [18 empty] | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 98160
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 5 | 5 | 11 | 11 | 176130
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | [19 empty] | 14 | 32 | 38 | 41 | 41 | 41 |  | 174257
169 | Natore 52 MW PP (Rajlanka) | [20 empty] | 16 | 16 |  |  |  |  | 17280
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 49 | 49 | 24 | 252216
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [20 empty] | 30 | 31 |  | 31 | 35 |  | 124896
172 | Confidence Power Bogura Unit-1 113 MW | [22 empty] | 10 | 35 | 35 |  | 81696
173 | Rangpur 20 MW GTPP | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | [19 empty] | 10 | 34 | 34 | 48 | 63 | 74 | 34 | 273600
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 3 | 4 | 5 | 7 | 7 | 6 | 3 | 1 | 1 | 1 | [8 empty] | 42904
178
178