## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-17 | Monday
|  |  | Date (day): | 2021-05-17 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14399.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15350 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-16 | 2021-05-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP Unit-3 |  | Gas | PDB | 1*210 | 210 | 170 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
|  | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 2 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 3 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 14 | 104 | 100 | 100
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 333 | 352 | 350 | 360 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 301 | 346 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 245 | 240 | 240 | 65 |  | Gas shortage
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 15 | 15 | 15 |  | 7 | Engine problem
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 70 | 150 | 120 | 150
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 100 | 100
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 219 | 220 | 220 |  | 115 | ST under maint.
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 17 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 52 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 30 | 42 | 42 |  | 38 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 20 |  | 13 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 42 | 42 | 42 |  | 10 | Engine problem
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 250 | 250 |  | 50 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 16 | 132 | 132 | 132 |  | 17 | Engine problem
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6206 | 5829 | 1770 | 2313 | 3715 | 4025 | 394 | 1246
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 6 | 43 | 43 |  | 7 | Engine problem
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 23 | 21 | 22 | 22 | 208 |  | Unit 4 & 5 Under S/D due to Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 204 | 225 | 225
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 130 | 120 | 140
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 85 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 30 | 42 | 10 | 30
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 90 | 90 |  | 18 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 35 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 742 | 1001 | 1627 | 1642 | 388 | 345
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 80 | 80 | 80 | 54 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 0 | 140 | 140 | 140
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 275 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 285 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 24 | 25 | 25 | 25 |  | 20 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 45 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 0 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 92 | 71 |  | Gas shortage
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 120 | 120 | 120 | 120 |  | 80 | Engine problem
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 19 | 19 | 19
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 140 | 145 | 179
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 3 | 43 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 19 | 20 | 20 |  | 5 | Engine problem
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 6 | 113 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1245 | 1559 | 2031 | 2217 | 539 | 151
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 206 | 205 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 57 | 65 | 65 | 65 |  | 30 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 72 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 44 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 336 | 500 | 672.6 | 621 | 0 | 33
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 331 | 330 | 330 | 330
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 31 | 53 | 51 | 51
| 94 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 95 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 96 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 51 | 51 | 51 |  | 15
| 97 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 75 | 75 | 75 |  | 11 | Engine problem
| 98 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 99 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 217 | 214 | 225 | 225
| 100 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 101 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 102 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 103 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under S/D due to gas line maint.
| 104 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 333 | 372 | 400 | 400
| 105 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 7 | 7 | 7 |  | 3 | Engine prolem
| 106 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 395 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1683 | 1782 | 1819 | 1819 | 0 | 567
| 107 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 750 | 845 | 763 | 860
| 108 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 38 | 99 | 99 | 99 |  | 16 | Engine problem
| 109 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 110 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 111 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 112 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 365 | 350 | 350 | 60 |  | Gas shortage
| 113 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 114 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 115 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 90 | 90 | 90 |  | 15 | Engine problem
| 116 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1158 | 1431 | 1564 | 1931 | 60 | 122
| 117 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 118 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 33 | 33
| 119 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 88 | 88 | 88 |  | 106 | GT-2 under maint
| 120 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 90 | 97 | 95 | 95
| 121 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 550 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | On Test
| 122 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 601 | 914 | 948 | 1028 | 0 | 106
| 123 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 124 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 125 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 126 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 42 | 42 |  | 8 | Engine problem
| 127 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 128 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 |  | 20 | Engine problem
| 129 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 110 | 140 | 140 |  |  | Gas shortage
| 130 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 138 | 200 | 200 |  |  | FGMO
| 131 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 186 | 192 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 377 | 419 | 400 | 400 |  |  | FGMO
| 133 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 32 |  | 18 | Engine problem
| 134 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 18 | 18 | 18
| 135 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 136 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 137 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 138 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 49 | 100 | 100
| 139 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 140 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| 141 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 0 | 113 | 113
|  | Rajshahi Area Total |  |  |  |  | 2193 | 2173 | 774 | 1024 | 1752 | 1784 | 171 | 53
| 142 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 143 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 144 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 146 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 147 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 157 | 263 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 21967 | 21219 | 8466 | 10787 | 14399.6 | 15350 | 1761 | 2728
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8088.495 | 10306 | 13757.5116 | 14665.5326
| A. |  | 2021-05-16 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 10845 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7153 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10787 | MW
| 3 | Day peak Generation : |  |  | 8466 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10306 | MW
| 4 | Evening peak Generation : |  |  | 10787 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 210.3443 | MKWHr | By Solar | 0.76379 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.0811 | MKWHr |  | By Oil: | 28.3678 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.4846 | MKWHr |  | By Hydro: | 0.42768 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1761 | MW | Dhaka | 3050 | 3050 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2728 | MW | Chittagong | 1169 | 1169 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4489 | MW | Khulna | 1404 | 1404 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1220.61 | MMCFD |  |  | Rajshahi | 1092 | 1092 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160881944.822 | ii) Oil : | Taka | 191697868.84 | Comilla | 1178 | 1178 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 71753786 | Total | Taka | 424333599.662 | Mymensingh | 913 | 913 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.4305 | MKWHr. | Sylhet | 390 | 390 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -48 | MW (E to W) at | 21:00 | hrs | Barisal | 361 | 361 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -520 | MW at | 2:00 | hrs | Rangpur | 749 | 749 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.4° C |  |  | Total | 10306 | 10306 |  | 0
| B. |  | 2021-05-17 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 40.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11600 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15350 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
| 4 | Reserve(Generation end) |  |  |  | 3750 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 224.9879 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8256 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 15.3855 | MKWHr. | ii) HVDC Flow at Peak Time |  | 845 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8339 | MKWHr. | iii) Maximum HVDC Flow : |  | 845 | MW at | 19:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.26 |  | (b) Today: | 75.18 |  | (c) Rule Curve: |  | 78.96
.

## YesterdayGen
2021-05-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP Unit-3 | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 327 | 301 |  | 0 | 280 | 230 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 270 | 270 | 61 | 8 | 90 | 26 | 57 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 17 | 122 | 212 | 65 | 19 | 0 | 0 | 42 | 53 | 0 | 130 | 330 | 53 | 78 | 0 | 190 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 368 | 55 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 726 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 96 | 0 | 180 | 0 | 327 | 53 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5839 | 2835 | 8674 | 4557 | 726 | 1585 | 1007 | 620 | 23 | 34 | 122 | 0 | 0 | 75.28
2:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 327 | 302 |  | 0 | 280 | 230 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 275 | 275 | 100 | 8 | 90 | 23 | 57 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 17 | 120 | 210 | 57 | 19 | 0 | 0 | 42 | 53 | 0 | 100 | 330 | 52 | 78 | 0 | 176 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 368 | 55 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 542 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 96 | 0 | 155 | 0 | 333 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5829 | 2619 | 8448 | 4562 | 542 | 1563 | 984 | 620 | 23 | 34 | 120 | 0 | 0 | 75.28
3:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 329 | 301 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 270 | 270 | 100 | 8 | 92 | 23 | 57 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 17 | 116 | 212 | 57 | 19 | 0 | 0 | 42 | 53 | 0 | 100 | 330 | 52 | 78 | 0 | 170 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 366 | 55 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 489 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 96 | 0 | 158 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5817 | 2414 | 8231 | 4555 | 489 | 1523 | 871 | 620 | 23 | 34 | 116 | 0 | 0 | 75.27
4:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 327 | 301 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 34 | 92 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 270 | 265 | 100 | 8 | 86 | 23 | 56 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 17 | 114 | 212 | 57 | 19 | 0 | 0 | 42 | 53 | 0 | 100 | 331 | 52 | 78 | 0 | 164 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 366 | 55 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 489 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 96 | 0 | 155 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5787 | 2313 | 8100 | 4503 | 489 | 1505 | 813 | 620 | 22 | 34 | 114 | 0 | 0 | 75.27
5:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 333 | 302 |  | 0 | 280 | 230 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 2 | 92 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 270 | 270 | 0 | 8 | 99 | 23 | 57 | 0 | 51 | 0 | 0 | 8 | 22 | 8 | 33 | 17 | 108 | 211 | 57 | 17 | 0 | 0 | 42 | 11 | 0 | 100 | 328 | 52 | 30 | 0 | 163 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 100 | 0 | 365 | 55 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 36 | 10 | 350 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 489 | 0 | 320 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 96 | 0 | 155 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 470 | 0 | 0 | 0 |  | 5522 | 2353 | 7875 | 4374 | 489 | 1452 | 808 | 620 | 22 | 2 | 108 | 0 | 0 | 75.26
6:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 318 | 302 |  | 0 | 280 | 230 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 0 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 70 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 270 | 270 | 0 | 8 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 33 | 17 | 96 | 211 | 10 | 17 | 0 | 0 | 42 | 11 | 0 | 100 | 331 | 52 | 10 | 0 | 163 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 50 | 70 | 0 | 331 | 0 | 0 | 34 | 0 | 0 | 54 | 0 | 0 | 0 | 10 | 350 | 0 | 1 | 0 | 0 | 0 | 17 | 1 |  | 394 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 94 | 0 | 145 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 0 | 0 | 0 |  | 5082 | 2135 | 7217 | 4238 | 394 | 1352 | 562 | 550 | 22 | 0 | 96 | 3 | 0 | 75.26
7:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 304 | 302 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 5 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 70 | 0 | 0 | 19 | 42 | 0 | 0 | 80 | 260 | 265 | 0 | 8 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 84 | 213 | 0 | 19 | 0 | 0 | 42 | 11 | 0 | 100 | 333 | 52 | 10 | 0 | 165 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 50 | 50 | 0 | 332 | 0 | 0 | 34 | 2 | 0 | 39 | 0 | 0 | 0 | 10 | 350 | 0 | 7 | 0 | 0 | 0 | 0 | 9 |  | 394 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 95 | 0 | 168 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 0 | 0 | 0 |  | 5027 | 2126 | 7153 | 4256 | 394 | 1318 | 505 | 550 | 21 | 0 | 84 | 25 | 0 | 75.25
8:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 304 | 303 |  | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 5 | 20 | 25 | 0 | 0 | 21 | 0 | 0 | 0 | 17 | 216 | 0 | 120 | 0 |  | 0 | 0 | 0 | 70 | 0 | 0 | 19 | 35 | 0 | 0 | 80 | 295 | 305 | 0 | 8 | 90 | 20 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 98 | 212 | 0 | 19 | 0 | 0 | 42 | 11 | 0 | 100 | 333 | 51 | 10 | 0 | 163 | 18 | 0 | 7 | 0 | 16 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 50 | 50 | 0 | 360 | 0 | 0 | 34 | 3 | 0 | 35 | 0 | 0 | 0 | 10 | 350 | 0 | 12 | 0 | 0 | 0 | 11 | 17 |  | 394 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 91 | 0 | 178 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 0 | 0 | 0 |  | 5166 | 2172 | 7338 | 4370 | 394 | 1344 | 517 | 550 | 21 | 0 | 98 | 44 | 0 | 75.25
9:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 348 | 301 |  | 0 | 280 | 250 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 216 | 0 | 120 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 30 | 0 | 0 | 80 | 310 | 300 | 0 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 0 | 33 | 17 | 108 | 208 | 15 | 19 | 0 | 0 | 42 | 11 | 0 | 163 | 330 | 51 | 10 | 0 | 163 | 18 | 0 | 7 | 0 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 50 | 50 | 0 | 377 | 2 | 0 | 35 | 4 | 0 | 35 | 0 | 0 | 0 | 10 | 401 | 0 | 15 | 0 | 0 | 0 | 17 | 22 |  | 394 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 91 | 0 | 183 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 400 | 0 | 0 | 0 |  | 5409 | 2308 | 7717 | 4571 | 394 | 1451 | 561 | 550 | 22 | 0 | 108 | 60 | 0 | 75.25
10:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 344 | 301 |  | 0 | 280 | 255 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 17 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 227 | 0 | 120 | 0 |  | 0 | 0 | 0 | 68 | 0 | 0 | 19 | 27 | 0 | 0 | 100 | 290 | 305 | 0 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 8 | 25 | 17 | 112 | 206 | 49 | 19 | 1 | 0 | 42 | 11 | 0 | 163 | 332 | 52 | 10 | 0 | 209 | 18 | 0 | 7 | 0 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 19 | 80 | 73 | 0 | 374 | 8 | 0 | 54 | 5 | 0 | 35 | 0 | 0 | 0 | 10 | 401 | 0 | 17 | 0 | 0 | 0 | 17 | 30 |  | 395 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 91 | 0 | 187 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 400 | 0 | 0 | 0 |  | 5611 | 2328 | 7939 | 4632 | 395 | 1480 | 670 | 549 | 23 | 0 | 112 | 78 | 0 | 75.24
11:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 337 | 301 |  | 0 | 280 | 250 | 0 | 0 | 6 | 180 | 0 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 205 | 0 | 120 | 0 |  | 0 | 0 | 0 | 68 | 0 | 0 | 19 | 27 | 0 | 0 | 100 | 295 | 305 | 0 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 18 | 5 | 33 | 17 | 108 | 206 | 57 | 19 | 1 | 0 | 42 | 11 | 0 | 163 | 330 | 51 | 10 | 0 | 216 | 18 | 0 | 7 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 80 | 119 | 0 | 376 | 8 | 0 | 85 | 5 | 0 | 39 | 0 | 0 | 0 | 10 | 400 | 0 | 49 | 0 | 0 | 0 | 17 | 31 |  | 394 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 190 | 0 | 92 | 0 | 196 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 400 | 0 | 0 | 0 |  | 5700 | 2344 | 8044 | 4620 | 394 | 1469 | 772 | 549 | 23 | 0 | 108 | 109 | 0 | 75.24
12:00 | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 333 | 301 |  | 0 | 280 | 260 | 0 | 0 | 15 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 30 | 0 | 0 | 100 | 285 | 300 | 0 | 8 | 90 | 24 | 56 | 0 | 51 | 0 | 0 | 3 | 18 | 5 | 33 | 17 | 112 | 206 | 57 | 19 | 2 | 0 | 42 | 31 | 0 | 163 | 331 | 51 | 75 | 0 | 217 | 18 | 0 | 6 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 80 | 120 | 0 | 333 | 8 | 0 | 85 | 2 | 0 | 54 | 0 | 0 | 6 | 10 | 395 | 0 | 44 | 0 | 0 | 0 | 17 | 33 |  | 750 | 0 | 370 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 90 | 0 | 186 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 400 | 0 | 0 | 0 |  | 5776 | 2690 | 8466 | 4534 | 750 | 1524 | 866 | 550 | 23 | 0 | 112 | 107 | 0 | 75.24
13:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 341 | 338 |  | 0 | 280 | 260 | 0 | 0 | 15 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 210 | 0 | 120 | 0 |  | 5 | 0 | 0 | 80 | 0 | 0 | 19 | 30 | 0 | 0 | 125 | 300 | 315 | 0 | 40 | 90 | 23 | 56 | 0 | 51 | 0 | 0 | 16 | 18 | 5 | 33 | 17 | 122 | 202 | 56 | 19 | 2 | 0 | 42 | 53 | 0 | 163 | 333 | 52 | 75 | 0 | 217 | 18 | 0 | 6 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 19 | 100 | 120 | 0 | 343 | 24 | 0 | 85 | 4 | 0 | 41 | 0 | 0 | 26 | 50 | 399 | 0 | 49 | 0 | 8 | 0 | 17 | 16 |  | 750 | 0 | 380 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 88 | 0 | 182 | 0 | 375 | 14 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 400 | 0 | 0 | 0 |  | 6122 | 2757 | 8879 | 4584 | 750 | 1694 | 1059 | 550 | 23 | 0 | 122 | 97 | 0 | 75.23
14:00 | 0 | 0 | 0 | 180 | 0 | 101 | 0 | 343 | 338 |  | 0 | 280 | 255 | 0 | 0 | 15 | 205 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 205 | 0 | 120 | 0 |  | 23 | 0 | 0 | 80 | 0 | 0 | 19 | 30 | 0 | 0 | 125 | 280 | 295 | 0 | 45 | 86 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 17 | 5 | 33 | 17 | 124 | 203 | 57 | 16 | 2 | 10 | 42 | 53 | 0 | 163 | 331 | 52 | 75 | 0 | 217 | 18 | 0 | 7 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 17 | 100 | 120 | 0 | 331 | 42 | 0 | 85 | 5 | 0 | 54 | 0 | 0 | 43 | 90 | 401 | 0 | 45 | 0 | 21 | 0 | 17 | 29 |  | 749 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 86 | 0 | 184 | 0 | 339 | 36 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 430 | 0 | 0 | 0 |  | 6338 | 2741 | 9079 | 4603 | 749 | 1667 | 1229 | 580 | 23 | 0 | 124 | 104 | 0 | 75.23
15:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 335 | 340 |  | 0 | 280 | 230 | 0 | 0 | 23 | 213 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 3 | 20 | 25 | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 209 | 0 | 120 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 19 | 28 | 0 | 0 | 125 | 295 | 310 | 0 | 45 | 91 | 23 | 57 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 17 | 116 | 201 | 56 | 16 | 1 | 10 | 42 | 52 | 0 | 110 | 331 | 51 | 75 | 0 | 217 | 18 | 0 | 7 | 0 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 13 | 100 | 120 | 0 | 336 | 75 | 0 | 89 | 4 | 0 | 54 | 0 | 0 | 113 | 90 | 390 | 0 | 37 | 0 | 35 | 0 | 17 | 23 |  | 750 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 8 | 85 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 10 | 0 | 163 | 0 | 89 | 0 | 180 | 0 | 376 | 60 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 470 | 0 | 0 | 0 |  | 6361 | 2902 | 9263 | 4579 | 750 | 1653 | 1441 | 620 | 22 | 0 | 116 | 82 | 0 | 75.23
16:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 330 | 300 |  | 0 | 280 | 230 | 0 | 0 | 30 | 160 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 5 | 0 | 22 | 0 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 19 | 28 | 0 | 0 | 125 | 280 | 295 | 0 | 45 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 34 | 18 | 8 | 25 | 17 | 114 | 201 | 56 | 16 | 1 | 10 | 42 | 53 | 0 | 110 | 330 | 51 | 72 | 0 | 218 | 18 | 0 | 7 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 9 | 50 | 120 | 0 | 332 | 75 | 0 | 85 | 2 | 0 | 54 | 0 | 0 | 26 | 30 | 395 | 0 | 5 | 0 | 35 | 0 | 17 | 16 |  | 750 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 159 | 0 | 90 | 0 | 176 | 0 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 470 | 0 | 0 | 0 |  | 5983 | 2815 | 8798 | 4495 | 750 | 1572 | 1189 | 620 | 22 | 0 | 114 | 36 | 0 | 75.23
17:00 | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 329 | 252 |  | 0 | 280 | 230 | 0 | 0 | 30 | 140 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 8 | 0 | 21 | 0 | 0 | 0 | 17 | 205 | 0 | 70 | 0 |  | 24 | 0 | 0 | 70 | 0 | 0 | 19 | 36 | 0 | 0 | 95 | 280 | 300 | 0 | 45 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 8 | 19 | 8 | 25 | 17 | 108 | 203 | 56 | 16 | 1 | 15 | 42 | 11 | 0 | 110 | 304 | 51 | 10 | 0 | 203 | 18 | 0 | 7 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 3 | 50 | 120 | 0 | 321 | 45 | 0 | 85 | 1 | 0 | 54 | 0 | 0 | 26 | 30 | 392 | 0 | 19 | 0 | 35 | 0 | 17 | 5 |  | 750 | 0 | 300 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 140 | 0 | 91 | 0 | 175 | 0 | 327 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 450 | 0 | 0 | 0 |  | 5624 | 2667 | 8291 | 4301 | 750 | 1416 | 1064 | 600 | 21 | 0 | 108 | 31 | 0 | 75.22
18:00 | 0 | 0 | 0 | 180 | 0 | 42 | 0 | 308 | 252 |  | 0 | 280 | 230 | 0 | 0 | 30 | 140 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 15 | 25 | 3 | 20 | 25 | 8 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 70 | 0 |  | 24 | 0 | 17 | 70 | 0 | 0 | 19 | 39 | 0 | 0 | 80 | 260 | 265 | 0 | 45 | 90 | 25 | 10 | 0 | 10 | 0 | 0 | 8 | 19 | 8 | 33 | 17 | 108 | 205 | 56 | 18 | 0 | 20 | 42 | 11 | 0 | 110 | 302 | 40 | 10 | 0 | 150 | 18 | 0 | 7 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 50 | 120 | 0 | 331 | 45 | 0 | 103 | 0 | 0 | 54 | 0 | 0 | 26 | 30 | 300 | 0 | 4 | 0 | 35 | 0 | 17 | 0 |  | 750 | 0 | 230 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 130 | 0 | 91 | 0 | 175 | 0 | 251 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 0 | 0 | 0 |  | 5290 | 2484 | 7774 | 4000 | 750 | 1201 | 1082 | 590 | 21 | 17 | 108 | 5 | 0 | 75.22
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 96 | 0 | 263 | 312 |  | 0 | 280 | 230 | 0 | 0 | 30 | 140 | 0 | 117 | 20 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 47 | 15 | 25 | 3 | 20 | 25 | 21 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 8 | 19 | 40 | 0 | 0 | 80 | 260 | 270 | 0 | 45 | 86 | 23 | 10 | 0 | 24 | 0 | 0 | 23 | 19 | 8 | 33 | 19 | 136 | 203 | 56 | 19 | 0 | 20 | 42 | 18 | 0 | 110 | 308 | 51 | 75 | 0 | 214 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 17 | 0 | 0 | 17 | 0 | 74 | 0 | 75 | 120 | 15 | 366 | 86 | 17 | 105 | 0 | 0 | 54 | 0 | 0 | 67 | 60 | 368 | 11 | 0 | 36 | 35 | 0 | 17 | 0 |  | 845 | 0 | 230 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 130 | 0 | 93 | 7 | 179 | 0 | 386 | 33 | 0 | 22 | 0 | 60 | 0 | 0 | 10 | 450 | 0 | 0 | 1 |  | 6311 | 3086 | 9397 | 4245 | 845 | 1547 | 1822 | 600 | 21 | 181 | 136 | 0 | 0 | 75.21
19:30 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 329 | 346 |  | 0 | 280 | 250 | 0 | 0 | 55 | 140 | 0 | 90 | 50 | 16 | 82 | 0 | 0 | 0 | 0 | 17 | 17 | 51 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 21 | 0 | 0 | 0 | 17 | 203 | 0 | 130 | 0 |  | 24 | 0 | 85 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 260 | 270 | 42 | 45 | 88 | 25 | 10 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 134 | 205 | 56 | 19 | 0 | 25 | 42 | 53 | 0 | 110 | 308 | 51 | 75 | 0 | 217 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 132 | 0 | 100 | 120 | 20 | 367 | 115 | 35 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 53 | 0 | 54 | 35 | 0 | 17 | 0 |  | 844 | 0 | 240 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | 0 | 40 | 0 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 50 | 0 | 134 | 0 | 96 | 0 | 173 | 0 | 350 | 90 | 0 | 35 | 0 | 90 | 0 | 0 | 35 | 460 | 0 | 0 | 17 |  | 7001 | 3287 | 10288 | 4396 | 844 | 1603 | 2417 | 610 | 21 | 263 | 134 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 329 | 346 |  | 0 | 280 | 250 | 0 | 0 | 55 | 140 | 0 | 98 | 50 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 21 | 0 | 0 | 0 | 17 | 205 | 0 | 130 | 0 |  | 24 | 0 | 68 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 285 | 285 | 139 | 45 | 90 | 25 | 53 | 0 | 44 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 136 | 203 | 56 | 19 | 0 | 30 | 42 | 53 | 0 | 110 | 296 | 51 | 75 | 0 | 214 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 132 | 0 | 100 | 120 | 0 | 379 | 115 | 35 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 39 | 0 | 17 | 35 | 0 | 17 | 0 |  | 845 | 0 | 260 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 96 | 0 | 175 | 0 | 351 | 90 | 0 | 35 | 0 | 100 | 0 | 0 | 0 | 480 | 0 | 0 | 17 |  | 7044 | 3278 | 10322 | 4573 | 845 | 1658 | 2294 | 630 | 21 | 165 | 136 | 0 | 0 | 75.21
21:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 352 | 346 |  | 0 | 280 | 245 | 0 | 0 | 55 | 219 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 21 | 0 | 0 | 0 | 17 | 204 | 0 | 130 | 0 |  | 24 | 0 | 68 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 275 | 285 | 140 | 45 | 90 | 25 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 140 | 205 | 65 | 19 | 0 | 30 | 42 | 53 | 0 | 163 | 330 | 51 | 75 | 0 | 214 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 132 | 0 | 100 | 120 | 0 | 372 | 115 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 0 | 0 | 17 | 35 | 0 | 17 | 0 |  | 845 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 138 | 0 | 97 | 0 | 192 | 0 | 419 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 550 | 0 | 0 | 35 |  | 7155 | 3632 | 10787 | 4930 | 845 | 1790 | 2212 | 700 | 21 | 149 | 140 | 0 | 0 | 75.21
22:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 334 | 348 |  | 0 | 280 | 250 | 0 | 0 | 55 | 220 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 54 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 22 | 0 | 0 | 0 | 17 | 210 | 0 | 120 | 0 |  | 24 | 0 | 68 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 270 | 275 | 141 | 45 | 90 | 25 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 142 | 205 | 65 | 19 | 0 | 30 | 42 | 53 | 0 | 163 | 331 | 51 | 72 | 0 | 214 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 130 | 0 | 100 | 120 | 0 | 375 | 115 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 0 | 0 | 0 | 35 | 0 | 17 | 0 |  | 845 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 44 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 128 | 0 | 183 | 0 | 98 | 0 | 191 | 0 | 420 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 36 |  | 7088 | 3709 | 10797 | 4961 | 845 | 1791 | 2193 | 710 | 22 | 133 | 142 | 0 | 0 | 75.2
23:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 341 | 347 |  | 0 | 280 | 270 | 0 | 0 | 55 | 221 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 22 | 0 | 0 | 0 | 17 | 208 | 0 | 120 | 0 |  | 24 | 0 | 68 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 270 | 275 | 142 | 45 | 92 | 25 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 128 | 183 | 65 | 19 | 0 | 30 | 42 | 53 | 0 | 163 | 328 | 51 | 75 | 0 | 218 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 132 | 0 | 100 | 120 | 0 | 375 | 115 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 0 | 0 | 0 | 35 | 0 | 17 | 0 |  | 844 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 136 | 0 | 194 | 0 | 97 | 0 | 196 | 0 | 421 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 54 |  | 7087 | 3758 | 10845 | 4973 | 844 | 1793 | 2242 | 710 | 22 | 133 | 128 | 0 | 0 | 75.2
24:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 336 | 349 |  | 0 | 280 | 275 | 0 | 0 | 55 | 220 | 0 | 140 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 22 | 0 | 0 | 0 | 17 | 204 | 0 | 110 | 0 |  | 24 | 0 | 68 | 92 | 0 | 0 | 19 | 40 | 0 | 0 | 80 | 260 | 265 | 141 | 8 | 90 | 25 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 136 | 193 | 65 | 19 | 0 | 30 | 42 | 53 | 0 | 163 | 332 | 52 | 75 | 0 | 217 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 131 | 0 | 100 | 115 | 0 | 368 | 115 | 0 | 105 | 0 | 0 | 44 | 0 | 0 | 113 | 100 | 400 | 0 | 0 | 0 | 35 | 0 | 17 | 0 |  | 845 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 133 | 0 | 191 | 0 | 96 | 0 | 193 | 0 | 395 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 54 |  | 6997 | 3707 | 10704 | 4912 | 845 | 1729 | 2217 | 710 | 22 | 133 | 136 | 0 | 0 | 75.2
KWH | 0 | 0 | 0 | 4315500 | 0 | 1699909 | 0 | 8004600 | 7460000 |  | 0 | 6477750 | 5877295 | 0 | 0 | 485188 | 4543966 | 0 | 2670000 | 81600 | 30096 | 174240 | 0 | 0 | 0 | 0 | 105480 | 25584 | 326348 | 310932 | 600000 | 98640 | 643900 | 567800 | 258240 | 0 | 427680 | 0 | 0 | 0 | 404789 | 4895767 | 0 | 2685808 | 0 |  | 271200 | 0 | 618163 | 2090760 | 0 | 37440 | 454080 | 986400 | 0 | 0 | 2163888 | 6982000 | 6902000 | 1041000 | 618909 | 2119750 | 532944 | 1294080 | 0 | 1192136 | 0 | 0 | 451042 | 466092 | 157140 | 791300 | 435810 | 2833920 | 4819160 | 1201920 | 403488 | 10200 | 229000 | 984480 | 823200 | 0 | 3296945 | 7482000 | 1204032 | 1268160 | 0 | 4645550 | 407000 | 0 | 156420 | 0 | 374376 | 172000 | 0 | 25091 | 0 | 0 | 381600 | 0 | 1073950 | 146610 | 1753920 | 2515 | 36800 | 8567000 | 1370400 | 55200 | 1738799 | 37199 | 0 | 1192043 | 0 | 0 | 1231440 | 996480 | 9089100 | 52800 | 285790 | 197280 | 391418 | 0 | 421200 | 233461 |  | 15385455 | 0 | 8423712 | 0 | 1419840 | 0 | 0 | 0 | 0 | 0 | 198000 | 2103280 | 685826 | 930720 | 0 | 0 | 0 | 1952 | 0 | 297144 | 0 | 0 | 0 | 265920 | 0 | 407040 | 0 | 184626 | 0 | 0 | 3666400 | 0 | 0 | 844900 | 0 | 4130964 | 0 | 2245378 | 18240 | 4513836 | 0 | 8507490 | 819840 | 0 | 210141 | 0 | 617280 | 0 | 50528 | 40032 | 11818200 | 0 | 0 | 188400 |  | 142369193 | 67975144 | 210344337 | 109961421 | 15385455 | 37119643 | 27276331 | 15484600 | 427680 | 1091499 | 2833920 | 763788 | 0
Fuel Cost | 0 | 0 | 0 | 6343785 | 0 | 2243879.88 | 0 | 8084646 | 7683800 |  | 0 | 7060747.5 | 6523797.45 | 0 | 0 | 4104690.48 | 4725724.64 | 0 | 4619100 | 614448 | 274475.52 | 1714521.6 | 0 | 0 | 0 | 0 | 770004 | 197764.32 | 3217791.28 | 233199 | 450000 | 0 | 0 | 0 | 2497180.8 | 0 | 115473.6 | 0 | 0 | 0 | 3760489.81 | 5336386.03 | 0 | 4565873.6 | 0 |  | 0 | 0 | 5996181.1 | 19966758 | 0 | 296524.8 | 572140.8 | 2929608 | 0 | 0 | 3180915.36 | 5166680 | 6902000 | 957720 | 798392.61 | 2437712.5 | 602226.72 | 1811712 | 0 | 2038552.56 | 0 | 0 | 4307451.1 | 591936.84 | 117855 | 1384775 | 326857.5 | 21254400 | 5108309.6 | 10913433.6 | 512429.76 | 162588 | 375560 | 1575168 | 1465296 | 0 | 3758517.3 | 7781280 | 2371943.04 | 2422185.6 | 0 | 8036801.5 | 891330 | 0 | 319096.8 | 0 | 280782 | 130720 | 0 | 189687.96 | 0 | 0 | 1984320 | 0 | 10567668 | 1713870.9 | 14294448 | 27287.75 | 259440 | 7967310 | 12498048 | 521640 | 15144939.29 | 0 | 0 | 10382694.53 | 0 | 0 | 10553440.8 | 6636556.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 88620220.8 | 0 | 8844897.6 | 0 | 11159942.4 | 0 | 0 | 0 | 0 | 0 | 2063160 | 2376706.4 | 1063030.3 | 9083827.2 | 0 | 0 | 0 | 19207.68 | 0 | 2629724.4 | 0 | 0 | 0 | 2576764.8 | 0 | 781516.8 | 0 | 139761.882 | 0 | 0 | 19871888 | 0 | 0 | 988533 | 0 | 5452872.48 | 0 | 3368067 | 310262.4 | 5281188.12 | 0 | 8422415.1 | 8559129.6 | 0 | 1994238.09 | 0 | 4790092.8 | 0 | 558334.4 | 295836.48 | 51881898 | 0 | 0 | 0 |  | 295624971.63 | 241133515.732 | 536758487.362 | 114715127.372 | 88620220.8 | 46166817.45 | 181338234.06 | 71753786 | 115473.6 | 10359634.78 | 21254400 | 2434793.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 14 | 0 | 333 | 301 |  | 0 | 280 | 260 | 0 | 0 | 15 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 3 | 20 | 25 | 0 | 0 | 23 | 0 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 30 | 0 | 0 | 100 | 285 | 300 | 0 | 8 | 90 | 24 | 56 | 0 | 51 | 0 | 0 | 3 | 18 | 5 | 33 | 17 | 112 | 206 | 57 | 19 | 2 | 0 | 42 | 31 | 0 | 163 | 331 | 51 | 75 | 0 | 217 | 18 | 0 | 6 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 19 | 80 | 120 | 0 | 333 | 8 | 0 | 85 | 2 | 0 | 54 | 0 | 0 | 6 | 10 | 395 | 0 | 44 | 0 | 0 | 0 | 17 | 33 |  | 750 | 0 | 370 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 90 | 0 | 186 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 400 | 0 | 0 | 0 |  | 8466 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 352 | 346 | 0 | 0 | 280 | 245 | 0 | 0 | 55 | 219 | 0 | 150 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 52 | 15 | 25 | 5 | 20 | 25 | 42 | 0 | 21 | 0 | 0 | 0 | 17 | 204 | 0 | 130 | 0 | 0 | 24 | 0 | 68 | 100 | 0 | 6 | 19 | 42 | 0 | 0 | 80 | 275 | 285 | 140 | 45 | 90 | 25 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 140 | 205 | 65 | 19 | 0 | 30 | 42 | 53 | 0 | 163 | 330 | 51 | 75 | 0 | 214 | 18 | 0 | 7 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 72 | 0 | 132 | 0 | 100 | 120 | 0 | 372 | 115 | 0 | 105 | 0 | 0 | 54 | 0 | 0 | 113 | 100 | 400 | 0 | 0 | 17 | 35 | 0 | 17 | 0 |  | 845 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 138 | 0 | 97 | 0 | 192 | 0 | 419 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 550 | 0 | 0 | 35 |  | 10787 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 360 | 360 | 0 | 0 | 280 | 240 | 100 | 0 | 55 | 220 | 0 | 150 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 25 | 17 | 20 | 25 | 42 | 0 | 22 | 0 | 0 | 0 | 17 | 225 | 0 | 140 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 30 | 0 | 0 | 80 | 330 | 330 | 140 | 45 | 92 | 25 | 55 | 0 | 51 | 0 | 50 | 43 | 19 | 11 | 33 | 20 | 179 | 200 | 65 | 19 | 0 | 30 | 42 | 51 | 0 | 163 | 330 | 51 | 75 | 0 | 225 | 18 | 0 | 7 | 0 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 132 | 0 | 100 | 120 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 0 | 162 | 116 | 0 | 17 |  |  | 860 | 0 | 350 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 32 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 140 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 80
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 350 | 360 | 0 | 0 | 280 | 240 | 100 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 15 | 25 | 17 | 20 | 25 | 42 | 0 | 22 | 0 | 0 | 0 | 17 | 225 | 0 | 120 | 0 | 0 | 22 |  | 68 | 100 | 90 | 43 | 22 | 10 | 0 | 0 | 80 | 330 | 330 | 140 | 45 | 90 | 25 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 145 | 200 | 65 | 19 | 1.6 | 30 | 42 | 51 | 0 | 163 | 330 | 51 | 75 | 0 | 225 | 18 | 0 | 7 | 0 | 16 | 11 | 100 | 250 | 100 | 100 | 200 | 0 | 132 | 20 | 100 | 120 | 150 | 400 | 115 | 105 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 162 | 116 | 0 | 17 | 30 |  | 763 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 120 | 0 | 52 | 0 | 329 | 271 | 0 | 0 | 280 | 240 | 0 | 0 | 15 | 160 | 0 | 98 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 25 | 5 | 20 |  | 0 | 0 | 22 | 0 | 0 | 0 | 17 | 213 | 0 | 110 | 0 | 0 | 0 | 0 | 17 | 92 | 0 | 0 | 19 | 10 | 0 | 0 | 80 | 260 | 270 | 142 | 45 | 90 | 23 | 10 | 0 | 15 | 0 | 0 | 16 | 19 | 8 | 33 | 20 | 114 | 207 | 65 | 19 | 1 | 30 | 42 | 14 | 0 | 163 | 331 | 51 | 20 | 0 | 163 | 18 | 0 | 7 | 0 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 100 | 120 | 0 | 322 | 45 | 0 | 0 | 3 | 0 | 35 | 0 | 0 | 26 | 20 | 400 | 0 | 14 | 0 | 0 | 0 | 17 | 13 | 0 | 821 | 0 | 280 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 19 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 163 | 0 | 94 | 0 | 172 | 0 | 346 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 360 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 7153 | 7:00
| Highest Generation |  | 10845 | 23:00
| Day Peak Generation |  | 8466 | 12:00
| Evening Peak Generation |  | 10787 | 21:00
| HVDC Max Flow |  | 845 | 19:00
| HVDC EvPeak Flow |  | 845 | 21:00
| Load factor L.F |  | 80.81%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-17
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8466 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8256 | MW
Evening Peak Generation : |  | 10787 | MW Hour : | 21:00 | Available Max Generation : |  | 15350 | MW
E.P. Demand (at gen end) : |  | 10787 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11600 | MW
Maximum Generation : |  | 10845 | MW Hour : | 23:00 | Reserve(Generation end) |  | 3750 | MW
Total Gen. (MKWH) : |  | 210.3443 | System Load Factor : | 80.81% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -520 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-17
Actual : | 75.18 | Ft.(MSL) , | Rule curve : | 78.96 | Ft.( MSL )
Gas Consumed : | Total = | 1220.61 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160881944.822
: |  | Coal : | 71753786 | Oil : | 191697868.84 | Total : | 424333599.662
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4124.0472 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1403.6811 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1257.8792 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1136.6807 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1027.1574 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 828.8829 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 461.8275 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 213.3716 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 639.2835 |  |  | 0 | 0%
Total | 0 |  | 11092.811 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #1,2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Gopalganj(O)-Madaripur 132 kV Ckt tripped at 10:17 showing dist.Z2,3-phase at Gopalganj end & dist.
3-phase at Madaripur end and was switched on at 10:45.
b) Tongi 132/33 kV T-1 & T-2 transformers tripped at 11:11 due to 33 kV Dokkhinkhan feeder fault and |  |  |  |  | About 40 MW power interruption occurred under Tongi S/S area
were switched on at 11:16. |  |  |  |  | from 11:11 to 11:16.
c) Natore 132/33 kV T-3 transformer was under shut down from 11:30 to 12:35 for C/M.
d) Hasnabad 230/132 kV T-1 transformer was under shut down from 14:09 to 17:45 for flashing from ground wire.
e) Sirajganj #1 GT was synchronized at 14:48.
f) Ashuganj-225 MW CCPP GT was synchronized at 19:13.
g) Ashuganj-B.Baria 132 kV Ckt-2 was under shut down from 14:14 to 15:19 for C/M.
h) Ashuganj-Ghorasal 132 kV Ckt-1 was under shut down from 15:24 to 15:53 for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
| Ghorasal Repowered CCPP Unit-3 |  | PDB | 1*210 | 170 | 0 | 0 | Under maint.
| Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4315500
2 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
3 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 1699909
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 352 | 8004600 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 346 | 7460000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6477750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 245 | 5877295 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 485188
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 310932 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 2670000 | FGMO
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 81600 | Reserve.
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 219 | 4543966
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 30096 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 105480 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 174240 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 25584 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 52 | 326348
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 30 | 698640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 643900 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 567800 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 258240 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 25091 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 1073950 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 55200 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 52800 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 197280 | Low demand
| Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 233461
| Dhaka area Total |  |  |  | 5829 | 2313 | 46394850
39 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
40 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 404789 | Engine problem
41 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 146610
42 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 6 | 37440 | Low demand
43 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 21 | 427680 | Unit-2 under maint
44 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4895767 | FGMO
45 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 130 | 2685808
46 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1738799
47 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | under S/D
48 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 618163 | Engine problem
49 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2090760
50 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1753920
51 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 454080
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 986400
52 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
53 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 37199
54 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
55 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1192043
56 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 0 | Reserve.
57 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 996480
| Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 35 | 391418 | Low demand
| Chattogram area Total |  |  |  | 2382 | 1001 | 18857356
58 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2163888 | Gas shortage
59 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 140 | 1041000 | FGMO
60 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6982000 | FGMO
61 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 285 | 6902000 | FGMO
62 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 25 | 532944 | Engine problem
63 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1294080 | Gas shortage
64 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 618909
65 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1192136 | Gas shortage
66 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 36800 | Reserve.
67 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
68 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2119750 | Machine problem
69 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 2515 | Engine problem
70 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 466092
71 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 157140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2833920 | Bad weather
72 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 791300
73 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 451042
74 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 435810 | Engine problem
75 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
76 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
77 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 113 | 1231440
| Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 421200 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1559 | 29673966
78 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4819160
79 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 403488 | Engine problem
80 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 65 | 1201920 | Engine problem
81 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10200
82 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 72 | 381600 | Low demand
83 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1370400
84 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 285790
85 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 271200
| Mymensingh Area Total |  |  |  | 709 | 500 | 8743758
86 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 229000
87 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 984480
88 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3296945
89 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 330 | 7482000
90 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 823200
91 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
92 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 172000
93 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1204032
94 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 75 | 1268160 | Engine problem
| Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
95 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 214 | 4645550
96 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 407000
97 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
98 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 374376 | Engine problem
99 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | under maint.
100 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 372 | 8567000 | FGMO
101 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 156420 | Engine problem
| Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9089100
| Sylhet Area Total |  |  |  | 2377 | 1782 | 38699263
102 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 845 | 15385455
103 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1419840 | Engine problem
104 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
105 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
106 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
107 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 8423712 | FGMO
108 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 198000 | Engine problem
109 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 18240 | Reserve.
110 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 819840 | Low demand
111 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1431 | 26265087
112 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 930720
113 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 685826
114 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2103280 | Machine problem
115 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 97 | 2245378
116 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 11818200
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
| United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 188400 | Low demand
| Barisal Area Total |  |  |  | 1826 | 914 | 17971804
117 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
118 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 1952 | Reserve.
119 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
120 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
121 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
122 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
123 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 110 | 844900 | sync at 14:48.
124 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 138 | 4130964 | FGMO
125 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 192 | 4513836 | FGMO
126 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 419 | 8507490 | FGMO
127 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
128 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 407040 | Engine problem
129 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
130 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 184626
131 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 265920
132 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 49 | 297144 | Low demand
133 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
134 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 210141 | Low demand
135 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 0 | 40032 | Reserve.
| Rajshahi Area Total |  |  |  | 2173 | 1024 | 19404045
136 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
137 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3666400 | Coal shortage
138 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
139 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
140 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 617280
141 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 50528
| Rangpur Area Total |  |  |  | 605 | 263 | 4334208
| Total |  |  |  | 21219 | 10787 | 210344337
| Eastern Grid Total |  |  |  | 14331 | 7155 | 142369193
| Western Grid Total |  |  |  | 6888 | 3632 | 67975144
| National Grid Total |  |  |  | 21219 | 10787 | 210344337
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-16
(a) ENTIRE EASTERN GRID : |  | 6700 | MW | (b) ENTIRE WESTERN GRID : |  | 3606 | MW
i) Dhaka area |  | 3050 | MW | i) Khulna area |  | 1404 | MW
ii) Chittagong area |  | 1169 | MW | ii) Rajshahi area |  | 1092 | MW
iii) Comilla area |  | 1178 | MW | iii) Barisal area |  | 361 | MW
iv) Mymensingh area |  | 913 | MW | iv) Rangpur area |  | 749 | MW
v) Sylhet area |  | 390 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10306 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 82 | 14:00 | Kishoreganj | 126 | 22:00 | Jessore | 113 | 19:00
Munsiganj | 96 | 23:00 | Netrokona | 119 | 21:00 | Benapol | 50 | 19:30
Sonargaon | 45 | 0:00 | Jamalpur | 124 | 21:00 | Jhenida | 92 | 14:00
Shyampur | 104 | 0:00 | Sherpur | 110 | 21:00 | Bottail | 108 | 21:00
Bhulta | 110 | 20:00 | Srimongal | 43 | 19:00 | G.K Project | 52 | 20:00
Madanganj | 30 | 22:00 | Shahjibazar | 89 | 24:00 | Faridpur | 146 | 23:00
Shitalakhya | 54 | 15:00 | Fenchuganj | 39 | 20:00 | Madaripur | 111 | 22:00
Rahim steel | 23 | 11:00 | Kulawara | 41 | 19:00 | Sariatpur | 74 | 21:00
Matuail | 29 | 0:00 | Sylhet | 100 | 20:00 | Gopalganj | 97 | 22:00
Ghorasal | 64 | 23:00 | Chatak | 25 | 19:30 | Bagerhat | 105 | 21:00
Narsingdi | 126 | 23:00 | Sunamganj | 42 | 21:00 | Mongla | 20 | 12:00
Haripur (SBU) | 67 | 0:00 | Biani Bazar | 55 | 19:00 | Satkhira | 126 | 22:00
Sreenagar | 43 | 0:00 | Comilla (S) | 142 | 22:00 | Gallamari | 31 | 23:00
Ullon | 57 | 1:00 | Comilla(N) | 133 | 21:00 | Magura | 50 | 21:00
Hasnabad | 60 | 19:30 | Chandpur | 85 | 23:00 | Norail | 48 | 20:00
Magbazar | 70 | 12:00 | Feni | 121 | 21:00 | Chuadanga | 80 | 15:00
Maniknagar | 56 | 13:00 | Chowmuhani | 190 | 22:00 | Borguna | 20 | 21:00
Bangabhaban | 188 | 11:00 | Ashuganj | 41 | 21:00 | Barisal(N) | 50 | 23:00
Narinda | 32 | 13:00 | Daudkandi | 144 | 21:00 | Barisal (S) | 104 | 22:00
Dhanmondi | 51 | 23:00 | B.Baria | 151 | 22:00 | Patuakhali | 125 | 22:00
Lalbag | 126 | 13:00 | Ramganj | 104 | 22:00 | Bhandaria | 56 | 21:00
Madartek | 30 | 13:00 | Chaddagram | 39 | 21:00 | Borhan Uddin | 45 | 23:00
Dhaka University | 62 | 23:00 | PHP | 6 | 19:30 | Ishurdi | 55 | 21:00
Aftabnagar | 24 | 13:00 | Kochua | 65 | 21:00 | Ruppur Paromanobik | 2 | 1:00
Fatullah | 8 | 10:00 | Madunaghat | 54 | 19:00 | Natore | 114 | 20:00
Nawabganj | 36 | 22:00 | Hathazari | 85 | 19:30 | Bogra | 115 | 19:30
Keraniganj | 54 | 21:00 | Khulshi | 164 | 21:00 | Noagaon | 99 | 21:00
Mirpur | 48 | 21:00 | Halishahar | 114 | 20:00 | Rajshahi | 139 | 21:00
Kalyanpur | 85 | 13:00 | Baraulia | 57 | 19:30 | Rajshahi New | 14 | 21:00
Gulshan | 96 | 23:00 | Sikalbaha | 36 | 18:00 | C.Nawabganj | 58 | 20:00
Uttara | 104 | 13:00 | Dohazari | 100 | 19:30 | Amnura | 45 | 19:30
Uttara New | 70 | 14:00 | Cox'sbazar | 103 | 20:00 | Pabna | 89 | 21:00
Kamrangirchar | 19 | 15:00 | Chandraghona | 32 | 14:00 | Shahjadpur | 64 | 21:00
Savar | 56 | 24:00 | Kaptai | 4 | 19:00 | Serajganj | 67 | 19:30
Bhasantec | 103 | 19:30 | A. Khaer Stl. | 0 |  | Niyamatpur | 55 | 21:00
Agargaon | 121 | 19:00 | Bakulia | 88 | 23:00 | Joypurhat | 51 | 19:30
Satmosjid | 62 | 13:00 | Julda | 15 | 18:00 | Sherpur(Bogura) | 46 | 20:00
Tongi | 76 | 0:00 | TK chemical | 19.5 | 19:00 | Mohastangor | 66 | 20:00
Kabirpur | 82 | 10:00 | Modern Steel | 0 | #N/A | Bangura | 29 | 13:00
Basundhara | 150 | 20:00 | Shahmirpur | 20 | 1:00 | Rangpur | 104 | 20:00
Manikganj | 142 | 13:00 | Khagrachhari | 26 | 18:00 | Lalmonirhat | 40 | 21:00
Joydevpur | 72 | 23:00 | Matarbari | 42.5 | 20:00 | Saidpur | 90 | 19:30
New Tongi | 99 | 19:30 | Baroiar Hat | 44 | 22:00 | Purbasadipur | 94 | 21:00
Kodda | 56 | 21:00 | Rangamati | 12 | 19:00 | Thakurgaon | 79 | 21:00
Dhamrai | 176 | 22:00 | Abul Khair 230 | 124 | 10:00 | Palashbari | 99 | 20:00
Rajendrapur | 66 | 10:00 | BSRM | 157 | 20:00 | Barapukuria | 50 | 21:00
Valuka | 76 | 21:00 | GPH Ispat | 68 | 17:00 | Panchagar | 50 | 20:00
Tangail | 86 | 15:00 | Goalpara | 20 | 23:00 | Joldhaka | 58 | 20:00
Mymensing | 174 | 20:00 | Central s/s | 93 | 20:00 | Kurigram | 53 | 20:00
Kishoreganj | 200 | 20:00 | Noapara | 47 | 21:00 | Mithapukur | 41 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer
Network Operation Division |  |  | Network Operation Division |  | Load Despatch Circle

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 6:00 | 398 | 23:00 | Kaliakoir | 394 | 0.77083 | 384 | 0.5
| Bheramara | 407 | 4:00 | 391 | 24:00 | Bhulta | 383 | 0.77083 | 374 | 0.45833
| Ashuganj(N) | 391 | 18:00 | 382 | 11:00 | Gopalganj | 401 | 0.625 | 385 | 0.91667
| Payra | 406 | 4:00 | 397 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 220 | 18:30 | 209 | 9:00
| Ishurdi | 235 | 6:00 | 225 | 13:00 | Megnaghat | 233 | 1:00 | 225 | 14:00
| Ashuganj | 235 | 4:00 | 230 | 9:00 | Fenchuganj | 240 | 2:00 | 237 | 11:00
| Serajganj | 230 | 5:00 | 225 | 1:00 | Siddhirganj | 231 | 19:00 | 225 | 13:00
| Baghabari | 234 | 17:00 | 226 | 13:00 | Maniknagar | 230 | 19:00 | 224 | 11:00
| Barapukuria | 234 | 4:00 | 224 | 19:30 | Agargaon | 229 | 18:30 | 221 | 11:00
| Bogra | 227 | 18:00 | 216 | 20:00 | Barisal | 247 | 14:00 | 236 | 4:00
| Rajshahi | 234 | 6:00 | 220 | 13:00 | Bhola 225 MW | 251 | 18:30 | 239 | 14:00
| Khulna South | 230 | 18:30 | 210 | 4:00 | AKSML | 220 | 14:00 | 210 | 9:00
| Rampura | 233 | 14:00 | 222 | 12:00 | BSRM | 222 | 4:00 | 212 | 9:00
| Haripur | 230 | 4:00 | 224 | 11:00 | Bibiyana | 240 | 6:00 | 236 | 12:00
| Hasnabad | 230 | 1:00 | 224 | 12:00 | Bhulta | 231 | 3:00 | 225 | 11:00
| Shyampur | 228 | 4:00 | 220 | 11:00 | Ashuganj (S) | 236 | 18:30 | 230 | 11:00
| Aminbazar | 228 | 1:00 | 223 | 2:00 | Kaliakoir | 228 | 4:00 | 221 | 12:00
| Tongi | 228 | 18:00 | 215 | 13:00 | GPH | 220 | 18:00 | 210 | 9:00
| Comilla (N) | 229 | 18:30 | 222 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 137 | 4:00 | 133 | 13:00 | Kochua | 133 | 0.58333 | 128 | 0.91667
| Munsiganj | 137 | 18:30 | 131 | 13:00 | Madanhat | 129 | 0.29167 | 126 | 0.41667
| Sonargaon | 135 | 1:00 | 131 | 9:00 | Hathazari | 131 | 0.77083 | 125 | 0.083333
| Shyampur | 135 | 3:00 | 132 | 10:00 | Khulshi | 128 | 0.77083 | 123 | 0.375
| Bhulta | 131 | 3:00 | 126 | 13:00 | Halishahar | 129 | 0.58333 | 124 | 0.375
| Madanganj | 134 | 4:00 | 130 | 8:00 | Baraulia | 129 | 0.75 | 125 | 0.041667
| Shitalakhya | 141 | 18:30 | 133 | 15:00 | Sikalbaha | 130 | 0.75 | 126 | 0.375
| Rahim steal | 136 | 3:00 | 133 | 12:00 | Dohazari | 127 | 0.77083 | 121 | 0.041667
| Matuail | 137 | 4:00 | 133 | 13:00 | Cox'sbazar | 121 | 0.75 | 108 | 0.041667
| Ghorasal | 140 | 6:00 | 136 | 2:00 | Chandraghona | 130 | 0.75 | 125 | 0.375
| Narsinghdi | 134 | 5:00 | 126 | 19:00 | Kaptai | 128 | 0.41667 | 127 | 0.041667
| Haripur (SBU) | 138 | 1:00 | 133 | 11:00 | A. Khaer Stl. | 127 | 0.083333 | 125 | 0.25
| Sreenagar | 132 | 18:30 | 127 | 11:00 | Bakulia | 130 | 0.75 | 125 | 0.125
| Ullon | 133 | 18:30 | 129 | 11:00 | Julda | 131 | 0.58333 | 126 | 0.45833
| Hasnabad | 138 | 18:30 | 132 | 15:00 | TK Chemical | 129 | 0.875 | 119 | 0.79167
| Magbazar | 132 | 4:00 | 126 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Maniknagar | 139 | 18:30 | 135 | 10:00 | Shahmirpur | 130 | 0.8125 | 125 | 0.33333
| Bangabhaban | 139 | 18:30 | 135 | 10:00 | Khagrachhari | 129 | 0.75 | 124 | 0.5
| Narinda | 139 | 18:30 | 135 | 10:00 | Matarbari | 119 | 0.54167 | 111 | 0.041667
| Dhanmondi | 139 | 6:00 | 135 | 10:00 | Baroiar Hat | 129 | 0.58333 | 122 | 0.375
| Lalbag | 137 | 6:00 | 133 | 10:00 | Rangamati | 129 | 18:30 | 124 | 9:00
| Madartek | 140 | 18:30 | 133 | 15:00 | Goalpara S/S | 139 | 18:30 | 126 | 12:00
| Dhaka University | 134 | 18:30 | 127 | 10:00 | Khulna Central S/S | 136 | 18:00 | 124 | 0.5
| Aftabnagar | 134 | 18:30 | 127 | 10:00 | Noapara | 135 | 18:00 | 122 | 0.54167
| Fatullah | 134 | 19:00 | 128 | 9:00 | Jessore | 131 | 18:00 | 117 | 0.083333
| Nawabganj | 136 | 6:00 | 132 | 11:00 | Benapol | 133 | 18:30 | 119 | 0.041667
| Keraniganj | 132 | 18:30 | 128 | 11:00 | Jhenida | 128 | 0.77083 | 112 | 0.91667
| Mirpur | 132 | 4:00 | 128 | 11:00 | Bottail | 133 | 18:30 | 122 | 0.91667
| Kalyanpur | 137 | 5:00 | 131 | 13:00 | G.K Project | 138 | 0.75 | 133 | 0.58333
| Gulshan | 137 | 2:00 | 132 | 11:00 | Faridpur | 135 | 0.16667 | 127 | 0.91667
| Uttara | 133 | 18:00 | 126 | 11:00 | Madaripur | 138 | 0.77083 | 130 | 0.58333
| Uttara New | 137 | 6:00 | 131 | 12:00 | Shariyatpur S/S | 139 | 0.77083 | 130 | 0.58333
| Kamrangirchar | 136 | 1:00 | 130 | 13:00 | Gopalganj | 139 | 5:00 | 131 | 0.91667
| Savar | 138 | 4:00 | 133 | 12:00 | Bagerhat | 132 | 0.625 | 120 | 0.16667
| Bhasantec | 138 | 4:00 | 133 | 12:00 | Mongla | 134 | 18:30 | 121 | 0.5
| Agargaon | 134 | 4:00 | 129 | 11:00 | Satkhira | 136 | 18:00 | 121 | 0.91667
| Satmosjid | 135 | 4:00 | 130 | 11:00 | Gallamari | 138 | 18:00 | 126 | 4:00
| Tongi | 134 | 4:00 | 129 | 12:00 | Magura | 125 | 0.75 | 110 | 23:00
| Kabirpur | 140 | 18:00 | 133 | 14:00 | Narail | 128 | 18:30 | 109 | 0.91667
| Basundhara | 138 | 18:30 | 132 | 22:00 | Chuadanga | 128 | 0.77083 | 106 | 0.041667
| Manikganj | 139 | 18:30 | 131 | 12:00 | Borguna | 138 | 18:30 | 127 | 0.125
| Joydevpur | 142 | 18:30 | 134 | 12:00 | Barisal(N) | 140 | 18:30 | 132 | 0.16667
| New Tongi | 139 | 0:00 | 130 | 15:00 | Barisal (S) | 139 | 18:30 | 130 | 4:00
| Kodda | 139 | 18:30 | 139 | 7:00 | Patuakhali(S) | 135 | 0.8125 | 127 | 0.041667
| Dhamrai | 140 | 19:30 | 129 | 12:00 | Bhandaria | 136 | 0.77083 | 126 | 0.041667
| Rajendrapur | 136 | 18:30 | 132 | 9:00 | Ishurdi | 136 | 0.25 | 130 | 0.83333
| Valuka | 137 | 19:30 | 125 | 13:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 21:00
| Tangail | 128 | 7:00 | 119 | 19:30 | Natore | 135 | 5:00 | 129 | 20:00
| Mymensing | 135 | 4:00 | 128 | 12:00 | Bogra | 134 | 6:00 | 125 | 21:00
| Kishorganj | 131 | 4:00 | 121 | 22:00 | Noagaon | 131 | 18:30 | 119 | 21:00
| Netrokona | 130 | 4:00 | 122 | 23:00 | Rajshahi | 134 | 18:00 | 125 | 21:00
| Jamalpur | 130 | 7:00 | 116 | 23:00 | Rajshahi New | 135 | 5:00 | 127 | 20:00
| Sherpur | 137 | 18:30 | 121 | 8:00 | C.Nawabganj | 132 | 6:00 | 124 | 13:00
| Srimongal | 135 | 18:30 | 121 | 12:00 | Amnura | 134 | 18:30 | 124 | 1:00
| Shahjibazar | 139 | 14:00 | 134 | 11:00 | Pabna | 135 | 6:00 | 129 | 20:00
| Fenchuganj | 135 | 1:00 | 131 | 11:00 | Shahjadpur | 140 | 18:00 | 136 | 19:00
| Khulawara | 138 | 3:00 | 134 | 19:30 | Serajganj | 135 | 18:00 | 127 | 19:30
| Sylhet | 137 | 14:00 | 135 | 17:00 | Niyamatpur | 131 | 18:30 | 117 | 21:00
| Chatak | 135 | 9:00 | 133 | 19:30 | Joypurhat | 134 | 18:30 | 120 | 21:00
| Sunamganj | 134 | 3:00 | 130 | 23:00 | Sherpur(Bogura) | 135 | 18:30 | 127 | 20:00
| Biani Bazar | 133 | 5:00 | 129 | 21:00 | Mohastangor | 134 | 18:30 | 124 | 21:00
| Comilla(s) | 134 | 4:00 | 131 | 19:00 | Bangura | 137 | 18:00 | 131 | 20:00
| Comilla(n) | 129 | 5:00 | 122 | 19:00 | Rangpur | 128 | 18:30 | 116 | 19:30
| Chandpur | 137 | 18:30 | 131 | 23:00 | Lalmonirhat | 128 | 6:00 | 118 | 21:00
| Feni | 131 | 10:00 | 126 | 22:00 | Saidpur | 130 | 17:00 | 118 | 19:30
| Chowmuhani | 128 | 18:30 | 123 | 0:00 | Purbasadipur | 130 | 3:00 | 112 | 21:00
| Ashuganj | 131 | 19:30 | 114 | 11:00 | Thakurgaon | 129 | 18:30 | 112 | 19:30
| Daudkandi | 135 | 16:00 | 132 | 14:00 | Palashbari | 130 | 5:00 | 121 | 20:00
| B.Baria | 132 | 18:30 | 127 | 23:00 | Barapukuria | 134 | 4:00 | 124 | 19:30
| Ramganj | 132 | 14:00 | 127 | 22:00 | Panchagar | 128 | 18:00 | 108 | 21:00
| Chaddagram | 128 | 14:00 | 122 | 23:00 | Joldhaka | 127 | 6:00 | 112 | 19:30
| PHP | 130 | 18:00 | 125 | 9:00 | Kurigram | 125 | 0.41667 | 114 | 0.8125

## L-Curve
Date | 2021-05-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 10 | 6997 | 3707 | 10704 |  |  |  | QF-LDC-11
0:30 | 159 | 6418 | 3271 | 9689 | Date: | 2021-05-16
1:00 | 308 | 5839 | 2835 | 8674
1:30 | 414 | 5834 | 2727 | 8561
2:00 | 520 | 5829 | 2619 | 8448
2:30 | 515 | 5823 | 2516.5 | 8339.5 | [5 empty] | Gen. at Eve. Peak | 10787 | 10787 MW (21:00 )
3:00 | 510 | 5817 | 2414 | 8231 | [6 empty] | 21:00
3:30 | 486 | 5802 | 2363.5 | 8165.5 | [5 empty] | Gen. at Day Peak | 8466 | 8466 MW (12:00 )
4:00 | 462 | 5787 | 2313 | 8100 | [6 empty] | 12:00
4:30 | 421 | 5654.5 | 2333 | 7987.5 | [5 empty] | Highest Generation | 10845
5:00 | 380 | 5522 | 2353 | 7875 | [6 empty] | 23:00
5:30 | 370 | 5302 | 2244 | 7546
6:00 | 360 | 5082 | 2135 | 7217
6:30 | 346 | 5054.5 | 2130.5 | 7185
7:00 | 332 | 5027 | 2126 | 7153
7:30 | 296 | 5096.5 | 2149 | 7245.5
8:00 | 260 | 5166 | 2172 | 7338
8:30 | 234 | 5287.5 | 2240 | 7527.5
9:00 | 208 | 5409 | 2308 | 7717
9:30 | 200 | 5510 | 2318 | 7828
10:00 | 192 | 5611 | 2328 | 7939
10:30 | 124 | 5655.5 | 2336 | 7991.5
11:00 | 56 | 5700 | 2344 | 8044
11:30 | 30 | 5738 | 2517 | 8255
12:00 | 4 | 5776 | 2690 | 8466
12:30 | 24 | 5949 | 2723.5 | 8672.5
13:00 | 44 | 6122 | 2757 | 8879
13:30 | 162 | 6230 | 2749 | 8979
14:00 | 280 | 6338 | 2741 | 9079
14:30 | 164 | 6349.5 | 2821.5 | 9171
15:00 | 48 | 6361 | 2902 | 9263
15:30 | 41 | 6172 | 2858.5 | 9030.5
16:00 | 34 | 5983 | 2815 | 8798
16:30 | 34 | 5803.5 | 2741 | 8544.5
17:00 | 34 | 5624 | 2667 | 8291
17:30 | 57 | 5457 | 2575.5 | 8032.5
18:00 | 80 | 5290 | 2484 | 7774
18:30 | 90 | 5800.5 | 2785 | 8585.5
19:00 | 100 | 6311 | 3086 | 9397
19:30 | 208 | 7001 | 3287 | 10288
20:00 | 206 | 7044 | 3278 | 10322 |  |  |  | Executive Engineer
20:30 | 127 | 7099.5 | 3455 | 10554.5 |  |  |  | Network Operation Division
21:00 | 48 | 7155 | 3632 | 10787
21:30 | 39 | 7121.5 | 3670.5 | 10792
22:00 | 30 | 7088 | 3709 | 10797 |  |  |  |  | Page 6 of 7
22:30 | 23 | 7087.5 | 3733.5 | 10821
23:00 | 16 | 7087 | 3758 | 10845
23:30 | 13 | 7042 | 3732.5 | 10774.5
24:00 | 10 | 6997 | 3707 | 10704
10787 MW (21:00 )
8466 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-16 |  | Energy | 210344337
[11 empty] | 2021-05-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4912 | 845 | 1729 | 2242 | 710 | 22 | 133 | 0 | 136 | 0
0:30 | 4734.5 | 785.5 | 1657 | 1624.5 | 665 | 22.5 | 83.5 | 0 | 129 | 0 | Date: | 2021-05-16
1:00 | 4557 | 726 | 1585 | 1007 | 620 | 23 | 34 | 0 | 122 | 0
1:30 | 4559.5 | 634 | 1574 | 995.5 | 620 | 23 | 34 | 0 | 121 | 0 | [7 empty] | Total Energy | 210.3443 | Total Energy Gen 210.344 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 210.344 MKWHr
2:00 | 4562 | 542 | 1563 | 984 | 620 | 23 | 34 | 0 | 120 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4558.5 | 515.5 | 1543 | 927.5 | 620 | 23 | 34 | 0 | 118 | 0 | [7 empty] | Energy Requirement | 210.3443
3:00 | 4555 | 489 | 1523 | 871 | 620 | 23 | 34 | 0 | 116 | 0
3:30 | 4529 | 489 | 1514 | 842 | 620 | 22.5 | 34 | 0 | 115 | 0 | [6 empty] | Shortage
4:00 | 4503 | 489 | 1505 | 813 | 620 | 22 | 34 | 0 | 114 | 0
4:30 | 4438.5 | 489 | 1478.5 | 810.5 | 620 | 22 | 18 | 0 | 111 | 0
5:00 | 4374 | 489 | 1452 | 808 | 620 | 22 | 2 | 0 | 108 | 0
5:30 | 4306 | 441.5 | 1402 | 685 | 585 | 22 | 1 | 0 | 102 | 1.5
6:00 | 4238 | 394 | 1352 | 562 | 550 | 22 | 0 | 0 | 96 | 3
6:30 | 4247 | 394 | 1335 | 533.5 | 550 | 21.5 | 0 | 0 | 90 | 14 |  |  |  |  | Coal
7:00 | 4256 | 394 | 1318 | 505 | 550 | 21 | 0 | 0 | 84 | 25
7:30 | 4313 | 394 | 1331 | 511 | 550 | 21 | 0 | 0 | 91 | 34.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4370 | 394 | 1344 | 517 | 550 | 21 | 0 | 0 | 98 | 44
8:30 | 4470.5 | 394 | 1397.5 | 539 | 550 | 21.5 | 0 | 0 | 103 | 52
9:00 | 4571 | 394 | 1451 | 561 | 550 | 22 | 0 | 0 | 108 | 60
9:30 | 4601.5 | 394.5 | 1465.5 | 615.5 | 549.5 | 22.5 | 0 | 0 | 110 | 69
10:00 | 4632 | 395 | 1480 | 670 | 549 | 23 | 0 | 0 | 112 | 78
10:30 | 4626 | 394.5 | 1474.5 | 721 | 549 | 23 | 0 | 0 | 110 | 93.5
11:00 | 4620 | 394 | 1469 | 772 | 549 | 23 | 0 | 0 | 108 | 109
11:30 | 4577 | 572 | 1496.5 | 819 | 549.5 | 23 | 0 | 0 | 110 | 108
12:00 | 4534 | 750 | 1524 | 866 | 550 | 23 | 0 | 0 | 112 | 107
12:30 | 4559 | 750 | 1609 | 962.5 | 550 | 23 | 0 | 0 | 117 | 102
13:00 | 4584 | 750 | 1694 | 1059 | 550 | 23 | 0 | 0 | 122 | 97
13:30 | 4584 | 750 | 1694 | 1059 | 550 | 23 | 0 | 0 | 122 | 97
14:00 | 4584 | 750 | 1694 | 1059 | 550 | 23 | 0 | 0 | 122 | 97
14:30 | 4581.5 | 750 | 1673.5 | 1250 | 585 | 22.5 | 0 | 0 | 119 | 89.5
15:00 | 4579 | 750 | 1653 | 1441 | 620 | 22 | 0 | 0 | 116 | 82
15:30 | 4537 | 750 | 1612.5 | 1315 | 620 | 22 | 0 | 0 | 115 | 59
16:00 | 4495 | 750 | 1572 | 1189 | 620 | 22 | 0 | 0 | 114 | 36
16:30 | 4398 | 750 | 1494 | 1126.5 | 610 | 21.5 | 0 | 0 | 111 | 33.5
17:00 | 4301 | 750 | 1416 | 1064 | 600 | 21 | 0 | 0 | 108 | 31
17:30 | 4150.5 | 750 | 1308.5 | 1073 | 595 | 21 | 8.5 | 0 | 108 | 18
18:00 | 4000 | 750 | 1201 | 1082 | 590 | 21 | 17 | 0 | 108 | 5
18:30 | 4122.5 | 797.5 | 1374 | 1452 | 595 | 21 | 99 | 0 | 122 | 2.5
19:00 | 4245 | 845 | 1547 | 1822 | 600 | 21 | 181 | 0 | 136 | 0
19:30 | 4396 | 844 | 1603 | 2417 | 610 | 21 | 263 | 0 | 134 | 0
20:00 | 4573 | 845 | 1658 | 2294 | 630 | 21 | 165 | 0 | 136 | 0
20:30 | 4751.5 | 845 | 1724 | 2253 | 665 | 21 | 157 | 0 | 138 | 0
21:00 | 4930 | 845 | 1790 | 2212 | 700 | 21 | 149 | 0 | 140 | 0
21:30 | 4945.5 | 845 | 1790.5 | 2202.5 | 705 | 21.5 | 141 | 0 | 141 | 0
22:00 | 4961 | 845 | 1791 | 2193 | 710 | 22 | 133 | 0 | 142 | 0
22:30 | 4967 | 844.5 | 1792 | 2217.5 | 710 | 22 | 133 | 0 | 135 | 0
23:00 | 4973 | 844 | 1793 | 2242 | 710 | 22 | 133 | 0 | 128 | 0
23:30 | 4942.5 | 844.5 | 1761 | 2242 | 710 | 22 | 133 | 0 | 132 | 0 | Max Temp. in Dhaka |  | 36.4° C
24:00 | 4912 | 845 | 1729 | 2242 | 710 | 22 | 133 | 0 | 136 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
Total Energy Gen 210.344 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 210.344 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 23 | 23 | 23 | 22 | 22 | 22 | 21 | 21 | 22 | 23 | 23 | 23 | 23 | 23 | 22 | 22 | 21 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 427680
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 404789
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 10 | 15 | 19 | 16 | 19 | 19 | 17 | 13 | 9 | 3 | 0 | [8 empty] | 146610
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 216 | 216 | 227 | 205 | 203 | 210 | 205 | 209 | 203 | 205 | 203 |  | 203 | 203 | 205 | 204 | 210 | 208 | 204 | 4895767
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 110 | 70 | 70 |  | 120 | 130 | 130 | 130 | 120 | 120 | 110 | 2685808
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 34 | 2 | [12 empty] | 17 |  | 85 | 85 | 68 | 68 | 68 | 68 | 68 | 618163
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 35 | 54 | 85 | 85 | 85 | 85 | 89 | 85 | 85 | 103 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1738799
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 120 | 120 | 120 | 75 | 75 | 75 | 75 | 100 | 95 | 70 | 70 | 145 | 70 | 70 | 72 | 72 |  | 117 | 90 | 98 | 150 | 140 | 140 | 140 | 2670000
17 | Siddhirganj 335 MW CCPP | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 205 | 213 | 160 | 140 | 140 |  | 140 | 140 | 140 | 219 | 220 | 221 | 220 | 4543966
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 17 | [6 empty] | 25091
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 40 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 8 | 618909
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP Unit-3
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4315500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 125 | 125 | 125 | 125 | 95 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2163888
32 | Ashuganj 50 MW PP | 26 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 26 | 26 | 26 | 24 | 23 | 23 | 23 | 23 | 23 | 25 |  | 23 | 25 | 25 | 25 | 25 | 25 | 25 | 532944
33 | Ashuganj 225 MW CCPP | 61 | 100 | 100 | 100 | [16 empty] | 42 | 139 | 140 | 141 | 142 | 141 | 1041000
34 | Ashuganj 450 MW CCPP(South) | 270 | 275 | 270 | 265 | 270 | 270 | 265 | 305 | 300 | 305 | 305 | 300 | 315 | 295 | 310 | 295 | 300 | 265 |  | 270 | 270 | 285 | 285 | 275 | 275 | 265 | 6902000
| Ashuganj 450 MW CCPP(North) | 270 | 275 | 270 | 270 | 270 | 270 | 260 | 295 | 310 | 290 | 295 | 285 | 300 | 280 | 295 | 280 | 280 | 260 |  | 260 | 260 | 285 | 275 | 270 | 270 | 260 | 6982000
35 | Ashuganj 55 MW PP (Precision) | 57 | 57 | 57 | 56 | 57 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 55 | 55 | 10 |  | 10 | 10 | 53 | 56 | 56 | 56 | 56 | 1294080
36 | Chandpur 150 MW CCPP | 90 | 90 | 92 | 86 | 99 | 90 | 90 | 90 | 90 | 92 | 90 | 90 | 90 | 86 | 91 | 90 | 90 | 90 |  | 86 | 88 | 90 | 90 | 90 | 92 | 90 | 2119750
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 327 | 327 | 329 | 327 | 333 | 318 | 304 | 304 | 348 | 344 | 337 | 333 | 341 | 343 | 335 | 330 | 329 | 308 |  | 263 | 329 | 329 | 352 | 334 | 341 | 336 | 8004600
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6477750
41 | Haripur 360MW CCPP(HPL) | 301 | 302 | 301 | 301 | 302 | 302 | 302 | 303 | 301 | 301 | 301 | 301 | 338 | 338 | 340 | 300 | 252 | 252 |  | 312 | 346 | 346 | 346 | 348 | 347 | 349 | 7460000
42 | RPCL 210MW CCPP | 212 | 210 | 212 | 212 | 211 | 211 | 213 | 212 | 208 | 206 | 206 | 206 | 202 | 203 | 201 | 201 | 203 | 205 |  | 203 | 205 | 203 | 205 | 205 | 183 | 193 | 4819160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 7 | 12 | 15 | 17 | 49 | 44 | 49 | 45 | 37 | 5 | 19 | 4 | [8 empty] | 285790
44 | Fenchugonj CCPP Phase-1 | [13 empty] | 10 | 10 | 10 | 15 | 20 |  | 20 | 25 | 30 | 30 | 30 | 30 | 30 | 229000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 984480
46 | Shajibazar 330 MW CCPP | 330 | 330 | 330 | 331 | 328 | 331 | 333 | 333 | 330 | 332 | 330 | 331 | 333 | 331 | 331 | 330 | 304 | 302 |  | 308 | 308 | 296 | 330 | 331 | 328 | 332 | 7482000
47 | Shahjibazar GTPP Unit- 8 & 9 | 53 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 52 | 51 | 51 | 52 | 52 | 51 | 51 | 51 | 40 |  | 51 | 51 | 51 | 51 | 51 | 51 | 52 | 1204032
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 30 | 10 | 10 | 10 | 10 | 10 | 10 | 75 | 75 | 75 | 75 | 72 | 10 | 10 |  | 75 | 75 | 75 | 75 | 72 | 75 | 75 | 1268160
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 190 | 176 | 170 | 164 | 163 | 163 | 165 | 163 | 163 | 209 | 216 | 217 | 217 | 217 | 217 | 218 | 203 | 150 |  | 214 | 217 | 214 | 214 | 214 | 218 | 217 | 4645550
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 407000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 156420
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 3 | 2 | 2 | 5 | 5 |  |  | 2 | 5 | 5 | 5 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 172000
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 31 | 53 | 53 | 52 | 53 | 11 | 11 |  | 18 | 53 | 53 | 53 | 53 | 53 | 53 | 823200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 374376
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 350 | 350 | 350 | 350 | 401 | 401 | 400 | 395 | 399 | 401 | 390 | 395 | 392 | 300 |  | 368 | 400 | 400 | 400 | 400 | 400 | 400 | 9089100
58 | Nababganj 55 MW PP (Southern power ) | [17 empty] | 17 |  | 47 | 51 | 52 | 52 | 54 | 55 | 55 | 326348
59 | Tangail Palli Power Gen 22 MW | [12 empty] | 5 | 23 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 271200
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 454080
61 | Narshingdi 22 MW PP (Doreen) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  |  |  | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 310932
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 18 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 403488
63 | Impoprt (Tripura) | 122 | 120 | 116 | 114 | 108 | 96 | 84 | 98 | 108 | 112 | 108 | 112 | 122 | 124 | 116 | 114 | 108 | 108 |  | 136 | 134 | 136 | 140 | 142 | 128 | 136 | 2833920
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 30 | 27 | 27 | 30 | 30 | 30 | 28 | 28 | 36 | 39 |  | 40 | 42 | 42 | 42 | 42 | 42 | 40 | 986400
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 17 | 18 | 18 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 466092
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 157140
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791300
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 435810
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 3 | 3 | 3 | 3 | 3 | 3 | 5 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 3 | 5 | 5 | 5 | 5 | 5 | 5 | 98640
71 | Maona 33 MW PP(Summit) | 20 | 20 | 20 | 20 | 20 | 0 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 643900
72 | Rupganj 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 17 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 567800
73 | Ghorashal 108MW PP (Regent) | 104 | 104 | 104 | 104 | 104 | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 97 | 101 | 100 | 97 | 98 | 42 |  | 96 | 103 | 104 | 104 | 104 | 104 | 104 | 1699909
| Feni Lanka Power | [25 empty] | 0 | 0
| Chowmuhani 113 MW | 36 | 36 | 36 | 36 | 36 | [6 empty] | 6 | 26 | 43 | 113 | 26 | 26 | 26 |  | 67 | 113 | 113 | 113 | 113 | 113 | 113 | 1231440
| Manikgonj 162MW PP(MPGL) | [19 empty] | 36 | 54 | 17 | 17 |  |  |  | 197280
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 20 | 50 | 50 |  |  |  | 0 | 81600
78 | Gazipur 52 MW PP | [15 empty] | 5 | 8 | 8 |  | 21 | 42 | 42 | 42 | 42 | 42 | 42 | 258240
79 | Kodda 150MW PP | [19 empty] | 48 | 82 | 48 | 32 | 16 | 16 | 16 | 174240
80 | Jamalpur 95 MW PP(Powerpac) | 65 | 57 | 57 | 57 | 57 | 10 |  |  | 15 | 49 | 57 | 57 | 56 | 57 | 56 | 56 | 56 | 56 |  | 56 | 56 | 56 | 65 | 65 | 65 | 65 | 1201920
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | [6 empty] | 3 | 16 | 34 | 43 | 34 | 8 | 8 |  | 23 | 43 | 43 | 43 | 43 | 43 | 43 | 451042
| Gazipur 100 MW PP | [19 empty] | 17 | 35 | 35 |  |  |  | 0 | 55200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 2 | 4 | 5 | 4 | 2 | 1 | 0 | [8 empty] | 37199
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 39 | 35 | 35 | 35 | 39 | 54 | 41 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 44 | 1192043
| Karnaphuli Power Ltd. | [25 empty] | 0 | 0
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 230 | 230 | 235 | 235 | 230 | 230 | 235 | 240 | 250 | 255 | 250 | 260 | 260 | 255 | 230 | 230 | 230 | 230 |  | 230 | 250 | 250 | 245 | 250 | 270 | 275 | 5877295
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 11 | 53 | 39 |  |  |  |  | 52800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 92 | 92 | 70 | 70 | 70 | 80 | 68 | 68 | 80 | 80 | 80 | 92 | 92 | 70 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 2090760
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 10 |  | 24 | 35 | 44 | 51 | 51 | 51 | 51 | 1192136
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 24 | 16 |  |  |  |  | 0 | 30096
95 | Patenga 50MW PP (Baraka) | [19 empty] | 8 | 6 | 6 | 6 | 6 | 6 | 0 | 37440
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [10 empty] | 6 | 15 | 15 | 15 | 23 | 30 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 485188
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 25584
101 | Kushiara 163 MW CCPP (KP) | 130 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 3296945
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 10200
103 | Kamalaghat 54 MW PP(Banco Energy) | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 105480
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [19 empty] | 17 | 72 | 65 | 72 | 72 | 72 | 72 | 381600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [9 empty] | 4 | 16 | 16 | 18 | 33 | 56 | 61 | 60 | 60 |  | 74 | 132 | 132 | 132 | 130 | 132 | 131 | 1073950
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 80 | 80 | 80 | 100 | 100 | 100 | 50 | 50 | 50 |  | 75 | 100 | 100 | 100 | 100 | 100 | 100 | 1753920
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 100 | 100 | 70 | 50 | 50 | 50 | 73 | 119 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 2515
117 | Ashuganj 150MW PP (Midland) | [19 empty] | 15 | 20 |  |  |  |  | 0 | 36800
118 | Bibiyana-III 400 MW CCPP | 368 | 368 | 366 | 366 | 365 | 331 | 332 | 360 | 377 | 374 | 376 | 333 | 343 | 331 | 336 | 332 | 321 | 331 |  | 366 | 367 | 379 | 372 | 375 | 375 | 368 | 8567000
| Jamalpur 115 MW PP (United) | 55 | 55 | 55 | 55 | 55 |  |  |  | 2 | 8 | 8 | 8 | 24 | 42 | 75 | 75 | 45 | 45 |  | 86 | 115 | 115 | 115 | 115 | 115 | 115 | 1370400
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 50 | 90 | 90 | 30 | 30 | 30 |  | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 996480
| Anlima Energy Ltd. | [12 empty] | 8 | 21 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 391418
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 |  | 11 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 421200
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 9 | 17 | 22 | 30 | 31 | 33 | 16 | 29 | 23 | 16 | 5 | [9 empty] | 233461
120 | Eastern Zone Total | 5839 | 5829 | 5817 | 5787 | 5522 | 5082 | 5027 | 5166 | 5409 | 5611 | 5700 | 5776 | 6122 | 6338 | 6361 | 5983 | 5624 | 5290 |  | 6311 | 7001 | 7044 | 7155 | 7088 | 7087 | 6997 | 142369193
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 66 | 32 | 32 | [6 empty] | 38 | 99 | 99 | 99 | 99 | 66 | 49 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1419840
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 53 | 53 | [10 empty] | 14 | 36 | 60 | 17 | 17 | 17 |  | 33 | 90 | 90 | 90 | 90 | 90 | 90 | 819840
130
131
132 | United Payra Power Ltd. | [19 empty] | 1 | 17 | 17 | 35 | 36 | 54 | 54 | 188400
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 32 | 16 | 16 | [9 empty] | 32 | 32 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 930720
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 96 | 96 | 96 | 94 | 95 | 91 | 91 | 91 | 92 | 90 | 88 | 86 | 89 | 90 | 91 | 91 |  | 93 | 96 | 96 | 97 | 98 | 97 | 96 | 2245378
| Bhola 225 MW CCPP | 87 | 87 | 87 | 88 | 88 | 88 | 88 | 88 | 87 | 87 | 86 | 86 | 85 | 84 | 85 | 85 | 85 | 86 |  | 87 | 87 | 87 | 88 | 88 | 88 | 87 | 2103280
140 | Bhola 33 MW PP (Venture) | 33 | 34 | 33 | 31 | 30 | 29 | 27 | 27 | 25 | 25 | 23 | 25 | 25 | 26 | 26 | 27 | 26 | 26 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 685826
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 7 | [5 empty] | 0 | 18240
142 | Noapara 40 MW PP (Khanjahan Ali) | [14 empty] | 8 |  |  |  |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 198000
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 726 | 542 | 489 | 489 | 489 | 394 | 394 | 394 | 394 | 395 | 394 | 750 | 750 | 749 | 750 | 750 | 750 | 750 |  | 845 | 844 | 845 | 845 | 845 | 844 | 845 | 15385455
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 320 | 320 | 320 | 320 | 320 | 390 | 370 | 370 | 370 | 380 | 355 | 375 | 350 | 300 | 230 |  | 230 | 240 | 260 | 365 | 375 | 375 | 360 | 8423712
148 | Payra 1320 MW | 470 | 470 | 470 | 470 | 470 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 430 | 470 | 470 | 450 | 440 |  | 450 | 460 | 480 | 550 | 560 | 560 | 560 | 11818200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3666400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [26 empty] | 1952
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [14 empty] | 10 | 50 | 50 | 50 |  | 50 | 50 | 60 | 110 | 128 | 136 | 133 | 844900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 159 | 160 | 162 | 160 | 165 | 159 | 160 | 163 | 172 | 174 | 190 | 183 | 166 | 167 | 163 | 159 | 140 | 130 |  | 130 | 134 | 130 | 138 | 183 | 194 | 191 | 4130964
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 155 | 158 | 155 | 155 | 145 | 168 | 178 | 183 | 187 | 196 | 186 | 182 | 184 | 180 | 176 | 175 | 175 |  | 179 | 173 | 175 | 192 | 191 | 196 | 193 | 4513836
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 327 | 333 | 295 | 280 | 316 | 330 | 297 | 333 | 386 | 418 | 409 | 377 | 375 | 339 | 376 | 340 | 327 | 251 |  | 386 | 350 | 351 | 419 | 420 | 421 | 395 | 8507490
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 407040
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 5 |  |  | 5 | 5 |  | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 184626
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | [12 empty] | 8 | 8 | 8 |  |  |  |  | 8 | 40 | 52 | 52 | 44 | 52 | 52 | 265920
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 48 | 96 | 49 | 49 | 49 | 49 | 49 | 297144
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 22 | 35 | 35 | 35 | 35 | 35 | 35 | 210141
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 10 | 35 |  |  |  |  | 0 | 40032
173 | Rangpur 20 MW GTPP | [21 empty] | 0 | 0 |  | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 15 | [18 empty] | 60 | 90 | 100 | 113 | 113 | 113 | 113 | 617280
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 6 | 7 | 7 | 7 | 6 | 4 | 3 | 2 | 1 | [8 empty] | 50528
178
178