## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-22 | Saturday
|  |  | Date (day): | 2021-05-22 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14469.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15750 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-21 | 2021-05-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 190 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 101 | 100 | 102
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 339 | 350 | 350 | 360 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 339 | 340 | 360 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Dust in gas line.
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 260 | 260 | 260 | 45 |  | Gas shortage
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 36 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 15 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 70 | 150 | 185 | 200 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 2 | 95 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 209 | 212 | 220 | 220 |  | 115 | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 72 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 98 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 35 | 35 | 35 |  | 20 | Engine problem
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 39 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 185 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 0 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 99 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 105 | 105
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 72 | 72 | 72 |  | 32 | Engine problem
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 162 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2164 | 3186 | 3727 | 4029 | 354 | 1242
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 12 | 43 | 43 |  | 7 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 140 | 130 | 210
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 110 | 110 | 110
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 70 | 89 | 70 | 90 |  | 15 | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 17 | 17 |  | 5 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 16 | 38 | 22 | 30
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 1 | 50 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 39 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 85 | 17 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 99 | 99 | 99 | 99 |  | 17 | Engine problem
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 782 | 1036 | 1490 | 1573 | 385 | 364
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 100 | 80 | 80 | 80 | 54 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 185 | 197 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 260 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 265 | 330 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 143 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 92 | 89 | 90 | 90 |  | 57 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 85 | 120 | 120 | 120 |  | 80 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 10 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 136 | 168 | 157 | 190
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 32 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 19 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 69 | 119 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 36 | 35 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1516 | 1866 | 2112 | 2296 | 505 | 179
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 162 | 176 | 190 | 200
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 55 | 63 | 64 | 64 |  | 31 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 131 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 35 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 22 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 23 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 318 | 527 | 661.6 | 620 | 0 | 34
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Under maint.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 0 | 0 | 0 |  | 90 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 328 | 154 | 330
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 20 | 52 | 52 | 52 |  | 14 | Gt-9 under maint.
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 74 | 76 | 76 | 76 |  | 10 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 0 | 140 |  | 89 | ST Under maint.
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 300 | 341
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 368 | 367 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 7 | 7 | 7 |  | 3 | Engine prolem
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 396 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1742 | 1943 | 1690 | 2047 | 0 | 343
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 915 | 915 | 932 | 932
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 73 | 99 | 99 |  | 16 | Engine problem
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 320 | 350 | 410 | 410
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 98 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1335 | 1573 | 1808 | 2078 | 0 | 107
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 82 | 85 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 87 | 96 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 430 | 520 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 6 | 27 | 50 | 50 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 44 | 0 | 80
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 630 | 916 | 998 | 1078 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 40 | 40
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 40 | 42 |  | 8 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 30 | 30 |  | 20 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 124 | 80 | 100 | 100 | 110 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 159 | 146 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 182 | 130 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 363 | 397 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 32 |  | 18 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 20 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 16 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 98 | 100 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 112 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 0 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 873 | 1209 | 1712 | 1746 | 281 | 53
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 186 | 263 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 22023 | 21315 | 9546 | 12519 | 14469.6 | 15750 | 1734 | 2533
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9115.1757 | 11954 | 13816.5667 | 15039.1804
| A. |  | 2021-05-21 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12561 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8870 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12519 | MW
| 3 | Day peak Generation : |  |  | 9546 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11954 | MW
| 4 | Evening peak Generation : |  |  | 12519 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 255.4824 | MKWHr | By Solar | 0.7436 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 154.9514 | MKWHr |  | By Oil: | 57.0453 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.3435 | MKWHr |  | By Hydro: | 0.608 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1734 | MW | Dhaka | 3778 | 3778 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2533 | MW | Chittagong | 1323 | 1323 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4267 | MW | Khulna | 1605 | 1605 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1280.25 | MMCFD |  |  | Rajshahi | 1226 | 1226 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 166901643.086 | ii) Oil : | Taka | 409682742.52 | Comilla | 1297 | 1297 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 75539498 | Total | Taka | 652123883.606 | Mymensingh | 1026 | 1026 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.581 | MKWHr. | Sylhet | 497 | 497 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 82 | MW (E to W) at | 21:00 | hrs | Barisal | 408 | 408 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -230 | MW at | 3:00 | hrs | Rangpur | 794 | 794 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 37° C |  |  | Total | 11954 | 11954 |  | 0
| B. |  | 2021-05-22 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 38.7° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15750 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 2750 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 264.4114 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9349 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.2136 | MKWHr. | ii) HVDC Flow at Peak Time |  | 915 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.577 | MKWHr. | iii) Maximum HVDC Flow : |  | 917 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.57 |  | (b) Today: | 74.44 |  | (c) Rule Curve: |  | 78
.

## YesterdayGen
2021-05-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 330 | 352 |  | 0 | 300 | 250 | 0 | 0 | 55 | 220 | 0 | 185 | 70 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 21 | 33 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 68 | 92 | 8 | 4 | 20 | 29 | 0 | 0 | 80 | 260 | 290 | 220 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 46 | 22 | 8 | 33 | 20 | 168 | 172 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 163 | 331 | 20 | 78 | 0 | 140 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 101 | 0 | 100 | 120 | 150 | 367 | 115 | 0 | 89 | 0 | 0 | 54 | 17 | 52 | 111 | 100 | 350 | 55 | 0 | 54 | 100 | 0 | 18 | 0 |  | 917 | 0 | 330 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 99 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 116 | 0 | 159 | 0 | 95 | 70 | 185 | 0 | 392 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 0 | 520 | 0 | 0 | 35 | 0 |  | 7652 | 3835 | 11487 | 4742 | 917 | 2023 | 2661 | 670 | 25 | 281 | 168 | 0 | 0 | 74.62
2:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 329 | 352 |  | 0 | 300 | 270 | 0 | 0 | 55 | 220 | 0 | 185 | 70 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 33 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 34 | 92 | 0 | 0 | 20 | 29 | 0 | 0 | 80 | 260 | 290 | 220 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 164 | 174 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 163 | 329 | 20 | 78 | 0 | 140 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 100 | 120 | 100 | 367 | 115 | 0 | 89 | 0 | 0 | 54 | 17 | 52 | 111 | 100 | 350 | 57 | 0 | 54 | 99 | 0 | 18 | 0 |  | 917 | 0 | 325 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 86 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 159 | 0 | 96 | 0 | 182 | 0 | 392 | 70 | 0 | 35 | 0 | 100 | 0 | 0 | 0 | 530 | 0 | 0 | 35 | 0 |  | 7499 | 3586 | 11085 | 4733 | 917 | 2025 | 2426 | 680 | 25 | 115 | 164 | 0 | 0 | 74.61
3:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 331 | 350 |  | 0 | 300 | 270 | 0 | 0 | 55 | 220 | 0 | 185 | 70 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 33 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 34 | 92 | 0 | 0 | 20 | 29 | 0 | 0 | 80 | 260 | 290 | 218 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 162 | 189 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 163 | 331 | 20 | 78 | 0 | 140 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 100 | 120 | 10 | 375 | 75 | 0 | 89 | 0 | 0 | 54 | 0 | 52 | 111 | 100 | 350 | 53 | 0 | 17 | 99 | 0 | 18 | 0 |  | 915 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 33 | 85 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 118 | 0 | 159 | 0 | 96 | 0 | 150 | 0 | 403 | 35 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 530 | 0 | 0 | 35 | 0 |  | 7341 | 3399 | 10740 | 4722 | 915 | 2044 | 2126 | 680 | 25 | 66 | 162 | 0 | 0 | 74.6
4:00 | 0 | 0 | 0 | 190 | 0 | 98 | 0 | 332 | 350 |  | 0 | 300 | 260 | 0 | 0 | 55 | 220 | 0 | 185 | 70 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 33 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 34 | 92 | 0 | 0 | 20 | 29 | 0 | 0 | 80 | 260 | 290 | 219 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 162 | 204 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 163 | 330 | 20 | 78 | 0 | 140 | 18 | 0 | 7 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 101 | 0 | 100 | 120 | 0 | 365 | 55 | 0 | 86 | 0 | 0 | 54 | 0 | 52 | 114 | 100 | 351 | 0 | 0 | 17 | 53 | 0 | 18 | 0 |  | 915 | 0 | 320 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 24 | 86 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 118 | 0 | 159 | 0 | 95 | 0 | 150 | 0 | 402 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 35 | 0 |  | 7187 | 3340 | 10527 | 4732 | 915 | 2034 | 1929 | 680 | 25 | 50 | 162 | 0 | 0 | 74.59
5:00 | 0 | 0 | 0 | 190 | 0 | 98 | 0 | 334 | 350 |  | 0 | 300 | 260 | 0 | 0 | 55 | 221 | 0 | 180 | 30 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 35 | 19 | 25 | 21 | 33 | 16 | 13 | 0 | 0 | 25 | 0 | 0 | 17 | 135 | 0 | 110 | 0 |  | 24 | 0 | 17 | 92 | 0 | 0 | 20 | 31 | 0 | 0 | 80 | 260 | 290 | 219 | 8 | 89 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 150 | 204 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 163 | 330 | 20 | 78 | 0 | 140 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 0 | 100 | 120 | 0 | 365 | 55 | 0 | 86 | 0 | 0 | 54 | 0 | 17 | 112 | 100 | 349 | 0 | 0 | 0 | 53 | 0 | 18 | 0 |  | 916 | 0 | 305 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 118 | 0 | 159 | 0 | 96 | 0 | 150 | 0 | 400 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 530 | 0 | 0 | 35 | 0 |  | 7022 | 3301 | 10323 | 4714 | 916 | 2030 | 1775 | 680 | 25 | 33 | 150 | 0 | 0 | 74.58
6:00 | 0 | 0 | 0 | 190 | 0 | 98 | 0 | 330 | 307 |  | 0 | 300 | 250 | 0 | 0 | 30 | 180 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 21 | 33 | 16 | 12 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 20 | 32 | 0 | 0 | 80 | 260 | 290 | 182 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 146 | 202 | 64 | 19 | 0 | 43 | 22 | 50 | 0 | 130 | 333 | 20 | 40 | 0 | 140 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 70 | 1 | 100 | 120 | 0 | 331 | 55 | 0 | 70 | 1 | 0 | 54 | 0 | 0 | 55 | 100 | 350 | 0 | 2 | 0 | 53 | 0 | 18 | 2 |  | 915 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 35 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 118 | 0 | 159 | 0 | 96 | 0 | 150 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 0 | 0 | 0 |  | 6504 | 3018 | 9522 | 4534 | 915 | 1843 | 1383 | 670 | 25 | 0 | 146 | 6 | 0 | 74.57
7:00 | 0 | 0 | 0 | 190 | 0 | 53 | 0 | 331 | 308 |  | 0 | 300 | 245 | 0 | 0 | 30 | 180 | 0 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 19 | 25 | 21 | 33 | 16 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 20 | 26 | 0 | 0 | 80 | 260 | 265 | 183 | 8 | 86 | 26 | 55 | 0 | 51 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 120 | 199 | 64 | 19 | 1 | 43 | 22 | 14 | 0 | 100 | 331 | 20 | 20 | 0 | 100 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 100 | 80 | 0 | 331 | 35 | 0 | 70 | 1 | 0 | 42 | 0 | 0 | 8 | 100 | 350 | 0 | 5 | 0 | 53 | 0 | 18 | 9 |  | 917 | 0 | 310 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 118 | 0 | 159 | 0 | 95 | 0 | 150 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 470 | 0 | 0 | 0 | 0 |  | 6084 | 2919 | 9003 | 4464 | 917 | 1683 | 1157 | 620 | 25 | 0 | 120 | 17 | 0 | 74.56
8:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 330 | 266 |  | 0 | 300 | 245 | 0 | 0 | 30 | 180 | 0 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 21 | 33 | 17 | 2 | 0 | 0 | 25 | 0 | 0 | 17 | 78 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 20 | 22 | 0 | 0 | 80 | 265 | 265 | 182 | 8 | 85 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 0 | 0 | 33 | 20 | 124 | 183 | 64 | 19 | 1 | 43 | 22 | 14 | 0 | 100 | 328 | 20 | 20 | 0 | 100 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 0 | 100 | 80 | 0 | 333 | 8 | 0 | 70 | 3 | 0 | 36 | 27 | 0 | 8 | 100 | 350 | 0 | 6 | 0 | 92 | 0 | 18 | 19 |  | 916 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 159 | 0 | 91 | 0 | 150 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 440 | 0 | 0 | 0 | 1 |  | 5986 | 2884 | 8870 | 4380 | 916 | 1615 | 1189 | 590 | 25 | 0 | 124 | 31 | 0 | 74.55
9:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 331 | 265 |  | 0 | 300 | 260 | 0 | 0 | 30 | 180 | 0 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 17 | 33 | 16 | 27 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 20 | 16 | 0 | 0 | 80 | 260 | 265 | 185 | 8 | 90 | 26 | 54 | 0 | 51 | 0 | 0 | 0 | 17 | 0 | 33 | 20 | 124 | 180 | 56 | 19 | 2 | 43 | 22 | 14 | 0 | 100 | 330 | 20 | 20 | 0 | 100 | 18 | 0 | 7 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 100 | 80 | 0 | 333 | 8 | 0 | 70 | 3 | 0 | 36 | 85 | 0 | 8 | 100 | 350 | 0 | 30 | 0 | 99 | 0 | 15 | 25 |  | 916 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 122 | 0 | 159 | 0 | 89 | 0 | 169 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 410 | 0 | 0 | 0 | 1 |  | 6032 | 2879 | 8911 | 4289 | 916 | 1627 | 1307 | 560 | 25 | 0 | 124 | 63 | 0 | 74.55
10:00 | 0 | 0 | 0 | 190 | 0 | 52 | 0 | 332 | 265 |  | 0 | 300 | 260 | 0 | 0 | 30 | 180 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 12 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 20 | 22 | 0 | 0 | 80 | 260 | 265 | 183 | 8 | 91 | 23 | 53 | 0 | 51 | 0 | 0 | 2 | 17 | 5 | 33 | 20 | 130 | 166 | 56 | 19 | 1 | 43 | 30 | 31 | 0 | 130 | 328 | 20 | 78 | 0 | 100 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 17 | 100 | 80 | 0 | 333 | 35 | 0 | 70 | 2 | 0 | 36 | 85 | 0 | 8 | 100 | 350 | 0 | 49 | 0 | 98 | 0 | 15 | 29 |  | 916 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 121 | 0 | 159 | 0 | 89 | 0 | 185 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 410 | 0 | 0 | 0 | 3 |  | 6235 | 2909 | 9144 | 4296 | 916 | 1753 | 1360 | 560 | 25 | 0 | 130 | 104 | 0 | 74.54
11:00 | 0 | 0 | 0 | 190 | 0 | 80 | 0 | 339 | 340 |  | 0 | 300 | 270 | 0 | 0 | 30 | 208 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 19 | 25 | 12 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 110 | 0 |  | 23 | 0 | 0 | 80 | 0 | 0 | 20 | 22 | 0 | 0 | 80 | 295 | 265 | 193 | 8 | 91 | 23 | 51 | 0 | 51 | 0 | 0 | 9 | 17 | 5 | 33 | 0 | 122 | 162 | 56 | 19 | 2 | 43 | 30 | 49 | 0 | 163 | 152 | 20 | 75 | 0 | 140 | 18 | 0 | 6 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 17 | 100 | 82 | 0 | 375 | 35 | 0 | 70 | 5 | 0 | 36 | 85 | 0 | 15 | 90 | 350 | 0 | 53 | 0 | 99 | 0 | 18 | 34 |  | 916 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 122 | 0 | 159 | 0 | 85 | 0 | 184 | 0 | 362 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 410 | 0 | 0 | 0 | 1 |  | 6338 | 2928 | 9266 | 4253 | 916 | 1935 | 1341 | 560 | 25 | 0 | 122 | 114 | 0 | 74.54
12:00 | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 339 | 339 |  | 0 | 300 | 270 | 0 | 0 | 36 | 209 | 0 | 70 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 19 | 25 | 12 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 110 | 0 |  | 22 | 0 | 0 | 92 | 1 | 0 | 20 | 16 | 0 | 0 | 100 | 315 | 270 | 185 | 8 | 92 | 26 | 51 | 0 | 51 | 0 | 0 | 32 | 17 | 8 | 33 | 20 | 136 | 162 | 55 | 19 | 3 | 42 | 30 | 50 | 0 | 163 | 158 | 20 | 74 | 0 | 140 | 17 | 0 | 6 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 19 | 100 | 85 | 0 | 368 | 35 | 0 | 70 | 6 | 0 | 39 | 85 | 0 | 69 | 100 | 350 | 0 | 22 | 0 | 99 | 0 | 18 | 27 |  | 915 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 124 | 0 | 159 | 0 | 87 | 0 | 182 | 0 | 363 | 17 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 430 | 6 | 0 | 0 | 3 |  | 6522 | 3024 | 9546 | 4315 | 915 | 1951 | 1542 | 580 | 25 | 0 | 136 | 82 | 0 | 74.53
13:00 | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 344 | 335 |  | 0 | 300 | 255 | 0 | 0 | 55 | 209 | 0 | 120 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 12 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 110 | 0 |  | 22 | 0 | 0 | 92 | 8 | 0 | 20 | 28 | 0 | 0 | 120 | 310 | 280 | 183 | 8 | 92 | 26 | 51 | 0 | 51 | 0 | 0 | 50 | 17 | 5 | 33 | 20 | 140 | 148 | 55 | 19 | 1 | 42 | 30 | 50 | 0 | 163 | 159 | 20 | 73 | 0 | 140 | 17 | 0 | 6 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 15 | 100 | 90 | 0 | 367 | 84 | 0 | 82 | 2 | 0 | 54 | 101 | 0 | 118 | 100 | 390 | 0 | 38 | 0 | 98 | 0 | 17 | 29 |  | 916 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 124 | 0 | 160 | 0 | 88 | 0 | 181 | 0 | 369 | 70 | 0 | 0 | 0 | 60 | 0 | 3 | 0 | 500 | 4 | 0 | 0 | 2 |  | 6909 | 3239 | 10148 | 4418 | 916 | 1974 | 1935 | 650 | 25 | 0 | 140 | 90 | 0 | 74.53
14:00 | 0 | 0 | 0 | 190 | 0 | 96 | 0 | 333 | 275 |  | 0 | 300 | 270 | 0 | 0 | 55 | 180 | 0 | 95 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 14 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 1 | 0 | 0 | 110 | 0 |  | 23 | 0 | 0 | 92 | 12 | 0 | 20 | 24 | 0 | 0 | 120 | 280 | 280 | 192 | 8 | 88 | 26 | 50 | 0 | 51 | 0 | 0 | 52 | 17 | 5 | 33 | 20 | 142 | 152 | 55 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 157 | 20 | 72 | 0 | 100 | 17 | 0 | 6 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 12 | 100 | 100 | 0 | 317 | 115 | 13 | 87 | 4 | 16 | 54 | 106 | 0 | 115 | 100 | 389 | 0 | 48 | 17 | 99 | 0 | 17 | 23 |  | 915 | 0 | 310 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 8 | 83 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 160 | 0 | 85 | 0 | 180 | 0 | 389 | 91 | 0 | 0 | 0 | 60 | 0 | 5 | 0 | 470 | 4 | 0 | 13 | 0 |  | 6744 | 3223 | 9967 | 4188 | 915 | 1854 | 2131 | 620 | 25 | 0 | 142 | 92 | 0 | 74.52
15:00 | 0 | 0 | 0 | 190 | 0 | 93 | 0 | 354 | 335 |  | 0 | 300 | 280 | 0 | 0 | 55 | 180 | 0 | 120 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 14 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 23 | 0 | 0 | 92 | 12 | 0 | 20 | 24 | 0 | 0 | 120 | 295 | 300 | 204 | 8 | 92 | 26 | 50 | 0 | 51 | 0 | 0 | 52 | 17 | 5 | 33 | 20 | 146 | 152 | 55 | 19 | 1 | 42 | 30 | 50 | 0 | 130 | 172 | 20 | 71 | 0 | 100 | 17 | 0 | 6 | 320 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 13 | 100 | 100 | 0 | 403 | 115 | 17 | 89 | 4 | 16 | 54 | 106 | 0 | 113 | 100 | 383 | 0 | 36 | 17 | 99 | 0 | 17 | 23 |  | 916 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 158 | 0 | 85 | 0 | 180 | 0 | 411 | 91 | 0 | 0 | 0 | 70 | 0 | 5 | 0 | 460 | 6 | 0 | 17 | 0 |  | 7065 | 3248 | 10313 | 4373 | 916 | 1984 | 2177 | 610 | 25 | 0 | 146 | 82 | 0 | 74.52
16:00 | 0 | 0 | 0 | 190 | 0 | 88 | 0 | 352 | 334 |  | 0 | 300 | 255 | 0 | 0 | 55 | 203 | 0 | 97 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 14 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 23 | 0 | 0 | 92 | 12 | 0 | 20 | 26 | 0 | 0 | 120 | 260 | 265 | 185 | 8 | 90 | 26 | 50 | 0 | 51 | 0 | 0 | 52 | 17 | 5 | 33 | 19 | 140 | 166 | 47 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 310 | 21 | 71 | 0 | 120 | 17 | 0 | 6 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 10 | 100 | 100 | 0 | 368 | 115 | 17 | 89 | 3 | 16 | 54 | 108 | 0 | 113 | 100 | 390 | 0 | 8 | 17 | 99 | 0 | 17 | 16 |  | 916 | 0 | 315 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 153 | 0 | 91 | 0 | 180 | 0 | 411 | 70 | 0 | 0 | 0 | 70 | 0 | 5 | 0 | 470 | 15 | 0 | 17 | 1 |  | 7012 | 3247 | 10259 | 4427 | 916 | 1961 | 2127 | 620 | 25 | 0 | 140 | 43 | 0 | 74.51
17:00 | 0 | 0 | 0 | 190 | 0 | 98 | 0 | 331 | 270 |  | 0 | 300 | 255 | 0 | 0 | 55 | 150 | 0 | 70 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 19 | 25 | 14 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 20 | 36 | 0 | 0 | 120 | 260 | 265 | 184 | 8 | 92 | 26 | 50 | 0 | 51 | 0 | 0 | 52 | 19 | 5 | 33 | 19 | 136 | 170 | 55 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 325 | 40 | 71 | 0 | 100 | 17 | 0 | 6 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 3 | 100 | 100 | 0 | 344 | 115 | 17 | 89 | 1 | 16 | 54 | 108 | 0 | 110 | 100 | 393 | 0 | 17 | 17 | 99 | 0 | 17 | 8 |  | 916 | 0 | 250 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 154 | 0 | 95 | 0 | 181 | 0 | 316 | 53 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 420 | 15 | 0 | 0 | 0 |  | 6844 | 2957 | 9801 | 4262 | 916 | 1809 | 2051 | 570 | 25 | 0 | 136 | 32 | 0 | 74.51
18:00 | 0 | 0 | 0 | 190 | 0 | 54 | 0 | 264 | 270 |  | 0 | 300 | 280 | 0 | 0 | 55 | 150 | 0 | 70 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 0 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 20 | 41 | 0 | 0 | 120 | 290 | 290 | 201 | 8 | 92 | 26 | 16 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 33 | 19 | 128 | 181 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 324 | 50 | 40 | 0 | 100 | 17 | 0 | 6 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0 | 70 | 100 | 0 | 351 | 115 | 17 | 51 | 0 | 16 | 54 | 108 | 0 | 75 | 50 | 300 | 0 | 2 | 17 | 99 | 0 | 17 | 2 |  | 915 | 0 | 230 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 19 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 142 | 0 | 94 | 0 | 130 | 0 | 250 | 53 | 0 | 0 | 0 | 38 | 0 | 2 | 0 | 410 | 15 | 0 | 0 | 0 |  | 6484 | 2756 | 9240 | 4133 | 915 | 1631 | 1842 | 560 | 25 | 0 | 128 | 6 | 0 | 74.5
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 298 | 340 |  | 0 | 300 | 280 | 0 | 0 | 55 | 201 | 0 | 150 | 40 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 100 | 0 | 110 | 0 |  | 24 | 0 | 0 | 85 | 24 | 1 | 20 | 41 | 0 | 0 | 120 | 335 | 320 | 164 | 8 | 90 | 26 | 16 | 0 | 51 | 0 | 0 | 33 | 22 | 10 | 33 | 19 | 160 | 176 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 325 | 50 | 75 | 0 | 140 | 17 | 0 | 6 | 310 | 16 | 2 | 0 | 41 | 0 | 0 | 22 | 0 | 140 | 0 | 100 | 100 | 30 | 393 | 115 | 17 | 51 | 0 | 0 | 54 | 34 | 36 | 94 | 100 | 350 | 24 | 0 | 40 | 99 | 0 | 17 | 0 |  | 916 | 0 | 340 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 86 | 34 | 110 | 0 | 0 | 0 | 25 | 0 | 99 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 88 | 0 | 135 | 0 | 93 | 0 | 147 | 0 | 398 | 70 | 0 | 17 | 0 | 112 | 0 | 0 | 50 | 440 | 15 | 0 | 13 | 0 |  | 7382 | 3518 | 10900 | 4699 | 916 | 1961 | 2393 | 590 | 25 | 156 | 160 | 0 | 0 | 74.49
19:30 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 329 | 300 |  | 0 | 300 | 280 | 0 | 0 | 55 | 150 | 0 | 80 | 50 | 32 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 131 | 0 | 110 | 0 |  | 24 | 0 | 68 | 90 | 80 | 12 | 20 | 41 | 0 | 0 | 105 | 260 | 265 | 172 | 8 | 89 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 160 | 177 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 110 | 329 | 52 | 75 | 0 | 140 | 17 | 0 | 6 | 300 | 16 | 5 | 0 | 95 | 0 | 0 | 130 | 0 | 149 | 0 | 100 | 120 | 140 | 366 | 115 | 36 | 89 | 0 | 0 | 54 | 34 | 114 | 119 | 100 | 395 | 72 | 0 | 162 | 99 | 0 | 35 | 0 |  | 915 | 0 | 350 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 40 | 0 | 99 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 155 | 0 | 95 | 50 | 180 | 0 | 320 | 105 | 0 | 65 | 0 | 113 | 0 | 0 | 108 | 490 | 51 | 0 | 35 | 0 |  | 8152 | 3863 | 12015 | 4637 | 915 | 1913 | 3420 | 640 | 25 | 305 | 160 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 340 | 300 |  | 0 | 300 | 280 | 0 | 0 | 55 | 152 | 0 | 70 | 70 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 151 | 0 | 110 | 0 |  | 24 | 0 | 68 | 90 | 75 | 10 | 20 | 33 | 0 | 0 | 80 | 260 | 265 | 200 | 8 | 90 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 164 | 176 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 110 | 325 | 52 | 75 | 0 | 120 | 17 | 0 | 7 | 290 | 16 | 11 | 0 | 154 | 0 | 0 | 140 | 0 | 149 | 0 | 100 | 111 | 122 | 368 | 115 | 74 | 84 | 0 | 0 | 54 | 34 | 114 | 120 | 100 | 395 | 65 | 0 | 158 | 99 | 0 | 31 | 0 |  | 915 | 0 | 350 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 99 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 161 | 0 | 96 | 57 | 130 | 0 | 315 | 105 | 0 | 98 | 0 | 113 | 0 | 0 | 108 | 500 | 91 | 0 | 35 | 0 |  | 8219 | 3870 | 12089 | 4523 | 915 | 1933 | 3564 | 650 | 25 | 315 | 164 | 0 | 0 | 74.49
21:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 350 | 340 |  | 0 | 300 | 260 | 0 | 0 | 55 | 212 | 0 | 150 | 95 | 72 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 140 | 0 | 110 | 0 |  | 23 | 0 | 68 | 100 | 50 | 12 | 17 | 38 | 0 | 0 | 80 | 260 | 265 | 197 | 8 | 89 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 168 | 176 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 130 | 328 | 52 | 76 | 0 | 140 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 185 | 0 | 0 | 131 | 0 | 149 | 0 | 100 | 120 | 143 | 367 | 115 | 105 | 89 | 0 | 0 | 54 | 17 | 114 | 119 | 100 | 396 | 72 | 0 | 162 | 99 | 0 | 36 | 0 |  | 915 | 0 | 350 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 146 | 0 | 96 | 98 | 130 | 0 | 397 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 520 | 27 | 0 | 44 | 0 |  | 8558 | 3961 | 12519 | 4661 | 915 | 2039 | 3727 | 670 | 25 | 314 | 168 | 0 | 0 | 74.49
22:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 336 | 340 |  | 0 | 300 | 285 | 0 | 0 | 55 | 180 | 0 | 115 | 92 | 72 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 21 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 141 | 0 | 110 | 0 |  | 24 | 0 | 68 | 100 | 41 | 12 | 17 | 38 | 0 | 0 | 80 | 295 | 300 | 196 | 8 | 91 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 172 | 165 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 110 | 328 | 51 | 77 | 0 | 145 | 17 | 0 | 7 | 300 | 16 | 11 | 0 | 145 | 0 | 0 | 131 | 0 | 149 | 0 | 100 | 120 | 150 | 402 | 115 | 105 | 89 | 0 | 0 | 54 | 17 | 88 | 122 | 100 | 390 | 72 | 0 | 162 | 99 | 0 | 36 | 0 |  | 916 | 0 | 350 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 145 | 0 | 96 | 100 | 130 | 0 | 406 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 37 | 0 | 72 | 0 |  | 8508 | 4046 | 12554 | 4679 | 916 | 2027 | 3721 | 700 | 25 | 314 | 172 | 0 | 0 | 74.48
23:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 363 | 340 |  | 0 | 300 | 285 | 0 | 0 | 55 | 180 | 0 | 115 | 100 | 72 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 21 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 141 | 0 | 110 | 0 |  | 24 | 0 | 68 | 100 | 31 | 12 | 17 | 38 | 0 | 0 | 80 | 310 | 290 | 185 | 8 | 91 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 172 | 167 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 110 | 328 | 51 | 77 | 0 | 145 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 145 | 0 | 0 | 130 | 0 | 145 | 0 | 100 | 120 | 150 | 404 | 115 | 105 | 89 | 0 | 0 | 54 | 17 | 88 | 113 | 100 | 392 | 74 | 0 | 162 | 97 | 0 | 36 | 0 |  | 915 | 0 | 350 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 32 | 84 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 140 | 0 | 96 | 100 | 130 | 0 | 413 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 19 | 0 | 72 | 0 |  | 8541 | 4020 | 12561 | 4701 | 915 | 2037 | 3697 | 700 | 25 | 314 | 172 | 0 | 0 | 74.47
24:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 353 | 340 |  | 0 | 300 | 275 | 0 | 0 | 55 | 180 | 0 | 115 | 100 | 72 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 21 | 33 | 33 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 141 | 0 | 110 | 0 |  | 24 | 0 | 68 | 100 | 31 | 12 | 17 | 38 | 0 | 0 | 80 | 285 | 275 | 186 | 8 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 168 | 167 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 110 | 328 | 51 | 77 | 0 | 145 | 17 | 0 | 7 | 315 | 16 | 11 | 0 | 145 | 0 | 0 | 130 | 0 | 149 | 0 | 100 | 120 | 150 | 372 | 115 | 105 | 89 | 0 | 0 | 54 | 17 | 88 | 111 | 100 | 396 | 76 | 0 | 162 | 84 | 0 | 36 | 0 |  | 916 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 140 | 0 | 82 | 100 | 130 | 0 | 416 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 29 | 0 | 72 | 0 |  | 8375 | 4055 | 12430 | 4610 | 916 | 2031 | 3666 | 700 | 25 | 314 | 168 | 0 | 0 | 74.47
KWH | 0 | 0 | 0 | 4441500 | 0 | 2017727 | 0 | 8200199 | 7640000 |  | 0 | 7081750 | 6469440 | 0 | 0 | 1169386 | 4730893 | 0 | 3120000 | 1111680 | 419616 | 684960 | 0 | 0 | 0 | 0 | 591120 | 474097 | 789764 | 404424 | 600000 | 392940 | 793000 | 519000 | 700800 | 0 | 0 | 608000 | 0 | 0 | 348327 | 1809585 | 0 | 2560178 | 0 |  | 572160 | 0 | 573501 | 2141040 | 317760 | 85440 | 448656 | 743040 | 0 | 0 | 2213978 | 6914000 | 6800000 | 4766000 | 217454 | 2106860 | 567000 | 1226400 | 0 | 1204696 | 0 | 0 | 971102 | 437148 | 151020 | 816900 | 464800 | 3576960 | 4063360 | 1429440 | 422388 | 10550 | 1007000 | 514080 | 1053600 | 0 | 3296945 | 6615000 | 696384 | 1579200 | 0 | 2963270 | 396000 | 0 | 155340 | 7357500 | 367416 | 207100 | 0 | 928363 | 0 | 0 | 700800 | 0 | 2760912 | 110160 | 2406720 | 2563200 | 1114036 | 8728000 | 2065200 | 607200 | 1966290 | 35039 | 87818 | 1199394 | 1288835 | 788880 | 2151240 | 2370240 | 8636000 | 563520 | 311310 | 1104480 | 2204236 | 0 | 519480 | 224083 |  | 22213636 | 0 | 7836480 | 0 | 1944960 | 0 | 0 | 0 | 0 | 0 | 326250 | 2062489 | 699386 | 1457184 | 0 | 0 | 0 | 312384 | 0 | 734248 | 0 | 0 | 0 | 847200 | 0 | 423360 | 0 | 226008 | 0 | 0 | 3681100 | 0 | 0 | 2667600 | 0 | 3931882 | 0 | 2222010 | 574080 | 4244309 | 0 | 8888455 | 1466880 | 0 | 704831 | 0 | 1305600 | 0 | 35183 | 575616 | 12662400 | 301718 | 0 | 555600 | 17280 |  | 172564310 | 82918129 | 255482439 | 108842847 | 22213636 | 46108581 | 54740217 | 16343500 | 608000 | 2305093 | 3576960 | 743605 | 0
Fuel Cost | 0 | 0 | 0 | 6529005 | 0 | 2663399.64 | 0 | 8282200.99 | 7869200 |  | 0 | 7719107.5 | 7181078.4 | 0 | 0 | 9893005.56 | 4920128.72 | 0 | 5397600 | 8370950.4 | 3826897.92 | 6740006.4 | 0 | 0 | 0 | 0 | 4315176 | 3664769.81 | 7787073.04 | 303318 | 450000 | 0 | 0 | 0 | 6776736 | 0 | 0 | 164160 | 0 | 0 | 3235957.83 | 1972447.65 | 0 | 4352302.6 | 0 |  | 0 | 0 | 5562959.7 | 20446932 | 2764512 | 676684.8 | 565306.56 | 2206828.8 | 0 | 0 | 3254547.66 | 5116360 | 6800000 | 4384720 | 280515.66 | 2422889 | 640710 | 1716960 | 0 | 2060030.16 | 0 | 0 | 9274024.1 | 555177.96 | 113265 | 1429575 | 348600 | 26827200 | 4307161.6 | 12979315.2 | 536432.76 | 168167 | 1651480 | 822528 | 1875408 | 0 | 3758517.3 | 6879600 | 1371876.48 | 3016272 | 0 | 5126457.1 | 867240 | 0 | 316893.6 | 7431075 | 275562 | 157396 | 0 | 7018424.28 | 0 | 0 | 3644160 | 0 | 27167374.08 | 1287770.4 | 19614768 | 27810720 | 7853953.8 | 8117040 | 18834624 | 5738040 | 17126385.9 | 0 | 663904.08 | 10446721.74 | 11328859.65 | 7873022.4 | 18436126.8 | 15785798.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127950543.36 | 0 | 8228304 | 0 | 15287385.6 | 0 | 0 | 0 | 0 | 0 | 3399525 | 2330612.57 | 1084048.3 | 14222115.84 | 0 | 0 | 0 | 3073858.56 | 0 | 6498094.8 | 0 | 0 | 0 | 8209368 | 0 | 812851.2 | 0 | 171088.056 | 0 | 0 | 19951562 | 0 | 0 | 3121092 | 0 | 5190084.24 | 0 | 3333015 | 9765100.8 | 4965841.53 | 0 | 8799570.45 | 15314227.2 | 0 | 6688846.19 | 0 | 10131456 | 0 | 388772.15 | 4253802.24 | 55587936 | 0 | 0 | 0 | 0 |  | 470151395.43 | 338759101.086 | 808910496.516 | 111957950.476 | 127950543.36 | 54943692.61 | 387807823.06 | 75539498 | 164160 | 21874919.46 | 26827200 | 1844709.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 339 | 339 |  | 0 | 300 | 270 | 0 | 0 | 36 | 209 | 0 | 70 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 19 | 25 | 12 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 110 | 0 |  | 22 | 0 | 0 | 92 | 1 | 0 | 20 | 16 | 0 | 0 | 100 | 315 | 270 | 185 | 8 | 92 | 26 | 51 | 0 | 51 | 0 | 0 | 32 | 17 | 8 | 33 | 20 | 136 | 162 | 55 | 19 | 3 | 42 | 30 | 50 | 0 | 163 | 158 | 20 | 74 | 0 | 140 | 17 | 0 | 6 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 19 | 100 | 85 | 0 | 368 | 35 | 0 | 70 | 6 | 0 | 39 | 85 | 0 | 69 | 100 | 350 | 0 | 22 | 0 | 99 | 0 | 18 | 27 |  | 915 | 0 | 320 | 0 | 83 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 17 | 0 | 9 | 0 | 0 | 150 | 0 | 0 | 124 | 0 | 159 | 0 | 87 | 0 | 182 | 0 | 363 | 17 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 430 | 6 | 0 | 0 | 3 |  | 9546 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 350 | 340 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 212 | 0 | 150 | 95 | 72 | 98 | 0 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 14 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 140 | 0 | 110 | 0 | 0 | 23 | 0 | 68 | 100 | 50 | 12 | 17 | 38 | 0 | 0 | 80 | 260 | 265 | 197 | 8 | 89 | 26 | 54 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 19 | 168 | 176 | 63 | 19 | 0 | 42 | 0 | 50 | 0 | 130 | 328 | 52 | 76 | 0 | 140 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 185 | 0 | 0 | 131 | 0 | 149 | 0 | 100 | 120 | 143 | 367 | 115 | 105 | 89 | 0 | 0 | 54 | 17 | 114 | 119 | 100 | 396 | 72 | 0 | 162 | 99 | 0 | 36 | 0 |  | 915 | 0 | 350 | 0 | 73 | 0 | 0 | 0 | 0 | 0 | 32 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 146 | 0 | 96 | 98 | 130 | 0 | 397 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 520 | 27 | 0 | 44 | 0 |  | 12519 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 360 | 360 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 220 | 0 | 200 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 35 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 210 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 43 | 17 | 30 | 0 | 0 | 80 | 330 | 330 | 215 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 190 | 200 | 64 | 19 | 0 | 42 | 0 | 51 | 0 | 163 | 330 | 52 | 76 | 0 | 140 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 120 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 0 | 162 | 99 | 0 | 36 |  |  | 932 | 0 | 410 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 32 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 100 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 50 |  | 80
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 350 | 360 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 220 | 0 | 185 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 35 | 15 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 130 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 43 | 17 | 22 | 0 | 0 | 80 | 330 | 330 | 215 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 157 | 190 | 64 | 19 | 1.6 | 42 | 0 | 51 | 0 | 163 | 154 | 52 | 76 | 0 | 0 | 18 | 0 | 7 | 300 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 120 | 150 | 400 | 115 | 105 | 70 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 50 | 162 | 99 | 0 | 35 | 30 |  | 932 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 43 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 50 |  | 0
Generation at 08:00(Today) | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 328 | 347 | 0 | 0 | 300 | 250 | 0 | 0 | 30 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 25 | 20 | 33 |  | 33 | 0 | 0 | 25 | 0 | 0 | 8 | 50 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 8 | 0 | 0 | 80 | 260 | 265 | 184 | 8 | 87 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 10 | 33 | 20 | 130 | 204 | 64 | 0 | 1 | 42 | 0 | 50 | 0 | 110 | 331 | 51 | 78 | 0 | 0 | 18 | 0 | 7 | 270 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 10 | 100 | 120 | 0 | 367 | 115 | 0 | 70 | 1 | 0 | 54 | 0 | 0 | 65 | 10 | 400 | 0 | 24 | 0 | 72 | 0 | 35 | 17 | 0 | 917 | 0 | 410 | 0 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 140 | 0 | 95 | 0 | 130 | 0 | 395 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 460 | 4 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 8870 | 8:00
| Highest Generation |  | 12561 | 23:00
| Day Peak Generation |  | 9546 | 12:00
| Evening Peak Generation |  | 12519 | 21:00
| HVDC Max Flow |  | 917 | 1:00
| HVDC EvPeak Flow |  | 915 | 21:00
| Load factor L.F |  | 84.75%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9546 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9349 | MW
Evening Peak Generation : |  | 12519 | MW Hour : | 21:00 | Available Max Generation : |  | 15750 | MW
E.P. Demand (at gen end) : |  | 12519 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12561 | MW Hour : | 23:00 | Reserve(Generation end) |  | 2750 | MW
Total Gen. (MKWH) : |  | 255.4824 | System Load Factor : | 84.75% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -230 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-22
Actual : | 74.44 | Ft.(MSL) , | Rule curve : | 78 | Ft.( MSL )
Gas Consumed : | Total = | 1280.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 166901643.086
: |  | Coal : | 75539498 | Oil : | 409682742.52 | Total : | 652123883.606
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4612.9387 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1573.4757 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1410.6412 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1274.9383 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1151.9751 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 929.6153 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 513.591 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 239.1867 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 716.9952 |  |  | 0 | 0%
Total | 0 |  | 12423.3572 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sikalbaha-225 MW was shut down at 08:19 for D/W and GT was synchronized at 18:13.
b) B.Pukuria 132 kV Bus-2 was under shut down from 07:53 to 11:26 for C/M.
c) Chowmuhani 132/33 kV t-2 transformer was under shut down from 08:15 to 09:42 due to red hot maint. |  |  |  |  | About 40 MW power interruption occurred under Chowmuhani S/S
area from 08:15 to 09:42.
d) Mohastanghor 132/33 kV T-1,T-2 & 33 kV Bus were shut down from 08:25 to 10:04 for C/M.
e) Rangpur 132/33 kV T-1 transformer & 33 kV Bus-1 were shut down from 08:30 to 18:42 for D/W. |  |  |  |  | About 25 MW power interruption occurred under Rangpur S/S
area from 08:30 to 18:42.
f) Savar 132/33 kV T-3 transformer was under shut down from 08:39 to 16:17 for D/W.
g) Sikalbaha-225 MW GT bay-Sikalbaha S/S 132 kV Ckt was under shut down from 09:19 to 11:14 for D/W.
h) C.Nawanganj 132/33 kV T-1 transformer was under shut down at 11:06 for oil leakage of 132 kV bushing.
i) Kabirpur-Kodda 132 kV Ckt-1 & 2 were under shut down from 09:43 to 12:36 for C/M.
j) Shahjadpur 132/33 kV T-3 transformer tripped at 10:15 showing O/C relay and was switched on at 10:32.
k) Sikalbaha-225 MW GT bay-Sikalbaha 230 kV S/S 132 kV Ckt was under shut down from 11:26 to 16:23 for D/W.
l) Sonargaon S/S-Sonargaon P/S 132 kV Ckt was under shut down from 09:38 to 17:15 for C/M.
m) Sylhet-Chattak 132 kV Ckt-1 tripped at 10:01 showing no relay and was switched on at 15:02. |  |  |  |  | About 9 MW power interruption occurred under Chattak S/S
area from 10:01 to 15:02.
n) Shahjibazar-330 MW GT-2 tripped at 10:25 due to heat vent loss of turbine compartment and was
synchronized at 14:45.
o) Chattak-Sunamganj 132 kV Ckt CB manually open at 11:40 due to flashing at bus coupler DS and was |  |  |  |  | About 23 MW power interruption occurred under Sunamganj S/S
closed at 12:19. |  |  |  |  | area from 11:40 to 12:19.
p) Rangpur 132/33 kV T-1 transformer was under shut down from 19:12 to 19:29 for project work. |  |  |  |  | About 20 MW power interruption occurred under Rangpur S/S
area from 19:12 to 19:29.
q) Purbasadipur-Thakurgaon 132 kV Ckt-1 & 2 tripped at 00:35(22/5/21) showing dist.ABC and was |  |  |  |  | About 115 MW power interruption occurred under Thakurgaon &
switched on at 00:48 & 00:57(22/5/21) respectively. |  |  |  |  | Panchaghar S/S areas from 00:35 to 00:48(22/5/21).
r) Purbasadipur-Saidpur 132 kV Ckt-1 tripped at 01:10(22/5/21) showing dist.C-phase and was switched
on at 01:22(22/5/21).
s) Bhulta-Haripur 230 kV Ckt-2 tripped at 04:20(22/5/21) showing dist. E/F relay at Haripur end and was
switched on at 05:16(22/5/21).
t) Haripur-Siddirganj 230 kV Ckt-2 tripped at 04:20(22/5/21) due to Y-phase PT burst at Haripur end.
u) Dohazari-Cox's Bazar 132 kV Ckt-2 is under shut down since 06:08(22/5/21) for D/W.
v) Tangail 132/33 kV T-2 transformer is under shut down since 06:40(22/5/21) for C/M.
w) Sylhet-Fenchuganj 132 kV Ckt is under shut down since 07:21(22/5/21) for C/M.
x) Julda S/S-Julda P/S 132 kV Ckt was under shut down from 07:03 to 08:52(22/5/21) for C/M.
y) Tangail-Kabirpur 132 kV Ckt-1 was under shut down from 07:30 to 08:25(22/5/21) for C/M.
z) Kabirpur-Kodda 132 kV Ckt-1 & 2 are under shut down since 07:29(22/5/21) for C/M.
aa) Sylhet-225 MW tripped at 03:34(22/5/21) showing E/F relay.
ab) B.Pukuria-Saidpur 132 kV ckt-2 is under shut down since 07:44(22/5/21) for C/M.
ac) Faridpur 132/33 kV T-1 transformer is under shut down since 07:48(22/5/21) for D/W.
ad) Faridpur 33 kV Bus section-1 is under shut down since 07:50(22/5/21) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 190 | 4441500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 2017727
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 350 | 8200199 | FGMO
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 340 | 7640000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7081750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6469440 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1169386
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 404424 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3120000 | Gas shortage.
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 95 | 1111680
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 212 | 4730893 | ST under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 72 | 419616 | Low demand
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 591120 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 98 | 684960 | Low demand
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 474097
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 789764 | Engine problem
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 39 | 992940 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 793000
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 519000 | Engine problem
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 41 | 700800
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 185 | 928363 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2760912
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 607200
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 72 | 563520 | Engine problem
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 1104480
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 224083
| Dhaka area Total |  |  |  | 5919 | 3186 | 58540854
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 348327 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 110160
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 12 | 85440 | Low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 608000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 140 | 1809585 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2560178
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 89 | 1966290 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 573501 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2141040
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2406720
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 448656
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 38 | 743040
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 317760 | Low demand
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 35039
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 87818 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1199394
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 1288835 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2370240
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 99 | 2204236
| Chattogram area Total |  |  |  | 2382 | 1036 | 21304259
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2213978 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 197 | 4766000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6914000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6800000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 567000 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1226400 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1204696
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 143 | 1114036
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 89 | 2106860 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 2563200 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 437148
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 10 | 151020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 168 | 3576960
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 971102
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 464800 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 788880
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 119 | 2151240
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 519480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1866 | 39571154
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 176 | 4063360 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 422388 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 63 | 1429440 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10550
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 131 | 700800 | Low demand
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2065200
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 311310
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 23 | 572160
| Mymensingh Area Total |  |  |  | 709 | 527 | 9575208
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1007000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 514080 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3296945 | frequency control.
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 328 | 6615000
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1053600
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 207100
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 52 | 696384 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 76 | 1579200 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 2963270
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 396000 | Machine problem
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 367416 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7357500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8728000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 155340 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 8636000 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1943 | 43572835
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 915 | 22213636
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 73 | 1944960 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 7836480 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 326250 | Engine problem
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 98 | 574080
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1466880
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1573 | 34362286
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1457184
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 699386
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2062489
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 96 | 2222010
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 12662400
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 27 | 301718 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 44 | 555600 | Low demand
| Barisal Area Total |  |  |  | 1826 | 916 | 19960787
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 312384
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Reserve.
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Reserve.
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 80 | 2667600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 146 | 3931882 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 130 | 4244309 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 397 | 8888455 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 423360 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 226008
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 847200
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 98 | 734248
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 704831
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 575616
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17280
| Rajshahi Area Total |  |  |  | 2179 | 1209 | 23573173
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3681100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1305600
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35183
| Rangpur Area Total |  |  |  | 605 | 263 | 5021883
| Total |  |  |  | 21315 | 12519 | 255482439
| Eastern Grid Total |  |  |  | 14421 | 8558 | 172564310
| Western Grid Total |  |  |  | 6894 | 3961 | 82918129
| National Grid Total |  |  |  | 21315 | 12519 | 255482439
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-21
(a) ENTIRE EASTERN GRID : |  | 7921 | MW | (b) ENTIRE WESTERN GRID : |  | 4033 | MW
i) Dhaka area |  | 3778 | MW | i) Khulna area |  | 1605 | MW
ii) Chittagong area |  | 1323 | MW | ii) Rajshahi area |  | 1226 | MW
iii) Comilla area |  | 1297 | MW | iii) Barisal area |  | 408 | MW
iv) Mymensingh area |  | 1026 | MW | iv) Rangpur area |  | 794 | MW
v) Sylhet area |  | 497 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11954 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 22:00 | Kishoreganj | 132 | 19:00 | Benapol | 66 | 22:00
Munsiganj | 105 | 0:00 | Netrokona | 128 | 19:30 | Jhenida | 117 | 21:00
Sonargaon | 55 | 22:00 | Jamalpur | 139 | 21:00 | Bottail | 126 | 21:00
Shyampur | 150 | 0:00 | Sherpur | 114 | 21:00 | G.K Project | 63 | 21:00
Bhulta | 148 | 22:00 | Srimongal | 58 | 21:00 | Faridpur | 197 | 21:00
Madanganj | 54 | 1:00 | Shahjibazar | 129 | 23:00 | Madaripur | 110 | 1:00
Shitalakhya | 74 | 1:00 | Fenchuganj | 46 | 19:30 | Sariatpur | 76 | 22:00
Rahim steel | 16 | 0:00 | Kulawara | 49 | 19:00 | Gopalganj | 101 | 21:00
Matuail | 45 | 23:00 | Sylhet | 110 | 21:00 | Bagerhat | 112 | 24:00
Ghorasal | 67 | 23:00 | Chatak | 29 | 20:00 | Mongla | 38 | 1:00
Narsingdi | 158 | 23:00 | Sunamganj | 50 | 21:00 | Satkhira | 119 | 22:00
Haripur (SBU) | 89 | 23:00 | Biani Bazar | 60 | 22:00 | Gallamari | 43 | 24:00
Sreenagar | 46 | 21:00 | Comilla (S) | 172 | 22:00 | Magura | 58 | 19:30
Ullon | 72 | 24:00 | Comilla(N) | 149 | 22:00 | Norail | 46 | 20:00
Hasnabad | 77 | 21:00 | Chandpur | 91 | 22:00 | Chuadanga | 88 | 21:00
Magbazar | 78 | 15:00 | Feni | 140 | 22:00 | Borguna | 20 | 21:00
Maniknagar | 60 | 23:00 | Chowmuhani | 196 | 19:30 | Barisal(N) | 51 | 5:00
Bangabhaban | 4 | 1:00 | Ashuganj | 44 | 1:00 | Barisal (S) | 116 | 22:00
Motijheel | 5 | 11:00 | Daudkandi | 150 | 21:0 | Patuakhali | 128 | 24:00
Narinda | 40 | 24:00 | B.Baria | 168 | 22:00 | Bhandaria | 60 | 22:00
Kazla | 65 | 1:00 | Ramganj | 110 | 23:00 | Borhan Uddin | 47 | 5:00
Dhanmondi | 138 | 19:00 | Chaddagram | 52 | 23:00 | Ishurdi | 65 | 21:00
Lalbag | 48 | 24:00 | PHP | 10 | 17:00 | Ruppur Paromanobik | 3 | 21:00
Madartek | 75 | 23:00 | Kochua | 75 | 22:00 | Natore | 119 | 21:00
Dhaka University | 24 | 19:00 | Madunaghat | 62 | 22:00 | Bogra | 139 | 20:00
Aftabnagar | 10 | 21:00 | Hathazari | 94 | 20:00 | Noagaon | 107 | 1:00
Fatullah | 48 | 1:00 | Khulshi | 206 | 23:00 | Rajshahi | 142 | 21:00
Nawabganj | 56 | 22:00 | Halishahar | 127 | 19:30 | Rajshahi New | 16 | 21:00
Keraniganj | 55 | 22:00 | Baraulia | 133 | 18:30 | C.Nawabganj | 72 | 21:00
Mirpur | 110 | 0:00 | Sikalbaha | 29 | 6:00 | Amnura | 51 | 21:00
Kalyanpur | 114 | 23:00 | Dohazari | 96 | 22:00 | Pabna | 96 | 21:00
Gulshan | 102 | 19:00 | Cox'sbazar | 109 | 19:30 | Shahjadpur | 88 | 21:00
Uttara | 100 | 19:00 | Chandraghona | 32 | 19:30 | Serajganj | 87 | 21:00
Uttara New | 25 | 23:00 | Kaptai | 5 | 6:00 | Niyamatpur | 61 | 21:00
Kamrangirchar | 68 | 23:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 57 | 21:00
Savar | 134 | 21:00 | Bakulia | 97 | 0:00 | Sherpur(Bogura) | 56 | 20:00
Bhasantec | 151 | 19:00 | Julda | 23 | 3:00 | Mohastangor | 72 | 24:00
Agargaon | 72 | 0:00 | TK chemical | 30.9 | 22:00 | Bhangura | 36 | 21:00
Satmosjid | 100 | 0:00 | Modern Steel | 0 | #N/A | Rangpur | 109 | 19:00
Tongi | 113 | 21:00 | Shahmirpur | 22 | 5:00 | Lalmonirhat | 41 | 20:00
Kabirpur | 230 | 21:00 | Khagrachhari | 24 | 9:00 | Saidpur | 94 | 20:00
Basundhara | 148 | 19:30 | Matarbari | 43 | 19:30 | Purbasadipur | 109 | 21:00
Manikganj | 84 | 21:00 | Baroiar Hat | 48 | 19:30 | Thakurgaon | 75 | 19:30
Joydevpur | 166 | 22:00 | Rangamati | 12 | 19:00 | Palashbari | 114 | 21:00
New Tongi | 76 | 22:00 | Abul Khair 230 | 135 | 14:00 | Barapukuria | 49 | 21:00
Kodda | 41 | 10:00 | BSRM | 152 | 21:00 | Panchagar | 52 | 21:00
Dhamrai | 100 | 20:00 | GPH Ispat | 91 | 6:00 | Joldhaka | 56 | 20:00
Rajendrapur | 106 | 23:00 | Goalpara | 30 | 24:00 | Kurigram | 60 | 19:30
Valuka | 120 | 23:00 | Central s/s | 96 | 1:00 | Mithapukur | 45 | 21:00
Tangail | 223 | 21:00 | Noapara | 50 | 23:00
Mymensing | 198 | 24:00 | Jessore | 121 | 23:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 1:00 | 397 | 16:00 | Kaliakoir | 391 | 0.75 | 383 | 0.875
| Bheramara | 396 | 2:00 | 387 | 11:00 | Bhulta | 385 | 0.041667 | 372 | 0.625
| Ashuganj(N) | 390 | 5:00 | 380 | 15:00 | Gopalganj | 403 | 0.625 | 382 | 0.5
| Payra | 408 | 1:00 | 394 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 228 | 10:00 | Hathazari | 217 | 1:00 | 207 | 17:00
| Ishurdi | 234 | 9:00 | 225 | 19:00 | Megnaghat | 230 | 10:00 | 224 | 15:00
| Ashuganj | 237 | 3:00 | 230 | 15:00 | Fenchuganj | 240 | 6:00 | 236 | 22:00
| Serajganj | 232 | 2:00 | 227 | 6:00 | Siddhirganj | 232 | 1:00 | 223 | 15:00
| Baghabari | 233 | 15:00 | 227 | 21:00 | Maniknagar | 229 | 1:00 | 222 | 15:00
| Barapukuria | 238 | 14:00 | 229 | 19:00 | Agargaon | 227 | 18:00 | 219 | 15:00
| Bogra | 229 | 15:00 | 218 | 19:30 | Barisal | 245 | 2:00 | 237 | 24:00
| Rajshahi | 235 | 18:30 | 222 | 24:00 | Bhola 225 MW | 248 | 14:00 | 239 | 12:00
| Khulna South | 227 | 9:00 | 203 | 14:00 | AKSML | 220 | 2:00 | 207 | 13:00
| Rampura | 229 | 1:00 | 222 | 16:00 | BSRM | 222 | 1:00 | 210 | 19:00
| Haripur | 229 | 1:00 | 221 | 15:00 | Bibiyana | 239 | 11:00 | 233 | 23:00
| Hasnabad | 230 | 1:00 | 224 | 22:00 | Bhulta | 232 | 1:00 | 223 | 14:00
| Shyampur | 227 | 1:00 | 220 | 15:00 | Ashuganj (S) | 235 | 1:00 | 229 | 15:00
| Aminbazar | 228 | 1:00 | 221 | 2:00 | Kaliakoir | 228 | 1:00 | 221 | 15:00
| Tongi | 225 | 1:00 | 219 | 18:00 | GPH | 218 | 1:00 | 205 | 19:00
| Comilla (N) | 228 | 1:00 | 219 | 19:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 21:00 | 132 | 11:00 | Kochua | 132 | 0.45833 | 127 | 0.83333
| Munsiganj | 135 | 18:00 | 131 | 11:00 | Madanhat | 131 | 0.70833 | 127 | 0.041667
| Sonargaon | 133 | 5:00 | 129 | 15:00 | Hathazari | 133 | 0.83333 | 126 | 0.041667
| Shyampur | 134 | 20:00 | 130 | 15:00 | Khulshi | 130 | 0.83333 | 124 | 0.20833
| Bhulta | 129 | 19:00 | 126 | 11:00 | Halishahar | 132 | 0.83333 | 126 | 0.16667
| Madanganj | 133 | 1:00 | 130 | 12:00 | Baraulia | 131 | 0.83333 | 125 | 0.083333
| Shitalakhya | 141 | 20:00 | 132 | 15:00 | Sikalbaha | 133 | 0.8125 | 128 | 0.041667
| Rahim steal | 135 | 20:00 | 133 | 10:00 | Dohazari | 127 | 0.75 | 122 | 0.125
| Matuail | 135 | 21:00 | 132 | 11:00 | Cox'sbazar | 122 | 0.75 | 109 | 0.041667
| Ghorasal | 140 | 11:00 | 136 | 1:00 | Chandraghona | 130 | 0.75 | 125 | 0.625
| Narsinghdi | 132 | 5:00 | 123 | 22:00 | Kaptai | 127 | 0.8125 | 125 | 0.041667
| Haripur (SBU) | 136 | 20:00 | 133 | 7:00 | A. Khaer Stl. | 129 | 0.75 | 125 | 0.041667
| Sreenagar | 128 | 19:30 | 126 | 1:00 | Bakulia | 131 | 0.375 | 126 | 0.5
| Ullon | 132 | 5:00 | 128 | 15:00 | Julda | 131 | 0.29167 | 128 | 0.041667
| Hasnabad | 135 | 7:00 | 133 | 11:00 | TK Chemical | 132 | 0.8125 | 127 | 0.5
| Magbazar | 132 | 4:00 | 128 | 15:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Maniknagar | 137 | 19:30 | 134 | 15:00 | Shahmirpur | 133 | 0.375 | 127 | 0.083333
| Bangabhaban | 137 | 19:30 | 134 | 15:00 | Khagrachhari | 129 | 0.375 | 124 | 0
| Motijheel | 137 | 19:30 | 134 | 15:00 | Matarbari | 126 | 0.375 | 112 | 0.16667
| Narinda | 137 | 19:30 | 134 | 15:00 | Baroiar Hat | 129 | 0.8125 | 121 | 0.625
| Kazla | 137 | 19:30 | 134 | 23:00 | Rangamati | 130 | 20:00 | 125 | 11:00
| Dhanmondi | 136 | 19:30 | 133 | 10:00 | Goalpara S/S | 138 | 18:30 | 123 | 3:00
| Lalbag | 138 | 20:00 | 133 | 11:00 | Khulna Central S/S | 138 | 18:00 | 124 | 0.083333
| Madartek | 132 | 6:00 | 128 | 12:00 | Noapara | 134 | 18:00 | 120 | 0.79167
| Dhaka University | 132 | 6:00 | 128 | 19:00 | Jessore | 129 | 18:00 | 112 | 0.8125
| Aftabnagar | 132 | 6:00 | 128 | 12:00 | Benapol | 129 | 18:00 | 111 | 0.8125
| Fatullah | 134 | 19:30 | 131 | 10:00 | Jhenida | 125 | 0.41667 | 105 | 0.8125
| Nawabganj | 128 | 20:00 | 124 | 12:00 | Bottail | 131 | 18:00 | 120 | 0.8125
| Keraniganj | 129 | 20:00 | 125 | 15:00 | G.K Project | 139 | 0.75 | 132 | 0.041667
| Mirpur | 135 | 19:30 | 129 | 15:00 | Faridpur | 135 | 0.41667 | 124 | 0.91667
| Kalyanpur | 136 | 21:00 | 130 | 15:00 | Madaripur | 138 | 0.41667 | 130 | 0.875
| Gulshan | 131 | 2:00 | 128 | 15:00 | Shariyatpur S/S | 137 | 0.41667 | 126 | 0.91667
| Uttara | 135 | 19:30 | 129 | 15:00 | Gopalganj | 140 | 10:00 | 127 | 0.875
| Uttara New | 135 | 19:30 | 128 | 15:00 | Bagerhat | 136 | 0.75 | 117 | 0.125
| Kamrangirchar | 138 | 20:00 | 132 | 11:00 | Mongla | 134 | 18:00 | 120 | 0.8125
| Savar | 137 | 19:30 | 128 | 15:00 | Satkhira | 136 | 18:00 | 117 | 0.125
| Bhasantec | 131 | 7:00 | 126 | 15:00 | Gallamari | 139 | 18:00 | 124 | 3:00
| Agargaon | 132 | 7:00 | 128 | 12:00 | Magura | 125 | 0.77083 | 102 | 23:00
| Satmosjid | 131 | 6:00 | 127 | 15:00 | Narail | 123 | 18:00 | 102 | 0.8125
| Tongi | 140 | D | 135 | 12:00 | Chuadanga | 119 | 0.41667 | 94 | 0.91667
| Kabirpur | 134 | 6.00 | 128 | 19:00 | Borguna | 136 | 18:30 | 130 | 0.54167
| Basundhara | 138 | 14:00 | 132 | 12:00 | Barisal(N) | 139 | 18:30 | 133 | 0.54167
| Manikganj | 142 | 19:30 | 124 | 18:00 | Barisal (S) | 137 | 5:00 | 131 | 13:00
| Joydevpur | 137 | 20:00 | 132 | 15:00 | Patuakhali(S) | 137 | 0.77083 | 128 | 0.54167
| New Tongi | 139 | 19:30 | 132 | 12:00 | Bhandaria | 134 | 0.75 | 126 | 0.041667
| Kodda | 139 | 19:00 | 132 | 7.00 | Ishurdi | 135 | 0.66667 | 130 | 0.875
| Dhamrai | 134 | 7.00 | 127 | 23:00 | Ruppur Paromanobik | 135 | 9:00 | 130 | 21:00
| Rajendrapur | 0 | 0 | 0 | 0 | Natore | 134 | 14:00 | 129 | 21:00
| Valuka | 124 | 7:00 | 107 | 22:00 | Bogra | 134 | 11:00 | 128 | 20:00
| Tangail | 132 | 7:00 | 121 | 19:00 | Noagaon | 129 | 18:30 | 122 | 20:00
| Mymensing | 128 | 6:00 | 112 | 22:00 | Rajshahi | 133 | 18:00 | 127 | 20:00
| Kishorganj | 130 | 5:00 | 117 | 22:00 | Rajshahi New | 134 | 18:30 | 127 | 20:00
| Netrokona | 127 | 7:00 | 108 | 22:00 | C.Nawabganj | 132 | 18:30 | 125 | 20:00
| Jamalpur | 134 | 18:00 | 122 | 19:00 | Amnura | 133 | 18:30 | 125 | 1:00
| Sherpur | 133 | 14:00 | 120 | 19:00 | Pabna | 136 | 18:30 | 128 | 20:00
| Srimongal | 137 | 6:00 | 132 | 22:00 | Shahjadpur | 139 | 17:00 | 135 | 21:00
| Shahjibazar | 135 | 6:00 | 129 | 22:00 | Serajganj | 133 | 9:00 | 128 | 21:00
| Fenchuganj | 138 | 8:00 | 132 | 23:00 | Niyamatpur | 129 | 6:00 | 119 | 20:00
| Khulawara | 136 | 5:00 | 132 | 23:00 | Joypurhat | 130 | 14:00 | 120 | 20:00
| Sylhet | 134 | 6:00 | 130 | 21:00 | Sherpur(Bogura) | 133 | 14:00 | 128 | 20:00
| Chatak | 135 | 5:00 | 128 | 22:00 | Mohastangor | 132 | 14:00 | 126 | 8:00
| Sunamganj | 133 | 6:00 | 124 | 23:00 | Bangura | 136 | 18:30 | 132 | 21:00
| Biani Bazar | 134 | 4:00 | 127 | 22:00 | Rangpur | 128 | 14:00 | 117 | 20:00
| Comilla(s) | 129 | 7:00 | 123 | 19:00 | Lalmonirhat | 130 | 4:00 | 118 | 19:30
| Comilla(n) | 134 | 19:00 | 130 | 14:00 | Saidpur | 130 | 6:00 | 114 | 20:00
| Chandpur | 132 | 8:00 | 125 | 15:00 | Purbasadipur | 129 | 6:00 | 110 | 19:30
| Feni | 128 | 19:30 | 121 | 15:00 | Thakurgaon | 131 | 4:00 | 108 | 20:00
| Chowmuhani | 129 | 14:00 | 122 | 19:30 | Palashbari | 128 | 6:00 | 120 | 11:00
| Ashuganj | 138 | 10:00 | 132 | 22:00 | Barapukuria | 138 | 3:00 | 124 | 8:00
| Daudkandi | 132 | 7:00 | 126 | 1:00 | Panchagar | 128 | 6:00 | 105 | 20:00
| B.Baria | 133 | 10:00 | 125 | 22:00 | Joldhaka | 128 | 6:00 | 113 | 20:00
| Ramganj | 127 | 18:00 | 121 | 15:00 | Kurigram | 128 | 0.16667 | 114 | 0.83333

## L-Curve
Date | 2021-05-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 4 | 8375 | 4055 | 12430 |  |  |  | QF-LDC-11
0:30 | 92 | 8013.5 | 3945 | 11958.5 | Date: | 2021-05-21
1:00 | 180 | 7652 | 3835 | 11487
1:30 | 175 | 7575.5 | 3710.5 | 11286
2:00 | 170 | 7499 | 3586 | 11085
2:30 | 200 | 7420 | 3492.5 | 10912.5 | [5 empty] | Gen. at Eve. Peak | 12519 | 12519 MW (21:00 )
3:00 | 230 | 7341 | 3399 | 10740 | [6 empty] | 21:00
3:30 | 205 | 7264 | 3369.5 | 10633.5 | [5 empty] | Gen. at Day Peak | 9546 | 9546 MW (12:00 )
4:00 | 180 | 7187 | 3340 | 10527 | [6 empty] | 12:00
4:30 | 125 | 7104.5 | 3320.5 | 10425 | [5 empty] | Highest Generation | 12561
5:00 | 70 | 7022 | 3301 | 10323 | [6 empty] | 23:00
5:30 | 57 | 6763 | 3159.5 | 9922.5
6:00 | 44 | 6504 | 3018 | 9522
6:30 | 39 | 6294 | 2968.5 | 9262.5
7:00 | 34 | 6084 | 2919 | 9003
7:30 | 33 | 6035 | 2901.5 | 8936.5
8:00 | 32 | 5986 | 2884 | 8870
8:30 | 106 | 6009 | 2881.5 | 8890.5
9:00 | 180 | 6032 | 2879 | 8911
9:30 | 190 | 6133.5 | 2894 | 9027.5
10:00 | 200 | 6235 | 2909 | 9144
10:30 | 202 | 6286.5 | 2918.5 | 9205
11:00 | 204 | 6338 | 2928 | 9266
11:30 | 291 | 6430 | 2976 | 9406
12:00 | 378 | 6522 | 3024 | 9546
12:30 | 406 | 6715.5 | 3131.5 | 9847
13:00 | 434 | 6909 | 3239 | 10148
13:30 | 448 | 6826.5 | 3231 | 10057.5
14:00 | 462 | 6744 | 3223 | 9967
14:30 | 621 | 6904.5 | 3235.5 | 10140
15:00 | 780 | 7065 | 3248 | 10313
15:30 | 662 | 7038.5 | 3247.5 | 10286
16:00 | 544 | 7012 | 3247 | 10259
16:30 | 438 | 6928 | 3102 | 10030
17:00 | 332 | 6844 | 2957 | 9801
17:30 | 344 | 6664 | 2856.5 | 9520.5
18:00 | 356 | 6484 | 2756 | 9240
18:30 | 250 | 6933 | 3137 | 10070
19:00 | 144 | 7382 | 3518 | 10900
19:30 | 88 | 8152 | 3863 | 12015
20:00 | 88 | 8219 | 3870 | 12089 |  |  |  | Executive Engineer
20:30 | 85 | 8388.5 | 3915.5 | 12304 |  |  |  | Network Operation Division
21:00 | 82 | 8558 | 3961 | 12519
21:30 | 61 | 8533 | 4003.5 | 12536.5
22:00 | 40 | 8508 | 4046 | 12554 |  |  |  |  | Page 6 of 7
22:30 | 23 | 8524.5 | 4033 | 12557.5
23:00 | 6 | 8541 | 4020 | 12561
23:30 | 5 | 8458 | 4037.5 | 12495.5
24:00 | 4 | 8375 | 4055 | 12430
12519 MW (21:00 )
9546 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-21 |  | Energy | 255482439
[11 empty] | 2021-05-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4610 | 916 | 2031 | 3697 | 700 | 25 | 314 | 0 | 168 | 168
0:30 | 4676 | 916.5 | 2027 | 3179 | 685 | 25 | 297.5 | 0 | 168 | 168 | Date: | 2021-05-21
1:00 | 4742 | 917 | 2023 | 2661 | 670 | 25 | 281 | 0 | 168 | 168
1:30 | 4737.5 | 917 | 2024 | 2543.5 | 675 | 25 | 198 | 0 | 166 | 166 | [7 empty] | Total Energy | 255.4824 | Total Energy Gen 255.482 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.482 MKWHr
2:00 | 4733 | 917 | 2025 | 2426 | 680 | 25 | 115 | 0 | 164 | 164 | [7 empty] | Energy not Served | 0
2:30 | 4727.5 | 916 | 2034.5 | 2276 | 680 | 25 | 90.5 | 0 | 163 | 163 | [7 empty] | Energy Requirement | 255.4824
3:00 | 4722 | 915 | 2044 | 2126 | 680 | 25 | 66 | 0 | 162 | 162
3:30 | 4727 | 915 | 2039 | 2027.5 | 680 | 25 | 58 | 0 | 162 | 162 | [6 empty] | Shortage
4:00 | 4732 | 915 | 2034 | 1929 | 680 | 25 | 50 | 0 | 162 | 162
4:30 | 4723 | 915.5 | 2032 | 1852 | 680 | 25 | 41.5 | 0 | 156 | 156
5:00 | 4714 | 916 | 2030 | 1775 | 680 | 25 | 33 | 0 | 150 | 150
5:30 | 4624 | 915.5 | 1936.5 | 1579 | 675 | 25 | 16.5 | 0 | 148 | 148
6:00 | 4534 | 915 | 1843 | 1383 | 670 | 25 | 0 | 0 | 146 | 146
6:30 | 4499 | 916 | 1763 | 1270 | 645 | 25 | 0 | 0 | 133 | 133 |  |  |  |  | Coal
7:00 | 4464 | 917 | 1683 | 1157 | 620 | 25 | 0 | 0 | 120 | 120
7:30 | 4422 | 916.5 | 1649 | 1173 | 605 | 25 | 0 | 0 | 122 | 122 |  |  |  | Oil |  |  |  | ,
8:00 | 4380 | 916 | 1615 | 1189 | 590 | 25 | 0 | 0 | 124 | 124
8:30 | 4334.5 | 916 | 1621 | 1248 | 575 | 25 | 0 | 0 | 124 | 124
9:00 | 4289 | 916 | 1627 | 1307 | 560 | 25 | 0 | 0 | 124 | 124
9:30 | 4292.5 | 916 | 1690 | 1333.5 | 560 | 25 | 0 | 0 | 127 | 127
10:00 | 4296 | 916 | 1753 | 1360 | 560 | 25 | 0 | 0 | 130 | 130
10:30 | 4274.5 | 916 | 1844 | 1350.5 | 560 | 25 | 0 | 0 | 126 | 126
11:00 | 4253 | 916 | 1935 | 1341 | 560 | 25 | 0 | 0 | 122 | 122
11:30 | 4284 | 915.5 | 1943 | 1441.5 | 570 | 25 | 0 | 0 | 129 | 129
12:00 | 4315 | 915 | 1951 | 1542 | 580 | 25 | 0 | 0 | 136 | 136
12:30 | 4366.5 | 915.5 | 1962.5 | 1738.5 | 615 | 25 | 0 | 0 | 138 | 138
13:00 | 4418 | 916 | 1974 | 1935 | 650 | 25 | 0 | 0 | 140 | 140
13:30 | 4418 | 916 | 1974 | 1935 | 650 | 25 | 0 | 0 | 140 | 140
14:00 | 4418 | 916 | 1974 | 1935 | 650 | 25 | 0 | 0 | 140 | 140
14:30 | 4395.5 | 916 | 1979 | 2056 | 630 | 25 | 0 | 0 | 143 | 143
15:00 | 4373 | 916 | 1984 | 2177 | 610 | 25 | 0 | 0 | 146 | 146
15:30 | 4400 | 916 | 1972.5 | 2152 | 615 | 25 | 0 | 0 | 143 | 143
16:00 | 4427 | 916 | 1961 | 2127 | 620 | 25 | 0 | 0 | 140 | 140
16:30 | 4344.5 | 916 | 1885 | 2089 | 595 | 25 | 0 | 0 | 138 | 138
17:00 | 4262 | 916 | 1809 | 2051 | 570 | 25 | 0 | 0 | 136 | 136
17:30 | 4197.5 | 915.5 | 1720 | 1946.5 | 565 | 25 | 0 | 0 | 132 | 132
18:00 | 4133 | 915 | 1631 | 1842 | 560 | 25 | 0 | 0 | 128 | 128
18:30 | 4416 | 915.5 | 1796 | 2117.5 | 575 | 25 | 78 | 0 | 144 | 144
19:00 | 4699 | 916 | 1961 | 2393 | 590 | 25 | 156 | 0 | 160 | 160
19:30 | 4637 | 915 | 1913 | 3420 | 640 | 25 | 305 | 0 | 160 | 160
20:00 | 4523 | 915 | 1933 | 3564 | 650 | 25 | 315 | 0 | 164 | 164
20:30 | 4592 | 915 | 1986 | 3645.5 | 660 | 25 | 314.5 | 0 | 166 | 166
21:00 | 4661 | 915 | 2039 | 3727 | 670 | 25 | 314 | 0 | 168 | 168
21:30 | 4670 | 915.5 | 2033 | 3724 | 685 | 25 | 314 | 0 | 170 | 170
22:00 | 4679 | 916 | 2027 | 3721 | 700 | 25 | 314 | 0 | 172 | 172
22:30 | 4690 | 915.5 | 2032 | 3709 | 700 | 25 | 314 | 0 | 172 | 172
23:00 | 4701 | 915 | 2037 | 3697 | 700 | 25 | 314 | 0 | 172 | 172
23:30 | 4655.5 | 915.5 | 2034 | 3697 | 700 | 25 | 314 | 0 | 170 | 170 | Max Temp. in Dhaka |  | 37° C
24:00 | 4610 | 916 | 2031 | 3697 | 700 | 25 | 314 | 0 | 168 | 168
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
Total Energy Gen 255.482 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 255.482 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 608000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 1 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 348327
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 |  |  |  | 17 | 17 | 19 | 15 | 12 | 13 | 10 | 3 | 0 | [8 empty] | 110160
6 | Sikalbaha 225MW CCPP (Gas) | 131 | 131 | 131 | 131 | 135 | 131 | 131 | 78 | [11 empty] | 100 | 131 | 151 | 140 | 141 | 141 | 141 | 1809585
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2560178
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 34 | 34 | 34 | 17 | [15 empty] | 68 | 68 | 68 | 68 | 68 | 68 | 573501
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 89 | 89 | 89 | 86 | 86 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 82 | 87 | 89 | 89 | 89 | 51 |  | 51 | 89 | 84 | 89 | 89 | 89 | 89 | 1966290
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 185 | 185 | 185 | 185 | 180 | 120 | 117 | 116 | 68 | 70 | 70 | 70 | 120 | 95 | 120 | 97 | 70 | 70 |  | 150 | 80 | 70 | 150 | 115 | 115 | 115 | 3120000
17 | Siddhirganj 335 MW CCPP | 220 | 220 | 220 | 220 | 221 | 180 | 180 | 180 | 180 | 180 | 208 | 209 | 209 | 180 | 180 | 203 | 150 | 150 |  | 201 | 150 | 152 | 212 | 180 | 180 | 180 | 4730893
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | [18 empty] | 41 | 95 | 154 | 185 | 145 | 145 | 145 | 928363
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 4441500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 105 | 80 | 80 | 80 | 80 | 80 | 2213978
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 567000
33 | Ashuganj 225 MW CCPP | 220 | 220 | 218 | 219 | 219 | 182 | 183 | 182 | 185 | 183 | 193 | 185 | 183 | 192 | 204 | 185 | 184 | 201 |  | 164 | 172 | 200 | 197 | 196 | 185 | 186 | 4766000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 290 | 290 | 265 | 265 | 265 | 265 | 265 | 270 | 280 | 280 | 300 | 265 | 265 | 290 |  | 320 | 265 | 265 | 265 | 300 | 290 | 275 | 6800000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 265 | 260 | 260 | 295 | 315 | 310 | 280 | 295 | 260 | 260 | 290 |  | 335 | 260 | 260 | 260 | 295 | 310 | 285 | 6914000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 54 | 54 | 53 | 51 | 51 | 51 | 50 | 50 | 50 | 50 | 16 |  | 16 | 52 | 52 | 54 | 52 | 53 | 53 | 1226400
36 | Chandpur 150 MW CCPP | 91 | 91 | 90 | 92 | 89 | 90 | 86 | 85 | 90 | 91 | 91 | 92 | 92 | 88 | 92 | 90 | 92 | 92 |  | 90 | 89 | 90 | 89 | 91 | 91 | 90 | 2106860
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 330 | 329 | 331 | 332 | 334 | 330 | 331 | 330 | 331 | 332 | 339 | 339 | 344 | 333 | 354 | 352 | 331 | 264 |  | 298 | 329 | 340 | 350 | 336 | 363 | 353 | 8200199
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7081750
41 | Haripur 360MW CCPP(HPL) | 352 | 352 | 350 | 350 | 350 | 307 | 308 | 266 | 265 | 265 | 340 | 339 | 335 | 275 | 335 | 334 | 270 | 270 |  | 340 | 300 | 300 | 340 | 340 | 340 | 340 | 7640000
42 | RPCL 210MW CCPP | 172 | 174 | 189 | 204 | 204 | 202 | 199 | 183 | 180 | 166 | 162 | 162 | 148 | 152 | 152 | 166 | 170 | 181 |  | 176 | 177 | 176 | 176 | 165 | 167 | 167 | 4063360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 5 | 6 | 30 | 49 | 53 | 22 | 38 | 48 | 36 | 8 | 17 | 2 | [8 empty] | 311310
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1007000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 0 |  |  |  |  | 514080
46 | Shajibazar 330 MW CCPP | 331 | 329 | 331 | 330 | 330 | 333 | 331 | 328 | 330 | 328 | 152 | 158 | 159 | 157 | 172 | 310 | 325 | 324 |  | 325 | 329 | 325 | 328 | 328 | 328 | 328 | 6615000
47 | Shahjibazar GTPP Unit- 8 & 9 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 40 | 50 |  | 50 | 52 | 52 | 52 | 51 | 51 | 51 | 696384
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 40 | 20 | 20 | 20 | 78 | 75 | 74 | 73 | 72 | 71 | 71 | 71 | 40 |  | 75 | 75 | 75 | 76 | 77 | 77 | 77 | 1579200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 100 | 100 | 100 | 140 | 140 | 140 | 100 | 100 | 120 | 100 | 100 |  | 140 | 140 | 120 | 140 | 145 | 145 | 145 | 2963270
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 18 | 17 | 18 | 17 | 396000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 7 | 7 | 7 | 7 | 7 | 155340
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 |  | 5 | 5 |  |  | 2 | 5 | 11 | 11 | 11 | 11 | 11 | 207100
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 14 | 14 | 14 | 31 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1053600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 367416
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 300 | 295 | 290 | 280 | 290 | 270 | 285 | 290 | 300 | 300 | 310 | 290 | 320 | 310 | 290 | 280 |  | 310 | 300 | 290 | 310 | 300 | 320 | 315 | 7357500
| Bibiyana South 400 MW | 350 | 350 | 350 | 351 | 349 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 390 | 389 | 383 | 390 | 393 | 300 |  | 350 | 395 | 395 | 396 | 390 | 392 | 396 | 8636000
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 17 | 17 |  |  |  |  | 25 | 55 | 55 | 55 | 55 | 55 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 789764
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 22 | 22 | 23 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 572160
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 448656
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 404424
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 422388
63 | Impoprt (Tripura) | 168 | 164 | 162 | 162 | 150 | 146 | 120 | 124 | 124 | 130 | 122 | 136 | 140 | 142 | 146 | 140 | 136 | 128 |  | 160 | 160 | 164 | 168 | 172 | 172 | 168 | 3576960
64 | Malancha, Ctg. EPZ (United) | 29 | 29 | 29 | 29 | 31 | 32 | 26 | 22 | 16 | 22 | 22 | 16 | 28 | 24 | 24 | 26 | 36 | 41 |  | 41 | 41 | 33 | 38 | 38 | 38 | 38 | 743040
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 19 | 19 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 437148
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 5 | 5 | 8 | 5 | 5 | 5 | 5 | 5 | 5 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 151020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816900
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 464800
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 12 | 12 | 12 | 12 | 14 | 14 | 14 | 14 | 14 |  | 14 | 14 | 14 | 14 | 21 | 21 | 21 | 392940
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 793000
72 | Rupganj 33 MW PP(Summit) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 17 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 519000
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 98 | 98 | 98 | 53 | 52 | 52 | 52 | 80 | 95 | 95 | 96 | 93 | 88 | 98 | 54 |  | 95 | 101 | 101 | 101 | 101 | 101 | 101 | 2017727
| Feni Lanka Power | 52 | 52 | 52 | 52 | 17 | [14 empty] | 36 | 114 | 114 | 114 | 88 | 88 | 88 | 788880
| Chowmuhani 113 MW | 111 | 111 | 111 | 114 | 112 | 55 | 8 | 8 | 8 | 8 | 15 | 69 | 118 | 115 | 113 | 113 | 110 | 75 |  | 94 | 119 | 120 | 119 | 122 | 113 | 111 | 2151240
| Manikgonj 162MW PP(MPGL) | 54 | 54 | 17 | 17 | [9 empty] | 17 | 17 | 17 | 17 | 17 |  | 40 | 162 | 158 | 162 | 162 | 162 | 162 | 1104480
77 | Siddhirganj 100 PP(Dutch Bangla) | 70 | 70 | 70 | 70 | 30 | 7 | [5 empty] | 2 | 14 | 40 | 40 | 40 | 40 | 40 |  | 40 | 50 | 70 | 95 | 92 | 100 | 100 | 1111680
78 | Gazipur 52 MW PP |  |  |  |  | 13 | 12 |  | 2 | 27 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 0 | 700800
79 | Kodda 150MW PP | 64 | 32 | 32 | 16 | 16 | [14 empty] | 32 | 98 | 98 | 98 | 98 | 98 | 98 | 684960
80 | Jamalpur 95 MW PP(Powerpac) | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 47 | 55 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 1429440
81 | Jangalia 52 MW PP (Lakdanavi) | 46 | 52 | 52 | 52 | 52 | 52 |  |  |  | 2 | 9 | 32 | 50 | 52 | 52 | 52 | 52 | 25 |  | 33 | 52 | 52 | 52 | 52 | 52 | 52 | 971102
| Gazipur 100 MW PP | [13 empty] | 13 | 17 | 17 | 17 | 17 |  | 17 | 36 | 74 | 105 | 105 | 105 | 105 | 607200
| Kaptai 7 MW Solar PP | [5 empty] | 1 | 1 | 3 | 3 | 2 | 5 | 6 | 2 | 4 | 4 | 3 | 1 | 0 | [8 empty] | 35039
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 42 | 36 | 36 | 36 | 36 | 39 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1199394
| Karnaphuli Power Ltd. | 17 | 17 | [5 empty] | 27 | 85 | 85 | 85 | 85 | 101 | 106 | 106 | 108 | 108 | 108 |  | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 1288835
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 250 | 270 | 270 | 260 | 260 | 250 | 245 | 245 | 260 | 260 | 270 | 270 | 255 | 270 | 280 | 255 | 255 | 280 |  | 280 | 280 | 280 | 260 | 285 | 285 | 275 | 6469440
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 55 | 57 | 53 | [16 empty] | 24 | 72 | 65 | 72 | 72 | 74 | 76 | 563520
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 92 | 80 | 80 | 80 | 92 | 80 | 92 | 92 | 92 | 92 | 92 | 92 | 92 |  | 85 | 90 | 90 | 100 | 100 | 100 | 100 | 2141040
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1204696
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [18 empty] | 7 | 32 | 58 | 72 | 72 | 72 | 72 | 419616
95 | Patenga 50MW PP (Baraka) | 4 | [18 empty] | 1 | 12 | 10 | 12 | 12 | 12 | 12 | 85440
96 | Chattogram 108 MW PP (ECPV) | 8 | [10 empty] | 1 | 8 | 12 | 12 | 12 |  |  |  | 24 | 80 | 75 | 50 | 41 | 31 | 31 | 317760
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 30 | 30 | 30 | 30 | 30 | 30 | 36 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1169386
100 | Manikganj 55 MW PP (Northern) | 17 | [7 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 474097
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 130 | 100 | 100 | 100 | 130 | 163 | 163 | 163 | 110 | 130 | 110 | 110 | 110 |  | 110 | 110 | 110 | 130 | 110 | 110 | 110 | 3296945
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 3 | 1 | 0 | 1 |  |  | 0 | [8 empty] | 10550
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 17 | [7 empty] | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 591120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 8 | [18 empty] | 22 | 130 | 140 | 131 | 131 | 130 | 130 | 700800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 101 | 101 | 101 | 101 | 70 | 70 | 75 | 105 | 112 | 111 | 102 | 99 | 103 | 105 | 115 | 117 | 132 | 132 |  | 140 | 149 | 149 | 149 | 149 | 145 | 149 | 2760912
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2406720
116 | Chandpur 200MW (Desh energy) | 120 | 120 | 120 | 120 | 120 | 120 | 80 | 80 | 80 | 80 | 82 | 85 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 120 | 111 | 120 | 120 | 120 | 120 | 2563200
117 | Ashuganj 150MW PP (Midland) | 150 | 100 | 10 | [16 empty] | 30 | 140 | 122 | 143 | 150 | 150 | 150 | 1114036
118 | Bibiyana-III 400 MW CCPP | 367 | 367 | 375 | 365 | 365 | 331 | 331 | 333 | 333 | 333 | 375 | 368 | 367 | 317 | 403 | 368 | 344 | 351 |  | 393 | 366 | 368 | 367 | 402 | 404 | 372 | 8728000
| Jamalpur 115 MW PP (United) | 115 | 115 | 75 | 55 | 55 | 55 | 35 | 8 | 8 | 35 | 35 | 35 | 84 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2065200
| Anwara 300 MW PP (United) | [13 empty] | 16 | 16 | 16 | 16 | 16 | [8 empty] | 87818
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2370240
| Anlima Energy Ltd. | 100 | 99 | 99 | 53 | 53 | 53 | 53 | 92 | 99 | 98 | 99 | 99 | 98 | 99 | 99 | 99 | 99 | 99 |  | 99 | 99 | 99 | 99 | 99 | 97 | 84 | 2204236
| Bhairob 54.5 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 35 | 31 | 36 | 36 | 36 | 36 | 519480
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 9 | 19 | 25 | 29 | 34 | 27 | 29 | 23 | 23 | 16 | 8 | 2 | [8 empty] | 224083
120 | Eastern Zone Total | 7652 | 7499 | 7341 | 7187 | 7022 | 6504 | 6084 | 5986 | 6032 | 6235 | 6338 | 6522 | 6909 | 6744 | 7065 | 7012 | 6844 | 6484 |  | 7382 | 8152 | 8219 | 8558 | 8508 | 8541 | 8375 | 172564310
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 66 |  | 66 | 66 | 70 | 73 | 78 | 70 | 99 | 1944960
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 70 | 35 | 35 | 35 | [6 empty] | 17 | 70 | 91 | 91 | 70 | 53 | 53 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 1466880
130
131
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | [8 empty] | 13 | 17 | 17 |  |  |  | 13 | 35 | 35 | 44 | 72 | 72 | 72 | 555600
133 | Bhola Nutan Biddut BD LTD (GAS) | [11 empty] | 6 | 4 | 4 | 6 | 15 | 15 | 15 |  | 15 | 51 | 91 | 27 | 37 | 19 | 29 | 301718
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 32 | 16 | [5 empty] | 24 | 32 | 32 | 32 | 16 | 16 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1457184
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 96 | 96 | 95 | 96 | 96 | 95 | 91 | 89 | 89 | 85 | 87 | 88 | 85 | 85 | 91 | 95 | 94 |  | 93 | 95 | 96 | 96 | 96 | 96 | 82 | 2222010
| Bhola 225 MW CCPP | 85 | 86 | 85 | 86 | 86 | 86 | 86 | 85 | 84 | 85 | 82 | 82 | 86 | 83 | 84 | 87 | 86 | 86 |  | 86 | 88 | 88 | 85 | 85 | 84 | 85 | 2062489
140 | Bhola 33 MW PP (Venture) | 33 | 34 | 34 | 34 | 34 | 35 | 28 | 25 | 23 | 24 | 25 | 25 | 26 | 27 | 27 | 23 | 24 | 27 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 699386
141 | Noapara 100 MW PP (Bangla Trac) | 70 | [19 empty] | 50 | 57 | 98 | 100 | 100 | 100 | 574080
142 | Noapara 40 MW PP (Khanjahan Ali) | 33 | 33 | 33 | 24 | [9 empty] | 8 | [5 empty] | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 326250
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 917 | 917 | 915 | 915 | 916 | 915 | 917 | 916 | 916 | 916 | 916 | 915 | 916 | 915 | 916 | 916 | 916 | 915 |  | 916 | 915 | 915 | 915 | 916 | 915 | 916 | 22213636
147 | Bheramara 410 MW CCPP | 330 | 325 | 320 | 320 | 305 | 305 | 310 | 320 | 320 | 320 | 320 | 320 | 315 | 310 | 315 | 315 | 250 | 230 |  | 340 | 350 | 350 | 350 | 350 | 350 | 355 | 7836480
148 | Payra 1320 MW | 520 | 530 | 530 | 530 | 530 | 520 | 470 | 440 | 410 | 410 | 410 | 430 | 500 | 470 | 460 | 470 | 420 | 410 |  | 440 | 490 | 500 | 520 | 550 | 550 | 550 | 12662400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3681100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [18 empty] | 25 | 40 | 50 | 50 | 50 | 50 | 50 | 312384
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 3 | 1 | 3 | 2 | 0 | 0 | 1 | 0 | 0 | [8 empty] | 17280
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 116 | 115 | 118 | 118 | 118 | 118 | 118 | 120 | 122 | 121 | 122 | 124 | 124 | 80 | 80 | 80 | 80 | 80 |  | 88 | 130 | 80 | 80 | 80 | 80 | 80 | 2667600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 159 | 160 | 160 | 158 | 153 | 154 | 142 |  | 135 | 155 | 161 | 146 | 145 | 140 | 140 | 3931882
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 182 | 150 | 150 | 150 | 150 | 150 | 150 | 169 | 185 | 184 | 182 | 181 | 180 | 180 | 180 | 181 | 130 |  | 147 | 180 | 130 | 130 | 130 | 130 | 130 | 4244309
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 392 | 392 | 403 | 402 | 400 | 335 | 310 | 317 | 325 | 335 | 362 | 363 | 369 | 389 | 411 | 411 | 316 | 250 |  | 398 | 320 | 315 | 397 | 406 | 413 | 416 | 8888455
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 19 | 19 |  | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 423360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 226008
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 52 | 52 | 52 | 8 | [5 empty] | 16 | 52 | 52 | 52 | 52 | 52 | 24 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 847200
170 | Chapainawabganj 100 MW Peaking PP | 99 | 49 | [17 empty] | 99 | 99 | 99 | 98 | 98 | 98 | 98 | 734248
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | [17 empty] | 17 | 65 | 98 | 112 | 113 | 113 | 113 | 704831
172 | Confidence Power Bogura Unit-1 113 MW | [19 empty] | 50 | 108 | 108 | 113 | 113 | 113 | 113 | 575616
173 | Rangpur 20 MW GTPP | [19 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 100 | 49 | [8 empty] | 34 | 60 | 60 | 70 | 70 | 35 | 38 |  | 112 | 113 | 113 | 113 | 113 | 113 | 113 | 1305600
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 3 | 2 | 2 | 3 | 5 | 5 | 5 | 3 | 2 | [8 empty] | 35183
178
178