## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-24 | Monday
|  |  | Date (day): | 2021-05-24 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14985.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15881 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-23 | 2021-05-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 190 | 180 | 190 | 190
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 100 | 104 | 100 | 102
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 344 | 391 | 360 | 390 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 276 | 272 | 360 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Dust in gas line.
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 240 | 300 | 300
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 27 | 85 | 85 | 85
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 178 | 179 | 180 | 185 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 208 | 208 | 220 | 220 |  | 115 | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 95 | 102 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 44 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 16 | 25 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 200 | 243 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 303 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 90 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 0 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 133 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 86 | 105 | 105 | 105
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 95 | 96 | 72 | 72 |  | 32 | Engine problem
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 3259 | 3921 | 3782 | 4089 | 309 | 1222
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 203 | 202 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 110 | 110 | 110
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 51 | 53 | 70 | 90 |  | 15 | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 51 | 45 | 68 | 68 |  | 34 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 75 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 30 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 57 | 75 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 0 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1018 | 1071 | 1595 | 1605 | 385 | 335
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 0 | 80 | 100 | 34 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 136 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 0 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 300 | 330 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 35 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 0 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 150 | 0 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 86 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 120 | 103 | 125 | 125 |  | 75 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 162 | 160 | 145 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 115 | 121 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 0 | 35 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1834 | 1468 | 2105 | 2312 | 485 | 190
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 145 | 99 | 160 | 160
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 17 | 19 | 19 |  | 3 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 54 | 62 | 64 | 64 |  | 31 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 80 | 191 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 105 | 106 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 17 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 15 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 434 | 499 | 631.6 | 580 | 0 | 34
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 42 | 42 | 42 |  | 28 | Under maint.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 316 | 329 | 330 | 330
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 48 | 44 | 44
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 51 | 57 | 57 |  | 9 | Engine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 72 | 77 | 76 | 76 |  | 10 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 140 | 140 |  | 91 | ST Under maint.
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 6 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 368 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 7 | 7 | 7 |  | 3 | Engine prolem
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 384 | 396 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1966 | 1985 | 2075 | 2075 | 0 | 310
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 912 | 913 | 909 | 909
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 80 | 99 | 99 | 99 |  | 16 | Engine problem
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 15 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 260 | 290 | 410 | 410
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1346 | 1554 | 1785 | 2055 | 0 | 107
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 32 | 110 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 34 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 87 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 89 | 93 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 540 | 580 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 0 | 50 | 50 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 81 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 773 | 985 | 998 | 1108 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 51 | 40 | 40
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 24 | 42 | 40 | 42 |  | 8 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 114 | 107 | 125 | 125 | 85 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 132 | 133 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 150 | 146 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 390 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 20 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 100 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 175 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 112 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1122 | 1603 | 1743 | 1774 | 256 | 50
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 269 | 271 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 22023 | 21315 | 12021 | 13357 | 14985.6 | 15881 | 1644 | 2459
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11410.8152 | 12679 | 14224.9324 | 15074.882
| A. |  | 2021-05-23 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13357 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10560 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13357 | MW
| 3 | Day peak Generation : |  |  | 12021 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12679 | MW
| 4 | Evening peak Generation : |  |  | 13357 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 292.5282 | MKWHr | By Solar | 0.84163 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 155.4289 | MKWHr |  | By Oil: | 91.7657 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.9752 | MKWHr |  | By Hydro: | 0.604 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1644 | MW | Dhaka | 4570 | 4570 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2459 | MW | Chittagong | 1111 | 1111 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4103 | MW | Khulna | 1689 | 1689 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1271.343 | MMCFD |  |  | Rajshahi | 1403 | 1403 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 167641644.41 | ii) Oil : | Taka | 703860797.73 | Comilla | 1262 | 1262 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 82687520 | Total | Taka | 954189962.14 | Mymensingh | 936 | 936 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.1325 | MKWHr. | Sylhet | 565 | 565 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -18 | MW (E to W) at | 21:00 | hrs | Barisal | 397 | 397 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -200 | MW at | 4:00 | hrs | Rangpur | 746 | 746 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 37.8° C |  |  | Total | 12679 | 12679 |  | 0
| B. |  | 2021-05-24 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 38.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 14500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15881 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 12100 | MW
| 4 | Reserve(Generation end) |  |  |  | 1381 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 317.5608 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10785 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.0305 | MKWHr. | ii) HVDC Flow at Peak Time |  | 913 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.8822 | MKWHr. | iii) Maximum HVDC Flow : |  | 916 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 74.23 |  | (b) Today: | 73.99 |  | (c) Rule Curve: |  | 77.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 338 | 345 |  | 0 | 300 | 260 | 0 | 0 | 55 | 214 | 0 | 146 | 100 | 102 | 150 | 84 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 16 | 203 | 0 | 110 | 0 |  | 24 | 0 | 68 | 80 | 51 | 50 | 19 | 28 | 0 | 0 | 80 | 260 | 265 | 185 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 50 | 52 | 22 | 8 | 33 | 15 | 170 | 153 | 63 | 17 | 0 | 42 | 22 | 44 | 0 | 130 | 330 | 56 | 78 | 0 | 140 | 18 | 0 | 7 | 310 | 16 | 11 | 46 | 245 | 0 | 0 | 192 | 22 | 149 | 0 | 100 | 115 | 155 | 366 | 107 | 88 | 53 | 0 | 0 | 54 | 34 | 114 | 115 | 96 | 367 | 78 | 0 | 158 | 116 | 0 | 35 | 0 |  | 916 | 0 | 305 | 0 | 71 | 0 | 0 | 0 | 10 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 97 | 0 | 0 | 30 | 52 | 34 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 145 | 0 | 96 | 99 | 185 | 0 | 398 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 107 | 0 |  | 8987 | 4202 | 13189 | 4745 | 916 | 2005 | 4109 | 730 | 25 | 489 | 170 | 0 | 0 | 74.28
2:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 331 | 346 |  | 0 | 300 | 280 | 0 | 0 | 55 | 214 | 0 | 125 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 16 | 204 | 0 | 110 | 0 |  | 24 | 0 | 34 | 80 | 51 | 5 | 19 | 28 | 0 | 0 | 80 | 260 | 265 | 200 | 8 | 92 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 168 | 153 | 63 | 17 | 0 | 42 | 22 | 44 | 0 | 130 | 328 | 57 | 78 | 0 | 140 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 245 | 0 | 0 | 192 | 0 | 139 | 0 | 100 | 111 | 155 | 367 | 107 | 88 | 53 | 0 | 0 | 54 | 34 | 114 | 115 | 97 | 395 | 90 | 0 | 144 | 116 | 0 | 35 | 0 |  | 913 | 0 | 305 | 0 | 66 | 0 | 0 | 0 | 10 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 89 | 0 | 0 | 0 | 52 | 34 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 134 | 0 | 140 | 0 | 96 | 99 | 185 | 0 | 398 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 560 | 0 | 0 | 107 | 0 |  | 8715 | 4126 | 12841 | 4753 | 913 | 1993 | 3912 | 710 | 25 | 367 | 168 | 0 | 0 | 74.27
3:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 350 | 343 |  | 0 | 300 | 290 | 0 | 0 | 55 | 216 | 0 | 125 | 100 | 58 | 84 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 217 | 0 | 110 | 0 |  | 24 | 0 | 17 | 80 | 0 | 0 | 19 | 28 | 0 | 0 | 80 | 295 | 305 | 184 | 8 | 92 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 166 | 153 | 63 | 17 | 0 | 42 | 22 | 44 | 0 | 163 | 328 | 57 | 78 | 0 | 140 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 45 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 105 | 154 | 402 | 107 | 88 | 53 | 0 | 0 | 54 | 17 | 88 | 114 | 98 | 387 | 94 | 0 | 144 | 116 | 0 | 35 | 0 |  | 913 | 0 | 295 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 89 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 132 | 0 | 140 | 0 | 95 | 60 | 181 | 0 | 414 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 70 | 560 | 0 | 0 | 72 | 0 |  | 8468 | 3968 | 12436 | 4857 | 913 | 2051 | 3470 | 710 | 25 | 244 | 166 | 0 | 0 | 74.26
4:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 364 | 346 |  | 0 | 300 | 280 | 0 | 0 | 55 | 216 | 0 | 185 | 100 | 58 | 84 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 210 | 0 | 110 | 0 |  | 24 | 0 | 34 | 80 | 0 | 0 | 19 | 38 | 0 | 0 | 80 | 285 | 290 | 176 | 8 | 91 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 164 | 153 | 55 | 17 | 0 | 42 | 22 | 44 | 0 | 163 | 330 | 56 | 78 | 0 | 140 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 85 | 155 | 388 | 107 | 88 | 53 | 0 | 0 | 54 | 0 | 88 | 120 | 99 | 390 | 94 | 0 | 162 | 116 | 0 | 35 | 0 |  | 912 | 0 | 295 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 50 | 0 | 89 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 131 | 0 | 139 | 0 | 95 | 0 | 179 | 0 | 414 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 54 | 0 |  | 8399 | 3816 | 12215 | 4876 | 912 | 2074 | 3193 | 710 | 25 | 261 | 164 | 0 | 0 | 74.25
5:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 354 | 345 |  | 0 | 300 | 270 | 0 | 0 | 55 | 218 | 0 | 185 | 100 | 7 | 84 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 20 | 33 | 0 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 204 | 0 | 110 | 0 |  | 24 | 0 | 9 | 80 | 0 | 0 | 19 | 38 | 0 | 0 | 80 | 260 | 270 | 179 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 160 | 153 | 55 | 17 | 0 | 42 | 22 | 44 | 0 | 163 | 327 | 56 | 78 | 0 | 140 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 84 | 50 | 367 | 107 | 34 | 53 | 0 | 0 | 54 | 0 | 70 | 120 | 100 | 394 | 93 | 0 | 158 | 116 | 0 | 35 | 0 |  | 913 | 0 | 290 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 32 | 88 | 34 | 110 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 138 | 0 | 95 | 0 | 179 | 0 | 416 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 0 | 560 | 0 | 0 | 35 | 0 |  | 8017 | 3704 | 11721 | 4759 | 913 | 2076 | 2931 | 710 | 25 | 147 | 160 | 0 | 0 | 74.24
6:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 336 | 345 |  | 0 | 300 | 280 | 0 | 0 | 55 | 170 | 0 | 120 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 17 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 214 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 19 | 16 | 0 | 0 | 80 | 285 | 290 | 184 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 150 | 153 | 55 | 17 | 0 | 42 | 22 | 44 | 0 | 163 | 327 | 56 | 78 | 0 | 140 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 143 | 1 | 100 | 85 | 10 | 383 | 115 | 17 | 53 | 0 | 0 | 54 | 0 | 0 | 122 | 100 | 394 | 70 | 3 | 17 | 90 | 0 | 35 | 2 |  | 912 | 0 | 285 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 88 | 33 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 131 | 0 | 139 | 0 | 95 | 0 | 177 | 0 | 413 | 53 | 0 | 50 | 0 | 55 | 0 | 0 | 0 | 530 | 0 | 0 | 0 | 0 |  | 7462 | 3329 | 10791 | 4712 | 912 | 2040 | 2262 | 680 | 25 | 4 | 150 | 6 | 0 | 74.23
7:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 364 | 343 |  | 0 | 300 | 280 | 0 | 0 | 45 | 170 | 0 | 120 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 17 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 215 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 1 | 19 | 25 | 0 | 0 | 80 | 290 | 290 | 182 | 8 | 90 | 26 | 24 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 140 | 151 | 55 | 17 | 1 | 42 | 22 | 44 | 0 | 163 | 326 | 56 | 78 | 0 | 140 | 18 | 0 | 7 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 145 | 4 | 100 | 85 | 10 | 400 | 115 | 17 | 53 | 1 | 0 | 54 | 0 | 0 | 120 | 50 | 390 | 17 | 14 | 17 | 53 | 0 | 35 | 8 |  | 913 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 129 | 0 | 139 | 0 | 94 | 0 | 173 | 0 | 415 | 35 | 0 | 35 | 0 | 35 | 0 | 1 | 0 | 530 | 0 | 0 | 0 | 0 |  | 7332 | 3228 | 10560 | 4741 | 913 | 2020 | 2008 | 680 | 25 | 4 | 140 | 29 | 0 | 74.22
8:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 359 | 343 |  | 0 | 300 | 280 | 0 | 0 | 45 | 170 | 0 | 120 | 100 | 7 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 35 | 19 | 25 | 17 | 25 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 214 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 14 | 19 | 10 | 0 | 0 | 80 | 285 | 290 | 185 | 8 | 90 | 26 | 24 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 15 | 148 | 151 | 48 | 17 | 1 | 42 | 22 | 44 | 0 | 163 | 320 | 55 | 75 | 0 | 140 | 17 | 0 | 6 | 320 | 16 | 11 | 0 | 0 | 0 | 0 | 110 | 0 | 149 | 10 | 100 | 85 | 16 | 383 | 115 | 25 | 51 | 2 | 0 | 54 | 0 | 0 | 115 | 80 | 388 | 20 | 25 | 19 | 53 | 0 | 35 | 15 |  | 913 | 0 | 285 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 126 | 0 | 138 | 0 | 92 | 0 | 155 | 0 | 413 | 40 | 0 | 35 | 0 | 64 | 0 | 2 | 0 | 530 | 0 | 0 | 0 | 1 |  | 7360 | 3241 | 10601 | 4682 | 913 | 1994 | 2099 | 680 | 25 | 4 | 148 | 56 | 0 | 74.21
9:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 358 | 340 |  | 0 | 300 | 280 | 0 | 0 | 45 | 214 | 0 | 185 | 100 | 7 | 48 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 17 | 25 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 18 | 19 | 3 | 0 | 0 | 80 | 260 | 265 | 199 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 14 | 150 | 150 | 48 | 17 | 1 | 42 | 22 | 44 | 0 | 163 | 326 | 56 | 74 | 0 | 140 | 17 | 0 | 6 | 300 | 16 | 11 | 0 | 2 | 0 | 0 | 90 | 0 | 149 | 15 | 100 | 103 | 56 | 368 | 115 | 60 | 51 | 3 | 0 | 54 | 0 | 0 | 121 | 100 | 388 | 62 | 37 | 71 | 75 | 0 | 35 | 20 |  | 913 | 0 | 280 | 0 | 66 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 24 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 123 | 0 | 138 | 0 | 89 | 0 | 150 | 0 | 393 | 80 | 0 | 63 | 0 | 113 | 0 | 4 | 10 | 530 | 0 | 0 | 0 | 2 |  | 7679 | 3333 | 11012 | 4711 | 913 | 1920 | 2479 | 680 | 25 | 52 | 150 | 82 | 0 | 74.2
10:00 | 0 | 0 | 0 | 190 | 0 | 97 | 0 | 337 | 336 |  | 0 | 300 | 265 | 0 | 0 | 50 | 212 | 0 | 180 | 100 | 16 | 48 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 25 | 17 | 25 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 19 | 19 | 3 | 0 | 0 | 80 | 265 | 265 | 207 | 8 | 90 | 23 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 14 | 148 | 147 | 47 | 17 | 2 | 41 | 22 | 42 | 0 | 163 | 322 | 55 | 72 | 0 | 140 | 17 | 0 | 6 | 310 | 16 | 11 | 0 | 52 | 0 | 0 | 90 | 0 | 149 | 17 | 100 | 120 | 113 | 368 | 97 | 86 | 51 | 3 | 0 | 54 | 0 | 13 | 120 | 90 | 385 | 91 | 48 | 130 | 116 | 0 | 35 | 28 |  | 912 | 0 | 275 | 0 | 76 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 25 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 119 | 0 | 138 | 0 | 87 | 0 | 150 | 0 | 410 | 105 | 0 | 112 | 0 | 113 | 0 | 4 | 35 | 530 | 0 | 0 | 0 | 3 |  | 7943 | 3448 | 11391 | 4675 | 912 | 1926 | 2868 | 680 | 25 | 52 | 148 | 105 | 0 | 74.19
11:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 353 | 311 |  | 0 | 300 | 280 | 0 | 0 | 55 | 208 | 0 | 178 | 100 | 48 | 48 | 2 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 25 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 206 | 0 | 110 | 0 |  | 22 | 0 | 0 | 80 | 10 | 19 | 19 | 3 | 0 | 0 | 80 | 285 | 290 | 210 | 8 | 90 | 23 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 14 | 160 | 145 | 47 | 17 | 2 | 41 | 22 | 41 | 0 | 163 | 318 | 55 | 74 | 0 | 140 | 17 | 0 | 6 | 310 | 6 | 11 | 0 | 145 | 0 | 0 | 90 | 0 | 135 | 18 | 100 | 120 | 140 | 392 | 105 | 86 | 51 | 4 | 0 | 54 | 0 | 17 | 119 | 77 | 383 | 93 | 41 | 148 | 116 | 0 | 35 | 32 |  | 912 | 0 | 270 | 0 | 71 | 0 | 0 | 0 | 4 | 0 | 0 | 82 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 135 | 0 | 87 | 0 | 142 | 0 | 405 | 90 | 0 | 112 | 0 | 99 | 0 | 6 | 50 | 530 | 0 | 0 | 0 | 2 |  | 8231 | 3399 | 11630 | 4740 | 912 | 1901 | 3055 | 680 | 25 | 52 | 160 | 105 | 0 | 74.18
12:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 344 | 276 |  | 0 | 300 | 280 | 0 | 0 | 55 | 208 | 0 | 178 | 100 | 95 | 98 | 27 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 15 | 0 | 51 | 80 | 57 | 19 | 19 | 3 | 0 | 0 | 80 | 350 | 265 | 210 | 8 | 90 | 23 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 14 | 162 | 145 | 54 | 17 | 1 | 41 | 30 | 44 | 0 | 163 | 316 | 60 | 72 | 0 | 140 | 17 | 0 | 5 | 310 | 6 | 11 | 0 | 200 | 0 | 0 | 80 | 0 | 133 | 18 | 100 | 120 | 150 | 367 | 105 | 86 | 51 | 5 | 0 | 54 | 0 | 52 | 115 | 90 | 384 | 95 | 17 | 162 | 116 | 0 | 35 | 33 |  | 912 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 132 | 0 | 89 | 0 | 150 | 0 | 398 | 90 | 0 | 112 | 0 | 113 | 0 | 6 | 113 | 540 | 0 | 0 | 0 | 1 |  | 8511 | 3510 | 12021 | 4741 | 912 | 1860 | 3397 | 690 | 25 | 153 | 162 | 81 | 0 | 74.18
13:00 | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 332 | 276 |  | 0 | 300 | 250 | 0 | 0 | 55 | 208 | 0 | 125 | 100 | 102 | 133 | 60 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 20 | 33 | 25 | 40 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 24 | 0 | 45 | 80 | 82 | 26 | 19 | 8 | 0 | 0 | 80 | 315 | 295 | 210 | 8 | 89 | 26 | 5 | 0 | 51 | 0 | 50 | 52 | 19 | 8 | 33 | 14 | 160 | 145 | 54 | 17 | 2 | 41 | 30 | 44 | 0 | 130 | 320 | 55 | 72 | 0 | 140 | 17 | 0 | 7 | 290 | 6 | 11 | 0 | 228 | 0 | 0 | 80 | 0 | 146 | 18 | 100 | 120 | 142 | 367 | 105 | 86 | 51 | 5 | 0 | 54 | 0 | 114 | 114 | 90 | 385 | 96 | 20 | 162 | 116 | 0 | 35 | 31 |  | 914 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 4 | 0 | 32 | 85 | 28 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 0 | 30 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 133 | 0 | 89 | 0 | 151 | 0 | 369 | 105 | 0 | 112 | 0 | 112 | 0 | 6 | 113 | 550 | 0 | 0 | 0 | 3 |  | 8618 | 3618 | 12236 | 4679 | 914 | 1793 | 3618 | 700 | 25 | 262 | 160 | 85 | 0 | 74.16
14:00 | 0 | 0 | 0 | 190 | 0 | 97 | 0 | 336 | 277 |  | 0 | 300 | 270 | 0 | 0 | 55 | 170 | 0 | 121 | 97 | 102 | 133 | 91 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 33 | 25 | 40 | 0 | 0 | 25 | 0 | 0 | 17 | 207 | 0 | 110 | 0 |  | 24 | 0 | 42 | 80 | 82 | 41 | 19 | 4 | 0 | 0 | 80 | 280 | 310 | 207 | 8 | 90 | 24 | 5 | 0 | 51 | 0 | 40 | 52 | 20 | 8 | 33 | 16 | 172 | 144 | 54 | 17 | 2 | 41 | 29 | 43 | 0 | 130 | 313 | 55 | 70 | 0 | 140 | 17 | 0 | 7 | 300 | 6 | 11 | 0 | 238 | 0 | 0 | 80 | 0 | 133 | 16 | 100 | 119 | 142 | 381 | 105 | 86 | 51 | 4 | 0 | 54 | 0 | 114 | 112 | 90 | 380 | 91 | 47 | 162 | 116 | 0 | 35 | 28 |  | 912 | 0 | 260 | 0 | 89 | 0 | 0 | 0 | 4 | 0 | 32 | 85 | 28 | 64 | 0 | 0 | 0 | 50 | 0 | 0 | 42 | 0 | 29 | 52 | 0 | 16 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 134 | 0 | 89 | 0 | 151 | 0 | 396 | 105 | 0 | 112 | 0 | 112 | 0 | 7 | 113 | 550 | 0 | 0 | 0 | 1 |  | 8654 | 3699 | 12353 | 4621 | 912 | 1821 | 3699 | 700 | 25 | 298 | 172 | 105 | 0 | 74.15
15:00 | 0 | 0 | 0 | 190 | 0 | 93 | 0 | 364 | 276 |  | 0 | 300 | 270 | 0 | 0 | 55 | 202 | 0 | 175 | 100 | 102 | 149 | 97 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 33 | 25 | 40 | 0 | 0 | 25 | 0 | 0 | 17 | 218 | 0 | 110 | 0 |  | 24 | 0 | 46 | 80 | 82 | 44 | 19 | 3 | 0 | 0 | 100 | 330 | 315 | 204 | 8 | 91 | 21 | 5 | 0 | 51 | 0 | 40 | 52 | 20 | 8 | 33 | 16 | 172 | 143 | 55 | 17 | 1 | 41 | 29 | 43 | 0 | 163 | 312 | 55 | 70 | 0 | 140 | 17 | 0 | 7 | 315 | 8 | 11 | 0 | 243 | 0 | 0 | 90 | 0 | 131 | 13 | 100 | 120 | 137 | 392 | 105 | 95 | 53 | 4 | 0 | 54 | 0 | 114 | 115 | 90 | 372 | 94 | 36 | 162 | 116 | 0 | 35 | 23 |  | 912 | 0 | 270 | 0 | 70 | 0 | 0 | 0 | 3 | 0 | 32 | 84 | 28 | 60 | 0 | 0 | 0 | 50 | 0 | 39 | 42 | 0 | 29 | 52 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 128 | 0 | 90 | 0 | 151 | 0 | 396 | 90 | 0 | 112 | 0 | 100 | 0 | 6 | 113 | 560 | 0 | 0 | 0 | 0 |  | 8933 | 3702 | 12635 | 4825 | 912 | 1864 | 3688 | 710 | 25 | 356 | 172 | 83 | 0 | 74.14
16:00 | 0 | 0 | 0 | 190 | 0 | 95 | 0 | 363 | 276 |  | 0 | 300 | 265 | 0 | 0 | 55 | 202 | 0 | 175 | 100 | 102 | 149 | 96 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 33 | 25 | 40 | 0 | 0 | 25 | 0 | 0 | 16 | 204 | 0 | 110 | 0 |  | 24 | 0 | 46 | 80 | 88 | 44 | 19 | 4 | 0 | 0 | 80 | 260 | 300 | 205 | 8 | 91 | 24 | 30 | 0 | 51 | 0 | 36 | 52 | 20 | 8 | 33 | 16 | 168 | 144 | 55 | 17 | 1 | 41 | 30 | 45 | 0 | 163 | 314 | 54 | 70 | 0 | 140 | 17 | 0 | 7 | 310 | 8 | 11 | 0 | 245 | 0 | 0 | 90 | 0 | 129 | 6 | 100 | 108 | 137 | 369 | 105 | 105 | 53 | 1 | 0 | 54 | 0 | 114 | 112 | 90 | 378 | 94 | 21 | 162 | 116 | 0 | 0 | 16 |  | 912 | 0 | 265 | 0 | 92 | 0 | 0 | 0 | 3 | 0 | 32 | 84 | 26 | 76 | 0 | 0 | 0 | 50 | 10 | 48 | 42 | 16 | 29 | 52 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 107 | 0 | 126 | 0 | 90 | 30 | 150 | 0 | 399 | 105 | 0 | 112 | 0 | 104 | 0 | 6 | 113 | 580 | 0 | 0 | 0 | 1 |  | 8747 | 3838 | 12585 | 4686 | 912 | 1891 | 3750 | 730 | 25 | 371 | 168 | 52 | 0 | 74.13
17:00 | 0 | 0 | 0 | 190 | 0 | 101 | 0 | 330 | 278 |  | 0 | 300 | 235 | 0 | 0 | 55 | 203 | 0 | 144 | 100 | 64 | 98 | 63 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 33 | 25 | 40 | 0 | 0 | 25 | 0 | 0 | 8 | 205 | 0 | 110 | 0 |  | 23 | 0 | 46 | 80 | 93 | 44 | 19 | 6 | 0 | 0 | 80 | 260 | 300 | 208 | 8 | 87 | 24 | 30 | 0 | 51 | 0 | 45 | 52 | 19 | 8 | 33 | 16 | 166 | 144 | 62 | 17 | 0 | 41 | 28 | 46 | 0 | 163 | 322 | 57 | 70 | 0 | 140 | 17 | 0 | 7 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 90 | 0 | 132 | 3 | 100 | 104 | 142 | 369 | 105 | 104 | 53 | 0 | 0 | 54 | 0 | 70 | 113 | 100 | 385 | 95 | 10 | 162 | 116 | 0 | 0 | 7 |  | 912 | 0 | 265 | 0 | 88 | 0 | 0 | 0 | 6 | 0 | 8 | 84 | 27 | 80 | 0 | 0 | 0 | 50 | 46 | 47 | 42 | 16 | 29 | 52 | 10 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 126 | 0 | 80 | 0 | 145 | 0 | 353 | 105 | 0 | 112 | 0 | 108 | 0 | 4 | 70 | 530 | 0 | 0 | 0 | 0 |  | 8452 | 3679 | 12131 | 4640 | 912 | 1827 | 3480 | 680 | 25 | 377 | 166 | 24 | 0 | 74.12
18:00 | 0 | 0 | 0 | 190 | 0 | 54 | 0 | 314 | 276 |  | 0 | 300 | 275 | 0 | 0 | 55 | 161 | 0 | 152 | 70 | 64 | 98 | 30 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 14 | 33 | 8 | 40 | 0 | 0 | 25 | 0 | 0 | 8 | 207 | 0 | 110 | 0 |  | 0 | 0 | 51 | 50 | 95 | 45 | 19 | 2 | 0 | 0 | 0 | 280 | 320 | 0 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 48 | 52 | 19 | 8 | 33 | 16 | 146 | 94 | 62 | 17 | 0 | 41 | 28 | 13 | 0 | 130 | 291 | 30 | 0 | 0 | 100 | 17 | 0 | 7 | 280 | 16 | 0 | 0 | 190 | 0 | 0 | 80 | 0 | 133 | 0 | 40 | 102 | 0 | 328 | 105 | 70 | 53 | 0 | 0 | 54 | 0 | 34 | 65 | 40 | 340 | 60 | 2 | 108 | 116 | 0 | 0 | 2 |  | 911 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 6 | 0 | 0 | 84 | 25 | 80 | 0 | 0 | 0 | 50 | 46 | 48 | 42 | 16 | 29 | 25 | 37 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 128 | 0 | 51 | 0 | 145 | 0 | 348 | 53 | 0 | 35 | 0 | 70 | 0 | 2 | 35 | 500 | 0 | 0 | 0 | 0 |  | 6977 | 3404 | 10381 | 4048 | 911 | 1504 | 2678 | 650 | 25 | 413 | 146 | 6 | 0 | 74.11
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 190 | 0 | 90 | 0 | 317 | 272 |  | 0 | 300 | 260 | 0 | 0 | 55 | 203 | 0 | 178 | 74 | 70 | 150 | 45 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 16 | 40 | 0 | 0 | 25 | 0 | 0 | 12 | 204 | 0 | 80 | 0 |  | 15 | 0 | 68 | 50 | 97 | 50 | 19 | 10 | 0 | 0 | 0 | 305 | 315 | 20 | 0 | 86 | 26 | 0 | 0 | 2 | 0 | 48 | 52 | 21 | 8 | 33 | 16 | 174 | 94 | 62 | 17 | 0 | 42 | 28 | 35 | 0 | 130 | 316 | 55 | 75 | 0 | 140 | 17 | 0 | 7 | 310 | 16 | 0 | 160 | 200 | 287 | 45 | 94 | 90 | 149 | 0 | 40 | 104 | 0 | 356 | 105 | 90 | 53 | 0 | 0 | 54 | 0 | 114 | 94 | 10 | 360 | 77 | 0 | 135 | 116 | 0 | 0 | 0 |  | 913 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 12 | 0 | 32 | 87 | 35 | 97 | 0 | 0 | 0 | 50 | 46 | 92 | 42 | 16 | 30 | 43 | 36 | 18 | 0 | 11 | 0 | 0 | 150 | 12 | 8 | 85 | 0 | 131 | 0 | 76 | 14 | 148 | 0 | 340 | 70 | 50 | 41 | 0 | 113 | 0 | 0 | 80 | 510 | 0 | 0 | 18 | 0 |  | 8314 | 3790 | 12104 | 4321 | 913 | 1700 | 3759 | 660 | 25 | 552 | 174 | 0 | 0 | 74.08
19:30 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 394 | 272 |  | 0 | 300 | 260 | 0 | 0 | 55 | 150 | 0 | 178 | 90 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 16 | 40 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 110 | 0 |  | 24 | 0 | 68 | 70 | 97 | 50 | 19 | 14 | 0 | 0 | 0 | 0 | 300 | 135 | 0 | 86 | 0 | 0 | 0 | 0 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 178 | 85 | 63 | 17 | 0 | 42 | 30 | 47 | 0 | 163 | 327 | 56 | 72 | 0 | 140 | 17 | 0 | 7 | 290 | 16 | 11 | 194 | 215 | 299 | 50 | 190 | 98 | 149 | 0 | 40 | 103 | 0 | 368 | 105 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 120 | 10 | 388 | 95 | 0 | 162 | 116 | 0 | 25 | 0 |  | 912 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 13 | 0 | 32 | 85 | 35 | 110 | 0 | 0 | 0 | 50 | 46 | 98 | 42 | 43 | 30 | 52 | 22 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 5 | 104 | 0 | 129 | 0 | 94 | 99 | 144 | 0 | 315 | 105 | 100 | 112 | 0 | 0 | 0 | 0 | 113 | 550 | 0 | 0 | 81 | 0 |  | 8627 | 4099 | 12726 | 4208 | 912 | 1727 | 4436 | 700 | 25 | 540 | 178 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 190 | 0 | 103 | 0 | 391 | 272 |  | 0 | 300 | 255 | 0 | 0 | 55 | 209 | 0 | 125 | 94 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 24 | 0 | 53 | 75 | 97 | 50 | 19 | 19 | 0 | 0 | 0 | 0 | 300 | 135 | 0 | 88 | 23 | 0 | 0 | 0 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 176 | 82 | 63 | 19 | 0 | 42 | 30 | 47 | 0 | 163 | 325 | 51 | 75 | 0 | 140 | 17 | 0 | 7 | 280 | 16 | 11 | 200 | 245 | 262 | 50 | 191 | 98 | 149 | 0 | 70 | 104 | 0 | 368 | 105 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 120 | 20 | 394 | 96 | 0 | 162 | 116 | 0 | 17 | 0 |  | 912 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 86 | 29 | 110 | 0 | 0 | 0 | 50 | 50 | 96 | 42 | 43 | 31 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 8 | 8 | 105 | 0 | 130 | 0 | 92 | 99 | 144 | 0 | 296 | 105 | 100 | 110 | 0 | 70 | 0 | 0 | 113 | 570 | 0 | 0 | 81 | 0 |  | 8687 | 4182 | 12869 | 4248 | 912 | 1703 | 4543 | 720 | 25 | 542 | 176 | 0 | 0 | 74.09
21:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 391 | 272 |  | 0 | 300 | 240 | 0 | 0 | 55 | 208 | 0 | 179 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 25 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 110 | 0 |  | 24 | 0 | 45 | 75 | 75 | 50 | 19 | 30 | 0 | 0 | 0 | 0 | 300 | 136 | 35 | 86 | 26 | 5 | 0 | 0 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 160 | 99 | 62 | 17 | 0 | 42 | 30 | 48 | 0 | 163 | 329 | 51 | 77 | 0 | 140 | 17 | 0 | 7 | 290 | 16 | 11 | 200 | 243 | 303 | 90 | 191 | 100 | 149 | 0 | 100 | 103 | 0 | 368 | 106 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 121 | 100 | 396 | 96 | 0 | 162 | 116 | 0 | 0 | 0 |  | 913 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 50 | 51 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 8 | 0 | 107 | 0 | 133 | 0 | 93 | 100 | 146 | 0 | 390 | 105 | 175 | 112 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 81 | 0 |  | 8944 | 4413 | 13357 | 4330 | 913 | 1868 | 4806 | 730 | 25 | 525 | 160 | 0 | 0 | 74.08
22:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 389 | 273 |  | 0 | 300 | 255 | 0 | 0 | 55 | 210 | 0 | 180 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 25 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 110 | 0 |  | 25 | 0 | 17 | 75 | 27 | 25 | 19 | 34 | 0 | 0 | 0 | 90 | 300 | 137 | 83 | 86 | 26 | 24 | 0 | 2 | 0 | 40 | 52 | 21 | 8 | 33 | 20 | 168 | 116 | 62 | 17 | 0 | 42 | 30 | 48 | 0 | 163 | 330 | 51 | 77 | 0 | 120 | 17 | 0 | 7 | 260 | 16 | 11 | 200 | 245 | 165 | 28 | 191 | 52 | 149 | 0 | 100 | 103 | 38 | 368 | 115 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 119 | 100 | 397 | 94 | 0 | 162 | 116 | 0 | 21 | 0 |  | 912 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 87 | 29 | 110 | 0 | 0 | 0 | 50 | 50 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 142 | 0 | 0 | 107 | 0 | 134 | 0 | 98 | 100 | 172 | 0 | 388 | 105 | 195 | 112 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 81 | 0 |  | 8813 | 4430 | 13243 | 4448 | 912 | 1910 | 4588 | 712 | 25 | 480 | 168 | 0 | 0 | 74.07
23:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 390 | 273 |  | 0 | 300 | 280 | 0 | 0 | 55 | 210 | 0 | 180 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 24 | 0 | 17 | 75 | 25 | 25 | 19 | 34 | 0 | 0 | 0 | 70 | 300 | 136 | 83 | 91 | 26 | 41 | 0 | 41 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 162 | 133 | 62 | 17 | 0 | 42 | 30 | 48 | 0 | 163 | 326 | 51 | 77 | 0 | 120 | 0 | 0 | 7 | 280 | 16 | 11 | 200 | 245 | 155 | 25 | 190 | 52 | 144 | 0 | 100 | 103 | 10 | 368 | 115 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 118 | 100 | 394 | 94 | 0 | 162 | 116 | 0 | 35 | 0 |  | 912 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 87 | 35 | 110 | 0 | 0 | 0 | 50 | 50 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 105 | 0 | 139 | 0 | 97 | 100 | 189 | 0 | 401 | 105 | 200 | 112 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 35 | 0 |  | 8874 | 4425 | 13299 | 4454 | 912 | 2003 | 4535 | 720 | 25 | 488 | 162 | 0 | 0 | 74.06
24:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 391 | 302 |  | 0 | 300 | 265 | 0 | 0 | 55 | 214 | 0 | 180 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 24 | 0 | 17 | 86 | 25 | 25 | 19 | 24 | 0 | 0 | 0 | 20 | 300 | 136 | 83 | 91 | 26 | 45 | 0 | 51 | 0 | 40 | 52 | 21 | 8 | 33 | 17 | 166 | 101 | 62 | 17 | 0 | 42 | 30 | 49 | 0 | 110 | 326 | 50 | 77 | 0 | 120 | 0 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 186 | 50 | 190 | 100 | 149 | 0 | 100 | 103 | 10 | 367 | 115 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 114 | 100 | 391 | 94 | 0 | 162 | 116 | 0 | 35 | 0 |  | 913 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 88 | 35 | 110 | 0 | 0 | 0 | 50 | 45 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 104 | 0 | 139 | 0 | 96 | 100 | 187 | 0 | 411 | 105 | 200 | 112 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 35 | 0 |  | 8887 | 4428 | 13315 | 4367 | 913 | 2013 | 4636 | 720 | 25 | 475 | 166 | 0 | 0 | 74.05
KWH | 0 | 0 | 0 | 4284000 | 0 | 2262363 | 0 | 8626170 | 7352000 |  | 0 | 7124500 | 6454720 | 0 | 0 | 1301664 | 4927439 | 0 | 4026000 | 2356848 | 1728000 | 2432640 | 1102058 | 0 | 0 | 0 | 852840 | 972309 | 1288334 | 401976 | 600000 | 411660 | 759600 | 584300 | 975840 | 0 | 0 | 604000 | 0 | 0 | 384480 | 3526077 | 0 | 2679325 | 0 |  | 554640 | 0 | 679907 | 1878720 | 1059840 | 653760 | 441888 | 453600 | 0 | 0 | 1462628 | 5850500 | 7147000 | 4173000 | 384727 | 2124960 | 527256 | 681 | 0 | 955716 | 0 | 561616 | 1242211 | 483084 | 172980 | 807200 | 406730 | 3882240 | 3164440 | 1358400 | 352368 | 12050 | 993000 | 618960 | 1025400 | 0 | 3613091 | 7359000 | 1295136 | 1711680 | 0 | 3245140 | 364000 | 0 | 148320 | 7437500 | 316616 | 253000 | 1191936 | 3831380 | 1136714 | 268454 | 3283200 | 493763 | 3454128 | 138510 | 2247360 | 2523360 | 2294981 | 9095000 | 2562000 | 2017200 | 1298872 | 34080 | 0 | 1298407 | 116254 | 1826280 | 2766960 | 1963200 | 9012300 | 1996800 | 336000 | 3365280 | 2634545 | 0 | 708480 | 247442 |  | 22030545 | 0 | 6907104 | 0 | 1895040 | 0 | 0 | 0 | 147360 | 0 | 475875 | 2065252 | 703356 | 1903104 | 0 | 0 | 0 | 776154 | 354409 | 1115432 | 547730 | 282374 | 353800 | 1192320 | 295599 | 447360 | 0 | 235890 | 0 | 0 | 3666400 | 23000 | 15000 | 2879600 | 0 | 3471400 | 0 | 2165647 | 870720 | 4138018 | 0 | 9453000 | 2270880 | 811837 | 2357952 | 0 | 2372160 | 0 | 54287 | 1787328 | 14308800 | 0 | 0 | 799200 | 19260 |  | 199335014 | 93193193 | 292528207 | 110189997 | 22030545 | 45238941 | 85010738 | 17975200 | 604000 | 6754917 | 3882240 | 841629 | 0
Fuel Cost | 0 | 0 | 0 | 6297480 | 0 | 2986319.16 | 0 | 8712431.7 | 7572560 |  | 0 | 7765705 | 7164739.2 | 0 | 0 | 11012077.44 | 5124536.56 | 0 | 6964980 | 17747065.44 | 15759360 | 23937177.6 | 10160974.76 | 0 | 0 | 0 | 6225732 | 7515948.57 | 12702973.24 | 301482 | 450000 | 0 | 0 | 0 | 9436372.8 | 0 | 0 | 163080 | 0 | 0 | 3571819.2 | 3843423.93 | 0 | 4554852.5 | 0 |  | 0 | 0 | 6595097.9 | 17941776 | 9220608 | 5177779.2 | 556778.88 | 1347192 | 0 | 0 | 2150063.16 | 4329370 | 7147000 | 3839160 | 496297.83 | 2443704 | 595799.28 | 953.4 | 0 | 1634274.36 | 0 | 5672321.6 | 11863115.05 | 613516.68 | 129735 | 1412600 | 305047.5 | 29116800 | 3354306.4 | 12334272 | 447507.36 | 192077 | 1628520 | 990336 | 1825212 | 0 | 4118923.74 | 7653360 | 2551417.92 | 3269308.8 | 0 | 5614092.2 | 797160 | 0 | 302572.8 | 7511875 | 237462 | 192280 | 20274831.36 | 28965232.8 | 19301403.72 | 4488550.88 | 17072640 | 8255717.36 | 33988619.52 | 1619181.9 | 18315984 | 27378456 | 16179616.05 | 8458350 | 23365440 | 19062540 | 11313175.12 | 0 | 0 | 11309124.97 | 1021872.66 | 18226274.4 | 23712847.2 | 13074912 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 126895939.2 | 0 | 7252459.2 | 0 | 14895014.4 | 0 | 0 | 0 | 1545806.4 | 0 | 4958617.5 | 2333734.76 | 1090201.8 | 18574295.04 | 0 | 0 | 0 | 7637355.36 | 3600795.44 | 9871573.2 | 4217521 | 3817696.48 | 3428322 | 11553580.8 | 2867310.3 | 858931.2 | 0 | 178568.73 | 0 | 0 | 19871888 | 796950 | 427950 | 3369132 | 0 | 4582248 | 0 | 3248470.5 | 14810947.2 | 4841481.06 | 0 | 9358470 | 23707987.2 | 13809347.37 | 22376964.48 | 0 | 18407961.6 | 0 | 599871.35 | 13208353.92 | 62815632 | 0 | 0 | 0 | 0 |  | 670965534.1 | 441811377.49 | 1112776911.59 | 114254376.82 | 126895939.2 | 53387267.59 | 637480137.93 | 82687520 | 163080 | 66380659.8 | 29116800 | 2411130.25 | 0
Yesterday Day Peak | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 344 | 276 |  | 0 | 300 | 280 | 0 | 0 | 55 | 208 | 0 | 178 | 100 | 95 | 98 | 27 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 16 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 110 | 0 |  | 15 | 0 | 51 | 80 | 57 | 19 | 19 | 3 | 0 | 0 | 80 | 350 | 265 | 210 | 8 | 90 | 23 | 5 | 0 | 43 | 0 | 0 | 52 | 19 | 8 | 33 | 14 | 162 | 145 | 54 | 17 | 1 | 41 | 30 | 44 | 0 | 163 | 316 | 60 | 72 | 0 | 140 | 17 | 0 | 5 | 310 | 6 | 11 | 0 | 200 | 0 | 0 | 80 | 0 | 133 | 18 | 100 | 120 | 150 | 367 | 105 | 86 | 51 | 5 | 0 | 54 | 0 | 52 | 115 | 90 | 384 | 95 | 17 | 162 | 116 | 0 | 35 | 33 |  | 912 | 0 | 260 | 0 | 80 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 26 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 114 | 0 | 132 | 0 | 89 | 0 | 150 | 0 | 398 | 90 | 0 | 112 | 0 | 113 | 0 | 6 | 113 | 540 | 0 | 0 | 0 | 1 |  | 12021 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 391 | 272 | 0 | 0 | 300 | 240 | 0 | 0 | 55 | 208 | 0 | 179 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 25 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 110 | 0 | 0 | 24 | 0 | 45 | 75 | 75 | 50 | 19 | 30 | 0 | 0 | 0 | 0 | 300 | 136 | 35 | 86 | 26 | 5 | 0 | 0 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 160 | 99 | 62 | 17 | 0 | 42 | 30 | 48 | 0 | 163 | 329 | 51 | 77 | 0 | 140 | 17 | 0 | 7 | 290 | 16 | 11 | 200 | 243 | 303 | 90 | 191 | 100 | 149 | 0 | 100 | 103 | 0 | 368 | 106 | 105 | 53 | 0 | 0 | 54 | 0 | 114 | 121 | 100 | 396 | 96 | 0 | 162 | 116 | 0 | 0 | 0 |  | 913 | 0 | 290 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 87 | 34 | 110 | 0 | 0 | 0 | 50 | 51 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 8 | 0 | 107 | 0 | 133 | 0 | 93 | 100 | 146 | 0 | 390 | 105 | 175 | 112 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 81 | 0 |  | 13357 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 190 | 0 | 102 | 0 | 390 | 360 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 185 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 220 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 50 | 20 | 25 | 0 | 0 | 100 | 330 | 330 | 215 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 181 | 160 | 64 | 19 | 0 | 42 | 30 | 44 | 0 | 163 | 330 | 57 | 76 | 0 | 140 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 125 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 0 | 162 | 116 | 0 | 36 |  |  | 909 | 0 | 410 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 35 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 125 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 50 |  | 110
Forecast for Day | 0 | 0 | 0 | 190 | 0 | 100 | 0 | 360 | 360 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 180 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 220 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 50 | 20 | 10 | 0 | 0 | 80 | 330 | 330 | 215 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 145 | 160 | 64 | 19 | 1.6 | 42 | 30 | 44 | 0 | 163 | 330 | 57 | 76 | 0 | 140 | 18 | 0 | 7 | 341 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 0 | 149 | 20 | 100 | 125 | 150 | 400 | 115 | 105 | 70 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 50 | 162 | 116 | 0 | 35 | 30 |  | 909 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 43 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 125 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 50 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 25 | 0 | 329 | 308 | 0 | 0 | 300 | 265 | 0 | 0 | 55 | 160 | 0 | 120 | 100 | 24 | 115 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 20 | 25 | 20 | 33 |  | 42 | 0 | 0 | 25 | 0 | 0 | 17 | 229 | 0 | 120 | 0 | 0 | 24 | 0 | 0 | 80 | 77 | 50 | 19 | 6 | 0 | 0 | 0 | 235 | 275 | 51 | 83 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 140 | 154 | 63 | 19 | 1 | 42 | 30 | 50 | 0 | 130 | 308 | 51 | 78 | 0 | 120 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 85 | 0 | 0 | 80 | 0 | 149 | 0 | 100 | 102 | 10 | 338 | 115 | 88 | 0 | 3 | 53 | 0 | 0 | 0 | 115 | 50 | 360 | 95 | 26 | 162 | 0 | 0 | 35 | 15 | 0 | 892 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 117 | 0 | 154 | 0 | 94 | 0 | 190 | 0 | 339 | 105 | 0 | 35 | 0 | 112 | 0 | 2 | 35 | 510 | 0 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 10560 | 7:00
| Highest Generation |  | 13357 | 21:00
| Day Peak Generation |  | 12021 | 12:00
| Evening Peak Generation |  | 13357 | 21:00
| HVDC Max Flow |  | 916 | 1:00
| HVDC EvPeak Flow |  | 913 | 21:00
| Load factor L.F |  | 91.25%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-24
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 12021 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10785 | MW
Evening Peak Generation : |  | 13357 | MW Hour : | 21:00 | Available Max Generation : |  | 15881 | MW
E.P. Demand (at gen end) : |  | 13357 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 14500 | MW
Maximum Generation : |  | 13357 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1381 | MW
Total Gen. (MKWH) : |  | 292.5282 | System Load Factor : | 91.25% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -200 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-24
Actual : | 73.99 | Ft.(MSL) , | Rule curve : | 77.6 | Ft.( MSL )
Gas Consumed : | Total = | 1271.343 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 167641644.41
: |  | Coal : | 82687520 | Oil : | 703860797.73 | Total : | 954189962.14
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 5109.6991 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1746.0033 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1565.8619 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1415.4212 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1278.8018 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 1031.969 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 566.1875 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 265.4174 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 795.9576 |  |  | 0 | 0%
Total | 0 |  | 13775.3187 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Bogura 132/33 kV T-4 transformer was under shut down from 08:09 to 10:57 due to R/H maintenance
at 33 kV B-phase CT connection.
b) Dohazari-Cox's Bazar 132 kV Ckt was under shut down from 08:34 to 10:13 for D/W.
c) Mymensingh 132/33 kV T-3 transformer was under shut down from 09:17 to 12:38 due to R/H maintenance.
d) Savar 132/33 kV T-3 transformer was under shut down from 08:32 to 17:07 for C/M.
e) Halishahar-Khulshi 132 kV Ckt-3 is under shut down since 10:35 for D/W.
f) Kodda 132/33 kV T-4 transformer was switched on at 11:58.
g) Jamalpur-Mymensingh 132 kV Ckt-1 was under shut down from 07:37 to 19:04 for C/M.
h) Sikalbaha-Anwara united 300 MW P/P 230 kV Ckt-2 was under shut down from 06:21 to 17:46 for D/W.
i) Kabirpur 132/33 kV T-1 transformer was under shut down from 15:35 to 16:37 due to R/H maintenance.
j) Dohazari-Cox's Bazar 132 kV Ckt-2 tripped at 18:06 from Dohazari end showing dist. Z2 and was switched
on at 18:25.
k) Hathazari-Baroirhat 132 kV Ckt-2 tripped at 17:28 from Hathazari end showing dist. C-phase, O/C and
was switched on at 17:44.
l) Natore 132/33 kV T-4 transformer was under shut down from 14:50 to 16:02 for D/W.
m) Ishwardi-Bheramara 132 kV Ckt-1 tripped at 21:10 from Ishwardi end showing dist. C-phase, O/C and
was switched on at 21:37.
n) Ishwardi 132/33 kV T-1 transformer tripped at 21:10 due to 33 kV BPS feeder fault showing self protection,
REF and was switched on at 22:11.
o) Ghorashal-Ishwardi 230 kV Ckt-2 was under shut down from 14:46 to 17:18 due to fire at Tongi area.
p) Ashuganj U-5 auxiliary transformer OAT-3 R-phase CT burst at 17:54. At the same time Ashuganj OAT-12,
Ashuganj-Ghorashal 132 kV both Ckts, Ashuganj-B.Baria 132 kV both Ckts, Ashuganj-Shahzibazar 132 kV
Ckt-3, Ashuganj 225 MW, Ashuganj Precision 55 MW, Ashuganj TSK, Ashuganj Modular, Ashuganj
Midland 150 MW & 55 MW, Shahzibazar 86 MW, Ashuganj unit-5 & Mymensingh RPCL ST got tripped.
q) All 132 kV Ckts including OAT-12 were normalized at 18:40.
r) All power plant and Ckts connected to APSCL 230 kV Bus were tripped at 19:07 due to B-phase CT
burst. At the same time Ashuganj North P.P. & Ashuganj(S)-Ghorashal got tripped.
s) Ashuganj-Sirajganj 230 kV Ckt-1 & Ckt-2 were switched on at 19:52 & 20:04 respectively.
t) Ashuganj-Cumilla(N) 230 kV Ckt-2 was switched on at 20:01.
u) Ashuganj OAT-12 Transformer was switched on at 20:30. |  |  |  |  | About 250 MW power interruption was imposed to control line load
v) Ashuganj(N) GT was synchronized at 21:25. |  |  |  |  | and voltage at Mymensingh & Ghorashal area.
w) Mymensingh RPCL ST was synchronized at 21:57.
x) Ashuganj-Ghorashal 230 kV Ckt-2 was switched on at 07:08(24/05/2021).
y) Dhamrai 132/33 kV T-1 transformer was under shut down from 06:05(24/05/2021) to 07:11(24/05/2021) for C/M.
z) Halishahar-Julda 132 kV Ckt is under shut down since 06:45(24/05/2021) for D/W.
aa) Kishoreganj 132/33 kV T-1 & T-2 transformers tripped at 00:30(24-05-2021) showing O/C, A,B-phases |  |  |  |  | About 90 MW power interruption occurred under Kishoreganj S/S area
relays due to 33 kV feeder fault and was switched on at 00:42(24-05-2021). |  |  |  |  | from 00:30(24-05-2021) to 00:42(24-05-2021).
ab) Munshiganj 132/33 kV T-1 & 33 kV Bus-1 transformer was under shut down from 06:40(24/05/2021) to |  |  |  |  | About 15 MW power interruption occurred under Munshiganj S/S area
09:25(24/05/2021) for C/M. |  |  |  |  | from 06:40(24-05-2021) to 09:25(24-05-2021).
ac) Sikalbaha-Anwara united 300 MW P/P 230 kV Ckt-1 is under shut down since 07:12(24/05/2021) for D/W.
ad) Purbasadipur-Thakurgaon 132 kV Ckt-1 is under shut down since 05:56(24/05/2021) for C/M.
ae) Chandraghona 132/33 kV T-2 transformer was under shut down from 07:26(24/05/2021) to
07:36(24/05/2021) for BPDB work.
af) Dhamrai 132/33 kV T-2 transformer was under shut down from 07:14(24/05/2021) to 09:23(24/05/2021) for C/M.
ag) Jamalpur-Mymensing 132 kV Ckt-1 is under shut down since 07:40(24/05/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4284000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 104 | 2262363
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 8626170 | Machine problem
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 272 | 7352000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7124500 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6454720 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1301664
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 85 | 1102058 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 401976 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 179 | 4026000 | Gas shortage.
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2356848
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 208 | 4927439 | ST under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1728000
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 852840 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2432640
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 972309
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1288334
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 44 | 1011660 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 759600
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 584300 | Engine problem
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 41 | 975840 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 243 | 3831380 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 303 | 1136714
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 90 | 268454 | Engine problem
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 493763
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3454128
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2017200
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 96 | 1996800
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3365280
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 247442
| Dhaka area Total |  |  |  | 5919 | 3921 | 77636422
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 384480 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138510
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 653760
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 604000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 202 | 3526077 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2679325
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 53 | 1298872
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 45 | 679907 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 75 | 1878720 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2247360
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 441888
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 30 | 453600
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 75 | 1059840 | Line over load.
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34080
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1298407
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 0 | 116254 | Reserve.
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1963200
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2634545
| Chattogram area Total |  |  |  | 2382 | 1071 | 22092825
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 1462628 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 136 | 4173000 | Synchronized at .
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 0 | 5850500 | Tripped at 19:07.
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7147000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 527256 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 681 | Synchronized at 20:10.
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 35 | 384727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 0 | 955716 | Tripped at 17:54.
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 2294981 | Tripped at 17:56.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 561616
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 86 | 2124960 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 103 | 2523360 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 483084
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 172980 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 160 | 3882240
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 807200
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1242211
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 406730 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1191936
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1826280
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 121 | 2766960
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 0 | 708480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1468 | 41494526
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 99 | 3164440 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 352368 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 62 | 1358400 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12050
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 191 | 3283200
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 2562000
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 336000
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 554640
| Mymensingh Area Total |  |  |  | 709 | 499 | 11623098
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 993000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 618960 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3613091
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 329 | 7359000
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 48 | 1025400
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 253000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1295136 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1711680 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3245140
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 364000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 316616 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7437500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 368 | 9095000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 148320 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 396 | 9012300 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1985 | 46488143
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 913 | 22030545
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 1895040 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 147360 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 290 | 6907104 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 475875 | Engine problem
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 870720
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2270880
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1554 | 34597524
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1903104
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 703356
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2065252 | Engine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 93 | 2165647
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 14308800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 0 | 0 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 81 | 799200 | Line over load.
| Barisal Area Total |  |  |  | 1826 | 985 | 21945359
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 776154
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 51 | 354409
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 547730 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 282374 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 353800 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 107 | 2879600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 133 | 3471400 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 146 | 4138018 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 390 | 9453000 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 295599 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 447360
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 235890
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1192320
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1115432
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 175 | 811837
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 2357952
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1787328
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 19260
| Rajshahi Area Total |  |  |  | 2179 | 1603 | 30519463
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3666400 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 23000 | Engine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 15000 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2372160
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 54287
| Rangpur Area Total |  |  |  | 605 | 271 | 6130847
| Total |  |  |  | 21315 | 13357 | 292528207
| Eastern Grid Total |  |  |  | 14421 | 8944 | 199335014
| Western Grid Total |  |  |  | 6894 | 4413 | 93193193
| National Grid Total |  |  |  | 21315 | 13357 | 292528207
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-23
(a) ENTIRE EASTERN GRID : |  | 8444 | MW | (b) ENTIRE WESTERN GRID : |  | 4235 | MW
i) Dhaka area |  | 4570 | MW | i) Khulna area |  | 1689 | MW
ii) Chittagong area |  | 1111 | MW | ii) Rajshahi area |  | 1403 | MW
iii) Comilla area |  | 1262 | MW | iii) Barisal area |  | 397 | MW
iv) Mymensingh area |  | 936 | MW | iv) Rangpur area |  | 746 | MW
v) Sylhet area |  | 565 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12679 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 15:00 | Kishoreganj | 130 | 22:00 | Benapol | 70 | 22:00
Munsiganj | 112 | 22:00 | Netrokona | 118 | 2:00 | Jhenida | 119 | 20:00
Sonargaon | 80 | 22:00 | Jamalpur | 163 | 19:30 | Bottail | 148 | 20:00
Shyampur | 184 | 0:00 | Sherpur | 140 | 22:00 | G.K Project | 64 | 21:00
Bhulta | 188 | 22:00 | Srimongal | 65 | 21:00 | Faridpur | 220 | 22:00
Madanganj | 49 | 1:00 | Shahjibazar | 135 | 22:00 | Madaripur | 129 | 22:00
Shitalakhya | 117 | 16:00 | Fenchuganj | 53 | 19:30 | Sariatpur | 84 | 22:00
Rahim steel | 30 | 12:00 | Kulawara | 50 | 20:00 | Gopalganj | 108 | 22:00
Matuail | 57 | 15:00 | Sylhet | 139 | 20:00 | Bagerhat | 113 | 21:00
Ghorasal | 79 | 20:00 | Chatak | 33 | 20:00 | Mongla | 38 | 23:00
Narsingdi | 169 | 20:00 | Sunamganj | 54 | 21:00 | Satkhira | 125 | 20:00
Haripur (SBU) | 115 | 20:00 | Biani Bazar | 80 | 22:00 | Gallamari | 46 | 13:00
Sreenagar | 48 | 21:00 | Comilla (S) | 178 | 19:30 | Magura | 56 | 1:00
Ullon | 82 | 24:00 | Comilla(N) | 157 | 19:30 | Norail | 44 | 19:30
Hasnabad | 89 | 23:00 | Chandpur | 88 | 21:00 | Chuadanga | 97 | 19:30
Magbazar | 114 | 15:00 | Feni | 134 | 19:30 | Borguna | 22 | 1:00
Maniknagar | 76 | 14:00 | Chowmuhani | 204 | 1:00 | Barisal(N) | 56 | 23:00
Bangabhaban | 14 | 10:00 | Ashuganj | 37 | 1:00 | Barisal (S) | 128 | 22:00
Motijheel | 16 | 11:00 | Daudkandi | 172 | 21:00 | Patuakhali | 131 | 21:00
Narinda | 56 | 12:00 | B.Baria | 164 | 1:00 | Bhandaria | 62 | 21:00
Kazla | 72 | 23:00 | Ramganj | 114 | 1:00 | Borhan Uddin | 47 | 2:00
Dhanmondi | 219 | 13:00 | Chaddagram | 54 | 19:00 | Ishurdi | 70 | 19:00
Lalbag | 78 | 16:00 | PHP | 10 | 21:00 | Ruppur Paromanobik | 4 | 18:00
Madartek | 86 | 23:00 | Kochua | 78 | 21:00 | Natore | 160 | 21:00
Dhaka University | 49 | 11:00 | Madunaghat | 64 | 17:00 | Bogra | 165 | 21:00
Aftabnagar | 12 | 15:00 | Hathazari | 99 | 19:00 | Noagaon | 130 | 21:00
Fatullah | 56 | 9:00 | Khulshi | 215 | 14:00 | Rajshahi | 155 | 20:00
Nawabganj | 57 | 21:00 | Halishahar | 155 | 14:00 | Rajshahi New | 23 | 21:00
Keraniganj | 64 | 19:00 | Baraulia | 153 | 23:00 | C.Nawabganj | 71 | 21:00
Mirpur | 130 | 19:00 | Sikalbaha | 35 | 14:00 | Amnura | 43 | 21:00
Kalyanpur | 129 | 19:00 | Dohazari | 90 | 1:00 | Pabna | 104 | 20:00
Gulshan | 158 | 13:00 | Cox'sbazar | 94 | 1:00 | Shahjadpur | 107 | 21:00
Uttara | 109 | 11:00 | Chandraghona | 32 | 13:00 | Serajganj | 102 | 21:00
Uttara New | 34 | 19:00 | Kaptai | 4.3 | 19:00 | Niyamatpur | 77 | 1:00
Kamrangirchar | 88 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 66 | 21:00
Savar | 183 | 19:00 | Bakulia | 116 | 19:30 | Sherpur(Bogura) | 64 | 21:00
Bhasantec | 178 | 10:00 | Julda | 22 | 10:00 | Mohastangor | 74 | 19:30
Agargaon | 89 | 15:00 | TK chemical | 28.5 | 15:00 | Bhangura | 40 | 20:00
Satmosjid | 110 | 0:00 | Modern Steel |  |  | Rangpur | 123 | 1:00
Tongi | 132 | 11:00 | Shahmirpur | 27 | 1:00 | Lalmonirhat | 42 | 1:00
Kabirpur | 267 | 9:00 | Khagrachhari | 28 | 18:00 | Saidpur | 95 | 1:00
Basundhara | 193 | 15:00 | Matarbari | 34 | 1:00 | Purbasadipur | 117 | 19:30
Manikganj | 82 | 1:00 | Baroiar Hat | 50 | 19:00 | Thakurgaon | 83 | 21:00
Joydevpur | 198 | 15:00 | Rangamati | 12 | 12:00 | Palashbari | 114 | 1:00
New Tongi | 109 | 12:00 | Abul Khair 230 | 10 | 12:00 | Barapukuria | 59 | 21:00
Kodda | 252 | 19:00 | BSRM | 146 | 20:00 | Panchagar | 51 | 19:30
Dhamrai | 126 | 19:30 | GPH Ispat | 95 | 17:00 | Joldhaka | 64 | 21:00
Rajendrapur | 110 | 10:00 | Goalpara | 29 | 1:00 | Kurigram | 62 | 19:00
Valuka | 130 | 11:00 | Central s/s | 105 | 19:30 | Mithapukur | 45 | 1:00
Tangail | 228 | 19:30 | Noapara | 64 | 22:00
Mymensing | 212 | 1:00 | Jessore | 131 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 399 | 7:00 | 394 | 22:00 | Kaliakoir | 385 | 0.20833 | 378 | 0.375
| Bheramara | 392 | 5:00 | 383 | 24:00 | Bhulta | 388 | 0.083333 | 366 | 0.875
| Ashuganj(N) | 388 | 2:00 | 373 | 21:00 | Gopalganj | 400 | 0.625 | 380 | 0.79167
| Payra | 406 | 1:00 | 396 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 15:00 | Hathazari | 221 | 21:00 | 212 | 10:00
| Ishurdi | 234 | 9:00 | 224 | 19:00 | Megnaghat | 232 | 3:00 | 227 | 10:00
| Ashuganj | 235 | 1:00 | 0 | 19:30 | Fenchuganj | 237 | 1:00 | 232 | 23:00
| Serajganj | 232 | 4:00 | 0 | 19:30 | Siddhirganj | 229 | 2:00 | 223 | 10:00
| Baghabari | 233 | 16:00 | 224 | 1:00 | Maniknagar | 227 | 2:00 | 220 | 16:00
| Barapukuria | 233 | 20:00 | 223 | 21:00 | Agargaon | 225 | 5:00 | 217 | 11:00
| Bogra | 226 | 19:30 | 215 | 22:00 | Barisal | 248 | 22:00 | 236 | 15:00
| Rajshahi | 234 | 16:00 | 224 | 7:00 | Bhola 225 MW | 250 | 20:00 | 238 | 19:00
| Khulna South | 226 | 9:00 | 206 | 23:00 | AKSML | 222 | 22:00 | 212 | 15:00
| Rampura | 227 | 1:00 | 220 | 15:00 | BSRM | 223 | 18:30 | 214 | 16:00
| Haripur | 226 | 1:00 | 221 | 10:00 | Bibiyana | 237 | 2:00 | 233 | 12:00
| Hasnabad | 230 | 23:00 | 220 | 10:00 | Bhulta | 230 | 2:00 | 221 | 15:00
| Shyampur | 226 | 1:00 | 220 | 10:00 | Ashuganj (S) | 235 | 1:00 | 230 | 21:00
| Aminbazar | 226 | 1:00 | 218 | 2:00 | Kaliakoir | 227 | 1:00 | 220 | 9:00
| Tongi | 223 | 18:00 | 218 | 5:00 | GPH | 221 | 18:30 | 211 | 15:00
| Comilla (N) | 227 | 1:00 | 221 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 131 | 11:00 | Kochua | 131 | 0.79167 | 127 | 0.083333
| Munsiganj | 135 | 3:00 | 131 | 11:00 | Madanhat | 131 | 0.125 | 127 | 0.625
| Sonargaon | 134 | 19:00 | 130 | 4:00 | Hathazari | 133 | 0.875 | 127 | 0.41667
| Shyampur | 133 | 1:00 | 128 | 10:00 | Khulshi | 130 | 0.77083 | 123 | 0.375
| Bhulta | 128 | 5:00 | 122 | 16:00 | Halishahar | 133 | 0.875 | 125 | 0.41667
| Madanganj | 135 | 5:00 | 129 | 13:00 | Baraulia | 130 | 0.041667 | 124 | 0.45833
| Shitalakhya | 140 | 2:00 | 131 | 9:00 | Sikalbaha | 133 | 0.77083 | 127 | 0.45833
| Rahim steal | 135 | 1:00 | 131 | 11:00 | Dohazari | 135 | 0.77083 | 122 | 0.45833
| Matuail | 135 | 1:00 | 131 | 11:00 | Cox'sbazar | 131 | 0.875 | 107 | 0.54167
| Ghorasal | 140 | 18:00 | 136 | 8:00 | Chandraghona | 131 | 0.875 | 125 | 0.45833
| Narsinghdi | 131 | 7:00 | 124 | 22:00 | Kaptai | 130 | 0.75 | 125 | 0.54167
| Haripur (SBU) | 135 | 1:00 | 131 | 9:00 | A. Khaer Stl. | 130 | 0 | 124 | 0.66667
| Sreenagar | 130 | 19:00 | 123 | 10:00 | Bakulia | 133 | 0.875 | 126 | 0.45833
| Ullon | 131 | 6:00 | 123 | 16:00 | Julda | 133 | 0.75 | 127 | 0.45833
| Hasnabad | 136 | 1:00 | 130 | 8:00 | TK Chemical | 133 | 0.875 | 126 | 0.41667
| Magbazar | 131 | 4:00 | 122 | 14:00 | Modern Steel
| Maniknagar | 137 | 1:00 | 131 | 15:00 | Shahmirpur | 134 | 0.875 | 127 | 0.41667
| Bangabhaban | 137 | 1:00 | 131 | 15:00 | Khagrachhari | 130 | 0.75 | 124 | 0.45833
| Motijheel | 137 | 1:00 | 131 | 15:00 | Matarbari | 137 | 0.875 | 115 | 0.041667
| Narinda | 137 | 1:00 | 131 | 15:00 | Baroiar Hat | 131 | 0.79167 | 125 | 0.45833
| Kazla | 137 | 1:00 | 131 | 15:00 | Rangamati | 130 | 18:00 | 124 | 11:00
| Dhanmondi | 135 | 2:00 | 130 | 11:00 | Goalpara S/S | 137 | 19:30 | 123 | 23:00
| Lalbag | 137 | 1:00 | 129 | 11:00 | Khulna Central S/S | 136 | 18:00 | 122 | 0.95833
| Madartek | 131 | 2:00 | 123 | 15:00 | Noapara | 134 | 19:30 | 119 | 0.91667
| Dhaka University | 131 | 5:00 | 123 | 14:00 | Jessore | 125 | 19:30 | 110 | 0.91667
| Aftabnagar | 130 | 1:00 | 123 | 15:00 | Benapol | 126 | 18:00 | 109 | 0.95833
| Fatullah | 133 | 1:00 | 128 | 10:00 | Jhenida | 120 | 0.375 | 104 | 0.91667
| Nawabganj | 129 | 21:00 | 123 | 9:00 | Bottail | 129 | 9:00 | 118 | 0.95833
| Keraniganj | 130 | 1:00 | 124 | 10:00 | G.K Project | 138 | 0.41667 | 131 | 0.95833
| Mirpur | 135 | 6:00 | 129 | 10:00 | Faridpur | 132 | 0.20833 | 125 | 0.95833
| Kalyanpur | 135 | 1:00 | 130 | 10:00 | Madaripur | 136 | 0.375 | 129 | 0.79167
| Gulshan | 130 | 3:00 | 123 | 14:00 | Shariyatpur S/S | 138 | 0.25 | 127 | 0.79167
| Uttara | 134 | 2:00 | 127 | 10:00 | Gopalganj | 139 | 7:00 | 129 | 0.79167
| Uttara New | 135 | 1:00 | 128 | 10:00 | Bagerhat | 133 | 0.41667 | 118 | 0.91667
| Kamrangirchar | 137 | 1:00 | 129 | 11:00 | Mongla | 132 | 10:00 | 116 | 0.91667
| Savar | 138 | 2:00 | 130 | 7:00 | Satkhira | 134 | 18:00 | 117 | 0.91667
| Bhasantec | 130 | 1:00 | 123 | 11:00 | Gallamari | 137 | 18:00 | 123 | 23:00
| Agargaon | 131 | 1:00 | 124 | 15:00 | Magura | 120 | 0.375 | 101 | 23:00
| Satmosjid | 130 | 1:00 | 124 | 11:00 | Narail | 120 | 9:00 | 103 | 0.875
| Tongi | 138 | 1:00 | 133 | 15:00 | Chuadanga | 115 | 0.375 | 92 | 0.91667
| Kabirpur | 129 | 19:00 | 126 | 12:00 | Borguna | 140 | 22:00 | 130 | 0.5
| Basundhara | 137 | 1:00 | 130 | 14:00 | Barisal(N) | 141 | 5:00 | 134 | 0.45833
| Manikganj | 140 | 18:30 | 136 | 21:00 | Barisal (S) | 138 | 19:30 | 132 | 14:00
| Joydevpur | 138 | 13:00 | 131 | 8:00 | Patuakhali(S) | 138 | 0.91667 | 128 | 0.45833
| New Tongi | 138 | 1:00 | 131 | 14:00 | Bhandaria | 133 | 0.33333 | 124 | 0.79167
| Kodda | 128 | 18:00 | 124 | 11:00 | Ishurdi | 136 | 0.75 | 130 | 0.79167
| Dhamrai | 128 | 5:00 | 124 | 11:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 21:00
| Rajendrapur | 136 | 4:00 | 128 | 15:00 | Natore | 136 | 17:00 | 129 | 21:00
| Valuka | 121 | 19:30 | 108 | 14:00 | Bogra | 134 | 19:30 | 127 | 21:00
| Tangail | 126 | 8:00 | 121 | 18:00 | Noagaon | 130 | 20:00 | 118 | 21:00
| Mymensing | 123 | 19:30 | 114 | 1:00 | Rajshahi | 134 | 17:00 | 128 | 19:00
| Kishorganj | 127 | 7:00 | 111 | 18:30 | Rajshahi New | 136 | 16:00 | 128 | 7:00
| Netrokona | 122 | 19:30 | 109 | 1:00 | C.Nawabganj | 135 | 19:30 | 126 | 9:00
| Jamalpur | 135 | 7:00 | 124 | 24:00 | Amnura | 136 | 19:30 | 126 | 7:00
| Sherpur | 135 | 8:00 | 122 | 24:00 | Pabna | 134 | 18:00 | 128 | 19:00
| Srimongal | 135 | 4:00 | 123 | 19:00 | Shahjadpur | 137 | 18:00 | 133 | 7:00
| Shahjibazar | 134 | 6:00 | 120 | 18:30 | Serajganj | 133 | 17:00 | 126 | 21:00
| Fenchuganj | 136 | 3:00 | 130 | 23:00 | Niyamatpur | 128 | 18:30 | 113 | 9:00
| Khulawara | 135 | 4:00 | 130 | 19:00 | Joypurhat | 129 | 20:00 | 115 | 21:00
| Sylhet | 132 | 4:00 | 127 | 18:30 | Sherpur(Bogura) | 133 | 17:00 | 126 | 21:00
| Chatak | 132 | 6:00 | 123 | 24:00 | Mohastangor | 132 | 20:00 | 124 | 7:00
| Sunamganj | 129 | 7:00 | 121 | 24:00 | Bangura | 136 | 18:00 | 131 | 21:00
| Biani Bazar | 131 | 5:00 | 122 | 22:00 | Rangpur | 127 | 20:00 | 115 | 1:00
| Comilla(s) | 127 | 6:00 | 123 | 1:00 | Lalmonirhat | 128 | 20:00 | 118 | 1:00
| Comilla(n) | 135 | 1:00 | 131 | 10:00 | Saidpur | 128 | 5:00 | 115 | 21:00
| Chandpur | 133 | 12:00 | 128 | 6:00 | Purbasadipur | 124 | 19:30 | 108 | 21:00
| Feni | 133 | 19:00 | 124 | 11:00 | Thakurgaon | 127 | 20:00 | 106 | 21:00
| Chowmuhani | 133 | 19:00 | 124 | 15:00 | Palashbari | 129 | 20:00 | 119 | 21:00
| Ashuganj | 136 | 6:00 | 120 | 18:30 | Barapukuria | 133 | 20:00 | 123 | 21:00
| Daudkandi | 137 | 1:00 | 127 | 2:00 | Panchagar | 123 | 20:00 | 104 | 21:00
| B.Baria | 132 | 6:00 | 113 | 18:30 | Joldhaka | 124 | 20:00 | 109 | 21:00
| Ramganj | 130 | 18:30 | 122 | 3:00 | Kurigram | 126 | 0.8125 | 113 | 0.33333

## L-Curve
Date | 2021-05-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 6 | 8887 | 4428 | 13315 |  |  |  | QF-LDC-11
0:30 | 88 | 8937 | 4315 | 13252 | Date: | 2021-05-23
1:00 | 170 | 8987 | 4202 | 13189
1:30 | 180 | 8851 | 4164 | 13015
2:00 | 190 | 8715 | 4126 | 12841
2:30 | 175 | 8591.5 | 4047 | 12638.5 | [5 empty] | Gen. at Eve. Peak | 13357 | 13357 MW (21:00 )
3:00 | 160 | 8468 | 3968 | 12436 | [6 empty] | 21:00
3:30 | 180 | 8433.5 | 3892 | 12325.5 | [5 empty] | Gen. at Day Peak | 12021 | 12021 MW (12:00 )
4:00 | 200 | 8399 | 3816 | 12215 | [6 empty] | 12:00
4:30 | 173 | 8208 | 3760 | 11968 | [5 empty] | Highest Generation | 13357
5:00 | 146 | 8017 | 3704 | 11721 | [6 empty] | 21:00
5:30 | 133 | 7739.5 | 3516.5 | 11256
6:00 | 120 | 7462 | 3329 | 10791
6:30 | 130 | 7397 | 3278.5 | 10675.5
7:00 | 140 | 7332 | 3228 | 10560
7:30 | 120 | 7346 | 3234.5 | 10580.5
8:00 | 100 | 7360 | 3241 | 10601
8:30 | 64 | 7519.5 | 3287 | 10806.5
9:00 | 28 | 7679 | 3333 | 11012
9:30 | 35 | 7811 | 3390.5 | 11201.5
10:00 | 42 | 7943 | 3448 | 11391
10:30 | 42 | 8087 | 3423.5 | 11510.5
11:00 | 42 | 8231 | 3399 | 11630
11:30 | 28 | 8371 | 3454.5 | 11825.5
12:00 | 14 | 8511 | 3510 | 12021
12:30 | 31 | 8564.5 | 3564 | 12128.5
13:00 | 48 | 8618 | 3618 | 12236
13:30 | 27 | 8636 | 3658.5 | 12294.5
14:00 | 6 | 8654 | 3699 | 12353
14:30 | 23 | 8793.5 | 3700.5 | 12494
15:00 | 40 | 8933 | 3702 | 12635
15:30 | 70 | 8840 | 3770 | 12610
16:00 | 100 | 8747 | 3838 | 12585
16:30 | 125 | 8599.5 | 3758.5 | 12358
17:00 | 150 | 8452 | 3679 | 12131
17:30 | 193 | 7714.5 | 3541.5 | 11256
18:00 | 236 | 6977 | 3404 | 10381
18:30 | 164 | 7645.5 | 3597 | 11242.5
19:00 | 92 | 8314 | 3790 | 12104
19:30 | 32 | 8627 | 4099 | 12726
20:00 | 53 | 8687 | 4182 | 12869 |  |  |  | Executive Engineer
20:30 | 35.5 | 8815.5 | 4297.5 | 13113 |  |  |  | Network Operation Division
21:00 | 18 | 8944 | 4413 | 13357
21:30 | 17 | 8878.5 | 4421.5 | 13300
22:00 | 16 | 8813 | 4430 | 13243 |  |  |  |  | Page 6 of 7
22:30 | 10 | 8843.5 | 4427.5 | 13271
23:00 | 4 | 8874 | 4425 | 13299
23:30 | 5 | 8880.5 | 4426.5 | 13307
24:00 | 6 | 8887 | 4428 | 13315
13357 MW (21:00 )
12021 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-23 |  | Energy | 292528207
[11 empty] | 2021-05-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4367 | 913 | 2013 | 4535 | 720 | 25 | 475 | 0 | 166 | 0
0:30 | 4556 | 914.5 | 2009 | 4322 | 725 | 25 | 482 | 0 | 168 | 0 | Date: | 2021-05-23
1:00 | 4745 | 916 | 2005 | 4109 | 730 | 25 | 489 | 0 | 170 | 0
1:30 | 4749 | 914.5 | 1999 | 4010.5 | 720 | 25 | 428 | 0 | 169 | 0 | [7 empty] | Total Energy | 292.5282 | Total Energy Gen 292.528 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 292.528 MKWHr
2:00 | 4753 | 913 | 1993 | 3912 | 710 | 25 | 367 | 0 | 168 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4805 | 913 | 2022 | 3691 | 710 | 25 | 305.5 | 0 | 167 | 0 | [7 empty] | Energy Requirement | 292.5282
3:00 | 4857 | 913 | 2051 | 3470 | 710 | 25 | 244 | 0 | 166 | 0
3:30 | 4866.5 | 912.5 | 2062.5 | 3331.5 | 710 | 25 | 252.5 | 0 | 165 | 0 | [6 empty] | Shortage
4:00 | 4876 | 912 | 2074 | 3193 | 710 | 25 | 261 | 0 | 164 | 0
4:30 | 4817.5 | 912.5 | 2075 | 3062 | 710 | 25 | 204 | 0 | 162 | 0
5:00 | 4759 | 913 | 2076 | 2931 | 710 | 25 | 147 | 0 | 160 | 0
5:30 | 4735.5 | 912.5 | 2058 | 2596.5 | 695 | 25 | 75.5 | 0 | 155 | 3
6:00 | 4712 | 912 | 2040 | 2262 | 680 | 25 | 4 | 0 | 150 | 6
6:30 | 4726.5 | 912.5 | 2030 | 2135 | 680 | 25 | 4 | 0 | 145 | 17.5 |  |  |  |  | Coal
7:00 | 4741 | 913 | 2020 | 2008 | 680 | 25 | 4 | 0 | 140 | 29
7:30 | 4711.5 | 913 | 2007 | 2053.5 | 680 | 25 | 4 | 0 | 144 | 42.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4682 | 913 | 1994 | 2099 | 680 | 25 | 4 | 0 | 148 | 56
8:30 | 4696.5 | 913 | 1957 | 2289 | 680 | 25 | 28 | 0 | 149 | 69
9:00 | 4711 | 913 | 1920 | 2479 | 680 | 25 | 52 | 0 | 150 | 82
9:30 | 4693 | 912.5 | 1923 | 2673.5 | 680 | 25 | 52 | 0 | 149 | 93.5
10:00 | 4675 | 912 | 1926 | 2868 | 680 | 25 | 52 | 0 | 148 | 105
10:30 | 4707.5 | 912 | 1913.5 | 2961.5 | 680 | 25 | 52 | 0 | 154 | 105
11:00 | 4740 | 912 | 1901 | 3055 | 680 | 25 | 52 | 0 | 160 | 105
11:30 | 4740.5 | 912 | 1880.5 | 3226 | 685 | 25 | 102.5 | 0 | 161 | 93
12:00 | 4741 | 912 | 1860 | 3397 | 690 | 25 | 153 | 0 | 162 | 81
12:30 | 4710 | 913 | 1826.5 | 3507.5 | 695 | 25 | 207.5 | 0 | 161 | 83
13:00 | 4679 | 914 | 1793 | 3618 | 700 | 25 | 262 | 0 | 160 | 85
13:30 | 4679 | 914 | 1793 | 3618 | 700 | 25 | 262 | 0 | 160 | 85
14:00 | 4679 | 914 | 1793 | 3618 | 700 | 25 | 262 | 0 | 160 | 85
14:30 | 4752 | 913 | 1828.5 | 3653 | 705 | 25 | 309 | 0 | 166 | 84
15:00 | 4825 | 912 | 1864 | 3688 | 710 | 25 | 356 | 0 | 172 | 83
15:30 | 4755.5 | 912 | 1877.5 | 3719 | 720 | 25 | 363.5 | 0 | 170 | 67.5
16:00 | 4686 | 912 | 1891 | 3750 | 730 | 25 | 371 | 0 | 168 | 52
16:30 | 4663 | 912 | 1859 | 3615 | 705 | 25 | 374 | 0 | 167 | 38
17:00 | 4640 | 912 | 1827 | 3480 | 680 | 25 | 377 | 0 | 166 | 24
17:30 | 4344 | 911.5 | 1665.5 | 3079 | 665 | 25 | 395 | 0 | 156 | 15
18:00 | 4048 | 911 | 1504 | 2678 | 650 | 25 | 413 | 0 | 146 | 6
18:30 | 4184.5 | 912 | 1602 | 3218.5 | 655 | 25 | 482.5 | 0 | 160 | 3
19:00 | 4321 | 913 | 1700 | 3759 | 660 | 25 | 552 | 0 | 174 | 0
19:30 | 4208 | 912 | 1727 | 4436 | 700 | 25 | 540 | 0 | 178 | 0
20:00 | 4248 | 912 | 1703 | 4543 | 720 | 25 | 542 | 0 | 176 | 0
20:30 | 4289 | 912.5 | 1785.5 | 4674.5 | 725 | 25 | 533.5 | 0 | 168 | 0
21:00 | 4330 | 913 | 1868 | 4806 | 730 | 25 | 525 | 0 | 160 | 0
21:30 | 4389 | 912.5 | 1889 | 4697 | 721 | 25 | 502.5 | 0 | 164 | 0
22:00 | 4448 | 912 | 1910 | 4588 | 712 | 25 | 480 | 0 | 168 | 0
22:30 | 4451 | 912 | 1956.5 | 4561.5 | 716 | 25 | 484 | 0 | 165 | 0
23:00 | 4454 | 912 | 2003 | 4535 | 720 | 25 | 488 | 0 | 162 | 0
23:30 | 4410.5 | 912.5 | 2008 | 4535 | 720 | 25 | 481.5 | 0 | 164 | 0 | Max Temp. in Dhaka |  | 37.8° C
24:00 | 4367 | 913 | 2013 | 4535 | 720 | 25 | 475 | 0 | 166 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 292.528 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 292.528 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 16 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 16 | 8 | 8 |  | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 384480
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 4 | 10 | 15 | 17 | 18 | 18 | 18 | 16 | 13 | 6 | 3 | [9 empty] | 138510
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 204 | 217 | 210 | 204 | 214 | 215 | 214 | 203 | 203 | 206 | 203 | 203 | 207 | 218 | 204 | 205 | 207 |  | 204 | 202 | 203 | 202 | 202 | 202 | 202 | 3526077
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 80 | 110 | 110 | 110 | 110 | 120 | 120 | 2679325
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 34 | 17 | 34 | 9 | [6 empty] | 51 | 45 | 42 | 46 | 46 | 46 | 51 |  | 68 | 68 | 53 | 45 | 17 | 17 | 17 | 679907
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1298872
| Daudkandi 200 MW PP (B.Trac) | 46 | [18 empty] | 160 | 194 | 200 | 200 | 200 | 200 | 200 | 1191936
14 | Titas 50 MW Peaking PP | 50 | [11 empty] | 50 | 40 | 40 | 36 | 45 | 48 |  | 48 | 48 | 48 | 48 | 40 | 48 | 40 | 561616
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 146 | 125 | 125 | 185 | 185 | 120 | 120 | 120 | 185 | 180 | 178 | 178 | 125 | 121 | 175 | 175 | 144 | 152 |  | 178 | 178 | 125 | 179 | 180 | 180 | 180 | 4026000
17 | Siddhirganj 335 MW CCPP | 214 | 214 | 216 | 216 | 218 | 170 | 170 | 170 | 214 | 212 | 208 | 208 | 208 | 170 | 202 | 202 | 203 | 161 |  | 203 | 150 | 209 | 208 | 210 | 210 | 214 | 4927439
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 245 | 45 | [5 empty] | 2 | 52 | 145 | 200 | 228 | 238 | 243 | 245 | 195 | 190 |  | 200 | 215 | 245 | 243 | 245 | 245 | 245 | 3831380
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 35 | 83 | 83 | 83 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 |  | 190 | 180 | 190 | 180 | 180 | 180 | 180 | 4284000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 80 | 80 | [8 empty] | 0 | 1462628
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 26 | 24 | 21 | 24 | 24 |  |  | 26 |  | 23 | 26 | 26 | 26 | 26 | 527256
33 | Ashuganj 225 MW CCPP | 185 | 200 | 184 | 176 | 179 | 184 | 182 | 185 | 199 | 207 | 210 | 210 | 210 | 207 | 204 | 205 | 208 |  |  | 20 | 135 | 135 | 136 | 137 | 136 | 136 | 4173000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 305 | 290 | 270 | 290 | 290 | 290 | 265 | 265 | 290 | 265 | 295 | 310 | 315 | 300 | 300 | 320 |  | 315 | 300 | 300 | 300 | 300 | 300 | 300 | 7147000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 295 | 285 | 260 | 285 | 290 | 285 | 260 | 265 | 285 | 350 | 315 | 280 | 330 | 260 | 260 | 280 |  | 305 |  |  |  | 90 | 70 | 20 | 5850500
35 | Ashuganj 55 MW PP (Precision) | 56 | 53 | 56 | 55 | 56 | 56 | 24 | 24 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 30 | 30 | [5 empty] | 5 | 24 | 41 | 45 | 681
36 | Chandpur 150 MW CCPP | 90 | 92 | 92 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 | 90 | 91 | 91 | 87 | 90 |  | 86 | 86 | 88 | 86 | 86 | 91 | 91 | 2124960
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 331 | 350 | 364 | 354 | 336 | 364 | 359 | 358 | 337 | 353 | 344 | 332 | 336 | 364 | 363 | 330 | 314 |  | 317 | 394 | 391 | 391 | 389 | 390 | 391 | 8626170
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7124500
41 | Haripur 360MW CCPP(HPL) | 345 | 346 | 343 | 346 | 345 | 345 | 343 | 343 | 340 | 336 | 311 | 276 | 276 | 277 | 276 | 276 | 278 | 276 |  | 272 | 272 | 272 | 272 | 273 | 273 | 302 | 7352000
42 | RPCL 210MW CCPP | 153 | 153 | 153 | 153 | 153 | 153 | 151 | 151 | 150 | 147 | 145 | 145 | 145 | 144 | 143 | 144 | 144 | 94 |  | 94 | 85 | 82 | 99 | 116 | 133 | 101 | 3164440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 14 | 25 | 37 | 48 | 41 | 17 | 20 | 47 | 36 | 21 | 10 | 2 | [8 empty] | 336000
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 993000
45 | Fenchugonj CCPP Phase-2 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 30 | 30 | 29 | 29 | 30 | 28 | 28 |  | 28 | 30 | 30 | 30 | 30 | 30 | 30 | 618960
46 | Shajibazar 330 MW CCPP | 330 | 328 | 328 | 330 | 327 | 327 | 326 | 320 | 326 | 322 | 318 | 316 | 320 | 313 | 312 | 314 | 322 | 291 |  | 316 | 327 | 325 | 329 | 330 | 326 | 326 | 7359000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 57 | 57 | 56 | 56 | 56 | 56 | 55 | 56 | 55 | 55 | 60 | 55 | 55 | 55 | 54 | 57 | 30 |  | 55 | 56 | 51 | 51 | 51 | 51 | 50 | 1295136
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 74 | 72 | 74 | 72 | 72 | 70 | 70 | 70 | 70 |  |  | 75 | 72 | 75 | 77 | 77 | 77 | 77 | 1711680
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 100 |  | 140 | 140 | 140 | 140 | 120 | 120 | 120 | 3245140
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 364000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 5 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 148320
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 253000
55 | Fenchugonj 51 MW PP (Barakatullah) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 41 | 44 | 44 | 43 | 43 | 45 | 46 | 13 |  | 35 | 47 | 47 | 48 | 48 | 48 | 49 | 1025400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 6 | 6 | 6 | 6 | 8 | 8 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 316616
57 | Bibiana-II 341 MW CCPP (Summit) | 310 | 300 | 310 | 320 | 320 | 310 | 320 | 320 | 300 | 310 | 310 | 310 | 290 | 300 | 315 | 310 | 290 | 280 |  | 310 | 290 | 280 | 290 | 260 | 280 | 300 | 7437500
| Bibiyana South 400 MW | 367 | 395 | 387 | 390 | 394 | 394 | 390 | 388 | 388 | 385 | 383 | 384 | 385 | 380 | 372 | 378 | 385 | 340 |  | 360 | 388 | 394 | 396 | 397 | 394 | 391 | 9012300
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1288334
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 15 | 24 | 24 | 24 | 24 | 23 |  |  | 15 | 24 | 24 | 24 | 25 | 24 | 24 | 554640
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 441888
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 401976
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 19 | 17 | 17 | 17 | 17 | 352368
63 | Impoprt (Tripura) | 170 | 168 | 166 | 164 | 160 | 150 | 140 | 148 | 150 | 148 | 160 | 162 | 160 | 172 | 172 | 168 | 166 | 146 |  | 174 | 178 | 176 | 160 | 168 | 162 | 166 | 3882240
64 | Malancha, Ctg. EPZ (United) | 28 | 28 | 28 | 38 | 38 | 16 | 25 | 10 | 3 | 3 | 3 | 3 | 8 | 4 | 3 | 4 | 6 | 2 |  | 10 | 14 | 19 | 30 | 34 | 34 | 24 | 453600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483084
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 172980
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 807200
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 14 | 14 | 14 | 14 | 14 | 16 | 16 | 16 | 16 | 16 |  | 16 | 20 | 20 | 20 | 20 | 20 | 17 | 406730
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 14 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 411660
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 759600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 |  | 16 | 16 | 16 | 33 | 33 | 25 | 16 | 25 | 25 | 25 | 25 | 25 | 8 |  | 16 | 16 | 16 | 25 | 25 | 33 | 33 | 584300
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 103 | 100 | 100 | 97 | 93 | 95 | 101 | 54 |  | 90 | 100 | 103 | 104 | 104 | 103 | 103 | 2262363
| Feni Lanka Power | 114 | 114 | 88 | 88 | 70 |  |  |  |  | 13 | 17 | 52 | 114 | 114 | 114 | 114 | 70 | 34 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1826280
| Chowmuhani 113 MW | 115 | 115 | 114 | 120 | 120 | 122 | 120 | 115 | 121 | 120 | 119 | 115 | 114 | 112 | 115 | 112 | 113 | 65 |  | 94 | 120 | 120 | 121 | 119 | 118 | 114 | 2766960
| Manikgonj 162MW PP(MPGL) | 158 | 144 | 144 | 162 | 158 | 17 | 17 | 19 | 71 | 130 | 148 | 162 | 162 | 162 | 162 | 162 | 162 | 108 |  | 135 | 162 | 162 | 162 | 162 | 162 | 162 | 3365280
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 97 | 100 | 100 | 100 | 70 |  | 74 | 90 | 94 | 100 | 100 | 100 | 100 | 2356848
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 | 41 | 41 | 41 | 41 | 41 | 975840
79 | Kodda 150MW PP | 150 | 150 | 84 | 84 | 84 |  |  |  | 48 | 48 | 48 | 98 | 133 | 133 | 149 | 149 | 98 | 98 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2432640
80 | Jamalpur 95 MW PP(Powerpac) | 63 | 63 | 63 | 55 | 55 | 55 | 55 | 48 | 48 | 47 | 47 | 54 | 54 | 54 | 55 | 55 | 62 | 62 |  | 62 | 63 | 63 | 62 | 62 | 62 | 62 | 1358400
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1242211
| Gazipur 100 MW PP | 88 | 88 | 88 | 88 | 34 | 17 | 17 | 25 | 60 | 86 | 86 | 86 | 86 | 86 | 95 | 105 | 104 | 70 |  | 90 | 105 | 105 | 105 | 105 | 105 | 105 | 2017200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 3 | 4 | 5 | 5 | 4 | 4 | 1 | 0 | [9 empty] | 34080
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1298407
| Karnaphuli Power Ltd. | 34 | 34 | 17 | [22 empty] | 0 | 116254
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 84 | [9 empty] | 2 | 27 | 60 | 91 | 97 | 96 | 63 | 30 |  | 45 | 86 | 86 | 85 | 86 | 86 | 86 | 1102058
86 | Meghnaghat CCPP ( Summit) | 260 | 280 | 290 | 280 | 270 | 280 | 280 | 280 | 280 | 265 | 280 | 280 | 250 | 270 | 270 | 265 | 235 | 275 |  | 260 | 260 | 255 | 240 | 255 | 280 | 265 | 6454720
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 78 | 90 | 94 | 94 | 93 | 70 | 17 | 20 | 62 | 91 | 93 | 95 | 96 | 91 | 94 | 94 | 95 | 60 |  | 77 | 95 | 96 | 96 | 94 | 94 | 94 | 1996800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 50 |  | 50 | 70 | 75 | 75 | 75 | 75 | 86 | 1878720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 |  |  | 2 |  |  |  | 2 | 41 | 51 | 955716
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 58 | 58 | 7 | 7 | 7 | 7 | 7 | 16 | 48 | 95 | 102 | 102 | 102 | 102 | 64 | 64 |  | 70 | 102 | 102 | 102 | 102 | 102 | 102 | 1728000
95 | Patenga 50MW PP (Baraka) | 50 | 5 |  |  |  |  | 1 | 14 | 18 | 19 | 19 | 19 | 26 | 41 | 44 | 44 | 44 | 45 |  | 50 | 50 | 50 | 50 | 25 | 25 | 25 | 653760
96 | Chattogram 108 MW PP (ECPV) | 51 | 51 | [8 empty] | 10 | 57 | 82 | 82 | 82 | 88 | 93 | 95 |  | 97 | 97 | 97 | 75 | 27 | 25 | 25 | 1059840
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 45 | 45 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1301664
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 |  |  |  |  | 5 | 17 | 35 | 55 | 55 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 972309
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 130 |  | 130 | 163 | 163 | 163 | 163 | 163 | 110 | 3613091
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 1 | 2 | 2 | 1 | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 12050
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 17 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 852840
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 287 | 299 | 262 | 303 | 165 | 155 | 186 | 1136714
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 45 | 50 | 50 | 90 | 28 | 25 | 50 | 268454
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 192 | 192 | 192 | 110 | 110 | 110 | 90 | 90 | 90 | 80 | 80 | 80 | 90 | 90 | 90 | 80 |  | 94 | 190 | 191 | 191 | 191 | 190 | 190 | 3283200
112 | Aurahati 100MW PP (Aggreko) | 22 | [18 empty] | 90 | 98 | 98 | 100 | 52 | 52 | 100 | 493763
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 139 | 149 | 149 | 149 | 143 | 145 | 149 | 149 | 149 | 135 | 133 | 146 | 133 | 131 | 129 | 132 | 133 |  | 149 | 149 | 149 | 149 | 149 | 144 | 149 | 3454128
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 40 |  | 40 | 40 | 70 | 100 | 100 | 100 | 100 | 2247360
116 | Chandpur 200MW (Desh energy) | 115 | 111 | 105 | 85 | 84 | 85 | 85 | 85 | 103 | 120 | 120 | 120 | 120 | 119 | 120 | 108 | 104 | 102 |  | 104 | 103 | 104 | 103 | 103 | 103 | 103 | 2523360
117 | Ashuganj 150MW PP (Midland) | 155 | 155 | 154 | 155 | 50 | 10 | 10 | 16 | 56 | 113 | 140 | 150 | 142 | 142 | 137 | 137 | 142 | [6 empty] | 38 | 10 | 10 | 2294981
118 | Bibiyana-III 400 MW CCPP | 366 | 367 | 402 | 388 | 367 | 383 | 400 | 383 | 368 | 368 | 392 | 367 | 367 | 381 | 392 | 369 | 369 | 328 |  | 356 | 368 | 368 | 368 | 368 | 368 | 367 | 9095000
| Jamalpur 115 MW PP (United) | 107 | 107 | 107 | 107 | 107 | 115 | 115 | 115 | 115 | 97 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 106 | 115 | 115 | 115 | 2562000
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 96 | 97 | 98 | 99 | 100 | 100 | 50 | 80 | 100 | 90 | 77 | 90 | 90 | 90 | 90 | 90 | 100 | 40 |  | 10 | 10 | 20 | 100 | 100 | 100 | 100 | 1963200
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 90 | 53 | 53 | 75 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2634545
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | [5 empty] | 25 | 17 |  | 21 | 35 | 35 | 708480
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 8 | 15 | 20 | 28 | 32 | 33 | 31 | 28 | 23 | 16 | 7 | 2 | [8 empty] | 247442
120 | Eastern Zone Total | 8987 | 8715 | 8468 | 8399 | 8017 | 7462 | 7332 | 7360 | 7679 | 7943 | 8231 | 8511 | 8618 | 8654 | 8933 | 8747 | 8452 | 6977 |  | 8314 | 8627 | 8687 | 8944 | 8813 | 8874 | 8887 | 199335014
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 71 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 76 | 71 | 80 | 80 | 89 | 70 | 92 | 88 | 99 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 1895040
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 6 | 6 |  | 12 | 13 | 15 | 15 | 15 | 15 | 15 | 147360
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 53 | 35 | 40 | 80 | 105 | 90 | 90 | 105 | 105 | 90 | 105 | 105 | 53 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 2270880
130
131
132 | United Payra Power Ltd. | 107 | 107 | 72 | 54 | 35 | [14 empty] | 18 | 81 | 81 | 81 | 81 | 35 | 35 | 799200
133 | Bhola Nutan Biddut BD LTD (GAS)
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 64 | 32 | 32 | 32 | 32 | 32 | 32 | 64 | 64 | 60 | 76 | 80 | 80 |  | 97 | 110 | 110 | 110 | 110 | 110 | 110 | 1903104
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 96 | 95 | 95 | 95 | 95 | 94 | 92 | 89 | 87 | 87 | 89 | 89 | 89 | 90 | 90 | 80 | 51 |  | 76 | 94 | 92 | 93 | 98 | 97 | 96 | 2165647
| Bhola 225 MW CCPP | 87 | 88 | 88 | 88 | 88 | 88 | 86 | 87 | 86 | 86 | 82 | 86 | 85 | 85 | 84 | 84 | 84 | 84 |  | 87 | 85 | 86 | 87 | 87 | 87 | 88 | 2065252
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 34 | 34 | 33 | 27 | 24 | 24 | 25 | 26 | 26 | 28 | 28 | 28 | 26 | 27 | 25 |  | 35 | 35 | 29 | 34 | 29 | 35 | 35 | 703356
141 | Noapara 100 MW PP (Bangla Trac) | 99 | 99 | 60 | [12 empty] | 30 |  |  |  | 14 | 99 | 99 | 100 | 100 | 100 | 100 | 870720
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | [7 empty] | 32 | 32 | 32 | 32 | 8 |  |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 475875
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 916 | 913 | 913 | 912 | 913 | 912 | 913 | 913 | 913 | 912 | 912 | 912 | 914 | 912 | 912 | 912 | 912 | 911 |  | 913 | 912 | 912 | 913 | 912 | 912 | 913 | 22030545
147 | Bheramara 410 MW CCPP | 305 | 305 | 295 | 295 | 290 | 285 | 280 | 285 | 280 | 275 | 270 | 260 | 260 | 260 | 270 | 265 | 265 | 280 |  | 285 | 290 | 290 | 290 | 290 | 280 | 280 | 6907104
148 | Payra 1320 MW | 580 | 560 | 560 | 560 | 560 | 530 | 530 | 530 | 530 | 530 | 530 | 540 | 550 | 550 | 560 | 580 | 530 | 500 |  | 510 | 550 | 570 | 580 | 570 | 570 | 570 | 14308800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 142 | 150 | 150 | 3666400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | [9 empty] | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 776154
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 2 | 3 | 2 | 1 | 3 | 1 | 0 | 1 | 0 | 0 | [8 empty] | 19260
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 134 | 132 | 131 | 130 | 131 | 129 | 126 | 123 | 119 | 115 | 114 | 110 | 108 | 108 | 107 | 106 | 80 |  | 85 | 104 | 105 | 107 | 107 | 105 | 104 | 2879600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 145 | 140 | 140 | 139 | 138 | 139 | 139 | 138 | 138 | 138 | 135 | 132 | 133 | 134 | 128 | 126 | 126 | 128 |  | 131 | 129 | 130 | 133 | 134 | 139 | 139 | 3471400
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 181 | 179 | 179 | 177 | 173 | 155 | 150 | 150 | 142 | 150 | 151 | 151 | 151 | 150 | 145 | 145 |  | 148 | 144 | 144 | 146 | 172 | 189 | 187 | 4138018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 398 | 398 | 414 | 414 | 416 | 413 | 415 | 413 | 393 | 410 | 405 | 398 | 369 | 396 | 396 | 399 | 353 | 348 |  | 340 | 315 | 296 | 390 | 388 | 401 | 411 | 9453000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [15 empty] | 10 | 46 | 46 |  | 46 | 46 | 50 | 51 | 50 | 50 | 45 | 354409
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 20 | 19 | 16 | 18 | 16 | 16 | 16 | 17 | 17 | 18 |  | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 447360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 235890
165 | Amnura 50 MW PP(Sinha) | [11 empty] | 24 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 547730
166 | Katakhali 50 MW PP (Northern) | [15 empty] | 16 | 16 | 16 |  | 16 | 43 | 43 | 43 | 43 | 43 | 43 | 282374
167 | Katakhali 50 MW Peaking PP | 30 | [11 empty] | 30 | 29 | 29 | 29 | 29 | 29 |  | 30 | 30 | 31 | 30 | 30 | 30 | 30 | 353800
168 | Santahar 50 MW Peaking PP | 34 | 34 | [14 empty] | 10 | 37 |  | 36 | 22 | 33 | 33 | 33 | 33 | 33 | 295599
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 |  | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 1192320
170 | Chapainawabganj 100 MW Peaking PP | 97 | 89 | 89 | 89 | 50 | [9 empty] | 39 | 48 | 47 | 48 |  | 92 | 98 | 96 | 95 | 95 | 95 | 95 | 1115432
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 50 | 100 | 100 | 175 | 195 | 200 | 200 | 811837
| Bagura 113 MW PP (Confidence)-2 | 112 | 112 | 112 | 112 | 112 | 50 | 35 | 35 | 63 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 35 |  | 41 | 112 | 110 | 112 | 112 | 112 | 112 | 2357952
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 70 | [5 empty] | 10 | 35 | 50 | 113 | 113 | 113 | 113 | 113 | 70 | 35 |  | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 1787328
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | [13 empty] | 12 | 10 | 8 | 8 | 0 | 0 | 0 | 23000
175 | Saidpur 20 MW GTPP | [19 empty] | 8 | 5 | 8 |  |  | 0 | 0 | 15000
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 55 | 35 | 64 | 113 | 113 | 99 | 113 | 112 | 112 | 100 | 104 | 108 | 70 |  | 113 |  | 70 | 113 | 113 | 113 | 113 | 2372160
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 4 | 6 | 6 | 6 | 7 | 6 | 6 | 4 | 2 | [8 empty] | 54287
178
178