## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-25 | Tuesday
|  |  | Date (day): | 2021-05-25 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14985.6 | MW |  |  | (b) At Evening Peak Hour : |  | 16053 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-24 | 2021-05-25 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 180 | 180 | 180 | 180
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 90 | 100 | 100 | 102
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 337 | 329 | 360 | 390 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 201 | 176 | 360 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Dust in gas line.
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 275 | 300 | 300
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 41 | 86 | 85 | 85
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 180 | 150 | 180 | 185 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 208 | 214 | 220 | 220 |  | 115 | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 75 | 102 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 149 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 37 | 37 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 41 | 41 | 41 |  | 11 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 200 | 245 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 105 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 82 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 88 | 86 | 105 | 105
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 95 | 95 | 72 | 72 |  | 32 | Engine problem
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 3173 | 3510 | 3822 | 4079 | 309 | 1222
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 0 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 47 | 46 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 71 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 0 | 110 | 110
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 0 | 70 | 90 |  | 15 | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 42 | 68 | 68 |  | 34 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 76 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 0 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 10 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 60 | 97 | 100 | 100
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 162 | 153 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 34 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 80 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 110 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 934 | 898 | 1595 | 1605 | 385 | 335
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 80 | 100 | 34 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 145 | 215 | 215 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 230 | 235 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 295 | 330 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 10 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 10 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 83 | 16 | 45 | 45 | 150 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 5 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 92 | 0 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 103 | 125 | 125 |  | 75 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 0 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 166 | 102 | 145 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 15 | 20 | 20 |  | 5 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 116 | 110 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 5 | 17 | 35 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1716 | 1452 | 2172 | 2379 | 448 | 190
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 150 | 151 | 160 | 160
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 19 | 19 |  | 3 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 55 | 63 | 64 | 64 |  | 31 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 88 | 190 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 27 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 480 | 562 | 631.6 | 580 | 0 | 34
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 41 | 42 | 42 | 42 |  | 28 | Under maint.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 130 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 320 | 328 | 163 | 330
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 46 | 50 | 44 | 44
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 56 | 56 | 57 | 57 |  | 9 | Engine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 73 | 77 | 76 | 76 |  | 10 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 120 | 120 | 140 | 140 |  | 91 | ST Under maint.
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 341 | 341
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 403 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 6 | 0 | 7 | 7 |  | 3 | Engine prolem
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 394 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1988 | 1984 | 1908 | 2075 | 0 | 310
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 892 | 827 | 909 | 909
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 90 | 99 | 99 | 99 |  | 16 | Engine problem
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 3 | 17 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 295 | 365 | 410 | 410
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 32 | 32 | 32 |  | 8 | Engine problem
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1350 | 1545 | 1785 | 2055 | 0 | 107
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 110 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 34 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 86 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 92 | 76 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 550 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 0 | 165 | 110 | 165 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 3 | 54 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 722 | 1075 | 1058 | 1223 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 31 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 7 | 45 | 40 | 40
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 42 | 40 | 42 |  | 8 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 107 | 142 | 125 | 125 | 85 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 136 | 132 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 172 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 401 | 0 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 14 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 20 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 70 | 96 | 100 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1204 | 1047 | 1743 | 1774 | 256 | 50
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 17 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 112 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 268 | 280 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 22023 | 21315 | 11835 | 12353 | 14985.6 | 16053 | 1607 | 2459
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 11238.1243 | 11730 | 14229.8298 | 15243.3976
| A. |  | 2021-05-24 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13012 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 10785 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12353 | MW
| 3 | Day peak Generation : |  |  | 11835 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11730 | MW
| 4 | Evening peak Generation : |  |  | 12353 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 279.6833 | MKWHr | By Solar | 0.73666 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.8325 | MKWHr |  | By Oil: | 89.1675 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 16.8218 | MKWHr |  | By Hydro: | 0.58 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1607 | MW | Dhaka | 4695 | 4695 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2459 | MW | Chittagong | 949 | 949 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4066 | MW | Khulna | 1530 | 1530 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1187.87 | MMCFD |  |  | Rajshahi | 1152 | 1152 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 157458024.594 | ii) Oil : | Taka | 697534734.17 | Comilla | 964 | 964 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 77625742 | Total | Taka | 932618500.764 | Mymensingh | 1047 | 1047 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.739 | MKWHr. | Sylhet | 310 | 310 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -154 | MW (E to W) at | 19:30 | hrs | Barisal | 404 | 404 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -438 | MW at | 22:00 | hrs | Rangpur | 679 | 679 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 38.1° C |  |  | Total | 11730 | 11730 |  | 0
| B. |  | 2021-05-25 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 16053 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 4253 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 253.6323 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7904 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 21.1455 | MKWHr. | ii) HVDC Flow at Peak Time |  | 827 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.3994 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.99 |  | (b) Today: | 73.75 |  | (c) Rule Curve: |  | 77.4
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-24
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 180 | 0 | 104 | 0 | 388 | 332 |  | 0 | 300 | 260 | 0 | 0 | 55 | 218 | 0 | 180 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 24 | 0 | 17 | 80 | 25 | 25 | 19 | 33 | 0 | 0 | 0 | 25 | 300 | 139 | 83 | 91 | 26 | 50 | 0 | 51 | 0 | 40 | 52 | 21 | 8 | 33 | 17 | 170 | 112 | 63 | 17 | 0 | 42 | 30 | 49 | 0 | 110 | 307 | 51 | 77 | 0 | 120 | 0 | 0 | 7 | 270 | 16 | 11 | 200 | 245 | 83 | 0 | 190 | 100 | 148 | 0 | 100 | 103 | 10 | 368 | 115 | 105 | 42 | 0 | 0 | 54 | 21 | 114 | 115 | 100 | 394 | 95 | 0 | 162 | 116 | 0 | 35 | 0 |  | 892 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 10 | 0 | 32 | 89 | 35 | 110 | 0 | 0 | 0 | 50 | 45 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 104 | 0 | 142 | 0 | 96 | 100 | 183 | 0 | 400 | 105 | 120 | 112 | 0 | 113 | 0 | 0 | 113 | 530 | 0 | 0 | 17 | 0 |  | 8760 | 4252 | 13012 | 4373 | 892 | 2017 | 4386 | 679 | 25 | 470 | 170 | 0 | 0 | 74.04
2:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 390 | 343 |  | 0 | 300 | 260 | 0 | 0 | 55 | 219 | 0 | 180 | 100 | 102 | 150 | 84 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 24 | 0 | 17 | 80 | 25 | 25 | 19 | 33 | 0 | 0 | 0 | 10 | 300 | 140 | 83 | 88 | 26 | 50 | 0 | 51 | 0 | 40 | 52 | 21 | 8 | 33 | 17 | 168 | 133 | 62 | 17 | 0 | 42 | 30 | 49 | 0 | 163 | 306 | 52 | 77 | 0 | 120 | 0 | 0 | 7 | 285 | 16 | 11 | 100 | 245 | 32 | 0 | 190 | 74 | 149 | 0 | 100 | 103 | 18 | 368 | 115 | 88 | 35 | 0 | 0 | 54 | 48 | 114 | 115 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 35 | 0 |  | 893 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 10 | 0 | 32 | 89 | 35 | 110 | 0 | 0 | 0 | 50 | 39 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 104 | 0 | 148 | 0 | 95 | 100 | 183 | 0 | 398 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 17 | 0 |  | 8678 | 4141 | 12819 | 4392 | 893 | 2089 | 4098 | 690 | 25 | 464 | 168 | 0 | 0 | 74.03
3:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 389 | 346 |  | 0 | 300 | 255 | 0 | 0 | 55 | 221 | 0 | 180 | 100 | 102 | 150 | 76 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 19 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 120 | 0 |  | 22 | 0 | 17 | 80 | 25 | 25 | 19 | 33 | 0 | 0 | 0 | 20 | 300 | 140 | 83 | 91 | 26 | 51 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 17 | 164 | 154 | 62 | 17 | 0 | 42 | 30 | 49 | 0 | 163 | 307 | 52 | 77 | 0 | 120 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 245 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 103 | 68 | 368 | 115 | 88 | 35 | 0 | 0 | 54 | 51 | 114 | 115 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 35 | 0 |  | 893 | 0 | 280 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 89 | 35 | 110 | 0 | 0 | 0 | 50 | 39 | 95 | 42 | 43 | 30 | 52 | 33 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 104 | 0 | 148 | 0 | 96 | 20 | 183 | 0 | 408 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 17 | 0 |  | 8506 | 4066 | 12572 | 4429 | 893 | 2102 | 3851 | 690 | 25 | 418 | 164 | 0 | 0 | 74.02
4:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 389 | 348 |  | 0 | 300 | 255 | 0 | 0 | 55 | 221 | 0 | 180 | 100 | 102 | 150 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 17 | 80 | 25 | 5 | 19 | 35 | 0 | 0 | 0 | 20 | 300 | 140 | 83 | 90 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 17 | 158 | 154 | 62 | 17 | 0 | 42 | 30 | 50 | 0 | 163 | 311 | 52 | 77 | 0 | 120 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 245 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 102 | 155 | 368 | 115 | 88 | 35 | 0 | 0 | 54 | 34 | 114 | 114 | 100 | 401 | 95 | 0 | 162 | 116 | 0 | 35 | 0 |  | 893 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 32 | 88 | 35 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 42 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 151 | 0 | 94 | 0 | 183 | 0 | 402 | 105 | 0 | 112 | 0 | 112 | 0 | 0 | 113 | 540 | 0 | 0 | 17 | 0 |  | 8475 | 3901 | 12376 | 4444 | 893 | 2100 | 3750 | 690 | 25 | 316 | 158 | 0 | 0 | 74.01
5:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 390 | 347 |  | 0 | 300 | 250 | 0 | 0 | 55 | 222 | 0 | 150 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 24 | 0 | 17 | 80 | 25 | 0 | 19 | 34 | 0 | 0 | 0 | 20 | 300 | 140 | 83 | 85 | 26 | 53 | 0 | 51 | 0 | 0 | 44 | 21 | 8 | 33 | 17 | 152 | 156 | 62 | 17 | 0 | 42 | 30 | 50 | 0 | 130 | 307 | 52 | 78 | 0 | 120 | 0 | 0 | 7 | 300 | 16 | 11 | 0 | 243 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 102 | 155 | 367 | 115 | 88 | 35 | 0 | 16 | 54 | 34 | 88 | 111 | 100 | 401 | 94 | 0 | 162 | 116 | 0 | 35 | 0 |  | 892 | 0 | 285 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 32 | 88 | 34 | 80 | 0 | 0 | 0 | 50 | 0 | 95 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 107 | 0 | 154 | 0 | 92 | 0 | 183 | 0 | 333 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 540 | 0 | 0 | 0 | 0 |  | 8359 | 3743 | 12102 | 4412 | 892 | 2015 | 3601 | 690 | 25 | 315 | 152 | 0 | 0 | 74
6:00 | 0 | 0 | 0 | 180 | 0 | 13 | 0 | 388 | 308 |  | 0 | 300 | 260 | 0 | 0 | 55 | 160 | 0 | 120 | 100 | 48 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 17 | 80 | 26 | 0 | 19 | 32 | 0 | 0 | 0 | 140 | 265 | 45 | 83 | 88 | 26 | 50 | 0 | 51 | 0 | 0 | 44 | 19 | 8 | 33 | 17 | 128 | 157 | 62 | 19 | 0 | 42 | 30 | 50 | 0 | 130 | 308 | 52 | 78 | 0 | 120 | 0 | 0 | 7 | 280 | 16 | 11 | 0 | 125 | 0 | 0 | 191 | 0 | 149 | 0 | 50 | 102 | 90 | 336 | 115 | 88 | 0 | 0 | 16 | 54 | 0 | 34 | 115 | 50 | 400 | 94 | 1 | 162 | 0 | 0 | 35 | 1 |  | 892 | 0 | 290 | 0 | 90 | 0 | 0 | 0 | 3 | 0 | 0 | 88 | 27 | 32 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 111 | 0 | 154 | 0 | 93 | 0 | 189 | 0 | 310 | 105 | 0 | 70 | 0 | 112 | 0 | 0 | 70 | 530 | 0 | 0 | 0 | 0 |  | 7472 | 3494 | 10966 | 4296 | 892 | 1832 | 2846 | 680 | 25 | 265 | 128 | 2 | 0 | 73.99
7:00 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 385 | 308 |  | 0 | 300 | 270 | 0 | 0 | 55 | 160 | 0 | 113 | 100 | 48 | 150 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 229 | 0 | 120 | 0 |  | 23 | 0 | 12 | 80 | 50 | 50 | 19 | 26 | 0 | 0 | 0 | 245 | 265 | 35 | 83 | 85 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 120 | 157 | 62 | 19 | 1 | 42 | 30 | 50 | 0 | 130 | 310 | 52 | 78 | 0 | 120 | 0 | 0 | 7 | 270 | 16 | 11 | 0 | 125 | 0 | 0 | 191 | 0 | 149 | 6 | 10 | 102 | 10 | 331 | 115 | 88 | 0 | 2 | 16 | 0 | 0 | 0 | 120 | 10 | 360 | 96 | 12 | 162 | 0 | 0 | 35 | 8 |  | 892 | 0 | 295 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 113 | 0 | 154 | 0 | 95 | 0 | 190 | 0 | 293 | 105 | 0 | 70 | 0 | 113 | 0 | 1 | 35 | 520 | 0 | 0 | 0 | 0 |  | 7390 | 3404 | 10794 | 4371 | 892 | 1802 | 2624 | 670 | 25 | 260 | 120 | 30 | 0 | 73.98
8:00 | 0 | 0 | 0 | 180 | 0 | 25 | 0 | 329 | 308 |  | 0 | 300 | 265 | 0 | 0 | 55 | 160 | 0 | 120 | 100 | 24 | 115 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 25 | 0 | 0 | 17 | 229 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 77 | 50 | 19 | 6 | 0 | 0 | 0 | 235 | 275 | 51 | 83 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 140 | 154 | 63 | 19 | 1 | 42 | 30 | 50 | 0 | 130 | 308 | 51 | 78 | 0 | 120 | 0 | 0 | 7 | 290 | 16 | 11 | 0 | 85 | 0 | 0 | 80 | 0 | 149 | 0 | 100 | 102 | 10 | 338 | 115 | 88 | 0 | 3 | 53 | 0 | 0 | 0 | 115 | 50 | 360 | 95 | 26 | 162 | 0 | 0 | 35 | 15 |  | 892 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 117 | 0 | 154 | 0 | 94 | 0 | 190 | 0 | 339 | 105 | 0 | 35 | 0 | 112 | 0 | 2 | 35 | 510 | 0 | 0 | 0 | 0 |  | 7377 | 3408 | 10785 | 4359 | 892 | 1859 | 2599 | 660 | 25 | 204 | 140 | 47 | 0 | 73.97
9:00 | 0 | 0 | 0 | 180 | 0 | 85 | 0 | 332 | 301 |  | 0 | 300 | 270 | 0 | 0 | 55 | 216 | 0 | 118 | 100 | 24 | 115 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 80 | 65 | 50 | 19 | 4 | 0 | 0 | 0 | 230 | 275 | 95 | 83 | 91 | 26 | 52 | 0 | 51 | 0 | 0 | 52 | 19 | 8 | 33 | 20 | 148 | 154 | 63 | 19 | 2 | 42 | 30 | 50 | 0 | 163 | 308 | 51 | 78 | 0 | 120 | 0 | 0 | 7 | 290 | 16 | 8 | 0 | 120 | 0 | 0 | 80 | 0 | 149 | 0 | 100 | 97 | 10 | 331 | 115 | 88 | 0 | 4 | 58 | 0 | 0 | 0 | 120 | 50 | 360 | 95 | 40 | 162 | 0 | 0 | 0 | 23 |  | 893 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 117 | 0 | 148 | 0 | 91 | 0 | 196 | 0 | 339 | 105 | 0 | 77 | 0 | 113 | 0 | 4 | 90 | 510 | 0 | 0 | 0 | 0 |  | 7568 | 3470 | 11038 | 4419 | 893 | 1936 | 2703 | 660 | 25 | 181 | 148 | 73 | 0 | 73.96
10:00 | 0 | 0 | 0 | 180 | 0 | 94 | 0 | 332 | 242 |  | 0 | 300 | 240 | 0 | 0 | 55 | 208 | 0 | 115 | 100 | 40 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 68 | 50 | 22 | 2 | 0 | 0 | 0 | 235 | 295 | 213 | 83 | 86 | 26 | 51 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 152 | 153 | 55 | 19 | 2 | 42 | 30 | 47 | 0 | 163 | 330 | 51 | 75 | 0 | 120 | 0 | 0 | 7 | 290 | 16 | 8 | 0 | 165 | 0 | 0 | 80 | 0 | 149 | 0 | 100 | 85 | 20 | 367 | 115 | 88 | 0 | 5 | 83 | 0 | 0 | 34 | 118 | 90 | 400 | 95 | 51 | 144 | 0 | 0 | 0 | 26 |  | 892 | 0 | 305 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 112 | 0 | 148 | 0 | 89 | 0 | 184 | 0 | 369 | 105 | 0 | 112 | 0 | 113 | 0 | 5 | 95 | 500 | 0 | 0 | 0 | 1 |  | 7867 | 3519 | 11386 | 4627 | 892 | 1904 | 2865 | 650 | 25 | 181 | 152 | 90 | 0 | 73.95
11:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 331 | 211 |  | 0 | 300 | 275 | 0 | 0 | 55 | 212 | 0 | 117 | 100 | 66 | 115 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 42 | 0 | 0 | 25 | 0 | 0 | 17 | 228 | 0 | 120 | 0 |  | 23 | 0 | 0 | 80 | 60 | 50 | 22 | 2 | 0 | 0 | 0 | 230 | 295 | 211 | 83 | 90 | 26 | 30 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 160 | 148 | 63 | 19 | 2 | 42 | 30 | 47 | 0 | 163 | 319 | 55 | 75 | 0 | 120 | 18 | 0 | 6 | 280 | 16 | 11 | 0 | 195 | 0 | 0 | 80 | 0 | 149 | 0 | 100 | 85 | 65 | 367 | 115 | 88 | 0 | 5 | 134 | 0 | 0 | 34 | 117 | 90 | 387 | 96 | 56 | 144 | 0 | 0 | 0 | 35 |  | 892 | 0 | 300 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 84 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 110 | 0 | 146 | 0 | 91 | 0 | 178 | 0 | 406 | 70 | 0 | 112 | 0 | 113 | 0 | 7 | 95 | 500 | 0 | 0 | 0 | 2 |  | 8033 | 3504 | 11537 | 4624 | 892 | 1882 | 3016 | 650 | 25 | 181 | 160 | 107 | 0 | 73.94
12:00 | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 337 | 201 |  | 0 | 300 | 265 | 0 | 0 | 55 | 208 | 0 | 180 | 100 | 75 | 150 | 41 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 60 | 47 | 22 | 2 | 0 | 0 | 0 | 230 | 295 | 211 | 83 | 90 | 26 | 30 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 166 | 150 | 55 | 19 | 2 | 41 | 30 | 46 | 0 | 163 | 320 | 56 | 73 | 0 | 120 | 17 | 0 | 6 | 300 | 16 | 11 | 0 | 200 | 0 | 0 | 88 | 0 | 149 | 0 | 100 | 100 | 92 | 404 | 115 | 88 | 0 | 5 | 162 | 0 | 0 | 98 | 116 | 90 | 385 | 95 | 27 | 144 | 0 | 0 | 5 | 27 |  | 892 | 0 | 295 | 0 | 90 | 0 | 0 | 0 | 3 | 0 | 0 | 84 | 23 | 0 | 0 | 0 | 0 | 0 | 7 | 70 | 12 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 107 | 0 | 136 | 0 | 92 | 0 | 172 | 0 | 401 | 70 | 0 | 112 | 0 | 112 | 0 | 7 | 113 | 520 | 0 | 0 | 3 | 3 |  | 8291 | 3544 | 11835 | 4678 | 892 | 1870 | 3234 | 669 | 25 | 230 | 166 | 71 | 0 | 73.93
13:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 355 | 192 |  | 0 | 300 | 275 | 0 | 0 | 55 | 186 | 0 | 178 | 100 | 102 | 150 | 77 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 20 | 0 | 0 | 10 | 0 | 0 | 0 | 0 |  | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 230 | 295 | 212 | 83 | 85 | 26 | 30 | 0 | 51 | 0 | 0 | 52 | 17 | 8 | 33 | 12 | 160 | 143 | 63 | 19 | 2 | 40 | 30 | 48 | 0 | 163 | 323 | 56 | 72 | 0 | 120 | 17 | 0 | 6 | 310 | 16 | 11 | 30 | 228 | 111 | 10 | 96 | 7 | 149 | 0 | 0 | 102 | 140 | 335 | 104 | 70 | 0 | 3 | 0 | 0 | 0 | 114 | 115 | 0 | 387 | 95 | 25 | 144 | 0 | 0 | 17 | 33 |  | 892 | 0 | 265 | 0 | 66 | 0 | 0 | 0 | 3 | 0 | 32 | 83 | 27 | 20 | 0 | 0 | 0 | 0 | 7 | 82 | 42 | 0 | 29 | 43 | 0 | 16 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 99 | 0 | 129 | 0 | 91 | 2 | 157 | 0 | 357 | 70 | 0 | 112 | 0 | 108 | 0 | 7 | 113 | 560 | 0 | 0 | 17 | 3 |  | 7641 | 3592 | 11233 | 4180 | 892 | 1850 | 3078 | 709 | 20 | 271 | 160 | 73 | 0 | 73.92
14:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 342 | 187 |  | 0 | 300 | 290 | 0 | 0 | 55 | 201 | 0 | 155 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 20 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 55 | 0 | 30 | 19 | 2 | 0 | 0 | 0 | 220 | 315 | 193 | 83 | 95 | 26 | 30 | 0 | 51 | 0 | 0 | 52 | 17 | 8 | 33 | 12 | 168 | 127 | 63 | 19 | 2 | 40 | 30 | 46 | 0 | 163 | 316 | 50 | 70 | 0 | 120 | 17 | 0 | 6 | 290 | 16 | 11 | 20 | 235 | 26 | 0 | 120 | 28 | 149 | 0 | 60 | 102 | 110 | 385 | 115 | 70 | 0 | 2 | 60 | 0 | 0 | 114 | 110 | 77 | 369 | 95 | 43 | 144 | 0 | 0 | 19 | 21 |  | 893 | 0 | 280 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 82 | 20 | 32 | 0 | 0 | 0 | 0 | 5 | 96 | 42 | 0 | 30 | 43 | 0 | 16 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 92 | 0 | 126 | 0 | 91 | 0 | 145 | 0 | 390 | 105 | 0 | 112 | 0 | 108 | 0 | 7 | 113 | 550 | 0 | 0 | 17 | 3 |  | 7845 | 3644 | 11489 | 4155 | 893 | 1845 | 3347 | 699 | 20 | 284 | 168 | 78 | 0 | 73.91
15:00 | 0 | 0 | 0 | 180 | 0 | 94 | 0 | 369 | 186 |  | 0 | 300 | 295 | 0 | 0 | 55 | 202 | 0 | 170 | 100 | 102 | 149 | 85 | 0 | 0 | 0 | 35 | 35 | 55 | 13 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 20 | 0 | 0 | 17 | 0 | 0 | 0 | 0 |  | 23 | 0 | 30 | 80 | 13 | 33 | 19 | 2 | 0 | 0 | 0 | 215 | 310 | 160 | 83 | 91 | 26 | 10 | 0 | 51 | 0 | 0 | 52 | 14 | 8 | 33 | 12 | 170 | 126 | 55 | 19 | 2 | 40 | 30 | 47 | 0 | 163 | 312 | 54 | 71 | 0 | 120 | 17 | 0 | 6 | 315 | 16 | 11 | 125 | 243 | 232 | 0 | 130 | 94 | 149 | 2 | 80 | 102 | 110 | 381 | 115 | 70 | 0 | 3 | 181 | 0 | 0 | 114 | 115 | 90 | 368 | 95 | 39 | 144 | 0 | 0 | 31 | 12 |  | 890 | 0 | 270 | 0 | 69 | 0 | 0 | 0 | 3 | 0 | 32 | 82 | 20 | 42 | 0 | 0 | 0 | 0 | 5 | 96 | 42 | 0 | 30 | 43 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 123 | 0 | 90 | 0 | 145 | 0 | 390 | 105 | 0 | 111 | 0 | 103 | 0 | 7 | 113 | 550 | 0 | 0 | 17 | 2 |  | 8470 | 3647 | 12117 | 4140 | 890 | 1844 | 3973 | 700 | 20 | 313 | 170 | 67 | 0 | 73.9
16:00 | 0 | 0 | 0 | 180 | 0 | 97 | 0 | 371 | 177 |  | 0 | 300 | 285 | 0 | 0 | 55 | 83 | 0 | 170 | 100 | 102 | 149 | 73 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 60 | 0 | 0 | 0 |  | 23 | 0 | 45 | 80 | 27 | 44 | 21 | 2 | 0 | 0 | 0 | 215 | 305 | 178 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 18 | 8 | 33 | 12 | 150 | 142 | 55 | 19 | 1 | 39 | 28 | 47 | 0 | 163 | 314 | 54 | 71 | 0 | 120 | 17 | 0 | 6 | 315 | 16 | 11 | 193 | 245 | 297 | 85 | 130 | 96 | 149 | 0 | 80 | 102 | 0 | 367 | 115 | 52 | 0 | 3 | 245 | 0 | 0 | 114 | 115 | 90 | 367 | 95 | 26 | 144 | 0 | 0 | 35 | 5 |  | 819 | 0 | 230 | 0 | 78 | 0 | 0 | 0 | 3 | 0 | 32 | 0 | 26 | 64 | 0 | 0 | 0 | 0 | 6 | 96 | 42 | 0 | 12 | 52 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 90 | 0 | 122 | 0 | 90 | 0 | 130 | 0 | 0 | 105 | 0 | 111 | 0 | 108 | 0 | 6 | 113 | 550 | 15 | 0 | 17 | 0 |  | 8403 | 3094 | 11497 | 3943 | 819 | 1325 | 4183 | 700 | 25 | 311 | 150 | 41 | 0 | 73.89
17:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 352 | 177 |  | 0 | 300 | 285 | 0 | 0 | 55 | 160 | 0 | 115 | 100 | 102 | 149 | 73 | 0 | 0 | 0 | 35 | 35 | 10 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 0 | 0 | 215 | 305 | 123 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 52 | 19 | 5 | 33 | 12 | 164 | 97 | 55 | 19 | 0 | 41 | 30 | 47 | 0 | 163 | 307 | 55 | 71 | 0 | 120 | 17 | 0 | 6 | 290 | 16 | 11 | 195 | 245 | 295 | 85 | 120 | 98 | 149 | 0 | 0 | 94 | 0 | 366 | 115 | 70 | 0 | 1 | 0 | 0 | 0 | 114 | 115 | 0 | 362 | 95 | 7 | 144 | 0 | 0 | 35 | 4 |  | 825 | 0 | 200 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 16 | 30 | 26 | 64 | 0 | 0 | 0 | 0 | 50 | 96 | 42 | 0 | 15 | 52 | 0 | 16 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 105 | 0 | 127 | 0 | 89 | 0 | 130 | 0 | 0 | 105 | 0 | 113 | 0 | 108 | 0 | 3 | 113 | 480 | 21 | 0 | 17 | 0 |  | 7555 | 3106 | 10661 | 3816 | 825 | 1308 | 3565 | 630 | 25 | 313 | 164 | 15 | 0 | 73.88
18:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 330 | 176 |  | 0 | 300 | 245 | 0 | 0 | 55 | 150 | 0 | 80 | 100 | 102 | 149 | 84 | 0 | 0 | 0 | 35 | 35 | 50 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 41 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 10 | 44 | 20 | 2 | 0 | 0 | 0 | 215 | 295 | 125 | 0 | 86 | 26 | 10 | 0 | 0 | 0 | 0 | 52 | 20 | 5 | 33 | 12 | 138 | 131 | 63 | 19 | 0 | 41 | 30 | 49 | 0 | 130 | 330 | 56 | 73 | 0 | 120 | 17 | 0 | 7 | 260 | 16 | 11 | 200 | 238 | 113 | 50 | 80 | 100 | 149 | 0 | 50 | 104 | 0 | 405 | 115 | 86 | 0 | 0 | 121 | 0 | 0 | 114 | 118 | 40 | 380 | 95 | 1 | 144 | 0 | 0 | 35 | 1 |  | 831 | 0 | 165 | 0 | 99 | 0 | 0 | 0 | 3 | 8 | 8 | 25 | 27 | 64 | 0 | 0 | 0 | 0 | 47 | 96 | 42 | 0 | 22 | 52 | 0 | 15 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 126 | 0 | 130 | 0 | 93 | 0 | 130 | 0 | 0 | 105 | 0 | 70 | 0 | 104 | 0 | 1 | 35 | 400 | 18 | 0 | 17 | 0 |  | 7639 | 2894 | 10533 | 3883 | 831 | 1260 | 3518 | 550 | 25 | 325 | 138 | 3 | 0 | 73.87
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 310 | 176 |  | 0 | 300 | 285 | 0 | 0 | 55 | 210 | 0 | 170 | 100 | 102 | 149 | 85 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 71 | 0 | 0 | 0 |  | 24 | 0 | 0 | 76 | 63 | 42 | 0 | 6 | 0 | 0 | 0 | 230 | 320 | 135 | 16 | 90 | 26 | 10 | 0 | 0 | 0 | 0 | 52 | 21 | 5 | 33 | 15 | 126 | 150 | 63 | 19 | 0 | 41 | 30 | 49 | 0 | 163 | 331 | 56 | 77 | 0 | 120 | 17 | 0 | 7 | 310 | 16 | 11 | 100 | 245 | 160 | 71 | 105 | 100 | 149 | 0 | 100 | 104 | 0 | 403 | 115 | 86 | 0 | 0 | 234 | 52 | 20 | 114 | 110 | 100 | 388 | 95 | 0 | 144 | 17 | 0 | 11 | 0 |  | 826 | 0 | 315 | 0 | 99 | 0 | 0 | 0 | 10 | 1 | 32 | 86 | 34 | 110 | 0 | 0 | 0 | 0 | 50 | 96 | 42 | 34 | 30 | 52 | 4 | 20 | 0 | 11 | 0 | 0 | 150 | 12 | 0 | 139 | 0 | 133 | 0 | 94 | 10 | 137 | 0 | 0 | 105 | 0 | 58 | 0 | 113 | 0 | 0 | 90 | 340 | 57 | 0 | 20 | 0 |  | 8379 | 3310 | 11689 | 4341 | 826 | 1419 | 4110 | 490 | 25 | 352 | 126 | 0 | 0 | 73.84
19:30 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 329 | 176 |  | 0 | 300 | 275 | 0 | 0 | 55 | 214 | 0 | 150 | 100 | 102 | 149 | 86 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 71 | 0 | 0 | 0 |  | 24 | 0 | 42 | 76 | 97 | 46 | 0 | 10 | 0 | 0 | 0 | 235 | 295 | 145 | 16 | 90 | 10 | 10 | 0 | 5 | 0 | 0 | 52 | 0 | 0 | 33 | 15 | 102 | 151 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 130 | 328 | 56 | 77 | 0 | 120 | 17 | 0 | 0 | 310 | 16 | 11 | 100 | 245 | 105 | 82 | 190 | 100 | 149 | 0 | 100 | 103 | 0 | 403 | 115 | 86 | 0 | 0 | 153 | 54 | 34 | 114 | 110 | 80 | 394 | 95 | 0 | 144 | 110 | 0 | 17 | 0 |  | 827 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 17 | 0 | 32 | 86 | 34 | 110 | 0 | 0 | 0 | 31 | 45 | 96 | 42 | 34 | 30 | 52 | 14 | 20 | 0 | 11 | 0 | 0 | 150 | 17 | 0 | 142 | 0 | 132 | 0 | 76 | 100 | 172 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 165 | 0 | 54 | 0 |  | 8406 | 3947 | 12353 | 4384 | 827 | 1479 | 4395 | 700 | 25 | 441 | 102 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 333 | 177 |  | 0 | 300 | 285 | 0 | 0 | 55 | 214 | 0 | 151 | 94 | 102 | 149 | 84 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 1 | 71 | 0 | 0 | 0 |  | 24 | 0 | 51 | 76 | 97 | 46 | 20 | 11 | 0 | 0 | 0 | 235 | 325 | 159 | 16 | 90 | 10 | 10 | 0 | 15 | 0 | 0 | 52 | 0 | 0 | 33 | 15 | 122 | 149 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 130 | 325 | 56 | 77 | 0 | 120 | 17 | 0 | 7 | 295 | 16 | 11 | 0 | 245 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 103 | 0 | 404 | 115 | 86 | 24 | 0 | 16 | 54 | 34 | 0 | 110 | 50 | 388 | 95 | 0 | 144 | 116 | 0 | 17 | 0 |  | 826 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 15 | 0 | 32 | 86 | 34 | 110 | 0 | 0 | 0 | 50 | 45 | 96 | 42 | 34 | 31 | 52 | 30 | 20 | 0 | 11 | 0 | 0 | 150 | 12 | 0 | 144 | 0 | 132 | 0 | 42 | 88 | 181 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 470 | 165 | 0 | 54 | 0 |  | 7872 | 3860 | 11732 | 4462 | 826 | 1449 | 3749 | 620 | 25 | 479 | 122 | 0 | 0 | 73.85
21:00 | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 357 | 171 |  | 0 | 300 | 240 | 0 | 0 | 55 | 216 | 0 | 180 | 92 | 102 | 149 | 74 | 0 | 0 | 0 | 35 | 35 | 55 | 20 | 25 | 21 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 12 | 80 | 0 | 0 | 0 |  | 24 | 0 | 51 | 76 | 97 | 46 | 21 | 30 | 0 | 0 | 0 | 245 | 295 | 181 | 16 | 86 | 10 | 10 | 0 | 43 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 16 | 0 | 57 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 330 | 32 | 77 | 0 | 120 | 17 | 0 | 7 | 305 | 16 | 11 | 0 | 245 | 0 | 0 | 0 | 0 | 149 | 0 | 100 | 103 | 8 | 401 | 0 | 86 | 53 | 0 | 16 | 54 | 51 | 0 | 115 | 100 | 399 | 95 | 0 | 144 | 116 | 0 | 17 | 0 |  | 826 | 0 | 390 | 0 | 104 | 0 | 0 | 0 | 15 | 0 | 32 | 86 | 25 | 80 | 0 | 0 | 0 | 50 | 42 | 96 | 42 | 34 | 30 | 52 | 34 | 21 | 0 | 11 | 0 | 0 | 150 | 8 | 0 | 142 | 0 | 142 | 0 | 15 | 100 | 206 | 0 | 94 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 196 | 0 | 0 | 0 |  | 7461 | 3977 | 11438 | 4378 | 826 | 1625 | 3433 | 660 | 25 | 475 | 16 | 0 | 0 | 73.84
22:00 | 0 | 0 | 0 | 180 | 0 | 103 | 0 | 317 | 161 |  | 0 | 300 | 220 | 0 | 0 | 30 | 150 | 0 | 0 | 100 | 48 | 82 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 25 | 0 | 33 | 0 | 41 | 0 | 0 | 25 | 0 | 0 | 8 | 122 | 0 | 0 | 0 |  | 24 | 0 | 60 | 76 | 0 | 19 | 21 | 30 | 0 | 0 | 0 | 200 | 280 | 175 | 16 | 86 | 10 | 10 | 0 | 51 | 0 | 0 | 25 | 0 | 0 | 33 | 0 | 80 | 70 | 18 | 19 | 0 | 43 | 30 | 50 | 0 | 110 | 330 | 33 | 78 | 0 | 120 | 17 | 0 | 7 | 250 | 16 | 0 | 0 | 95 | 0 | 0 | 70 | 0 | 149 | 0 | 100 | 17 | 103 | 364 | 36 | 86 | 51 | 0 | 0 | 54 | 51 | 0 | 16 | 100 | 369 | 88 | 0 | 144 | 53 | 0 | 17 | 0 |  | 865 | 0 | 175 | 0 | 115 | 0 | 0 | 0 | 15 | 0 | 32 | 81 | 34 | 48 | 0 | 0 | 0 | 50 | 0 | 96 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 8 | 0 | 144 | 0 | 195 | 0 | 15 | 100 | 211 | 0 | 244 | 105 | 0 | 98 | 0 | 113 | 0 | 0 | 113 | 480 | 172 | 0 | 0 | 0 |  | 6312 | 3743 | 10055 | 3860 | 865 | 1652 | 2632 | 630 | 25 | 311 | 80 | 0 | 0 | 73.83
23:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 283 | 252 |  | 0 | 300 | 225 | 0 | 0 | 15 | 150 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 202 | 0 | 0 | 0 |  | 24 | 0 | 34 | 50 | 0 | 0 | 21 | 37 | 0 | 0 | 0 | 200 | 270 | 163 | 16 | 86 | 10 | 10 | 0 | 51 | 0 | 0 | 8 | 0 | 0 | 33 | 0 | 106 | 76 | 38 | 19 | 0 | 44 | 30 | 11 | 0 | 130 | 332 | 33 | 20 | 0 | 120 | 17 | 0 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 118 | 0 | 50 | 17 | 0 | 304 | 115 | 17 | 51 | 0 | 0 | 54 | 0 | 0 | 16 | 50 | 300 | 0 | 0 | 0 | 17 | 0 | 0 | 0 |  | 892 | 0 | 280 | 0 | 115 | 0 | 0 | 0 | 15 | 0 | 32 | 86 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 8 | 0 | 100 | 0 | 162 | 0 | 15 | 100 | 210 | 0 | 305 | 105 | 0 | 112 | 0 | 113 | 0 | 0 | 70 | 450 | 149 | 0 | 0 | 0 |  | 5223 | 3651 | 8874 | 3777 | 892 | 1669 | 1700 | 600 | 25 | 105 | 106 | 0 | 0 | 73.82
24:00 | 0 | 0 | 0 | 180 | 0 | 53 | 0 | 283 | 304 |  | 0 | 300 | 265 | 0 | 0 | 15 | 180 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 0 | 0 |  | 0 | 0 | 34 | 80 | 0 | 7 | 21 | 35 | 0 | 0 | 0 | 200 | 305 | 195 | 16 | 91 | 10 | 10 | 0 | 10 | 0 | 0 | 8 | 22 | 0 | 8 | 0 | 110 | 92 | 63 | 19 | 0 | 43 | 30 | 14 | 0 | 163 | 330 | 32 | 20 | 0 | 120 | 17 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 55 | 0 | 70 | 17 | 0 | 340 | 85 | 0 | 53 | 0 | 0 | 54 | 0 | 0 | 0 | 70 | 300 | 0 | 0 | 0 | 26 | 0 | 11 | 0 |  | 892 | 0 | 340 | 0 | 115 | 0 | 0 | 0 | 8 | 0 | 0 | 85 | 34 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 8 | 0 | 100 | 0 | 169 | 0 | 14 | 0 | 207 | 0 | 334 | 17 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 420 | 155 | 0 | 0 | 0 |  | 5528 | 3433 | 8961 | 4039 | 892 | 1763 | 1512 | 570 | 25 | 50 | 110 | 0 | 0 | 73.81
KWH | 0 | 0 | 0 | 4158000 | 0 | 2015636 | 0 | 8511490 | 5944000 |  | 0 | 7120750 | 6335622 | 0 | 0 | 1267427 | 4756402 | 0 | 3532000 | 2214710 | 1906416 | 3137280 | 1136815 | 0 | 0 | 0 | 711000 | 789008 | 1162833 | 347076 | 600000 | 344340 | 750600 | 708800 | 881760 | 0 | 0 | 580000 | 0 | 0 | 333518 | 4816254 | 0 | 1518189 | 0 |  | 546720 | 0 | 444683 | 1653480 | 910080 | 694080 | 410592 | 362880 | 0 | 0 | 0 | 4423500 | 7152000 | 3511000 | 1421818 | 2126210 | 504000 | 756960 | 0 | 948766 | 0 | 108576 | 1128475 | 375912 | 135360 | 743400 | 353190 | 3399360 | 3071280 | 1362240 | 385344 | 15150 | 999000 | 699720 | 1111800 | 0 | 3502064 | 7256000 | 1184928 | 1704960 | 0 | 2893770 | 209000 | 0 | 143280 | 7109500 | 347424 | 230000 | 1280448 | 4767271 | 1504531 | 467916 | 3242400 | 805180 | 3482640 | 27540 | 1890240 | 2209920 | 1532218 | 8862000 | 2611200 | 1886976 | 459163 | 37680 | 1523018 | 692221 | 441598 | 1557240 | 2522520 | 1752960 | 9030900 | 2112000 | 368840 | 3405600 | 1014927 | 0 | 591480 | 213349 |  | 21145455 | 0 | 6927264 | 0 | 2167680 | 0 | 0 | 0 | 148800 | 11264 | 451500 | 1909309 | 694090 | 1316160 | 0 | 0 | 0 | 434114 | 399957 | 1962280 | 593560 | 244211 | 320029 | 1170720 | 197100 | 440400 | 0 | 229842 | 0 | 0 | 3668000 | 0 | 0 | 2793900 | 0 | 3689745 | 0 | 1913567 | 743040 | 4466900 | 0 | 6760327 | 2480160 | 228035 | 2468256 | 0 | 2697600 | 0 | 56163 | 2352288 | 13153800 | 917073 | 0 | 302400 | 17940 |  | 190210404 | 89472929 | 279683333 | 104964641 | 21145455 | 42867871 | 82003461 | 16821800 | 580000 | 7164083 | 3399360 | 736662 | 0
Fuel Cost | 0 | 0 | 0 | 6112260 | 0 | 2660639.52 | 0 | 8596604.9 | 6122320 |  | 0 | 7761617.5 | 7032540.42 | 0 | 0 | 10722432.42 | 4946658.08 | 0 | 6110360 | 16676766.3 | 17386513.92 | 30870835.2 | 10481434.3 | 0 | 0 | 0 | 5190300 | 6099031.84 | 11465533.38 | 260307 | 450000 | 0 | 0 | 0 | 8526619.2 | 0 | 0 | 156600 | 0 | 0 | 3098382.22 | 5249716.86 | 0 | 2580921.3 | 0 |  | 0 | 0 | 4313425.1 | 15790734 | 7917696 | 5497113.6 | 517345.92 | 1077753.6 | 0 | 0 | 0 | 3273390 | 7152000 | 3230120 | 1834145.22 | 2445141.5 | 569520 | 1059744 | 0 | 1622389.86 | 0 | 1096617.6 | 10776936.25 | 477408.24 | 101520 | 1300950 | 264892.5 | 25495200 | 3255556.8 | 12369139.2 | 489386.88 | 241491 | 1638360 | 1119552 | 1979004 | 0 | 3992352.96 | 7546240 | 2334308.16 | 3256473.6 | 0 | 5006222.1 | 457710 | 0 | 292291.2 | 7180595 | 260568 | 174800 | 21780420.48 | 36040568.76 | 25546936.38 | 7823555.52 | 16860480 | 13462609.6 | 34269177.6 | 321942.6 | 15405456 | 23977632 | 10802136.9 | 8241660 | 23814144 | 17831923.2 | 3999309.73 | 0 | 11514016.08 | 6029244.91 | 3881646.42 | 15541255.2 | 21617996.4 | 11674713.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 121797820.8 | 0 | 7273627.2 | 0 | 17037964.8 | 0 | 0 | 0 | 1560912 | 118046.72 | 4704630 | 2157519.17 | 1075839.5 | 12845721.6 | 0 | 0 | 0 | 4271681.76 | 4063563.12 | 17366178 | 4570412 | 3301732.72 | 3101081.01 | 11344276.8 | 1911870 | 845568 | 0 | 173990.394 | 0 | 0 | 19880560 | 0 | 0 | 3268863 | 0 | 4870463.4 | 0 | 2870350.5 | 12639110.4 | 5226273 | 0 | 6692723.73 | 25892870.4 | 3878875.35 | 23423749.44 | 0 | 20933376 | 0 | 620601.15 | 17383408.32 | 57745182 | 0 | 0 | 0 | 0 |  | 656403314.03 | 424848842.284 | 1081252156.314 | 107134216.404 | 121797820.8 | 50323808.19 | 628860523.66 | 77625742 | 156600 | 68674210.51 | 25495200 | 1184034.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 180 | 0 | 90 | 0 | 337 | 201 |  | 0 | 300 | 265 | 0 | 0 | 55 | 208 | 0 | 180 | 100 | 75 | 150 | 41 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 60 | 47 | 22 | 2 | 0 | 0 | 0 | 230 | 295 | 211 | 83 | 90 | 26 | 30 | 0 | 43 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 166 | 150 | 55 | 19 | 2 | 41 | 30 | 46 | 0 | 163 | 320 | 56 | 73 | 0 | 120 | 17 | 0 | 6 | 300 | 16 | 11 | 0 | 200 | 0 | 0 | 88 | 0 | 149 | 0 | 100 | 100 | 92 | 404 | 115 | 88 | 0 | 5 | 162 | 0 | 0 | 98 | 116 | 90 | 385 | 95 | 27 | 144 | 0 | 0 | 5 | 27 |  | 892 | 0 | 295 | 0 | 90 | 0 | 0 | 0 | 3 | 0 | 0 | 84 | 23 | 0 | 0 | 0 | 0 | 0 | 7 | 70 | 12 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 107 | 0 | 136 | 0 | 92 | 0 | 172 | 0 | 401 | 70 | 0 | 112 | 0 | 112 | 0 | 7 | 113 | 520 | 0 | 0 | 3 | 3 |  | 11835 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 329 | 176 | 0 | 0 | 300 | 275 | 0 | 0 | 55 | 214 | 0 | 150 | 100 | 102 | 149 | 86 | 0 | 0 | 0 | 35 | 35 | 55 | 19 | 25 | 12 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 0 | 71 | 0 | 0 | 0 | 0 | 24 | 0 | 42 | 76 | 97 | 46 | 0 | 10 | 0 | 0 | 0 | 235 | 295 | 145 | 16 | 90 | 10 | 10 | 0 | 5 | 0 | 0 | 52 | 0 | 0 | 33 | 15 | 102 | 151 | 63 | 19 | 0 | 42 | 30 | 50 | 0 | 130 | 328 | 56 | 77 | 0 | 120 | 17 | 0 | 0 | 310 | 16 | 11 | 100 | 245 | 105 | 82 | 190 | 100 | 149 | 0 | 100 | 103 | 0 | 403 | 115 | 86 | 0 | 0 | 153 | 54 | 34 | 114 | 110 | 80 | 394 | 95 | 0 | 144 | 110 | 0 | 17 | 0 |  | 827 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 17 | 0 | 32 | 86 | 34 | 110 | 0 | 0 | 0 | 31 | 45 | 96 | 42 | 34 | 30 | 52 | 14 | 20 | 0 | 11 | 0 | 0 | 150 | 17 | 0 | 142 | 0 | 132 | 0 | 76 | 100 | 172 | 0 | 0 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 165 | 0 | 54 | 0 |  | 12353 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 180 | 0 | 102 | 0 | 390 | 360 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 185 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 220 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 50 | 20 | 25 | 0 | 0 | 100 | 360 | 330 | 215 | 45 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 181 | 160 | 64 | 19 | 0 | 42 | 30 | 44 | 0 | 163 | 330 | 57 | 76 | 0 | 140 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 125 | 150 | 400 | 115 | 105 | 90 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 0 | 162 | 116 | 0 | 36 |  |  | 909 | 0 | 410 | 0 | 99 | 220 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 30 | 52 | 35 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 125 | 0 | 200 | 0 | 95 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 165 |  | 110
Forecast for Day | 0 | 0 | 0 | 180 | 0 | 100 | 0 | 360 | 360 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 180 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 25 | 0 | 0 | 17 | 220 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 100 | 50 | 20 | 10 | 0 | 0 | 80 | 360 | 330 | 215 | 45 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 145 | 160 | 64 | 19 | 1.6 | 42 | 30 | 44 | 0 | 163 | 163 | 57 | 76 | 0 | 140 | 18 | 0 | 7 | 341 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 125 | 150 | 400 | 115 | 105 | 70 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 72 | 50 | 162 | 116 | 0 | 35 | 30 |  | 909 | 0 | 410 | 0 | 99 | 0 | 0 | 0 | 20 | 60 | 32 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 43 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 125 | 0 | 200 | 0 | 95 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 110 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 180 | 0 | 98 | 0 | 302 | 302 | 0 | 0 | 300 | 265 | 0 | 0 | 0 | 222 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 21 | 33 |  | 0 | 0 | 0 | 25 | 0 | 0 | 17 | 203 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 51 | 25 | 21 | 8 | 0 | 0 | 0 | 360 | 300 | 185 | 45 | 91 | 23 | 52 | 0 | 10 | 0 | 0 | 43 | 19 | 5 | 33 | 8 | 100 | 159 | 19 | 0 | 0 | 42 | 30 | 14 | 0 | 163 | 163 | 32 | 78 | 0 | 120 | 17 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 10 | 34 | 0 | 340 | 13 | 39 | 53 | 2 | 0 | 54 | 0 | 0 | 36 | 10 | 300 | 0 | 21 | 0 | 53 | 0 | 17 | 8 | 0 | 892 | 0 | 240 | 0 | 32 | 0 | 0 | 0 | 5 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 65 | 0 | 135 | 0 | 15 | 0 | 130 | 0 | 235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 110 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 10785 | 8:00
| Highest Generation |  | 13012 | 1:00
| Day Peak Generation |  | 11835 | 12:00
| Evening Peak Generation |  | 12353 | 19:30
| HVDC Max Flow |  | 893 | 2:00
| HVDC EvPeak Flow |  | 827 | 19:30
| Load factor L.F |  | 89.56%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-25
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-24 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11835 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7904 | MW
Evening Peak Generation : |  | 12353 | MW Hour : | 19:30 | Available Max Generation : |  | 16053 | MW
E.P. Demand (at gen end) : |  | 12353 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 11800 | MW
Maximum Generation : |  | 13012 | MW Hour : | 1:00 | Reserve(Generation end) |  | 4253 | MW
Total Gen. (MKWH) : |  | 279.6833 | System Load Factor : | 89.56% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -438 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-25
Actual : | 73.75 | Ft.(MSL) , | Rule curve : | 77.4 | Ft.( MSL )
Gas Consumed : | Total = | 1187.87 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157458024.594
: |  | Coal : | 77625742 | Oil : | 697534734.17 | Total : | 932618500.764
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4169.4587 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1419.4527 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1272.0687 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1149.523 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1038.7513 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 838.2396 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 466.6357 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 215.7695 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 646.5019 |  |  | 0 | 0%
Total | 0 |  | 11216.401 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3,4
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Natore 132/33 kV T3 transformer was under shut down from 08:16 to 09:56 for C/M.
b) Shahjibazar 132/33 kV T4 transformer was under shut down from 09:06 to 15:10 for C/M
c) Haripur 132 kV reserve bus section-2 was shut down since at 09:04 for bus coupler loop changing.
d) Natore 132/33 kV T2 transformer was under shut down from 10:22 to 11:29 for C/M.
e) Sonargaon 132/33 kV T2 transformer was under shut down from 11:02 to 12:04 for C/M. |  |  |  |  | About 23 MW power interruption occurred under Sonargaon S/S
f) Natore-Rajlanka 132 kV Ckt-1 was under shut down from 12:03 to 13:50 for C/M. |  |  |  |  | areas from 11:02 to 12:04.
g) Saidpur 132/33 kV T3 transformer was under shut down from 10:34 to 11:39 for C/M.
h) Cantonment 132/33 kV T1 transformer tripped at 13:47 showing 87,OTI & master trip relay and was |  |  |  |  | About 28 MW power interruption occurred under Cantonment S/S
switched on at 14:20. |  |  |  |  | areas from 11:02 to 12:04.
i) Ashuganj(S)- Ashuganj 230 kV Ckt-1 was switched on at 13:46.
j) Bakulia-Kulshi 132 kV Ckt-1,2 tripped at 12:35 showing dist Z1,L3-E relay at Ckt-1 & directional O/C relay
at Ckt-2 and were switched on at 13:28,17:19 respectively.
k) Sikalbaha-Madunaghat 132 kV Ckt tripped at 12:35 from Sikalbaha end showing O/C,RYB,51,67N and
was switched on at 12:55.
l) Sikalbaha-TK 132 kV Ckt tripped at 12:38 from TK end showing dist ABC 3 phase AR in progress and
was switched on at 13:30.
m) Above the tripping Chattogram zone partially tripped, tripped S/S are Dohazari,Cox's bazar, Matarbari |  |  |  |  | About 364 MW power interruption occurred under Chattogram zone
Juldah,Shahmirpur,Sikalbaha,Bakulia following power station also tripped Sikalbaha 225 MW=204 MW
Anowara 300 MW=155,ECPV 108 MW=60,Juldha-1=80MW,Juldha-2=100,Juldha-3=100 total
699 MW load out of Chattogram zone.
n) Sikalbaha 225 MW GT & ST were synchronized at 15:35,20:54 respectively.
o) Ashuganj network-Ashuganj (S) 230 kV Ckt- tripped at 15:49 due to Y-phase CT burst
p) Ashuganj 230 kV bus-1,2 with all 230 kV line tripped at 15:49 showing L1,L2,L3, gen trip differential trip
and were switched on at 17:18 & Ashuganj-Sirajganj Ckt-1,2 were switched on at 17:31,17:33 &
Ashuganj-Cumilla(N)Ckt-1,2 were switched on at 17:18,17:48 respectively
q) Ghorasal(1)-Ishurdi(2) 230 kV Ckt tripped at 15:54 showing dist Z2 ST at Ghorasal end & dist B phase
at Ishurdi end and in this tripping Eastern grid and western grid are isolated in the National
grid was switched on at 17:14
r) Ashuganj 230/132 kV OAT12 was switched on at 18:06.
s) Chattogram Zone partially black out at 16:57 due to tripping of Sikalbaha 230 kV bus tripping and was |  |  |  |  | About 244 MW power interruption occurred under Juldah-Shahmirpur
switched on at 17:06. |  |  |  |  | Bakulia,Dohazari,Cox's bazar,Matarbari S/S areas from 16:57 to 17:06.
t) Mymensing RPCL,UMPL & UJPL are tripped at 20:54 due to SPS operated at Mymensing S/S then all
transformer are got trip and were switched on at 21:05.
u) Mymensing S/S-Mymensing RPCL 132 kV Ckt-1,2 were switched on at 21:12.
v) Siddhirganj PP GT-1 tripped at 21:45 showing O/C.
w) Siddhirganj-Matuail 132 kV Ckt tripped at 21:45 showing O/C and was switched on at 22:26.
x) Ashuganj-Sirajganj 230 kV Ckt-2 tripped at 23:41 showing dist Z1 at Ashuganj end & dist z2 126 km
at Sirajganj end and was switched on at 11:54.
y) Mymensing RPCL-Tangail 132 kV Ckt-1 tripped at 23:58 from RPCL end and was switched on at 00:10.
z) Dohazari-Cox's Bazar 132 kV Ckt-2 was shut down since 06:34(25-05-2021) for D/W.
aa) Shajibazar 330 MW GT-1 tripped at 05:44 and was synchronized at 06:50(25-05-2021) again trip at 08:00.
ab) Daudkandi 132/33 kV T2 transformer was under shut down from 07:09(25-05-2021) due to red hot maint.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-24 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 180 | 4158000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 100 | 2015636
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 329 | 8511490 | Machine problem
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 176 | 5944000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7120750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6335622 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1267427
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 86 | 1136815 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 347076 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 150 | 3532000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2214710
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 214 | 4756402 | ST under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1906416
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 711000 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 149 | 3137280
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 789008 | Engine problem
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1162833
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 37 | 944340 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 750600
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 708800
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 41 | 881760 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 4767271 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 105 | 1504531 | Engine problem
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 82 | 467916 | Low demand
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 805180
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3482640
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 1886976 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 95 | 2112000
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3405600 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 213349
| Dhaka area Total |  |  |  | 5919 | 3510 | 76977428
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 333518 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 27540
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 694080
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 580000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 71 | 4816254 | Synchronized at 15:35.
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 1518189 | Tripped at 15:50.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 0 | 459163 | Tripped at 15:50.
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 42 | 444683 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 76 | 1653480 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1890240
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 410592
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 10 | 362880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 910080
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 37680
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 153 | 1523018 | Low demand
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 692221
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 34 | 441598 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 1752960 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 1014927
| Chattogram area Total |  |  |  | 2382 | 898 | 19563103
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 145 | 3511000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 235 | 4423500
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7152000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 10 | 504000 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 756960
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 1421818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 948766
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 0 | 1532218 | Tripped at 15:50.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 108576 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2126210 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 103 | 2209920 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 375912 | Tripped at 15:50.
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 135360 | Tripped at 15:50.
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 102 | 3399360
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 743400
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1128475
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 15 | 353190 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 1280448 | Low demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1557240
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 110 | 2522520
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 591480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1452 | 36782353
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 151 | 3071280 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 385344 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 63 | 1362240 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 15150
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 190 | 3242400
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2611200
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 368840
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 546720
| Mymensingh Area Total |  |  |  | 709 | 562 | 11603174
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 999000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 699720 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 130 | 3502064 | Frequency control
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 328 | 7256000
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1111800
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 230000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1184928 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 77 | 1704960 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 120 | 2893770 | Machine problem
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 209000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 347424 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7109500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 8862000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 143280 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 394 | 9030900 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1984 | 45284346
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 827 | 21145455
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2167680 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 17 | 148800 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 11264 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 6927264 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 32 | 451500 | Engine problem
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 743040
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2480160
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1545 | 34075163
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 110 | 1316160
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 694090
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 1909309 | Engine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1913567 | Engine problem
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 550 | 13153800
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 165 | 917073 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 302400 | Line over load.
| Barisal Area Total |  |  |  | 1826 | 1075 | 20206399
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 31 | 434114
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 45 | 399957
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 593560 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 244211 | Low demand
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 320029 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 142 | 2793900 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3689745 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 172 | 4466900 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 0 | 6760327 | tripped at 15:54.
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 14 | 197100 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 20 | 440400
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 229842
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1170720
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 96 | 1962280
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 228035 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2468256
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2352288
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17940
| Rajshahi Area Total |  |  |  | 2179 | 1047 | 28769604
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3668000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 0
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2697600
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 56163
| Rangpur Area Total |  |  |  | 605 | 280 | 6421763
| Total |  |  |  | 21315 | 12353 | 279683333
| Eastern Grid Total |  |  |  | 14421 | 8406 | 190210404
| Western Grid Total |  |  |  | 6894 | 3947 | 89472929
| National Grid Total |  |  |  | 21315 | 12353 | 279683333
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-24
(a) ENTIRE EASTERN GRID : |  | 7965 | MW | (b) ENTIRE WESTERN GRID : |  | 3765 | MW
i) Dhaka area |  | 4695 | MW | i) Khulna area |  | 1530 | MW
ii) Chittagong area |  | 949 | MW | ii) Rajshahi area |  | 1152 | MW
iii) Comilla area |  | 964 | MW | iii) Barisal area |  | 404 | MW
iv) Mymensingh area |  | 1047 | MW | iv) Rangpur area |  | 679 | MW
v) Sylhet area |  | 310 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11730 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 118 | 13:00 | Kishoreganj | 136 | 19:30 | Benapol | 66 | 1:00
Munsiganj | 107 | 21:00 | Netrokona | 130 | 20:00 | Jhenida | 117 | 22:00
Sonargaon | 69 | 4:00 | Jamalpur | 157 | 1:00 | Bottail | 138 | 1:00
Shyampur | 196 | 11:00 | Sherpur | 136 | 1:00 | G.K Project | 59 | 1:00
Bhulta | 177 | 1:00 | Srimongal | 63 | 21:00 | Faridpur | 211 | 22:00
Madanganj | 50 | 1:00 | Shahjibazar | 132 | 21:00 | Madaripur | 114 | 1:00
Shitalakhya | 114 | 15:00 | Fenchuganj | 46 | 1:00 | Sariatpur | 78 | 1:00
Rahim steel | 24 | 7:00 | Kulawara | 44 | 1:00 | Gopalganj | 103 | 21:00
Matuail | 58 | 1:00 | Sylhet | 128 | 17:00 | Bagerhat | 113 | 1:00
Ghorasal | 75 | 1:00 | Chatak | 31 | 1:00 | Mongla | 40 | 9:00
Narsingdi | 160 | 1:00 | Sunamganj | 50 | 1:00 | Satkhira | 118 | 21:00
Haripur (SBU) | 116 | 9:00 | Biani Bazar | 68 | 1:00 | Gallamari | 44 | 1:00
Sreenagar | 46 | 21:00 | Comilla (S) | 170 | 15:00 | Magura | 60 | 20:00
Ullon | 78 | 19:00 | Comilla(N) | 147 | 1:00 | Norail | 47 | 21:00
Hasnabad | 84 | 1:00 | Chandpur | 87 | 19:00 | Chuadanga | 93 | 2:00
Magbazar | 114 | 15:00 | Feni | 137 | 19:00 | Borguna | 20 | 22:00
Maniknagar | 84 | 13:00 | Chowmuhani | 192 | 1:00 | Barisal(N) | 51 | 1:00
Bangabhaban | 14 | 11:00 | Ashuganj | 52 | 11:00 | Barisal (S) | 122 | 19:00
Motijheel | 16 | 11:00 | Daudkandi | 160 | 1:00 | Patuakhali | 117 | 19:30
Narinda | 58 | 13:00 | B.Baria | 164 | 1:00 | Bhandaria | 60 | 19:30
Kazla | 77 | 18:00 | Ramganj | 116 | 19:00 | Borhan Uddin | 45 | 20:00
Dhanmondi | 232 | 13:00 | Chaddagram | 46 | 16:00 | Ishurdi | 68 | 1:00
Lalbag | 85 | 13:00 | PHP | 11 | 9:00 | Ruppur Paromanobik | 4 | 9:00
Madartek | 84 | 19:00 | Kochua | 72 | 19:00 | Natore | 137 | 1:00
Dhaka University | 52 | 13:00 | Madunaghat | 66 | 12:00 | Bogra | 161 | 21:00
Aftabnagar | 12 | 15:00 | Hathazari | 90 | 23:00 | Noagaon | 125 | 20:00
Fatullah | 60 | 12:00 | Khulshi | 214 | 12:00 | Rajshahi | 152 | 1:00
Nawabganj | 56 | 22:00 | Halishahar | 149 | 10:00 | Rajshahi New | 23 | 1:00
Keraniganj | 64 | 19:00 | Baraulia | 135 | 1:00 | C.Nawabganj | 66 | 1:00
Mirpur | 134 | 19:00 | Sikalbaha | 35 | 16:00 | Amnura | 40 | 1:00
Kalyanpur | 132 | 19:00 | Dohazari | 100 | 21:00 | Pabna | 105 | 1:00
Gulshan | 174 | 15:00 | Cox'sbazar | 85 | 23:00 | Shahjadpur | 88 | 1:00
Uttara | 103 | 12:00 | Chandraghona | 34 | 21:00 | Serajganj | 95 | 1:00
Uttara New | 36 | 13:00 | Kaptai | 3.5 | 22:00 | Niyamatpur | 86 | 1:00
Kamrangirchar | 90 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 62 | 1:00
Savar | 185 | 19:00 | Bakulia | 118 | 19:30 | Sherpur(Bogura) | 61 | 1:00
Bhasantec | 184 | 13:00 | Julda | 22 | 1:00 | Mohastangor | 66 | 19:30
Agargaon | 93 | 13:00 | TK chemical | 17 | 21:00 | Bhangura | 36 | 1:00
Satmosjid | 112 | 19:30 | Modern Steel |  |  | Rangpur | 127 | 3:00
Tongi | 133 | 11:00 | Shahmirpur | 27 | 21:00 | Lalmonirhat | 43 | 2:00
Kabirpur | 264 | 15:00 | Khagrachhari | 24 | 18:30 | Saidpur | 110 | 21:00
Basundhara | 202 | 17:00 | Matarbari | 35 | 20:00 | Purbasadipur | 116 | 21:00
Manikganj | 86 | 22:00 | Baroiar Hat | 44 | 15:00 | Thakurgaon | 79 | 1:00
Joydevpur | 190 | 19:00 | Rangamati | 12 | 12:00 | Palashbari | 114 | 1:00
New Tongi | 107 | 15:00 | Abul Khair 230 | 14 | 18:00 | Barapukuria | 54 | 23:00
Kodda | 291 | 19:00 | BSRM | 157 | 16:00 | Panchagar | 52 | 19:00
Dhamrai | 126 | 0:00 | GPH Ispat | 87 | 8:00 | Joldhaka | 64 | 19:30
Rajendrapur | 104 | 19:30 | Goalpara | 30 | 1:00 | Kurigram | 58 | 2:00
Valuka | 124 | 12:00 | Central s/s | 99 | 1:00 | Mithapukur | 34 | 1:00
Tangail | 219 | 21:00 | Noapara | 60 | 1:00
Mymensing | 232 | 23:00 | Jessore | 124 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-24 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 22:00 | 394 | 14:00 | Kaliakoir | 390 | 0.75 | 375 | 0.5
| Bheramara | 399 | 6:00 | 386 | 1:00 | Bhulta | 389 | 0.29167 | 366 | 0.45833
| Ashuganj(N) | 390 | 7:00 | 372 | 12:00 | Gopalganj | 408 | 0.625 | 384 | 0.8125
| Payra | 412 | 22:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 12:00 | Hathazari | 224 | 19:00 | 190 | 13:00
| Ishurdi | 235 | 18:00 | 224 | 20:00 | Megnaghat | 232 | 5:00 | 223 | 11:00
| Ashuganj | 240 | 4:00 | 0 | 16:00 | Fenchuganj | 239 | 6:00 | 233 | 15:00
| Serajganj | 232 | 13:00 | 0 | 16:00 | Siddhirganj | 230 | 22:00 | 220 | 12:00
| Baghabari | 234 | 9:00 | 227 | 19:00 | Maniknagar | 232 | 22:00 | 218 | 12:00
| Barapukuria | 236 | 18:00 | 222 | 21:00 | Agargaon | 228 | 18:00 | 214 | 12:00
| Bogra | 227 | 18:00 | 214 | 23:00 | Barisal | 250 | 21:00 | 239 | 21:00
| Rajshahi | 236 | 18:00 | 222 | 23:00 | Bhola 225 MW | 253 | 6:00 | 242 | 15:00
| Khulna South | 230 | 16:00 | 212 | 20:00 | AKSML | 226 | 21:00 | 200 | 14:00
| Rampura | 231 | 22:00 | 219 | 11:00 | BSRM | 226 | 19:30 | 204 | 15:00
| Haripur | 232 | 22:00 | 219 | 14:00 | Bibiyana | 239 | 7:00 | 234 | 9:00
| Hasnabad | 230 | 1:00 | 218 | 12:00 | Bhulta | 234 | 22:00 | 219 | 11:00
| Shyampur | 230 | 22:00 | 220 | 11:00 | Ashuganj (S) | 238 | 22:00 | 226 | 12:00
| Aminbazar | 231 | 1:00 | 218 | 2:00 | Kaliakoir | 228 | 22:00 | 216 | 11:00
| Tongi | 226 | 4:00 | 215 | 12:00 | GPH | 228 | 1:00 | 198 | 15:00
| Comilla (N) | 228 | 22:00 | 218 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 140 | 22:00 | 130 | 11:00 | Kochua | 139 | 0.875 | 126 | 0.58333
| Munsiganj | 142 | 22:00 | 130 | 11:00 | Madanhat | 135 | 0.79167 | 116 | 0.58333
| Sonargaon | 140 | 22:00 | 129 | 12:00 | Hathazari | 137 | 0.79167 | 115 | 0.54167
| Shyampur | 137 | 22:00 | 126 | 11:00 | Khulshi | 132 | 0.8125 | 111 | 0.58333
| Bhulta | 135 | 22:00 | 123 | 12:00 | Halishahar | 133 | 0.8125 | 110 | 0.58333
| Madanganj | 140 | 22:00 | 128 | 11:00 | Baraulia | 134 | 0.8125 | 116 | 0.66667
| Shitalakhya | 143 | 22:00 | 129 | 11:00 | Sikalbaha | 136 | 0.75 | 118 | 0.54167
| Rahim steal | 140 | 22:00 | 130 | 11:00 | Dohazari | 132 | 0.79167 | 112 | 0.58333
| Matuail | 140 | 22:00 | 130 | 11:00 | Cox'sbazar | 129 | 0.77083 | 0 | 0.54167
| Ghorasal | 138 | 1:00 | 135 | 11:00 | Chandraghona | 134 | 0.77083 | 117 | 0.58333
| Narsinghdi | 136 | 23:00 | 125 | 1:00 | Kaptai | 132 | 0.91667 | 127 | 0.29167
| Haripur (SBU) | 140 | 22:00 | 130 | 12:00 | A. Khaer Stl. | 130 | 0.75 | 116 | 0.70833
| Sreenagar | 132 | 22:00 | 122 | 11:00 | Bakulia | 137 | 0.8125 | 117 | 0.625
| Ullon | 134 | 23:00 | 123 | 11:00 | Julda | 138 | 0.79167 | 117 | 0.58333
| Hasnabad | 136 | 1:00 | 129 | 11:00 | TK Chemical | 136 | 0.79167 | 117 | 0.58333
| Magbazar | 137 | 22:00 | 121 | 11:00 | Modern Steel
| Maniknagar | 139 | 22:00 | 129 | 12:00 | Shahmirpur | 138 | 0.8125 | 116 | 0.58333
| Bangabhaban | 139 | 22:00 | 129 | 12:00 | Khagrachhari | 132 | 0.77083 | 118 | 0.8125
| Motijheel | 139 | 22:00 | 129 | 12:00 | Matarbari | 128 | 0.041667 | 110 | 0
| Narinda | 139 | 22:00 | 129 | 12:00 | Baroiar Hat | 135 | 0.875 | 124 | 0.95833
| Kazla | 139 | 22:00 | 129 | 12:00 | Rangamati | 134 | 19:30 | 117 | 14:00
| Dhanmondi | 137 | 23:00 | 128 | 13:00 | Goalpara S/S | 138 | 16:00 | 128 | 20:00
| Lalbag | 139 | 22:00 | 127 | 11:00 | Khulna Central S/S | 138 | 18:00 | 127 | 0.83333
| Madartek | 138 | 22:00 | 122 | 11:00 | Noapara | 136 | 18:00 | 126 | 0.8125
| Dhaka University | 136 | 22:00 | 123 | 10:00 | Jessore | 131 | 18:00 | 117 | 0.041667
| Aftabnagar | 136 | 22:00 | 123 | 10:00 | Benapol | 132 | 18:00 | 117 | 0.125
| Fatullah | 136 | 22:00 | 127 | 11:00 | Jhenida | 127 | 0.75 | 106 | 0.041667
| Nawabganj | 129 | 1:00 | 122 | 11:00 | Bottail | 133 | 18:00 | 120 | 0.041667
| Keraniganj | 131 | 22:00 | 123 | 11:00 | G.K Project | 140 | 0.75 | 132 | 0.8125
| Mirpur | 139 | 22:00 | 127 | 12:00 | Faridpur | 135 | 0.75 | 125 | 0.83333
| Kalyanpur | 137 | 7:00 | 129 | 12:00 | Madaripur | 140 | 0.75 | 130 | 0.875
| Gulshan | 137 | 22:00 | 122 | 11:00 | Shariyatpur S/S | 139 | 0.75 | 130 | 0.875
| Uttara | 138 | 22:00 | 126 | 13:00 | Gopalganj | 143 | 18:00 | 130 | 0.8125
| Uttara New | 136 | 3:00 | 128 | 15:00 | Bagerhat | 135 | 0.25 | 123 | 0.83333
| Kamrangirchar | 139 | 22:00 | 127 | 11:00 | Mongla | 134 | 10:00 | 124 | 0.8125
| Savar | 137 | 6:00 | 129 | 12:00 | Satkhira | 137 | 18:00 | 125 | 0.83333
| Bhasantec | 132 | 22:00 | 121 | 12:00 | Gallamari | 139 | 13:00 | 127 | 20:00
| Agargaon | 133 | 22:00 | 123 | 12:00 | Magura | 126 | 0.75 | 106 | 20:00
| Satmosjid | 133 | 22:00 | 122 | 15:00 | Narail | 126 | 18:00 | 104 | 0.041667
| Tongi | 139 | 4.00 | 131 | 11:00 | Chuadanga | 124 | 0.75 | 100 | 0.041667
| Kabirpur | 138 | 23:00 | 124 | 15:00 | Borguna | 140 | 17:00 | 131 | 0.45833
| Basundhara | 137 | 6:00 | 128 | 16:00 | Barisal(N) | 141 | 18:00 | 134 | 0.875
| Manikganj | 142 | 6.00 | 132 | 19:00 | Barisal (S) | 140 | 18:00 | 131 | 21:00
| Joydevpur | 140 | 5.00 | 130 | 12:00 | Patuakhali(S) | 139 | 0.75 | 125 | 0.875
| New Tongi | 138 | 22:00 | 132 | 9:00 | Bhandaria | 136 | 0.083333 | 125 | 0.875
| Kodda | 137 | 5.00 | 127 | 11:00 | Ishurdi | 138 | 0.75 | 130 | 0.83333
| Dhamrai | 128 | 2:00 | 124 | 12:00 | Ruppur Paromanobik | 137 | 18:00 | 131 | 19:30
| Rajendrapur | 137 | 6:00 | 126 | 14:00 | Natore | 138 | 18:00 | 130 | 1:00
| Valuka | 137 | 0:00 | 108 | 19:30 | Bogra | 136 | 19:00 | 126 | 1:00
| Tangail | 135 | 0:00 | 120 | 19:00 | Noagaon | 133 | 17:00 | 116 | 22:00
| Mymensing | 139 | 0:00 | 112 | 19:30 | Rajshahi | 134 | 10:00 | 128 | 22:00
| Kishorganj | 138 | 0:00 | 117 | 19:30 | Rajshahi New | 137 | 18:00 | 127 | 22:00
| Netrokona | 139 | 0:00 | 106 | 21:00 | C.Nawabganj | 137 | 18:00 | 125 | 23:00
| Jamalpur | 140 | 0:00 | 120 | 21:00 | Amnura | 141 | 18:00 | 124 | 23:00
| Sherpur | 138 | 0:00 | 115 | 21:00 | Pabna | 138 | 18:00 | 128 | 20:00
| Srimongal | 140 | 22:00 | 130 | 1:00 | Shahjadpur | 142 | 18:00 | 134 | 1:00
| Shahjibazar | 139 | 22:00 | 128 | 1:00 | Serajganj | 135 | 18:00 | 128 | 1:00
| Fenchuganj | 139 | 23:00 | 132 | 1:00 | Niyamatpur | 132 | 17:00 | 114 | 22:00
| Khulawara | 136 | 18:00 | 132 | 1:00 | Joypurhat | 135 | 17:00 | 115 | 24:00
| Sylhet | 135 | 23:00 | 128 | 1:00 | Sherpur(Bogura) | 135 | 18:00 | 125 | 23:00
| Chatak | 134 | 20:00 | 124 | 1:00 | Mohastangor | 135 | 18:00 | 123 | 24:00
| Sunamganj | 134 | 20:00 | 122 | 1:00 | Bangura | 138 | 18:00 | 132 | 1:00
| Biani Bazar | 136 | 18:30 | 123 | 1:00 | Rangpur | 132 | 18:30 | 114 | 22:00
| Comilla(s) | 134 | 21:00 | 123 | 15:00 | Lalmonirhat | 131 | 18:30 | 115 | 24:00
| Comilla(n) | 139 | 21:00 | 130 | 14:00 | Saidpur | 130 | 10:00 | 111 | 21:00
| Chandpur | 140 | 21:00 | 128 | 6:00 | Purbasadipur | 127 | 18:00 | 108 | 22:00
| Feni | 137 | 21:00 | 122 | 15:00 | Thakurgaon | 122 | 11:00 | 104 | 22:00
| Chowmuhani | 136 | 21:00 | 120 | 14:00 | Palashbari | 134 | 18:30 | 119 | 24:00
| Ashuganj | 140 | 23:00 | 132 | 1:00 | Barapukuria | 136 | 18:00 | 122 | 21:00
| Daudkandi | 140 | 22:00 | 126 | 11:00 | Panchagar | 122 | 18:00 | 100 | 23:00
| B.Baria | 137 | 22:00 | 125 | 1:00 | Joldhaka | 126 | 18:00 | 107 | 22:00
| Ramganj | 142 | 21:00 | 121 | 15:00 | Kurigram | 130 | 0.77083 | 111 | 0.95833

## L-Curve
Date | 2021-05-24
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 86 | 5528 | 3433 | 8961 |  |  |  | QF-LDC-11
0:30 | 96 | 7144 | 3842.5 | 10986.5 | Date: | 2021-05-24
1:00 | 106 | 8760 | 4252 | 13012
1:30 | 132 | 8719 | 4196.5 | 12915.5
2:00 | 158 | 8678 | 4141 | 12819
2:30 | 95 | 8592 | 4103.5 | 12695.5 | [5 empty] | Gen. at Eve. Peak | 12353 | 12353 MW (19:30 )
3:00 | 32 | 8506 | 4066 | 12572 | [6 empty] | 19:30
3:30 | 63 | 8490.5 | 3983.5 | 12474 | [5 empty] | Gen. at Day Peak | 11835 | 11835 MW (12:00 )
4:00 | 94 | 8475 | 3901 | 12376 | [6 empty] | 12:00
4:30 | 93 | 8417 | 3822 | 12239 | [5 empty] | Highest Generation | 13012
5:00 | 92 | 8359 | 3743 | 12102 | [6 empty] | 1:00
5:30 | 47 | 7915.5 | 3618.5 | 11534
6:00 | 2 | 7472 | 3494 | 10966
6:30 | 3 | 7431 | 3449 | 10880
7:00 | 4 | 7390 | 3404 | 10794
7:30 | 23 | 7383.5 | 3406 | 10789.5
8:00 | 42 | 7377 | 3408 | 10785
8:30 | 142 | 7472.5 | 3439 | 10911.5
9:00 | 242 | 7568 | 3470 | 11038
9:30 | 250 | 7717.5 | 3494.5 | 11212
10:00 | 258 | 7867 | 3519 | 11386
10:30 | 234 | 7950 | 3511.5 | 11461.5
11:00 | 210 | 8033 | 3504 | 11537
11:30 | 169 | 8162 | 3524 | 11686
12:00 | 128 | 8291 | 3544 | 11835
12:30 | 154 | 7966 | 3568 | 11534
13:00 | 180 | 7641 | 3592 | 11233
13:30 | 168 | 7743 | 3618 | 11361
14:00 | 156 | 7845 | 3644 | 11489
14:30 | 146.5 | 8157.5 | 3645.5 | 11803
15:00 | 137 | 8470 | 3647 | 12117
15:30 | 68.5 | 8436.5 | 3370.5 | 11807
16:00 | 0 | 8403 | 3094 | 11497
16:30 | 0 | 7979 | 3100 | 11079
17:00 | 0 | 7555 | 3106 | 10661
17:30 | 31 | 7597 | 3000 | 10597
18:00 | 62 | 7639 | 2894 | 10533
18:30 | 81 | 8009 | 3102 | 11111
19:00 | 100 | 8379 | 3310 | 11689
19:30 | 154 | 8406 | 3947 | 12353
20:00 | 184 | 7872 | 3860 | 11732 |  |  |  | Executive Engineer
20:30 | 191 | 7666.5 | 3918.5 | 11585 |  |  |  | Network Operation Division
21:00 | 198 | 7461 | 3977 | 11438
21:30 | 318 | 6886.5 | 3860 | 10746.5
22:00 | 438 | 6312 | 3743 | 10055 |  |  |  |  | Page 6 of 7
22:30 | 279 | 5767.5 | 3697 | 9464.5
23:00 | 120 | 5223 | 3651 | 8874
23:30 | 103 | 5375.5 | 3542 | 8917.5
24:00 | 86 | 5528 | 3433 | 8961
12353 MW (19:30 )
11835 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-24 |  | Energy | 279683333
[11 empty] | 2021-05-24 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4039 | 892 | 1763 | 1700 | 570 | 25 | 50 | 0 | 110 | 0
0:30 | 4206 | 892 | 1890 | 3043 | 624.5 | 25 | 260 | 0 | 140 | 0 | Date: | 2021-05-24
1:00 | 4373 | 892 | 2017 | 4386 | 679 | 25 | 470 | 0 | 170 | 0
1:30 | 4382.5 | 892.5 | 2053 | 4242 | 684.5 | 25 | 467 | 0 | 169 | 0 | [7 empty] | Total Energy | 279.6833 | Total Energy Gen 279.683 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.683 MKWHr
2:00 | 4392 | 893 | 2089 | 4098 | 690 | 25 | 464 | 0 | 168 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4410.5 | 893 | 2095.5 | 3974.5 | 690 | 25 | 441 | 0 | 166 | 51.5 | [7 empty] | Energy Requirement | 279.6833
3:00 | 4429 | 893 | 2102 | 3851 | 690 | 25 | 418 | 0 | 164 | 103
3:30 | 4436.5 | 893 | 2101 | 3800.5 | 690 | 25 | 367 | 0 | 161 | 51.5 | [6 empty] | Shortage
4:00 | 4444 | 893 | 2100 | 3750 | 690 | 25 | 316 | 0 | 158 | 0
4:30 | 4428 | 892.5 | 2057.5 | 3675.5 | 690 | 25 | 315.5 | 0 | 155 | 0
5:00 | 4412 | 892 | 2015 | 3601 | 690 | 25 | 315 | 0 | 152 | 0
5:30 | 4354 | 892 | 1923.5 | 3223.5 | 685 | 25 | 290 | 0 | 140 | 1
6:00 | 4296 | 892 | 1832 | 2846 | 680 | 25 | 265 | 0 | 128 | 2
6:30 | 4333.5 | 892 | 1817 | 2735 | 675 | 25 | 262.5 | 0 | 124 | 16 |  |  |  |  | Coal
7:00 | 4371 | 892 | 1802 | 2624 | 670 | 25 | 260 | 0 | 120 | 30
7:30 | 4365 | 892 | 1830.5 | 2611.5 | 665 | 25 | 232 | 0 | 130 | 38.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4359 | 892 | 1859 | 2599 | 660 | 25 | 204 | 0 | 140 | 47
8:30 | 4389 | 892.5 | 1897.5 | 2651 | 660 | 25 | 192.5 | 0 | 144 | 60
9:00 | 4419 | 893 | 1936 | 2703 | 660 | 25 | 181 | 0 | 148 | 73
9:30 | 4523 | 892.5 | 1920 | 2784 | 655 | 25 | 181 | 0 | 150 | 81.5
10:00 | 4627 | 892 | 1904 | 2865 | 650 | 25 | 181 | 0 | 152 | 90
10:30 | 4625.5 | 892 | 1893 | 2940.5 | 650 | 25 | 181 | 0 | 156 | 98.5
11:00 | 4624 | 892 | 1882 | 3016 | 650 | 25 | 181 | 0 | 160 | 107
11:30 | 4651 | 892 | 1876 | 3125 | 659.5 | 25 | 205.5 | 0 | 163 | 89
12:00 | 4678 | 892 | 1870 | 3234 | 669 | 25 | 230 | 0 | 166 | 71
12:30 | 4429 | 892 | 1860 | 3156 | 689 | 22.5 | 250.5 | 0 | 163 | 72
13:00 | 4180 | 892 | 1850 | 3078 | 709 | 20 | 271 | 0 | 160 | 73
13:30 | 4180 | 892 | 1850 | 3078 | 709 | 20 | 271 | 0 | 160 | 73
14:00 | 4180 | 892 | 1850 | 3078 | 709 | 20 | 271 | 0 | 160 | 73
14:30 | 4160 | 891 | 1847 | 3525.5 | 704.5 | 20 | 292 | 0 | 165 | 70
15:00 | 4140 | 890 | 1844 | 3973 | 700 | 20 | 313 | 0 | 170 | 67
15:30 | 4041.5 | 854.5 | 1584.5 | 4078 | 700 | 22.5 | 312 | 0 | 160 | 54
16:00 | 3943 | 819 | 1325 | 4183 | 700 | 25 | 311 | 0 | 150 | 41
16:30 | 3879.5 | 822 | 1316.5 | 3874 | 665 | 25 | 312 | 0 | 157 | 28
17:00 | 3816 | 825 | 1308 | 3565 | 630 | 25 | 313 | 0 | 164 | 15
17:30 | 3849.5 | 828 | 1284 | 3541.5 | 590 | 25 | 319 | 0 | 151 | 9
18:00 | 3883 | 831 | 1260 | 3518 | 550 | 25 | 325 | 0 | 138 | 3
18:30 | 4112 | 828.5 | 1339.5 | 3814 | 520 | 25 | 338.5 | 0 | 132 | 1.5
19:00 | 4341 | 826 | 1419 | 4110 | 490 | 25 | 352 | 0 | 126 | 0
19:30 | 4384 | 827 | 1479 | 4395 | 700 | 25 | 441 | 0 | 102 | 0
20:00 | 4462 | 826 | 1449 | 3749 | 620 | 25 | 479 | 0 | 122 | 0
20:30 | 4420 | 826 | 1537 | 3591 | 640 | 25 | 477 | 0 | 69 | 0
21:00 | 4378 | 826 | 1625 | 3433 | 660 | 25 | 475 | 0 | 16 | 0
21:30 | 4119 | 845.5 | 1638.5 | 3032.5 | 645 | 25 | 393 | 0 | 48 | 0
22:00 | 3860 | 865 | 1652 | 2632 | 630 | 25 | 311 | 0 | 80 | 0
22:30 | 3818.5 | 878.5 | 1660.5 | 2166 | 615 | 25 | 208 | 0 | 93 | 0
23:00 | 3777 | 892 | 1669 | 1700 | 600 | 25 | 105 | 0 | 106 | 0
23:30 | 3908 | 892 | 1716 | 1700 | 585 | 25 | 77.5 | 0 | 108 | 0 | Max Temp. in Dhaka |  | 38.1° C
24:00 | 4039 | 892 | 1763 | 1700 | 570 | 25 | 50 | 0 | 110 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 279.683 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.683 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-24
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 20 | 20 | 20 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 580000
3 | Chattogram TPP-1
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 10 | 17 | 17 | 17 | [5 empty] | 1 | 12 | 8 | 17 | 17 | 333518
| Teknaf 20MW PP (Solartech) | [6 empty] | 6 | [7 empty] | 2 | [11 empty] | 27540
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 202 | 202 | 203 | 203 | 203 | 229 | 229 | 203 | 203 | 228 | 204 |  |  |  | 60 | 0 | 41 |  | 71 | 71 | 71 | 80 | 122 | 202 | 203 | 4816254
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | [14 empty] | 1518189
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 17 | 17 | 17 | 17 | 17 | 17 | 12 | [7 empty] | 30 | 45 |  |  |  |  | 42 | 51 | 51 | 60 | 34 | 34 | 444683
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 42 | 35 | 35 | 35 | 35 | 0 | [15 empty] | 24 | 53 | 51 | 51 | 53 | 459163
| Daudkandi 200 MW PP (B.Trac) | 200 | 100 | 0 | [9 empty] | 30 | 20 | 125 | 193 | 195 | 200 |  | 100 | 100 | [5 empty] | 1280448
14 | Titas 50 MW Peaking PP | 40 | 40 | 0 | [23 empty] | 108576
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 180 | 180 | 180 | 180 | 150 | 120 | 113 | 120 | 118 | 115 | 117 | 180 | 178 | 155 | 170 | 170 | 115 | 80 |  | 170 | 150 | 151 | 180 |  | 30 | 92 | 3532000
17 | Siddhirganj 335 MW CCPP | 218 | 219 | 221 | 221 | 222 | 160 | 160 | 160 | 216 | 208 | 212 | 208 | 186 | 201 | 202 | 83 | 160 | 150 |  | 210 | 214 | 214 | 216 | 150 | 150 | 180 | 4756402
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 245 | 245 | 245 | 243 | 125 | 125 | 85 | 120 | 165 | 195 | 200 | 228 | 235 | 243 | 245 | 245 | 238 |  | 245 | 245 | 245 | 245 | 95 |  |  | 4767271
19 | Ashuganj 195MW PP (APSCL-United) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 1421818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 4158000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 23 | 26 |  | 26 | 10 | 10 | 10 | 10 | 10 | 10 | 504000
33 | Ashuganj 225 MW CCPP | 139 | 140 | 140 | 140 | 140 | 45 | 35 | 51 | 95 | 213 | 211 | 211 | 212 | 193 | 160 | 178 | 123 | 125 |  | 135 | 145 | 159 | 181 | 175 | 163 | 195 | 3511000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 265 | 265 | 275 | 275 | 295 | 295 | 295 | 295 | 315 | 310 | 305 | 305 | 295 |  | 320 | 295 | 325 | 295 | 280 | 270 | 305 | 7152000
| Ashuganj 450 MW CCPP(North) | 25 | 10 | 20 | 20 | 20 | 140 | 245 | 235 | 230 | 235 | 230 | 230 | 230 | 220 | 215 | 215 | 215 | 215 |  | 230 | 235 | 235 | 245 | 200 | 200 | 200 | 4423500
35 | Ashuganj 55 MW PP (Precision) | 50 | 50 | 51 | 52 | 53 | 50 | 52 | 53 | 52 | 51 | 30 | 30 | 30 | 30 | 10 |  | 0 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 756960
36 | Chandpur 150 MW CCPP | 91 | 88 | 91 | 90 | 85 | 88 | 85 | 90 | 91 | 86 | 90 | 90 | 85 | 95 | 91 | 90 | 87 | 86 |  | 90 | 90 | 90 | 86 | 86 | 86 | 91 | 2126210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 388 | 390 | 389 | 389 | 390 | 388 | 385 | 329 | 332 | 332 | 331 | 337 | 355 | 342 | 369 | 371 | 352 | 330 |  | 310 | 329 | 333 | 357 | 317 | 283 | 283 | 8511490
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7120750
41 | Haripur 360MW CCPP(HPL) | 332 | 343 | 346 | 348 | 347 | 308 | 308 | 308 | 301 | 242 | 211 | 201 | 192 | 187 | 186 | 177 | 177 | 176 |  | 176 | 176 | 177 | 171 | 161 | 252 | 304 | 5944000
42 | RPCL 210MW CCPP | 112 | 133 | 154 | 154 | 156 | 157 | 157 | 154 | 154 | 153 | 148 | 150 | 143 | 127 | 126 | 142 | 97 | 131 |  | 150 | 151 | 149 |  | 70 | 76 | 92 | 3071280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 12 | 26 | 40 | 51 | 56 | 27 | 25 | 43 | 39 | 26 | 7 | 1 | [8 empty] | 368840
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 41 | 40 | 40 | 40 | 39 | 41 | 41 |  | 41 | 42 | 42 | 43 | 43 | 44 | 43 | 999000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 28 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 699720
46 | Shajibazar 330 MW CCPP | 307 | 306 | 307 | 311 | 307 | 308 | 310 | 308 | 308 | 330 | 319 | 320 | 323 | 316 | 312 | 314 | 307 | 330 |  | 331 | 328 | 325 | 330 | 330 | 332 | 330 | 7256000
47 | Shahjibazar GTPP Unit- 8 & 9 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 51 | 55 | 56 | 56 | 50 | 54 | 54 | 55 | 56 |  | 56 | 56 | 56 | 32 | 33 | 33 | 32 | 1184928
48 | Shahjibazar 86MW PP (Shahjibazar) | 77 | 77 | 77 | 77 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 73 | 72 | 70 | 71 | 71 | 71 | 73 |  | 77 | 77 | 77 | 77 | 78 | 20 | 20 | 1704960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2893770
51 | Sylhet 20 MW GTPP | [10 empty] | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 209000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 7 |  | 7 | 0 | 7 | 7 | 7 |  |  | 143280
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 |  |  |  | 230000
55 | Fenchugonj 51 MW PP (Barakatullah) | 49 | 49 | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 46 | 48 | 46 | 47 | 47 | 47 | 49 |  | 49 | 50 | 50 | 50 | 50 | 11 | 14 | 1111800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 |  |  | 347424
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 285 | 280 | 280 | 300 | 280 | 270 | 290 | 290 | 290 | 280 | 300 | 310 | 290 | 315 | 315 | 290 | 260 |  | 310 | 310 | 295 | 305 | 250 | 265 | 280 | 7109500
| Bibiyana South 400 MW | 394 | 400 | 400 | 401 | 401 | 400 | 360 | 360 | 360 | 400 | 387 | 385 | 387 | 369 | 368 | 367 | 362 | 380 |  | 388 | 394 | 388 | 399 | 369 | 300 | 300 | 9030900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 10 | 50 |  | 55 | 55 | 55 | 55 |  |  |  | 1162833
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 22 | 23 | 24 | 23 | 23 | 24 | 23 | 24 | 23 | 24 | 21 | 23 | 23 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 |  | 546720
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 |  | 19 | 19 | 21 | 21 | 20 |  |  |  | 20 | 21 | 21 | 21 | 21 | 410592
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 |  | 13 | 19 | 19 | 19 |  | 19 | 19 | 19 | 20 |  |  |  | 347076
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 385344
63 | Impoprt (Tripura) | 170 | 168 | 164 | 158 | 152 | 128 | 120 | 140 | 148 | 152 | 160 | 166 | 160 | 168 | 170 | 150 | 164 | 138 |  | 126 | 102 | 122 | 16 | 80 | 106 | 110 | 3399360
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 33 | 35 | 34 | 32 | 26 | 6 | 4 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 6 | 10 | 11 | 30 | 30 | 37 | 35 | 362880
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 17 | 17 | 14 | 18 | 19 | 20 |  | 21 | [5 empty] | 22 | 375912
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 |  | 5 | [6 empty] | 135360
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 |  | 33 | 33 | 8 | 743400
68 | Cumilla 25 MW PP (Summit) | 17 | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 12 | 12 |  | 15 | 15 | 15 |  |  |  |  | 353190
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 20 | 21 | 0 | 0 | 0 | 344340
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 |  |  | 750600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 |  |  |  | 708800
73 | Ghorashal 108MW PP (Regent) | 104 | 100 | 103 | 103 | 103 | 13 | 12 | 25 | 85 | 94 | 100 | 90 | 102 | 100 | 94 | 97 | 100 | 100 |  | 100 | 100 | 100 | 102 | 103 | 53 | 53 | 2015636
| Feni Lanka Power | 114 | 114 | 114 | 114 | 88 | 34 |  |  |  | 34 | 34 | 98 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | [5 empty] | 1557240
| Chowmuhani 113 MW | 115 | 115 | 115 | 114 | 111 | 115 | 120 | 115 | 120 | 118 | 117 | 116 | 115 | 110 | 115 | 115 | 115 | 118 |  | 110 | 110 | 110 | 115 | 16 | 16 |  | 2522520
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 |  |  | 3405600
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 94 | 92 | 100 |  |  | 2214710
78 | Gazipur 52 MW PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 |  |  | 881760
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 115 | 115 | 115 | 115 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 82 |  |  | 3137280
80 | Jamalpur 95 MW PP(Powerpac) | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 63 | 63 | 55 | 63 | 55 | 63 | 63 | 55 | 55 | 55 | 63 |  | 63 | 63 | 63 | 57 | 18 | 38 | 63 | 1362240
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 44 | 44 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 1128475
| Gazipur 100 MW PP | 105 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 70 | 70 | 70 | 52 | 70 | 86 |  | 86 | 86 | 86 | 86 | 86 | 17 |  | 1886976
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 3 | 2 | 3 | 3 | 1 | [9 empty] | 37680
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | [13 empty] | 52 | 54 | 54 | 54 | 54 | 54 | 54 | 692221
| Karnaphuli Power Ltd. | 21 | 48 | 51 | 34 | 34 | 0 | [13 empty] | 20 | 34 | 34 | 51 | 51 |  |  | 441598
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 86 | 84 | 76 | 10 | 0 | [6 empty] | 41 | 77 | 85 | 85 | 73 | 73 | 84 |  | 85 | 86 | 84 | 74 |  |  |  | 1136815
86 | Meghnaghat CCPP ( Summit) | 260 | 260 | 255 | 255 | 250 | 260 | 270 | 265 | 270 | 240 | 275 | 265 | 275 | 290 | 295 | 285 | 285 | 245 |  | 285 | 275 | 285 | 240 | 220 | 225 | 265 | 6335622
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 95 | 95 | 95 | 95 | 94 | 94 | 96 | 95 | 95 | 95 | 96 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 95 | 95 | 95 | 95 | 88 |  |  | 2112000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 55 | 80 | 80 |  | 30 |  | 76 | 76 | 76 | 76 | 76 | 50 | 80 | 1653480
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | [5 empty] | 5 | 15 | 43 | 51 | 51 | 10 | 948766
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 48 | 48 | 24 | 24 | 40 | 66 | 75 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 48 |  |  | 1906416
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 5 | 0 |  | 50 | 50 | 50 | 50 | 50 | 47 |  | 30 | 33 | 44 |  | 44 |  | 42 | 46 | 46 | 46 | 19 |  | 7 | 694080
96 | Chattogram 108 MW PP (ECPV) | 25 | 25 | 25 | 25 | 25 | 26 | 50 | 77 | 65 | 68 | 60 | 60 |  |  | 13 | 27 |  | 10 |  | 63 | 97 | 97 | 97 |  |  |  | 910080
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 30 | 15 | 15 | 1267427
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 35 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 17 |  |  | 789008
101 | Kushiara 163 MW CCPP (KP) | 110 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 130 |  | 163 | 130 | 130 | 163 | 110 | 130 | 163 | 3502064
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | [9 empty] | 15150
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 |  |  |  | 711000
104 | Keranigonj 300 MW PP (APR) | 83 | 32 | 0 | [9 empty] | 111 | 26 | 232 | 297 | 295 | 113 |  | 160 | 105 | [5 empty] | 1504531
105 | Bramhangoan 100 MW PP (Aggreko) | [12 empty] | 10 |  |  | 85 | 85 | 50 |  | 71 | 82 | [5 empty] | 467916
106 | Mymensingh 200 MW PP (United) | 190 | 190 | 191 | 191 | 191 | 191 | 191 | 80 | 80 | 80 | 80 | 88 | 96 | 120 | 130 | 130 | 120 | 80 |  | 105 | 190 | 191 |  | 70 | 103 | 120 | 3242400
112 | Aurahati 100MW PP (Aggreko) | 100 | 74 | 0 | [9 empty] | 7 | 28 | 94 | 96 | 98 | 100 |  | 100 | 100 | [5 empty] | 805180
114 | Kodda 149 MW PP Unit-1 (Summit) | 148 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 118 | 55 | 3482640
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 10 | 100 | 100 | 100 | 100 | 100 |  | 60 | 80 | 80 |  | 50 |  | 100 | 100 | 100 | 100 | 100 | 50 | 70 | 1890240
116 | Chandpur 200MW (Desh energy) | 103 | 103 | 103 | 102 | 102 | 102 | 102 | 102 | 97 | 85 | 85 | 100 | 102 | 102 | 102 | 102 | 94 | 104 |  | 104 | 103 | 103 | 103 | 17 | 17 | 17 | 2209920
117 | Ashuganj 150MW PP (Midland) | 10 | 18 | 68 | 155 | 155 | 90 | 10 | 10 | 10 | 20 | 65 | 92 | 140 | 110 | 110 | [7 empty] | 8 | 103 |  |  | 1532218
118 | Bibiyana-III 400 MW CCPP | 368 | 368 | 368 | 368 | 367 | 336 | 331 | 338 | 331 | 367 | 367 | 404 | 335 | 385 | 381 | 367 | 366 | 405 |  | 403 | 403 | 404 | 401 | 364 | 304 | 340 | 8862000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 104 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 |  | 36 | 115 | 85 | 2611200
| Anwara 300 MW PP (United) |  |  |  | 0 | 16 | 16 | 16 | 53 | 58 | 83 | 134 | 162 |  | 60 | 181 | 245 |  | 121 |  | 234 | 153 | 16 | 16 |  |  |  | 1523018
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 10 | 50 | 50 | 90 | 90 | 90 |  | 77 | 90 | 90 |  | 40 |  | 100 | 80 | 50 | 100 | 100 | 50 | 70 | 1752960
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 0 | [13 empty] | 17 | 110 | 116 | 116 | 53 | 17 | 26 | 1014927
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  | 5 | 17 | 19 | 31 | 35 | 35 | 35 |  | 11 | 17 | 17 | 17 | 17 |  | 11 | 591480
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 8 | 15 | 23 | 26 | 35 | 27 | 33 | 21 | 12 | 5 | 4 | 1 | [8 empty] | 213349
120 | Eastern Zone Total | 8760 | 8678 | 8506 | 8475 | 8359 | 7472 | 7390 | 7377 | 7568 | 7867 | 8033 | 8291 | 7641 | 7845 | 8470 | 8403 | 7555 | 7639 |  | 8379 | 8406 | 7872 | 7461 | 6312 | 5223 | 5528 | 190210404
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 90 | 83 | 83 | 83 | 83 | 83 | 90 | 66 | 83 | 69 | 78 | 99 | 99 |  | 99 | 99 | 99 | 104 | 115 | 115 | 115 | 2167680
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 10 | 10 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 |  | 10 | 17 | 15 | 15 | 15 | 15 | 8 | 148800
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 70 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 17 | 2480160
130
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | 17 | 0 | [6 empty] | 3 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 54 | 54 |  |  |  |  | 302400
133 | Bhola Nutan Biddut BD LTD (GAS) | [15 empty] | 15 | 21 | 18 |  | 57 | 165 | 165 | 196 | 172 | 149 | 155 | 917073
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 80 | 32 | [6 empty] | 20 | 32 | 42 | 64 | 64 | 64 |  | 110 | 110 | 110 | 80 | 48 | 16 | 16 | 1316160
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 96 | 95 | 96 | 94 | 92 | 93 | 95 | 94 | 91 | 89 | 91 | 92 | 91 | 91 | 90 | 90 | 89 | 93 |  | 94 | 76 | 42 | 15 | 15 | 15 | 14 | 1913567
| Bhola 225 MW CCPP | 89 | 89 | 89 | 88 | 88 | 88 | 87 | 88 | 87 | 87 | 84 | 84 | 83 | 82 | 82 |  | 30 | 25 |  | 86 | 86 | 86 | 86 | 81 | 86 | 85 | 1909309
140 | Bhola 33 MW PP (Venture) | 35 | 35 | 35 | 35 | 34 | 27 | 27 | 25 | 22 | 29 | 26 | 23 | 27 | 20 | 20 | 26 | 26 | 27 |  | 34 | 34 | 34 | 25 | 34 | 34 | 34 | 694090
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 20 | 0 | [8 empty] | 2 | [6 empty] | 10 | 100 | 88 | 100 | 100 | 100 |  | 743040
142 | Noapara 40 MW PP (Khanjahan Ali) | 32 | 32 | 32 | 32 | 32 | 0 | [6 empty] | 32 |  | 32 | 32 | 16 | 8 |  | 32 | 32 | 32 | 32 | 32 | 32 |  | 451500
143 | Gopalganj 100 MW Peaking PP | [17 empty] | 8 |  | 1 | [6 empty] | 11264
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 892 | 893 | 893 | 893 | 892 | 892 | 892 | 892 | 893 | 892 | 892 | 892 | 892 | 893 | 890 | 819 | 825 | 831 |  | 826 | 827 | 826 | 826 | 865 | 892 | 892 | 21145455
147 | Bheramara 410 MW CCPP | 280 | 280 | 280 | 285 | 285 | 290 | 295 | 305 | 305 | 305 | 300 | 295 | 265 | 280 | 270 | 230 | 200 | 165 |  | 315 | 365 | 365 | 390 | 175 | 280 | 340 | 6927264
148 | Payra 1320 MW | 530 | 540 | 540 | 540 | 540 | 530 | 520 | 510 | 510 | 500 | 500 | 520 | 560 | 550 | 550 | 550 | 480 | 400 |  | 340 | 550 | 470 | 510 | 480 | 450 | 420 | 13153800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3668000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 0 | [14 empty] | 31 | 50 | 50 | 50 |  |  | 434114
| Sirajgonj 6.55 MW Solar | [8 empty] | 0 | 1 | 2 | 3 | 3 | 3 | 2 | 0 | 0 | 0 | [8 empty] | 17940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 104 | 104 | 104 | 106 | 107 | 111 | 113 | 117 | 117 | 112 | 110 | 107 | 99 | 92 | 90 | 90 | 105 | 126 |  | 139 | 142 | 144 | 142 | 144 | 100 | 100 | 2793900
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 142 | 148 | 148 | 151 | 154 | 154 | 154 | 154 | 148 | 148 | 146 | 136 | 129 | 126 | 123 | 122 | 127 | 130 |  | 133 | 132 | 132 | 142 | 195 | 162 | 169 | 3689745
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 183 | 183 | 183 | 183 | 183 | 189 | 190 | 190 | 196 | 184 | 178 | 172 | 157 | 145 | 145 | 130 | 130 | 130 |  | 137 | 172 | 181 | 206 | 211 | 210 | 207 | 4466900
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 400 | 398 | 408 | 402 | 333 | 310 | 293 | 339 | 339 | 369 | 406 | 401 | 357 | 390 | 390 | [7 empty] | 94 | 244 | 305 | 334 | 6760327
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 45 | 39 | 39 | 0 | [7 empty] | 7 | 7 | 5 | 5 | 6 | 50 | 47 |  | 50 | 45 | 45 | 42 |  |  |  | 399957
162 | Bogra 22 MW PP (GBB) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 17 | 16 | 16 | 16 | 16 | 16 | 15 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 440400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 |  | 229842
165 | Amnura 50 MW PP(Sinha) | 42 | 42 | 42 | 42 | 0 | [6 empty] | 12 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 |  |  |  | 593560
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | 0 | [15 empty] | 34 | 34 | 34 | 34 |  |  |  | 244211
167 | Katakhali 50 MW Peaking PP | 30 | 30 | 30 | 0 | [8 empty] | 29 | 30 | 30 | 12 | 15 | 22 |  | 30 | 30 | 31 | 30 |  |  |  | 320029
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 0 | [15 empty] | 4 | 14 | 30 | 34 |  |  |  | 197100
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1170720
170 | Chapainawabganj 100 MW Peaking PP | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 86 | 63 | 63 | 63 | 70 | 82 | 96 | 96 | 96 | 96 | 96 |  | 96 | 96 | 96 | 96 | 96 | 48 |  | 1962280
171 | Baghabari 200 MW PP (Paramount) | 120 | 0 | [24 empty] | 228035
| Bagura 113 MW PP (Confidence)-2 | 112 | 112 | 112 | 112 | 112 | 70 | 70 | 35 | 77 | 112 | 112 | 112 | 112 | 112 | 111 | 111 | 113 | 70 |  | 58 | 113 | 113 | 113 | 98 | 112 | 113 | 2468256
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 90 | 95 | 95 | 113 | 113 | 113 | 113 | 113 | 113 | 35 |  | 90 | 113 | 113 | 113 | 113 | 70 | 70 | 2352288
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | [14 empty] | 12 | 17 | 12 | 8 | 8 | 8 | 8
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 112 | 113 | 112 | 113 | 112 | 113 | 113 | 113 | 112 | 108 | 108 | 103 | 108 | 108 | 104 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2697600
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 5 | 7 | 7 | 7 | 7 | 7 | 6 | 3 | 1 | [8 empty] | 56163
178
178