## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-05-31 | Monday
|  |  | Date (day): | 2021-05-31 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13445.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14397 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-05-30 | 2021-05-31 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 91 | 99 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | Gas Line problem.
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 92 | 118 | 110 | 120 | 240 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 145 | 260 | 260 | 260 |  |  | GT-2 under maint
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 79 | 80 | 100 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 0 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 120 | 185 | 120 | 185 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 24 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 209 | 214 | 220 | 220 |  | 115 | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 45 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 41 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 228 | 245 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 21 | 108 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 38 | 100 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 53 | 102 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 84 | 83 | 85 | 85 |  | 20 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 104 | 104 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 144 | 144
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 29 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2599 | 3160 | 3111 | 3406 | 569 | 1209
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 90 | 90 | 100 | 100 | 90 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 45 | 46 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 20 | 20 | 20 | 20 | 210 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 204 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 94 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 68 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 26 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 6 | 6 |  | 102 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 91 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 60 | 80 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 882 | 1057 | 1523 | 1530 | 480 | 225
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 80 | 80 | 80 | 80 | 49 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 189 | 211 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 265 | 300 | 300 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 275 | 300 | 300 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 20 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 25 | 43 | 49 | 49 | 6 |  | Gas shortage
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 132 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 44 | 47 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 92 | 100 | 100 | 100 |  | 100 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 156 | 172 | 145 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 52 | 52
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 50 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 84 | 100 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 108 | 120 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1922 | 2074 | 2009 | 2196 | 511 | 215
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 116 | 130 | 150 | 150 | 52 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 18 | 19 | 19 |  | 3 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 16 | 24 | 24 |  | 71 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 171 | 196 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 35 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 494 | 499 | 581.6 | 530 | 52 | 74
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 42 | 42 | 42 |  | 28 | Under maint.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 161 | 163 | 163 |  | 160 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 55 | 56 | 56 | 56 |  | 10 | Engine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 75 | 78 | 80 | 80 |  | 6 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 212 | 210 | 210 |  | 89
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 17 | 17 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 300 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 365 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 7 | 7 |  | 3 | Engine prolem
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 387 | 395 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1920 | 1918 | 2000 | 2000 | 0 | 453
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 832 | 820 | 609 | 685
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 83 | 99 | 115 | 115
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 20 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 370 | 365 | 350 | 350 | 35 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  | 8 | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 90 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1359 | 1509 | 1394 | 1755 | 35 | 91
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 96 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 34 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 84 | 85 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 89 | 66 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 520 | 570 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 10 | 109 | 0 | 0 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 718 | 977 | 948 | 1058 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 48 | 40 | 40
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 24 | 40 | 42 |  | 8 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 186 | 187 | 190 | 190 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 201 | 189 | 190 | 190 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 390 | 420 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 21 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 45 | 87 | 100 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1170 | 1522 | 1608 | 1639 | 381 | 40
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 | 85 |  | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 15 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 268 | 278 | 271 | 283 | 209 | 105
|  | Total |  |  |  |  | 22023 | 21315 | 11332 | 12994 | 13445.6 | 14397 | 2237 | 2518
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10743.336 | 12319 | 12747.1407 | 13649.1183
| A. |  | 2021-05-30 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 13016 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10128 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12994 | MW
| 3 | Day peak Generation : |  |  | 11332 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12319 | MW
| 4 | Evening peak Generation : |  |  | 12994 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 285.3501 | MKWHr | By Solar | 0.73375 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.6869 | MKWHr |  | By Oil: | 95.3364 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 17.4214 | MKWHr |  | By Hydro: | 0.484 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2237 | MW | Dhaka | 4121 | 4121 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2518 | MW | Chittagong | 1342 | 1342 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4755 | MW | Khulna | 1564 | 1564 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1200 | MMCFD |  |  | Rajshahi | 1251 | 1251 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 159995091.988 | ii) Oil : | Taka | 791761709.52 | Comilla | 1263 | 1263 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 80267050 | Total | Taka | 1032023851.508 | Mymensingh | 1005 | 1005 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.066 | MKWHr. | Sylhet | 552 | 552 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 20 | MW (E to W) at | 21:00 | hrs | Barisal | 412 | 412 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -40 | MW at | 3:00 | hrs | Rangpur | 809 | 809 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.4° C |  |  | Total | 12319 | 12319 |  | 0
| B. |  | 2021-05-31 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14397 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1197 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 289.3839 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9893 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.9724 | MKWHr. | ii) HVDC Flow at Peak Time |  | 820 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.7152 | MKWHr. | iii) Maximum HVDC Flow : |  | 832 | MW at | 11:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.79 |  | (b) Today: | 72.69 |  | (c) Rule Curve: |  | 76.2
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-05-30
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 148 |  | 0 | 280 | 145 | 0 | 0 | 55 | 180 | 0 | 120 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 0 | 46 | 22 | 38 | 0 | 80 | 0 | 275 | 265 | 218 | 8 | 87 | 20 | 15 | 0 | 51 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 166 | 152 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 163 | 163 | 57 | 80 | 0 | 218 | 18 | 0 | 7 | 280 | 16 | 11 | 200 | 228 | 304 | 98 | 173 | 103 | 149 | 0 | 100 | 85 | 147 | 403 | 115 | 82 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 0 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 16 | 88 | 42 | 34 | 31 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 97 | 100 | 213 | 0 | 382 | 103 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 0 | 0 | 89 | 0 |  | 8647 | 4354 | 13001 | 4327 | 829 | 1747 | 4667 | 740 | 20 | 505 | 166 | 0 | 0 | 72.8
2:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 178 |  | 0 | 280 | 145 | 0 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 21 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 0 | 46 | 22 | 38 | 0 | 80 | 0 | 275 | 265 | 217 | 8 | 89 | 20 | 15 | 0 | 51 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 156 | 152 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 163 | 163 | 57 | 80 | 0 | 218 | 17 | 0 | 7 | 270 | 16 | 11 | 150 | 228 | 106 | 60 | 173 | 63 | 149 | 0 | 100 | 85 | 150 | 403 | 115 | 80 | 102 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 22 | 88 | 42 | 34 | 31 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 97 | 100 | 215 | 0 | 397 | 91 | 150 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 54 | 0 |  | 8377 | 4266 | 12643 | 4367 | 829 | 1781 | 4251 | 730 | 20 | 509 | 156 | 0 | 0 | 72.8
3:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 190 |  | 0 | 280 | 145 | 0 | 0 | 55 | 221 | 0 | 120 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 17 | 0 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 0 | 46 | 22 | 38 | 0 | 80 | 0 | 275 | 265 | 216 | 8 | 90 | 20 | 20 | 0 | 51 | 0 | 48 | 52 | 21 | 8 | 33 | 20 | 150 | 155 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 163 | 161 | 57 | 80 | 0 | 218 | 17 | 0 | 7 | 285 | 16 | 11 | 100 | 228 | 52 | 0 | 173 | 0 | 149 | 0 | 100 | 85 | 150 | 403 | 115 | 80 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 829 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 8 | 88 | 42 | 34 | 31 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 95 | 60 | 214 | 0 | 412 | 91 | 70 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 54 | 0 |  | 8170 | 4122 | 12292 | 4378 | 829 | 1826 | 3897 | 730 | 20 | 462 | 150 | 0 | 0 | 72.8
4:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 200 |  | 0 | 280 | 145 | 0 | 0 | 55 | 219 | 0 | 120 | 100 | 102 | 150 | 50 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 0 | 46 | 22 | 38 | 0 | 80 | 0 | 280 | 270 | 216 | 8 | 90 | 20 | 20 | 0 | 51 | 0 | 49 | 52 | 22 | 8 | 33 | 20 | 142 | 155 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 163 | 161 | 57 | 80 | 0 | 218 | 17 | 0 | 7 | 285 | 16 | 11 | 20 | 228 | 0 | 0 | 173 | 0 | 149 | 0 | 100 | 85 | 150 | 403 | 115 | 80 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 19 | 0 | 0 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 8 | 88 | 42 | 34 | 31 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 96 | 20 | 214 | 0 | 417 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 0 | 0 | 35 | 0 |  | 8016 | 3990 | 12006 | 4396 | 829 | 1843 | 3583 | 730 | 20 | 463 | 142 | 0 | 0 | 72.79
5:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 208 |  | 0 | 280 | 145 | 0 | 0 | 55 | 221 | 0 | 120 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 0 | 19 | 22 | 39 | 0 | 80 | 0 | 275 | 265 | 218 | 8 | 90 | 20 | 20 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 136 | 155 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 163 | 160 | 57 | 80 | 0 | 218 | 17 | 0 | 7 | 295 | 16 | 11 | 0 | 228 | 0 | 0 | 164 | 0 | 141 | 0 | 100 | 85 | 147 | 403 | 115 | 80 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 829 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 85 | 32 | 110 | 0 | 0 | 0 | 50 | 5 | 88 | 42 | 0 | 31 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 96 | 0 | 214 | 0 | 373 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 0 | 0 | 0 | 0 |  | 7855 | 3820 | 11675 | 4394 | 829 | 1816 | 3374 | 710 | 20 | 396 | 136 | 0 | 0 | 72.79
6:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 198 |  | 0 | 280 | 145 | 0 | 0 | 15 | 180 | 0 | 120 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 19 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 23 | 92 | 0 | 19 | 22 | 40 | 0 | 80 | 0 | 280 | 270 | 217 | 8 | 90 | 20 | 25 | 0 | 51 | 0 | 0 | 52 | 22 | 8 | 33 | 20 | 122 | 154 | 16 | 17 | 0 | 42 | 41 | 50 | 0 | 110 | 162 | 57 | 80 | 0 | 218 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 95 | 0 | 0 | 120 | 0 | 50 | 1 | 100 | 85 | 142 | 401 | 115 | 80 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 60 | 400 | 0 | 3 | 90 | 17 | 0 | 35 | 1 |  | 829 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 85 | 28 | 16 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 97 | 0 | 192 | 0 | 401 | 35 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 540 | 0 | 0 | 0 | 0 |  | 7089 | 3256 | 10345 | 4340 | 829 | 1769 | 2305 | 690 | 20 | 265 | 122 | 5 | 0 | 72.79
7:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 150 |  | 0 | 280 | 145 | 0 | 0 | 15 | 180 | 0 | 120 | 60 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 17 | 92 | 0 | 19 | 22 | 40 | 0 | 80 | 0 | 290 | 280 | 216 | 8 | 90 | 20 | 25 | 0 | 51 | 0 | 0 | 52 | 21 | 8 | 33 | 20 | 138 | 152 | 16 | 17 | 1 | 42 | 41 | 50 | 0 | 110 | 162 | 56 | 80 | 0 | 218 | 17 | 0 | 7 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 51 | 3 | 100 | 85 | 143 | 402 | 115 | 80 | 105 | 1 | 0 | 54 | 85 | 100 | 111 | 60 | 400 | 0 | 13 | 90 | 17 | 0 | 35 | 5 |  | 829 | 0 | 375 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0 | 0 | 44 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 180 | 0 | 400 | 35 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 540 | 0 | 0 | 0 | 0 |  | 6981 | 3154 | 10135 | 4332 | 829 | 1734 | 2109 | 690 | 20 | 259 | 138 | 24 | 0 | 72.78
8:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 100 |  | 0 | 280 | 145 | 0 | 0 | 15 | 217 | 0 | 185 | 30 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 209 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 0 | 19 | 22 | 10 | 0 | 80 | 0 | 280 | 285 | 216 | 8 | 90 | 20 | 25 | 0 | 51 | 0 | 0 | 52 | 19 | 0 | 33 | 20 | 136 | 152 | 16 | 17 | 1 | 42 | 41 | 50 | 0 | 110 | 163 | 56 | 80 | 0 | 218 | 17 | 0 | 7 | 310 | 16 | 11 | 0 | 95 | 0 | 0 | 80 | 0 | 62 | 6 | 100 | 85 | 143 | 403 | 115 | 81 | 105 | 3 | 0 | 54 | 85 | 100 | 114 | 63 | 396 | 0 | 28 | 90 | 17 | 0 | 35 | 12 |  | 829 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 94 | 0 | 180 | 0 | 413 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 540 | 0 | 0 | 0 | 1 |  | 6994 | 3134 | 10128 | 4439 | 829 | 1666 | 2093 | 690 | 20 | 202 | 136 | 53 | 0 | 72.78
9:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 101 |  | 0 | 280 | 145 | 0 | 0 | 20 | 215 | 0 | 185 | 8 | 40 | 150 | 13 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 21 | 28 | 33 | 33 | 0 | 0 | 20 | 80 | 0 | 17 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 0 | 22 | 22 | 4 | 0 | 100 | 0 | 360 | 265 | 215 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 0 | 52 | 18 | 8 | 33 | 20 | 134 | 132 | 16 | 17 | 2 | 42 | 42 | 50 | 0 | 163 | 161 | 56 | 76 | 0 | 218 | 17 | 0 | 7 | 310 | 16 | 11 | 0 | 127 | 0 | 0 | 96 | 0 | 107 | 9 | 100 | 85 | 143 | 405 | 115 | 81 | 105 | 2 | 0 | 54 | 92 | 88 | 114 | 80 | 400 | 19 | 27 | 121 | 17 | 0 | 35 | 12 |  | 829 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 93 | 0 | 180 | 0 | 415 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 540 | 0 | 0 | 0 | 1 |  | 7278 | 3108 | 10386 | 4459 | 829 | 1710 | 2287 | 690 | 20 | 202 | 134 | 55 | 0 | 72.78
10:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 97 |  | 0 | 280 | 145 | 0 | 0 | 55 | 211 | 0 | 185 | 7 | 102 | 150 | 50 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 21 | 33 | 33 | 33 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 0 | 45 | 19 | 4 | 0 | 100 | 0 | 310 | 265 | 214 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 0 | 43 | 18 | 5 | 33 | 20 | 144 | 129 | 8 | 18 | 2 | 43 | 42 | 50 | 0 | 163 | 162 | 55 | 75 | 0 | 218 | 17 | 0 | 7 | 305 | 16 | 11 | 0 | 228 | 0 | 0 | 171 | 0 | 149 | 18 | 100 | 85 | 142 | 404 | 115 | 81 | 105 | 5 | 0 | 54 | 51 | 100 | 115 | 60 | 390 | 84 | 43 | 144 | 17 | 0 | 35 | 5 |  | 829 | 0 | 360 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 85 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 91 | 0 | 180 | 0 | 412 | 35 | 0 | 20 | 0 | 40 | 0 | 2 | 25 | 520 | 8 | 0 | 0 | 2 |  | 7674 | 3169 | 10843 | 4393 | 829 | 1704 | 2804 | 670 | 20 | 202 | 144 | 77 | 0 | 72.77
11:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 98 |  | 0 | 280 | 145 | 0 | 0 | 55 | 211 | 0 | 185 | 7 | 102 | 150 | 52 | 0 | 0 | 0 | 35 | 35 | 17 | 0 | 25 | 21 | 33 | 33 | 33 | 0 | 0 | 20 | 90 | 0 | 17 | 216 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 45 | 19 | 4 | 0 | 80 | 0 | 335 | 290 | 197 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 0 | 43 | 18 | 8 | 33 | 20 | 138 | 114 | 16 | 18 | 1 | 42 | 42 | 50 | 0 | 163 | 162 | 55 | 75 | 0 | 219 | 17 | 0 | 7 | 300 | 16 | 11 | 0 | 230 | 0 | 0 | 171 | 0 | 149 | 18 | 100 | 85 | 142 | 405 | 115 | 84 | 105 | 5 | 0 | 54 | 51 | 84 | 115 | 60 | 390 | 104 | 54 | 144 | 17 | 0 | 35 | 33 |  | 832 | 0 | 385 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 90 | 0 | 198 | 0 | 412 | 53 | 0 | 102 | 0 | 106 | 0 | 3 | 113 | 520 | 12 | 0 | 0 | 3 |  | 7725 | 3489 | 11214 | 4470 | 832 | 1698 | 3067 | 670 | 20 | 202 | 138 | 117 | 0 | 72.77
12:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 92 |  | 0 | 280 | 145 | 0 | 0 | 55 | 209 | 0 | 120 | 24 | 102 | 150 | 79 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 25 | 21 | 33 | 33 | 0 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 45 | 19 | 7 | 0 | 80 | 0 | 335 | 290 | 189 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 44 | 43 | 18 | 8 | 33 | 20 | 156 | 116 | 16 | 17 | 2 | 43 | 42 | 53 | 0 | 130 | 160 | 55 | 75 | 0 | 219 | 17 | 0 | 7 | 300 | 16 | 11 | 50 | 228 | 21 | 38 | 171 | 53 | 149 | 18 | 100 | 92 | 140 | 405 | 115 | 84 | 94 | 6 | 0 | 54 | 51 | 84 | 108 | 60 | 387 | 104 | 35 | 144 | 17 | 0 | 35 | 29 |  | 832 | 0 | 370 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 89 | 0 | 201 | 0 | 390 | 70 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 520 | 10 | 0 | 0 | 1 |  | 7817 | 3515 | 11332 | 4365 | 832 | 1640 | 3260 | 670 | 20 | 293 | 156 | 96 | 0 | 72.77
13:00 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 86 |  | 0 | 280 | 150 | 0 | 0 | 55 | 206 | 0 | 187 | 50 | 102 | 150 | 78 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 21 | 33 | 33 | 13 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 45 | 19 | 11 | 0 | 80 | 0 | 310 | 265 | 178 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 47 | 43 | 18 | 8 | 33 | 20 | 154 | 110 | 16 | 17 | 1 | 42 | 42 | 53 | 0 | 163 | 160 | 55 | 74 | 0 | 219 | 17 | 0 | 7 | 305 | 16 | 11 | 100 | 228 | 53 | 50 | 169 | 98 | 149 | 0 | 100 | 92 | 138 | 406 | 115 | 84 | 105 | 0 | 0 | 54 | 51 | 98 | 109 | 60 | 390 | 104 | 47 | 144 | 17 | 0 | 35 | 32 |  | 832 | 0 | 355 | 0 | 99 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 18 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 4 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 94 | 0 | 161 | 0 | 410 | 70 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 520 | 10 | 0 | 0 | 3 |  | 8067 | 3503 | 11570 | 4316 | 832 | 1708 | 3480 | 670 | 20 | 302 | 154 | 88 | 0 | 72.76
14:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 87 |  | 0 | 280 | 150 | 0 | 0 | 55 | 210 | 0 | 185 | 56 | 102 | 150 | 84 | 0 | 0 | 0 | 35 | 35 | 35 | 19 | 25 | 20 | 33 | 33 | 26 | 0 | 0 | 20 | 90 | 0 | 17 | 205 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 45 | 21 | 7 | 0 | 80 | 0 | 295 | 280 | 209 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 47 | 43 | 17 | 8 | 33 | 20 | 158 | 100 | 16 | 17 | 1 | 42 | 42 | 53 | 0 | 163 | 160 | 55 | 74 | 0 | 219 | 17 | 0 | 7 | 290 | 16 | 11 | 100 | 238 | 57 | 50 | 169 | 102 | 149 | 14 | 100 | 95 | 138 | 406 | 115 | 84 | 105 | 5 | 0 | 54 | 51 | 98 | 0 | 60 | 385 | 104 | 43 | 144 | 17 | 0 | 35 | 27 |  | 831 | 0 | 370 | 0 | 93 | 0 | 0 | 0 | 7 | 0 | 0 | 84 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 30 | 43 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 92 | 0 | 177 | 0 | 405 | 70 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 520 | 16 | 0 | 0 | 3 |  | 8004 | 3555 | 11559 | 4357 | 831 | 1681 | 3413 | 670 | 20 | 331 | 158 | 98 | 0 | 72.76
15:00 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 87 |  | 0 | 280 | 240 | 0 | 0 | 55 | 211 | 0 | 185 | 56 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 0 | 19 | 25 | 20 | 33 | 33 | 32 | 0 | 0 | 20 | 90 | 0 | 17 | 217 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 45 | 21 | 2 | 0 | 80 | 0 | 290 | 295 | 208 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 47 | 43 | 17 | 8 | 33 | 20 | 170 | 107 | 16 | 18 | 1 | 42 | 42 | 53 | 0 | 163 | 158 | 55 | 74 | 0 | 213 | 17 | 0 | 7 | 310 | 16 | 11 | 150 | 243 | 144 | 100 | 170 | 102 | 149 | 13 | 100 | 90 | 100 | 403 | 115 | 84 | 105 | 4 | 0 | 54 | 51 | 98 | 0 | 60 | 383 | 104 | 33 | 144 | 17 | 0 | 35 | 7 |  | 821 | 0 | 390 | 0 | 83 | 0 | 0 | 0 | 3 | 0 | 0 | 82 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 0 | 0 | 37 | 43 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 92 | 0 | 187 | 0 | 409 | 70 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 520 | 38 | 0 | 0 | 0 |  | 8233 | 3588 | 11821 | 4403 | 821 | 1720 | 3623 | 670 | 20 | 334 | 170 | 60 | 0 | 72.76
16:00 | 0 | 0 | 0 | 185 | 0 | 93 | 0 | 0 | 102 |  | 0 | 280 | 275 | 0 | 0 | 55 | 209 | 0 | 185 | 56 | 102 | 150 | 72 | 0 | 0 | 0 | 35 | 55 | 35 | 0 | 25 | 20 | 33 | 33 | 38 | 0 | 0 | 20 | 90 | 0 | 17 | 212 | 0 | 0 | 0 |  | 24 | 0 | 0 | 20 | 0 | 45 | 21 | 2 | 0 | 80 | 0 | 280 | 285 | 208 | 8 | 90 | 23 | 5 | 0 | 51 | 0 | 47 | 43 | 20 | 8 | 33 | 20 | 166 | 131 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 160 | 55 | 76 | 0 | 212 | 17 | 0 | 7 | 300 | 16 | 11 | 150 | 235 | 130 | 100 | 179 | 101 | 149 | 7 | 100 | 95 | 100 | 402 | 115 | 83 | 105 | 2 | 0 | 54 | 51 | 98 | 49 | 100 | 382 | 104 | 8 | 144 | 17 | 0 | 35 | 3 |  | 820 | 0 | 335 | 0 | 86 | 0 | 0 | 0 | 3 | 0 | 0 | 84 | 29 | 16 | 0 | 0 | 0 | 50 | 0 | 87 | 0 | 0 | 38 | 43 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 157 | 0 | 92 | 0 | 167 | 0 | 336 | 70 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 510 | 71 | 0 | 0 | 0 |  | 8273 | 3346 | 11619 | 4296 | 820 | 1689 | 3571 | 660 | 20 | 375 | 166 | 22 | 0 | 72.75
17:00 | 0 | 0 | 0 | 185 | 0 | 88 | 0 | 0 | 112 |  | 0 | 280 | 255 | 0 | 0 | 55 | 210 | 0 | 186 | 56 | 102 | 150 | 71 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 90 | 0 | 17 | 206 | 0 | 0 | 0 |  | 24 | 0 | 5 | 80 | 0 | 45 | 21 | 7 | 0 | 80 | 0 | 260 | 265 | 210 | 8 | 90 | 20 | 5 | 0 | 51 | 0 | 47 | 43 | 20 | 8 | 33 | 20 | 160 | 132 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 159 | 55 | 75 | 0 | 212 | 17 | 0 | 7 | 310 | 16 | 11 | 100 | 238 | 30 | 0 | 150 | 72 | 149 | 3 | 100 | 95 | 100 | 405 | 115 | 66 | 105 | 1 | 0 | 54 | 51 | 98 | 113 | 70 | 388 | 104 | 8 | 144 | 17 | 0 | 35 | 1 |  | 821 | 0 | 335 | 0 | 99 | 0 | 0 | 0 | 3 | 0 | 0 | 85 | 27 | 16 | 0 | 0 | 0 | 50 | 0 | 87 | 0 | 0 | 38 | 52 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 94 | 0 | 130 | 0 | 334 | 70 | 0 | 70 | 0 | 34 | 0 | 2 | 70 | 470 | 71 | 0 | 0 | 0 |  | 8041 | 3264 | 11305 | 4216 | 821 | 1706 | 3367 | 620 | 20 | 380 | 160 | 15 | 0 | 72.75
18:00 | 0 | 0 | 0 | 185 | 0 | 45 | 0 | 0 | 108 |  | 0 | 280 | 255 | 0 | 0 | 55 | 212 | 0 | 150 | 56 | 102 | 150 | 36 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 17 | 80 | 0 | 45 | 21 | 7 | 0 | 80 | 0 | 260 | 270 | 210 | 8 | 89 | 20 | 5 | 0 | 20 | 0 | 47 | 43 | 20 | 8 | 33 | 20 | 148 | 132 | 16 | 18 | 0 | 42 | 42 | 22 | 0 | 110 | 160 | 40 | 20 | 0 | 212 | 17 | 0 | 7 | 290 | 16 | 11 | 0 | 240 | 0 | 0 | 150 | 0 | 146 | 1 | 100 | 90 | 100 | 405 | 115 | 83 | 105 | 0 | 0 | 54 | 51 | 99 | 116 | 40 | 390 | 85 | 1 | 144 | 17 | 0 | 35 | 0 |  | 821 | 0 | 335 | 0 | 83 | 0 | 0 | 0 | 21 | 0 | 0 | 86 | 29 | 16 | 0 | 0 | 0 | 50 | 10 | 87 | 0 | 0 | 38 | 52 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 94 | 0 | 130 | 0 | 329 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 450 | 105 | 0 | 0 | 0 |  | 7478 | 3176 | 10654 | 4168 | 821 | 1500 | 2975 | 600 | 20 | 420 | 148 | 2 | 0 | 72.75
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 104 |  | 0 | 280 | 265 | 0 | 0 | 55 | 211 | 0 | 97 | 62 | 102 | 150 | 59 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 33 | 33 | 38 | 0 | 0 | 20 | 90 | 0 | 17 | 216 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 45 | 21 | 5 | 0 | 80 | 0 | 285 | 295 | 211 | 8 | 90 | 20 | 5 | 0 | 34 | 0 | 47 | 35 | 21 | 8 | 33 | 20 | 178 | 132 | 16 | 18 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 56 | 76 | 0 | 212 | 17 | 0 | 7 | 290 | 16 | 11 | 155 | 243 | 236 | 90 | 182 | 99 | 149 | 0 | 100 | 95 | 100 | 385 | 115 | 83 | 105 | 0 | 0 | 54 | 55 | 100 | 117 | 65 | 386 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 820 | 0 | 390 | 0 | 99 | 0 | 0 | 0 | 21 | 0 | 0 | 85 | 34 | 103 | 0 | 0 | 0 | 50 | 6 | 87 | 42 | 16 | 38 | 52 | 33 | 21 | 0 | 11 | 0 | 0 | 150 | 12 | 0 | 0 | 0 | 139 | 0 | 83 | 24 | 144 | 0 | 335 | 70 | 100 | 53 | 0 | 100 | 0 | 0 | 70 | 450 | 108 | 0 | 3 | 0 |  | 8495 | 3749 | 12244 | 4259 | 820 | 1700 | 4138 | 600 | 20 | 529 | 178 | 0 | 0 | 72.73
19:30 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 112 |  | 0 | 280 | 240 | 0 | 0 | 55 | 214 | 0 | 150 | 100 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 38 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 45 | 22 | 8 | 0 | 80 | 0 | 260 | 270 | 214 | 8 | 86 | 20 | 30 | 0 | 51 | 0 | 47 | 43 | 21 | 8 | 33 | 20 | 176 | 132 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 56 | 76 | 0 | 212 | 17 | 0 | 7 | 270 | 16 | 11 | 200 | 243 | 255 | 97 | 182 | 95 | 149 | 0 | 100 | 105 | 100 | 368 | 115 | 83 | 105 | 0 | 0 | 54 | 90 | 100 | 118 | 80 | 399 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 820 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 21 | 0 | 0 | 86 | 34 | 110 | 0 | 0 | 0 | 50 | 7 | 87 | 42 | 34 | 38 | 52 | 36 | 21 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 0 | 0 | 168 | 0 | 83 | 100 | 181 | 0 | 321 | 90 | 200 | 102 | 0 | 113 | 0 | 0 | 113 | 490 | 107 | 0 | 17 | 0 |  | 8684 | 4148 | 12832 | 4278 | 820 | 1721 | 4641 | 640 | 20 | 536 | 176 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 118 |  | 0 | 280 | 245 | 0 | 0 | 55 | 213 | 0 | 150 | 100 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 38 | 0 | 0 | 20 | 90 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 45 | 22 | 17 | 0 | 80 | 0 | 260 | 270 | 213 | 8 | 86 | 20 | 30 | 0 | 51 | 0 | 47 | 43 | 21 | 8 | 33 | 20 | 176 | 132 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 56 | 78 | 0 | 212 | 17 | 0 | 7 | 270 | 16 | 11 | 200 | 245 | 171 | 98 | 185 | 100 | 149 | 0 | 100 | 100 | 97 | 366 | 115 | 83 | 105 | 0 | 0 | 54 | 88 | 100 | 118 | 80 | 399 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 821 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 21 | 0 | 0 | 85 | 34 | 110 | 0 | 0 | 0 | 50 | 7 | 87 | 42 | 34 | 40 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 0 | 0 | 175 | 0 | 67 | 100 | 183 | 0 | 326 | 105 | 150 | 108 | 0 | 113 | 0 | 0 | 113 | 520 | 107 | 0 | 17 | 0 |  | 8618 | 4148 | 12766 | 4281 | 821 | 1727 | 4534 | 670 | 20 | 537 | 176 | 0 | 0 | 72.74
21:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 118 |  | 0 | 280 | 260 | 0 | 0 | 55 | 214 | 0 | 185 | 100 | 102 | 150 | 80 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 46 | 22 | 26 | 0 | 80 | 0 | 265 | 275 | 211 | 8 | 90 | 20 | 43 | 0 | 51 | 0 | 47 | 43 | 21 | 8 | 33 | 20 | 172 | 130 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 161 | 56 | 78 | 0 | 212 | 17 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 108 | 100 | 196 | 102 | 149 | 0 | 100 | 100 | 132 | 365 | 115 | 83 | 105 | 0 | 0 | 54 | 91 | 100 | 120 | 80 | 395 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 820 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 0 | 85 | 34 | 96 | 0 | 0 | 0 | 50 | 48 | 87 | 24 | 34 | 38 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 0 | 0 | 187 | 0 | 66 | 100 | 189 | 0 | 420 | 105 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 109 | 0 | 17 | 0 |  | 8708 | 4286 | 12994 | 4336 | 820 | 1876 | 4475 | 720 | 20 | 575 | 172 | 0 | 0 | 72.73
22:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 128 |  | 0 | 280 | 270 | 0 | 0 | 55 | 216 | 0 | 185 | 80 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 90 | 0 | 17 | 217 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 48 | 22 | 32 | 0 | 80 | 0 | 295 | 300 | 212 | 8 | 90 | 20 | 46 | 0 | 51 | 0 | 48 | 43 | 21 | 8 | 33 | 20 | 176 | 130 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 161 | 56 | 78 | 0 | 212 | 17 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 55 | 100 | 200 | 102 | 149 | 0 | 100 | 100 | 135 | 402 | 115 | 83 | 105 | 0 | 0 | 54 | 91 | 100 | 119 | 80 | 391 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 820 | 0 | 395 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 0 | 86 | 34 | 110 | 0 | 0 | 0 | 50 | 39 | 87 | 24 | 34 | 38 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 196 | 0 | 64 | 100 | 197 | 0 | 413 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 109 | 0 | 22 | 0 |  | 8786 | 4230 | 13016 | 4488 | 820 | 1886 | 4344 | 720 | 20 | 562 | 176 | 0 | 0 | 72.73
23:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 140 |  | 0 | 280 | 260 | 0 | 0 | 55 | 212 | 0 | 185 | 80 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 33 | 17 | 42 | 0 | 0 | 20 | 80 | 0 | 17 | 217 | 0 | 0 | 0 |  | 24 | 0 | 68 | 90 | 0 | 50 | 22 | 30 | 0 | 80 | 0 | 305 | 290 | 195 | 8 | 90 | 20 | 50 | 0 | 51 | 0 | 48 | 43 | 21 | 8 | 33 | 20 | 180 | 134 | 16 | 18 | 0 | 42 | 43 | 53 | 0 | 163 | 161 | 56 | 78 | 0 | 212 | 17 | 0 | 7 | 310 | 16 | 11 | 200 | 245 | 55 | 100 | 197 | 102 | 149 | 0 | 100 | 100 | 137 | 403 | 115 | 83 | 105 | 0 | 0 | 54 | 91 | 100 | 118 | 70 | 391 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 831 | 0 | 395 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 0 | 84 | 34 | 110 | 0 | 0 | 0 | 50 | 36 | 87 | 24 | 34 | 38 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 201 | 0 | 94 | 100 | 203 | 0 | 416 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 3 | 0 | 73 | 0 |  | 8727 | 4215 | 12942 | 4456 | 831 | 1837 | 4366 | 720 | 20 | 532 | 180 | 0 | 0 | 72.72
24:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 150 |  | 0 | 280 | 260 | 0 | 0 | 55 | 215 | 0 | 185 | 80 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 17 | 41 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 68 | 90 | 0 | 50 | 22 | 30 | 0 | 80 | 0 | 285 | 275 | 174 | 8 | 90 | 20 | 50 | 0 | 51 | 0 | 48 | 43 | 21 | 8 | 33 | 21 | 180 | 139 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 57 | 80 | 0 | 212 | 17 | 0 | 7 | 310 | 16 | 11 | 200 | 243 | 159 | 98 | 200 | 101 | 149 | 0 | 100 | 100 | 142 | 373 | 115 | 83 | 105 | 0 | 0 | 54 | 91 | 100 | 119 | 70 | 395 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 830 | 0 | 370 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 0 | 86 | 34 | 98 | 0 | 0 | 0 | 50 | 26 | 88 | 24 | 34 | 38 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 199 | 0 | 95 | 100 | 202 | 0 | 416 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 0 | 0 | 100 | 0 |  | 8801 | 4192 | 12993 | 4385 | 830 | 1847 | 4488 | 720 | 20 | 523 | 180 | 0 | 0 | 72.72
KWH | 0 | 0 | 0 | 4378500 | 0 | 2150500 | 0 | 0 | 3094000 |  | 0 | 6646850 | 4489600 | 0 | 0 | 1201721 | 5131093 | 0 | 3979000 | 1638720 | 2082672 | 3604800 | 1465997 | 0 | 0 | 0 | 874800 | 1002266 | 768491 | 228996 | 600000 | 473940 | 799800 | 763900 | 846240 | 0 | 0 | 484000 | 2200000 | 0 | 410635 | 4958502 | 0 | 0 | 0 |  | 586080 | 0 | 888837 | 2022000 | 0 | 992640 | 505344 | 472320 | 0 | 1969105 | 0 | 7289000 | 6793000 | 5034000 | 200727 | 2126610 | 454896 | 586560 | 0 | 1183045 | 0 | 819824 | 1109381 | 471888 | 168120 | 816800 | 498340 | 3715200 | 3137880 | 367680 | 394524 | 12200 | 1002000 | 990360 | 1202400 | 0 | 3607445 | 3547000 | 1329120 | 1794240 | 0 | 5120110 | 399000 | 0 | 161280 | 7296500 | 363360 | 264000 | 2284416 | 5211380 | 1724985 | 1062298 | 3921600 | 1255546 | 3288960 | 117180 | 2415360 | 2233920 | 3206618 | 9558000 | 2750400 | 1944000 | 2559272 | 27959 | 0 | 1299168 | 2004762 | 2362080 | 2485560 | 1631040 | 9514900 | 2166720 | 343490 | 3353760 | 429055 | 0 | 887040 | 177932 |  | 19972363 | 0 | 8978976 | 0 | 2233920 | 0 | 0 | 0 | 248160 | 0 | 0 | 2057109 | 653585 | 1312032 | 0 | 0 | 0 | 902048 | 222533 | 1743656 | 402130 | 317168 | 532168 | 1162560 | 266660 | 483840 | 0 | 209394 | 0 | 0 | 3676800 | 57000 | 0 | 0 | 0 | 4458491 | 0 | 2172999 | 855360 | 4769300 | 0 | 9378145 | 1813440 | 995022 | 2117856 | 0 | 1944922 | 0 | 38133 | 2038656 | 13744600 | 868145 | 0 | 520800 | 16860 |  | 194185240 | 91164831 | 285350071 | 105734358 | 19972363 | 41952581 | 86050729 | 17421400 | 484000 | 9285686 | 3715200 | 733754 | 0
Fuel Cost | 0 | 0 | 0 | 6436395 | 0 | 2838660 | 0 | 0 | 3186820 |  | 0 | 7245066.5 | 4983456 | 0 | 0 | 10166559.66 | 5336336.72 | 0 | 6883670 | 12339561.6 | 18993968.64 | 35471232 | 13516492.34 | 0 | 0 | 0 | 6386040 | 7747516.18 | 7577321.26 | 171747 | 450000 | 0 | 0 | 0 | 8183140.8 | 0 | 0 | 130680 | 3982000 | 0 | 3814799.15 | 5404767.18 | 0 | 0 | 0 |  | 0 | 0 | 8621718.9 | 19310100 | 0 | 7861708.8 | 636733.44 | 1402790.4 | 0 | 2914275.4 | 0 | 5393860 | 6793000 | 4631280 | 258937.83 | 2445601.5 | 514032.48 | 821184 | 0 | 2023006.95 | 0 | 8280222.4 | 10594588.55 | 599297.76 | 126090 | 1429400 | 373755 | 27864000 | 3326152.8 | 3338534.4 | 501045.48 | 194468 | 1643280 | 1584576 | 2140272 | 0 | 4112487.3 | 3688880 | 2618366.4 | 3426998.4 | 0 | 8857790.3 | 873810 | 0 | 329011.2 | 7369465 | 272520 | 200640 | 38857916.16 | 39398032.8 | 29290245.3 | 17761622.56 | 20392320 | 20992729.12 | 32363366.4 | 1369834.2 | 19685184 | 24238032 | 22606656.9 | 8888940 | 25083648 | 18370800 | 22291259.12 | 0 | 0 | 11315753.28 | 17621857.98 | 23573558.4 | 21301249.2 | 10862726.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115040810.88 | 0 | 9427924.8 | 0 | 17558611.2 | 0 | 0 | 0 | 2603198.4 | 0 | 0 | 2324533.17 | 1013056.75 | 12805432.32 | 0 | 0 | 0 | 8876152.32 | 2260935.28 | 15431355.6 | 3096401 | 4288111.36 | 5156707.92 | 11265206.4 | 2586602 | 928972.8 | 0 | 158511.258 | 0 | 0 | 19928256 | 1975050 | 0 | 0 | 0 | 5885208.12 | 0 | 3259498.5 | 14549673.6 | 5580081 | 0 | 9284363.55 | 18932313.6 | 16925324.22 | 20098453.44 | 0 | 15092594.72 | 0 | 421369.65 | 15065667.84 | 60338794 | 0 | 0 | 0 | 0 |  | 754885842.54 | 422159171.698 | 1177045014.238 | 110354500.808 | 115040810.88 | 49640591.18 | 700498534.7 | 80267050 | 130680 | 91263174.82 | 27864000 | 1985671.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 92 |  | 0 | 280 | 145 | 0 | 0 | 55 | 209 | 0 | 120 | 24 | 102 | 150 | 79 | 0 | 0 | 0 | 35 | 35 | 35 | 0 | 25 | 21 | 33 | 33 | 0 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 45 | 19 | 7 | 0 | 80 | 0 | 335 | 290 | 189 | 8 | 90 | 23 | 25 | 0 | 51 | 0 | 44 | 43 | 18 | 8 | 33 | 20 | 156 | 116 | 16 | 17 | 2 | 43 | 42 | 53 | 0 | 130 | 160 | 55 | 75 | 0 | 219 | 17 | 0 | 7 | 300 | 16 | 11 | 50 | 228 | 21 | 38 | 171 | 53 | 149 | 18 | 100 | 92 | 140 | 405 | 115 | 84 | 94 | 6 | 0 | 54 | 51 | 84 | 108 | 60 | 387 | 104 | 35 | 144 | 17 | 0 | 35 | 29 |  | 832 | 0 | 370 | 0 | 83 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 15 | 0 | 0 | 0 | 0 | 50 | 0 | 45 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 89 | 0 | 201 | 0 | 390 | 70 | 0 | 113 | 0 | 113 | 0 | 5 | 113 | 520 | 10 | 0 | 0 | 1 |  | 11332 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 118 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 214 | 0 | 185 | 100 | 102 | 150 | 80 | 0 | 0 | 0 | 35 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 90 | 0 | 17 | 204 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 100 | 0 | 46 | 22 | 26 | 0 | 80 | 0 | 265 | 275 | 211 | 8 | 90 | 20 | 43 | 0 | 51 | 0 | 47 | 43 | 21 | 8 | 33 | 20 | 172 | 130 | 16 | 18 | 0 | 42 | 42 | 53 | 0 | 163 | 161 | 56 | 78 | 0 | 212 | 17 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 108 | 100 | 196 | 102 | 149 | 0 | 100 | 100 | 132 | 365 | 115 | 83 | 105 | 0 | 0 | 54 | 91 | 100 | 120 | 80 | 395 | 104 | 0 | 144 | 17 | 0 | 35 | 0 |  | 820 | 0 | 365 | 0 | 99 | 0 | 0 | 0 | 20 | 0 | 0 | 85 | 34 | 96 | 0 | 0 | 0 | 50 | 48 | 87 | 24 | 34 | 38 | 52 | 35 | 21 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 0 | 0 | 187 | 0 | 66 | 100 | 189 | 0 | 420 | 105 | 100 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 109 | 0 | 17 | 0 |  | 12994 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 120 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 220 | 0 | 185 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 25 | 0 | 80 | 0 | 300 | 300 | 210 | 8 | 90 | 26 | 49 | 0 | 51 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 181 | 150 | 24 | 19 | 0 | 42 | 42 | 51 | 0 | 163 | 163 | 56 | 80 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 100 | 150 | 400 | 115 | 85 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 35 |  |  | 685 | 0 | 350 | 0 | 115 | 220 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 42 | 43 | 40 | 52 | 35 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 190 | 0 | 95 | 100 | 190 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 0 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 110 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 220 | 0 | 120 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 0 | 0 | 0 | 22 |  | 68 | 100 | 6 | 50 | 22 | 10 | 0 | 80 | 0 | 300 | 300 | 210 | 8 | 90 | 26 | 49 | 0 | 51 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 145 | 150 | 24 | 19 | 1.6 | 42 | 42 | 51 | 0 | 163 | 163 | 56 | 80 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 100 | 150 | 400 | 115 | 85 | 105 | 5 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 35 | 30 |  | 609 | 0 | 350 | 0 | 115 | 0 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 100 | 40 | 43 | 40 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 95 | 50 | 190 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 0 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 112 | 0 | 0 | 280 | 238 | 0 | 0 | 15 | 170 | 0 | 120 | 7 | 7 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 20 | 25 | 18 | 33 |  | 41 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 | 0 | 24 | 0 | 34 | 90 | 0 | 11 | 22 | 8 | 0 | 80 | 0 | 260 | 265 | 208 | 8 | 89 | 20 | 50 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 112 | 151 | 16 | 17 | 0 | 42 | 42 | 53 | 0 | 130 | 162 | 56 | 77 | 0 | 164 | 17 | 0 | 7 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 70 | 0 | 35 | 0 | 90 | 104 | 100 | 367 | 115 | 82 | 105 | 3 | 0 | 54 | 91 | 90 | 116 | 70 | 399 | 17 | 10 | 108 | 17 | 0 | 35 | 6 | 0 | 835 | 0 | 350 | 0 | 99 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 95 | 0 | 172 | 0 | 363 | 0 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 540 | 0 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 10128 | 8:00
| Highest Generation |  | 13016 | 22:00
| Day Peak Generation |  | 11332 | 12:00
| Evening Peak Generation |  | 12994 | 21:00
| HVDC Max Flow |  | 832 | 11:00
| HVDC EvPeak Flow |  | 820 | 21:00
| Load factor L.F |  | 91.35%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-05-31
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-05-30 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11332 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9893 | MW
Evening Peak Generation : |  | 12994 | MW Hour : | 21:00 | Available Max Generation : |  | 14397 | MW
E.P. Demand (at gen end) : |  | 12994 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 13016 | MW Hour : | 22:00 | Reserve(Generation end) |  | 1197 | MW
Total Gen. (MKWH) : |  | 285.3501 | System Load Factor : | 91.35% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -40 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-05-31
Actual : | 72.69 | Ft.(MSL) , | Rule curve : | 76.2 | Ft.( MSL )
Gas Consumed : | Total = | 1200 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 159995091.988
: |  | Coal : | 80267050 | Oil : | 791761709.52 | Total : | 1032023851.508
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4650.6748 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1586.5817 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1422.4324 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1285.61 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1161.6094 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 937.3905 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 517.5864 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 241.1793 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 722.9935 |  |  | 0 | 0%
Total | 0 |  | 12526.0579 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
7) Siddhirganj 335 MW ST
8) Bhola 225 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Haripur 230/132 kV T1 transformer was shut down at 08:47 for D/W.
b) Haripur 230 kV Bus-2 was shut down at 08:27 for D/W.
c) Haripur S/S-Haripur 412 MW CCPP 230 kV Ckt was under shut down from 12:33 to 14:42 due to unit
transformer of P/P maintenance.
d) Ishwardi 132/33 kV T-1 transformer was under shut down from 10:32 to 13:15 for Oil filling.
e) Mymensing 132/33 kV T-1 transformer was under shut down from 09:20 to 16:42 for C/M.
f) Nutan Bidyut GT-2 was synchronized at 09:24.
g) Meghnaghat Summit 305 MW GT-2 was synchronized at 12:58.
h) Chowmuhuni S/S-Chowmuhuni P/P 132 kV Ckt was under shut down from 13:38 to 15:02 due to red
hot maintenance at Chowmuhuni P/P end.
i) Aminbazar 230 kV Bus-1 was under shut down from 15:05 to 19:07 for D/W.
j) Dohazari-Cox'sbazar 132 kV Ckt-2 was switched ion at 20:27.
k) Norail-Magura 132 kV Ckt-1 was under shut down from 15:30 to 16:16 for D/W.
l) Norail-Magura 132 kV Ckt-2 was under shut down from 16:27 to 17:06 for D/W.
m) Kishoreganj 132/33 kV T3 & T4 transformers tripped at 22:06 showing O/C relay at 33 kV end and was |  |  |  |  | About 60 MW power interruption occurred under Kishoreganj S/S
switched on at 22:36. |  |  |  |  | area from 22:06 to 22:36
n) Raozan Unit-1 was shut down at 23:20 and was synchronized at 23:31.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-05-30 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4378500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2150500
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Shut down due to gas problem
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 118 | 3094000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6646850 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 4489600 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1201721
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 80 | 1465997 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 0 | 228996 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 185 | 3979000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1638720
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 214 | 5131093 | ST under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2082672
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 874800 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3604800
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1002266
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 768491
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1073940 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 799800
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 763900
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 41 | 846240 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 5211380 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 108 | 1724985 | Low demand
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 1062298
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 102 | 1255546
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3288960
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 83 | 1944000 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2166720
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 3353760 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 177932
| Dhaka area Total |  |  |  | 5919 | 3160 | 66407467
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 2200000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 410635 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 117180
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 992640 | Engine problem
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 484000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 204 | 4958502 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2559272
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 888837 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2022000
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2415360
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505344
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 472320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27959
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | TF O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1299168
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 91 | 2004762 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 80 | 1631040 | Line O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 429055 | Line O/L
| Chattogram area Total |  |  |  | 2382 | 1057 | 23418074
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 80 | 1969105 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 5034000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 7289000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6793000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 20 | 454896 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 43 | 586560 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1183045
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 132 | 3206618 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 47 | 819824
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2126610 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 2233920 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 471888
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 168120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 172 | 3715200
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816800
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1109381 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 498340 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2284416
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2362080 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 120 | 2485560
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 887040 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2074 | 46696130
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 130 | 3137880 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 394524 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 367680 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12200
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 196 | 3921600
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2750400
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 343490
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 586080
| Mymensingh Area Total |  |  |  | 709 | 499 | 11513854
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1002000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 990360 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3607445
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3547000 | Machine problem
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1202400
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1329120 | Engine problem
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1794240 | Engine problem
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 212 | 5120110
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 17 | 399000 | Engine problem
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 363360 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 300 | 7296500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 365 | 9558000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 161280 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 395 | 9514900 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1918 | 46149715
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 820 | 19972363
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 99 | 2233920 | Engine problem
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 248160 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 365 | 8978976 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 855360
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1813440
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1509 | 34102219
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 96 | 1312032 | Engine problem
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 653585
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 85 | 2057109 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 66 | 2172999 | Machine problem
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 570 | 13744600
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 109 | 868145 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 520800 | Low demand
| Barisal Area Total |  |  |  | 1826 | 977 | 21329270
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 902048
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 48 | 222533 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 24 | 402130 | Raj. 132 kV Bus O/L
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 317168 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 532168 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4458491 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 189 | 4769300 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 9378145 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 266660 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 483840
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 209394
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1162560
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1743656 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 995022 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2117856
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2038656
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 16860
| Rajshahi Area Total |  |  |  | 2179 | 1522 | 30016487
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676800 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 15 | 57000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1944922
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 38133
| Rangpur Area Total |  |  |  | 605 | 278 | 5716855
| Total |  |  |  | 21315 | 12994 | 285350071
| Eastern Grid Total |  |  |  | 14421 | 8708 | 194185240
| Western Grid Total |  |  |  | 6894 | 4286 | 91164831
| National Grid Total |  |  |  | 21315 | 12994 | 285350071
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-05-30
(a) ENTIRE EASTERN GRID : |  | 8283 | MW | (b) ENTIRE WESTERN GRID : |  | 4036 | MW
i) Dhaka area |  | 4121 | MW | i) Khulna area |  | 1564 | MW
ii) Chittagong area |  | 1342 | MW | ii) Rajshahi area |  | 1251 | MW
iii) Comilla area |  | 1263 | MW | iii) Barisal area |  | 412 | MW
iv) Mymensingh area |  | 1005 | MW | iv) Rangpur area |  | 809 | MW
v) Sylhet area |  | 552 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12319 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 19:00 | Kishoreganj | 138 | 20:00 | Benapol | 66 | 21:00
Munsiganj | 112 | 1:00 | Netrokona | 116 | 20:00 | Jhenida | 116 | 21:00
Sonargaon | 78 | 20:00 | Jamalpur | 152 | 2:00 | Bottail | 140 | 21:00
Shyampur | 198 | 0:00 | Sherpur | 134 | 23:00 | G.K Project | 56 | 23:00
Bhulta | 213 | 16:00 | Srimongal | 61 | 21:00 | Faridpur | 204 | 1:00
Madanganj | 54 | 11:00 | Shahjibazar | 126 | 24:00 | Madaripur | 116 | 23:00
Shitalakhya | 120 | 16:00 | Fenchuganj | 51 | 21:00 | Sariatpur | 74 | 21:00
Rahim steel | 29 | 12:00 | Kulawara | 49 | 22:00 | Gopalganj | 103 | 22:00
Matuail | 60 | 10:00 | Sylhet | 134 | 15:00 | Bagerhat | 110 | 20:00
Ghorasal | 80 | 19:30 | Chatak | 34 | 21:00 | Mongla | 40 | 11:00
Narsingdi | 183 | 19:30 | Sunamganj | 55 | 22:00 | Satkhira | 116 | 21:00
Haripur (SBU) | 114 | 23:00 | Biani Bazar | 72 | 19:30 | Gallamari | 40 | 23:00
Sreenagar | 44 | 21:00 | Comilla (S) | 180 | 23:00 | Magura | 56 | 22:00
Ullon | 74 | 24:00 | Comilla(N) | 145 | 00:0 | Norail | 48 | 21:00
Hasnabad | 86 | 21:00 | Chandpur | 89 | 23:00 | Chuadanga | 88 | 1:00
Magbazar | 108 | 12:00 | Feni | 128 | 22:00 | Borguna | 22 | 23:00
Maniknagar | 76 | 12:00 | Chowmuhani | 212 | 22:00 | Barisal(N) | 53 | 22:00
Bangabhaban | 14 | 10:00 | Ashuganj | 35 | 0:00 | Barisal (S) | 120 | 19:00
Motijheel | 26 | 11:00 | Daudkandi | 162 | 0:00 | Patuakhali | 127 | 23:00
Narinda | 58 | 13:00 | B.Baria | 170 | 21:00 | Bhandaria | 60 | 22:00
Kazla | 79 | 15:00 | Ramganj | 110 | 19:00 | Borhan Uddin |  | 3:00
Dhanmondi | 218 | 13:00 | Chaddagram | 51 | 22:00 | Ishurdi | 63 | 1:00
Lalbag | 93 | 13:00 | PHP | 6 | 0:00 | Ruppur Paromanobik | 3 | 1:00
Madartek | 81 | 23:00 | Kochua | 72 | 21:00 | Natore | 124 | 1:00
Dhaka University | 46 | 13:00 | Madunaghat | 64 | 15:00 | Bogra | 155 | 20:00
Aftabnagar | 11 | 15:00 | Hathazari | 95 | 21:00 | Noagaon | 119 | 21:00
Fatullah | 65 | 10:00 | Khulshi | 208 | 1:00 | Rajshahi | 158 | 1:00
Nawabganj | 54 | 22:00 | Halishahar | 151 | 15:00 | Rajshahi New | 21 | 22:00
Keraniganj | 67 | 12:00 | Baraulia | 167 | 0:00 | C.Nawabganj | 67 | 20:00
Mirpur | 121 | 19:00 | Sikalbaha | 41 | 16:00 | Amnura | 38 | 1:00
Kalyanpur | 120 | 19:00 | Dohazari | 106 | 19:00 | Pabna | 100 | 1:00
Gulshan | 148 | 13:00 | Cox'sbazar | 108 | 21:00 | Shahjadpur | 82 | 21:00
Uttara | 85 | 17:00 | Chandraghona | 34 | 19:30 | Serajganj | 86 | 1:00
Uttara New | 32 | 19:00 | Kaptai | 4 | 19:00 | Niyamatpur | 67 | 21:00
Kamrangirchar | 93 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Joypurhat | 62 | 21:00
Savar | 173 | 15:00 | Bakulia | 113 | 19:00 | Sherpur(Bogura) | 57 | 1:00
Bhasantec | 167 | 15:00 | Julda | 23 | 16:00 | Mohastangor | 62 | 1:00
Agargaon | 84 | 14:00 | TK chemical | 31 | 19:30 | Bhangura | 30 | 1:00
Satmosjid | 104 | 19:00 | Modern Steel | 0 | #N/A | Rangpur | 118 | 1:00
Tongi | 125 | 16:00 | Shahmirpur | 26.3 | 2:00 | Lalmonirhat | 41 | 1:00
Kabirpur | 250 | 11:00 | Khagrachhari | 28 | 7:00 | Saidpur | 102 | 19:30
Basundhara | 163 | 10:00 | Matarbari | 39.5 | 21:00 | Purbasadipur | 110 | 22:00
Manikganj | 76 | 1:00 | Baroiar Hat | 46 | 19:00 | Thakurgaon | 81 | 2:00
Joydevpur | 182 | 15:00 | Rangamati | 12 | 12:00 | Palashbari | 119 | 20:00
New Tongi | 113 | 16:00 | Abul Khair 230 | 6 | 16:00 | Barapukuria | 52 | 21:00
Kodda | 278 | 17:00 | BSRM | 144 | 22:00 | Panchagar | 56 | 20:00
Dhamrai | 110 | 13:00 | GPH Ispat | 95 | 15:00 | Joldhaka | 62 | 20:00
Rajendrapur | 106 | 22:00 | Goalpara | 30 | 13:00 | Kurigram | 59 | 19:30
Valuka | 134 | 17:00 | Central s/s | 99 | 19:30 | Mithapukur | 47 | 3:00
Tangail | 202 | 1:00 | Noapara | 60 | 20:00
Mymensing | 218 | 0:00 | Jessore | 126 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-05-30 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 5:00 | 393 | 12:00 | Kaliakoir | 389 | 0.70833 | 374 | 0.625
| Bheramara | 398 | 1:00 | 391 | 1:00 | Bhulta | 382 | 0.125 | 360 | 0.45833
| Ashuganj(N) | 3888 | 5:00 | 370 | 11:00 | Gopalganj | 404 | 0.625 | 385 | 0.83333
| Payra | 406 | 1:00 | 396 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 225 | 18:00 | Hathazari | 221 | 5:00 | 205 | 15:00
| Ishurdi | 234 | 5:00 | 224 | 21:00 | Megnaghat | 231 | 10:00 | 30 | 21:00
| Ashuganj | 238 | 2:00 | 231 | 15:00 | Fenchuganj | 238 | 5:00 | 235 | 14:00
| Serajganj | 230 | 2:00 | 225 | 22:00 | Siddhirganj | 228 | 3:00 | 216 | 11:00
| Baghabari | 232 | 17:00 | 224 | 7:00 | Maniknagar | 227 | 3:00 | 214 | 11:00
| Barapukuria | 235 | 12:00 | 227 | 8:00 | Agargaon | 226 | 5:00 | 211 | 11:00
| Bogra | 225 | 14:00 | 213 | 8:00 | Barisal | 250 | 7:00 | 240 | 20:00
| Rajshahi | 237 | 18:30 | 222 | 7:00 | Bhola 225 MW | 259 | 1:00 | 244 | 21:00
| Khulna South | 227 | 18:00 | 211 | 22:00 | AKSML | 220 | 7:00 | 211 | 15:00
| Rampura | 227 | 1:00 | 215 | 11:00 | BSRM | 224 | 4:00 | 212 | 15:00
| Haripur | 224 | 23:00 | 212 | 11:00 | Bibiyana | 237 | 2:00 | 232 | 24:00
| Hasnabad | 230 | 1:00 | 215 | 9:00 | Bhulta | 229 | 1:00 | 215 | 11:00
| Shyampur | 226 | 1:00 | 220 | 11:00 | Ashuganj (S) | 235 | 1:00 | 224 | 11:00
| Aminbazar | 227 | 1:00 | 215 | 2:00 | Kaliakoir | 228 | 5:00 | 216 | 11:00
| Tongi | 226 | 21:00 | 212 | 15:00 | GPH | 221 | 6:00 | 208 | 15:00
| Comilla (N) | 226 | 19:00 | 217 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 2:00 | 122 | 11:00 | Kochua | 133 | 0.20833 | 126 | 0.58333
| Munsiganj | 135 | 4:00 | 121 | 11:00 | Madanhat | 136 | 0.041667 | 125 | 0.58333
| Sonargaon | 132 | 1:00 | 123 | 11:00 | Hathazari | 132 | 0.20833 | 123 | 0.625
| Shyampur | 133 | 1:00 | 122 | 11:00 | Khulshi | 129 | 0.20833 | 122 | 0.5
| Bhulta | 126 | 2:00 | 114 | 11:00 | Halishahar | 129 | 0.16667 | 118 | 0.625
| Madanganj | 131 | 2:00 | 121 | 11:00 | Baraulia | 129 | 0.20833 | 121 | 0.625
| Shitalakhya | 141 | 1:00 | 125 | 8:00 | Sikalbaha | 133 | 0.25 | 123 | 0.66667
| Rahim steal | 132 | 1:00 | 121 | 11:00 | Dohazari | 129 | 0.20833 | 119 | 0.625
| Matuail | 135 | 2:00 | 122 | 11:00 | Cox'sbazar | 115 | 0.77083 | 103 | 0.625
| Ghorasal | 138 | 1:00 | 136 | 13:00 | Chandraghona | 130 | 0.20833 | 124 | 0.58333
| Narsinghdi | 137 | 7:00 | 124 | 1:00 | Kaptai | 130 | 0.041667 | 125 | 0.29167
| Haripur (SBU) | 134 | 1:00 | 122 | 11:00 | A. Khaer Stl. | 128 | 0.20833 | 123 | 0.5
| Sreenagar | 131 | 20:00 | 121 | 11:00 | Bakulia | 132 | 0.29167 | 103 | 0.95833
| Ullon | 135 | 1:00 | 124 | 12:00 | Julda | 134 | 0.16667 | 126 | 0.625
| Hasnabad | 137 | 1:00 | 126 | 10:00 | TK Chemical | 132 | 0.16667 | 125 | 0.58333
| Magbazar | 134 | 4:00 | 124 | 11:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Maniknagar | 136 | 3:00 | 127 | 11:00 | Shahmirpur | 134 | 0.20833 | 127 | 0.5
| Bangabhaban | 136 | 3:00 | 127 | 11:00 | Khagrachhari | 130 | 0.29167 | 124 | 0.45833
| Motijheel | 136 | 3:00 | 127 | 11:00 | Matarbari | 118 | 0.20833 | 108 | 0.625
| Narinda | 136 | 3:00 | 127 | 11:00 | Baroiar Hat | 132 | 0.25 | 122 | 0.625
| Kazla | 136 | 3:00 | 127 | 11:00 | Rangamati | 130 | 6:00 | 125 | 11:00
| Dhanmondi | 134 | 1:00 | 120 | 11:00 | Goalpara S/S | 136 | 12:00 | 126 | 22:00
| Lalbag | 138 | 1:00 | 122 | 11:00 | Khulna Central S/S | 138 | 18:30 | 126 | 0.91667
| Madartek | 135 | 2:00 | 125 | 11:00 | Noapara | 132 | 12:00 | 122 | 0.91667
| Dhaka University | 135 | 1:00 | 125 | 11:00 | Jessore | 128 | 12:00 | 114 | 0.91667
| Aftabnagar | 136 | 1:00 | 125 | 11:00 | Benapol | 128 | 9:00 | 114 | 0.91667
| Fatullah | 133 | 2:00 | 122 | 11:00 | Jhenida | 126 | 0.77083 | 107 | 0.91667
| Nawabganj | 131 | 1:00 | 121 | 11:00 | Bottail | 132 | 18:30 | 120 | 0.875
| Keraniganj | 132 | 1:00 | 121 | 11:00 | G.K Project | 139 | 0.77083 | 133 | 0.95833
| Mirpur | 137 | 2:00 | 127 | 11:00 | Faridpur | 134 | 0.20833 | 125 | 0.95833
| Kalyanpur | 138 | 20:00 | 128 | 11:00 | Madaripur | 139 | 0.29167 | 132 | 0.83333
| Gulshan | 135 | 5:00 | 124 | 11:00 | Shariyatpur S/S | 139 | 0.25 | 130 | 0.83333
| Uttara | 137 | 20:00 | 127 | 11:00 | Gopalganj | 141 | 6:00 | 132 | 0.91667
| Uttara New | 137 | 1:00 | 126 | 11:00 | Bagerhat | 133 | 0.75 | 120 | 0.91667
| Kamrangirchar | 137 | 0:00 | 123 | 11:00 | Mongla | 133 | 18:00 | 120 | 0.95833
| Savar | 138 | 20:00 | 128 | 11:00 | Satkhira | 135 | 18:00 | 121 | 0.91667
| Bhasantec | 131 | 1:00 | 120 | 11:00 | Gallamari | 138 | 18:00 | 126 | 22:00
| Agargaon | 132 | 1:00 | 122 | 11:00 | Magura | 125 | 0.75 | 105 | 22:00
| Satmosjid | 132 | 5:00 | 122 | 11:00 | Narail | 122 | 11:00 | 103 | 0.91667
| Tongi | 138 | 21:00 | 129 | 7.00 | Chuadanga | 118 | 0.375 | 97 | 0.91667
| Kabirpur | 132 | 19:30 | 127 | 10:00 | Borguna | 138 | 1:00 | 130 | 0.875
| Basundhara | 135 | 1:00 | 127 | 11:00 | Barisal(N) | 141 | 5:00 | 135 | 0.58333
| Manikganj | 139 | 4.00 | 132 | 15:00 | Barisal (S) | 139 | 1:00 | 133 | 14:00
| Joydevpur | 140 | 5.00 | 130 | 12:00 | Patuakhali(S) | 138 | 0.041667 | 127 | 0.875
| New Tongi | 137 | 21:00 | 132 | 13:00 | Bhandaria | 135 | 0.77083 | 125 | 0.95833
| Kodda | 138 | 19:00 | 127 | 8:00 | Ishurdi | 136 | 0.70833 | 130 | 0.875
| Dhamrai | 132 | 6:00 | 124 | 12:00 | Ruppur Paromanobik | 136 | 5:00 | 130 | 21:00
| Rajendrapur | 133 | 2:00 | 124 | 9:00 | Natore | 137 | 18:30 | 129 | 7:00
| Valuka | 122 | 6:00 | 108 | 21:00 | Bogra | 135 | 12:00 | 124 | 8:00
| Tangail | 130 | 6:00 | 122 | 1:00 | Noagaon | 131 | 18:30 | 120 | 8:00
| Mymensing | 128 | 6:00 | 114 | 20:00 | Rajshahi | 135 | 18:30 | 128 | 7:00
| Kishorganj | 129 | 6:00 | 118 | 20:00 | Rajshahi New | 138 | 18:30 | 127 | 21:00
| Netrokona | 124 | 6:00 | 110 | 1:00 | C.Nawabganj | 135 | 18:00 | 126 | 21:00
| Jamalpur | 138 | 6:00 | 124 | 20:00 | Amnura | 135 | 18:00 | 127 | 7:00
| Sherpur | 137 | 6:00 | 121 | 20:00 | Pabna | 134 | 17:00 | 129 | 7:00
| Srimongal | 137 | 6:00 | 132 | 22:00 | Shahjadpur | 139 | 4:00 | 134 | 7:00
| Shahjibazar | 136 | 6:00 | 131 | 1:00 | Serajganj | 133 | 14:00 | 128 | 1:00
| Fenchuganj | 137 | 7:00 | 133 | 23:00 | Niyamatpur | 129 | 14:00 | 118 | 1:00
| Khulawara | 136 | 10:00 | 132 | 1:00 | Joypurhat | 134 | 18:30 | 118 | 7:00
| Sylhet | 134 | 9:00 | 130 | 1:00 | Sherpur(Bogura) | 135 | 14:00 | 125 | 8:00
| Chatak | 134 | 9:00 | 127 | 18:30 | Mohastangor | 134 | 14:00 | 123 | 8:00
| Sunamganj | 131 | 6:00 | 124 | 1:00 | Bangura | 136 | 16:00 | 132 | 8:00
| Biani Bazar | 135 | 8:00 | 127 | 19:00 | Rangpur | 129 | 11:00 | 117 | 8:00
| Comilla(s) | 129 | 6:00 | 123 | 1:00 | Lalmonirhat | 130 | 12:00 | 116 | 8:00
| Comilla(n) |  |  |  |  | Saidpur | 129 | 12:00 | 116 | 21:00
| Chandpur | 135 | 10:00 | 128 | 1:00 | Purbasadipur | 128 | 12:00 | 113 | 21:00
| Feni | 132 | 6:00 | 122 | 15:00 | Thakurgaon | 128 | 18:30 | 110 | 1:00
| Chowmuhani | 133 | 7:00 | 119 | 14:00 | Palashbari | 130 | 12:00 | 119 | 9:00
| Ashuganj | 140 | 8:00 | 135 | 2:00 | Barapukuria | 135 | 12:00 | 127 | 8:00
| Daudkandi | 136 | 19:30 | 123 | 11:00 | Panchagar | 128 | 12:00 | 108 | 1:00
| B.Baria | 136 | 8:00 | 127 | 21:00 | Joldhaka | 128 | 13:00 | 112 | 21:00
| Ramganj | 131 | 8:00 | 120 | 14:00 | Kurigram | 128 | 0.58333 | 115 | 0.33333

## L-Curve
Date | 2021-05-30
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 10 | 8801 | 4192 | 12993 |  |  |  | QF-LDC-11
0:30 | 7 | 8724 | 4273 | 12997 | Date: | 2021-05-30
1:00 | 4 | 8647 | 4354 | 13001
1:30 | 12 | 8512 | 4310 | 12822
2:00 | 20 | 8377 | 4266 | 12643
2:30 | 30 | 8273.5 | 4194 | 12467.5 | [5 empty] | Gen. at Eve. Peak | 12994 | 12994 MW (21:00 )
3:00 | 40 | 8170 | 4122 | 12292 | [6 empty] | 21:00
3:30 | 25 | 8093 | 4056 | 12149 | [5 empty] | Gen. at Day Peak | 11332 | 11332 MW (12:00 )
4:00 | 10 | 8016 | 3990 | 12006 | [6 empty] | 12:00
4:30 | 23 | 7935.5 | 3905 | 11840.5 | [5 empty] | Highest Generation | 13016
5:00 | 36 | 7855 | 3820 | 11675 | [6 empty] | 22:00
5:30 | 38 | 7472 | 3538 | 11010
6:00 | 40 | 7089 | 3256 | 10345
6:30 | 35 | 7035 | 3205 | 10240
7:00 | 30 | 6981 | 3154 | 10135
7:30 | 55 | 6987.5 | 3144 | 10131.5
8:00 | 80 | 6994 | 3134 | 10128
8:30 | 75 | 7136 | 3121 | 10257
9:00 | 70 | 7278 | 3108 | 10386
9:30 | 145 | 7476 | 3138.5 | 10614.5
10:00 | 220 | 7674 | 3169 | 10843
10:30 | 280 | 7699.5 | 3329 | 11028.5
11:00 | 340 | 7725 | 3489 | 11214
11:30 | 310 | 7771 | 3502 | 11273
12:00 | 280 | 7817 | 3515 | 11332
12:30 | 215 | 7942 | 3509 | 11451
13:00 | 150 | 8067 | 3503 | 11570
13:30 | 235 | 8035.5 | 3529 | 11564.5
14:00 | 320 | 8004 | 3555 | 11559
14:30 | 370 | 8118.5 | 3571.5 | 11690
15:00 | 420 | 8233 | 3588 | 11821
15:30 | 355 | 8253 | 3467 | 11720
16:00 | 290 | 8273 | 3346 | 11619
16:30 | 315 | 8157 | 3305 | 11462
17:00 | 340 | 8041 | 3264 | 11305
17:30 | 330 | 7759.5 | 3220 | 10979.5
18:00 | 320 | 7478 | 3176 | 10654
18:30 | 300 | 7986.5 | 3462.5 | 11449
19:00 | 280 | 8495 | 3749 | 12244
19:30 | 100 | 8684 | 4148 | 12832
20:00 | 20 | 8618 | 4148 | 12766 |  |  |  | Executive Engineer
20:30 | 20 | 8663 | 4217 | 12880 |  |  |  | Network Operation Division
21:00 | 20 | 8708 | 4286 | 12994
21:30 | 12 | 8747 | 4258 | 13005
22:00 | 4 | 8786 | 4230 | 13016 |  |  |  |  | Page 6 of 7
22:30 | 22 | 8756.5 | 4222.5 | 12979
23:00 | 40 | 8727 | 4215 | 12942
23:30 | 25 | 8764 | 4203.5 | 12967.5
24:00 | 10 | 8801 | 4192 | 12993
12994 MW (21:00 )
11332 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-05-30 |  | Energy | 285350071
[11 empty] | 2021-05-30 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4385 | 830 | 1847 | 4366 | 720 | 20 | 523 | 0 | 180 | 0
0:30 | 4356 | 829.5 | 1797 | 4516.5 | 730 | 20 | 514 | 0 | 173 | 0 | Date: | 2021-05-30
1:00 | 4327 | 829 | 1747 | 4667 | 740 | 20 | 505 | 0 | 166 | 0
1:30 | 4347 | 829 | 1764 | 4459 | 735 | 20 | 507 | 0 | 161 | 0 | [7 empty] | Total Energy | 285.3501 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4367 | 829 | 1781 | 4251 | 730 | 20 | 509 | 0 | 156 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4372.5 | 829 | 1803.5 | 4074 | 730 | 20 | 485.5 | 0 | 153 | 0 | [7 empty] | Energy Requirement | 285.3501
3:00 | 4378 | 829 | 1826 | 3897 | 730 | 20 | 462 | 0 | 150 | 0
3:30 | 4387 | 829 | 1834.5 | 3740 | 730 | 20 | 462.5 | 0 | 146 | 0 | [6 empty] | Shortage
4:00 | 4396 | 829 | 1843 | 3583 | 730 | 20 | 463 | 0 | 142 | 0
4:30 | 4395 | 829 | 1829.5 | 3478.5 | 720 | 20 | 429.5 | 0 | 139 | 0
5:00 | 4394 | 829 | 1816 | 3374 | 710 | 20 | 396 | 0 | 136 | 0
5:30 | 4367 | 829 | 1792.5 | 2839.5 | 700 | 20 | 330.5 | 0 | 129 | 2.5
6:00 | 4340 | 829 | 1769 | 2305 | 690 | 20 | 265 | 0 | 122 | 5
6:30 | 4336 | 829 | 1751.5 | 2207 | 690 | 20 | 262 | 0 | 130 | 14.5 |  |  |  |  | Coal
7:00 | 4332 | 829 | 1734 | 2109 | 690 | 20 | 259 | 0 | 138 | 24
7:30 | 4385.5 | 829 | 1700 | 2101 | 690 | 20 | 230.5 | 0 | 137 | 38.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4439 | 829 | 1666 | 2093 | 690 | 20 | 202 | 0 | 136 | 53
8:30 | 4449 | 829 | 1688 | 2190 | 690 | 20 | 202 | 0 | 135 | 54
9:00 | 4459 | 829 | 1710 | 2287 | 690 | 20 | 202 | 0 | 134 | 55
9:30 | 4426 | 829 | 1707 | 2545.5 | 680 | 20 | 202 | 0 | 139 | 66
10:00 | 4393 | 829 | 1704 | 2804 | 670 | 20 | 202 | 0 | 144 | 77
10:30 | 4431.5 | 830.5 | 1701 | 2935.5 | 670 | 20 | 202 | 0 | 141 | 97
11:00 | 4470 | 832 | 1698 | 3067 | 670 | 20 | 202 | 0 | 138 | 117
11:30 | 4417.5 | 832 | 1669 | 3163.5 | 670 | 20 | 247.5 | 0 | 147 | 106.5
12:00 | 4365 | 832 | 1640 | 3260 | 670 | 20 | 293 | 0 | 156 | 96
12:30 | 4340.5 | 832 | 1674 | 3370 | 670 | 20 | 297.5 | 0 | 155 | 92
13:00 | 4316 | 832 | 1708 | 3480 | 670 | 20 | 302 | 0 | 154 | 88
13:30 | 4316 | 832 | 1708 | 3480 | 670 | 20 | 302 | 0 | 154 | 88
14:00 | 4316 | 832 | 1708 | 3480 | 670 | 20 | 302 | 0 | 154 | 88
14:30 | 4359.5 | 826.5 | 1714 | 3551.5 | 670 | 20 | 318 | 0 | 162 | 74
15:00 | 4403 | 821 | 1720 | 3623 | 670 | 20 | 334 | 0 | 170 | 60
15:30 | 4349.5 | 820.5 | 1704.5 | 3597 | 665 | 20 | 354.5 | 0 | 168 | 41
16:00 | 4296 | 820 | 1689 | 3571 | 660 | 20 | 375 | 0 | 166 | 22
16:30 | 4256 | 820.5 | 1697.5 | 3469 | 640 | 20 | 377.5 | 0 | 163 | 18.5
17:00 | 4216 | 821 | 1706 | 3367 | 620 | 20 | 380 | 0 | 160 | 15
17:30 | 4192 | 821 | 1603 | 3171 | 610 | 20 | 400 | 0 | 154 | 8.5
18:00 | 4168 | 821 | 1500 | 2975 | 600 | 20 | 420 | 0 | 148 | 2
18:30 | 4213.5 | 820.5 | 1600 | 3556.5 | 600 | 20 | 474.5 | 0 | 163 | 1
19:00 | 4259 | 820 | 1700 | 4138 | 600 | 20 | 529 | 0 | 178 | 0
19:30 | 4278 | 820 | 1721 | 4641 | 640 | 20 | 536 | 0 | 176 | 0
20:00 | 4281 | 821 | 1727 | 4534 | 670 | 20 | 537 | 0 | 176 | 0
20:30 | 4308.5 | 820.5 | 1801.5 | 4504.5 | 695 | 20 | 556 | 0 | 174 | 0
21:00 | 4336 | 820 | 1876 | 4475 | 720 | 20 | 575 | 0 | 172 | 0
21:30 | 4412 | 820 | 1881 | 4409.5 | 720 | 20 | 568.5 | 0 | 174 | 0
22:00 | 4488 | 820 | 1886 | 4344 | 720 | 20 | 562 | 0 | 176 | 0
22:30 | 4472 | 825.5 | 1861.5 | 4355 | 720 | 20 | 547 | 0 | 178 | 0
23:00 | 4456 | 831 | 1837 | 4366 | 720 | 20 | 532 | 0 | 180 | 0
23:30 | 4420.5 | 830.5 | 1842 | 4366 | 720 | 20 | 527.5 | 0 | 180 | 0 | Max Temp. in Dhaka |  | 35.4° C
24:00 | 4385 | 830 | 1847 | 4366 | 720 | 20 | 523 | 0 | 180 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-05-30
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 484000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 80 | 100 | 2200000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 410635
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 6 | 9 | 18 | 18 | 18 |  | 14 | 13 | 7 | 3 | 1 | [8 empty] | 117180
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 203 | 202 | 202 | 204 | 204 | 204 | 209 | 203 | 204 | 216 | 204 | 204 | 205 | 217 | 212 | 206 | 204 |  | 216 | 204 | 203 | 204 | 217 | 217 | 204 | 4958502
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 68 | 68 | 68 | 68 | 23 | 17 | [9 empty] | 5 | 17 |  | 85 | 85 | 85 | 85 | 85 | 68 | 68 | 888837
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 102 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 94 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2559272
| Daudkandi 200 MW PP (B.Trac) | 200 | 150 | 100 | 20 | 0 | [6 empty] | 50 | 100 | 100 | 150 | 150 | 100 |  |  | 155 | 200 | 200 | 200 | 200 | 200 | 200 | 2284416
14 | Titas 50 MW Peaking PP | 48 | 48 | 48 | 49 | 0 | [6 empty] | 44 | 47 | 47 | 47 | 47 | 47 | 47 |  | 47 | 47 | 47 | 47 | 48 | 48 | 48 | 819824
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 185 | 185 | 185 | 185 | 120 | 187 | 185 | 185 | 185 | 186 | 150 |  | 97 | 150 | 150 | 185 | 185 | 185 | 185 | 3979000
17 | Siddhirganj 335 MW CCPP | 180 | 220 | 221 | 219 | 221 | 180 | 180 | 217 | 215 | 211 | 211 | 209 | 206 | 210 | 211 | 209 | 210 | 212 |  | 211 | 214 | 213 | 214 | 216 | 212 | 215 | 5131093
18 | Kodda 300 MW PP Unit-2 (Summit) | 228 | 228 | 228 | 228 | 228 | 95 | 95 | 95 | 127 | 228 | 230 | 228 | 228 | 238 | 243 | 235 | 238 | 240 |  | 243 | 243 | 245 | 245 | 245 | 245 | 243 | 5211380
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4378500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1969105
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 454896
33 | Ashuganj 225 MW CCPP | 218 | 217 | 216 | 216 | 218 | 217 | 216 | 216 | 215 | 214 | 197 | 189 | 178 | 209 | 208 | 208 | 210 | 210 |  | 211 | 214 | 213 | 211 | 212 | 195 | 174 | 5034000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 270 | 265 | 270 | 280 | 285 | 265 | 265 | 290 | 290 | 265 | 280 | 295 | 285 | 265 | 270 |  | 295 | 270 | 270 | 275 | 300 | 290 | 275 | 6793000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 280 | 275 | 280 | 290 | 280 | 360 | 310 | 335 | 335 | 310 | 295 | 290 | 280 | 260 | 260 |  | 285 | 260 | 260 | 265 | 295 | 305 | 285 | 7289000
35 | Ashuganj 55 MW PP (Precision) | 15 | 15 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 5 | 5 | 5 | 5 | 5 |  | 5 | 30 | 30 | 43 | 46 | 50 | 50 | 586560
36 | Chandpur 150 MW CCPP | 87 | 89 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 89 |  | 90 | 86 | 86 | 90 | 90 | 90 | 90 | 2126610
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6646850
41 | Haripur 360MW CCPP(HPL) | 148 | 178 | 190 | 200 | 208 | 198 | 150 | 100 | 101 | 97 | 98 | 92 | 86 | 87 | 87 | 102 | 112 | 108 |  | 104 | 112 | 118 | 118 | 128 | 140 | 150 | 3094000
42 | RPCL 210MW CCPP | 152 | 152 | 155 | 155 | 155 | 154 | 152 | 152 | 132 | 129 | 114 | 116 | 110 | 100 | 107 | 131 | 132 | 132 |  | 132 | 132 | 132 | 130 | 130 | 134 | 139 | 3137880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 13 | 28 | 27 | 43 | 54 | 35 | 47 | 43 | 33 | 8 | 8 | 1 | [8 empty] | 343490
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 43 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1002000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 43 | 42 | 990360
46 | Shajibazar 330 MW CCPP | 163 | 163 | 161 | 161 | 160 | 162 | 162 | 163 | 161 | 162 | 162 | 160 | 160 | 160 | 158 | 160 | 159 | 160 |  | 162 | 162 | 162 | 161 | 161 | 161 | 162 | 3547000
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 |  | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 1329120
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 76 | 75 | 75 | 75 | 74 | 74 | 74 | 76 | 75 | 20 |  | 76 | 76 | 78 | 78 | 78 | 78 | 80 | 1794240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 219 | 219 | 219 | 219 | 213 | 212 | 212 | 212 |  | 212 | 212 | 212 | 212 | 212 | 212 | 212 | 5120110
51 | Sylhet 20 MW GTPP | 18 | 17 | 17 | 17 | 17 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 399000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 161280
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 22 |  | 50 | 53 | 53 | 53 | 53 | 53 | 53 | 1202400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 363360
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 270 | 285 | 285 | 295 | 280 | 300 | 310 | 310 | 305 | 300 | 300 | 305 | 290 | 310 | 300 | 310 | 290 |  | 290 | 270 | 270 | 300 | 300 | 310 | 310 | 7296500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 396 | 400 | 390 | 390 | 387 | 390 | 385 | 383 | 382 | 388 | 390 |  | 386 | 399 | 399 | 395 | 391 | 391 | 395 | 9514900
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 0 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 |  | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 768491
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 586080
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 505344
61 | Narshingdi 22 MW PP (Doreen) |  |  | 0 | 19 | 19 | 19 | [6 empty] | 19 | 19 | 19 |  | 19 | 19 |  | 19 | 19 | 19 |  |  |  | 20 | 228996
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 17 | 17 | 17 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 394524
63 | Impoprt (Tripura) | 166 | 156 | 150 | 142 | 136 | 122 | 138 | 136 | 134 | 144 | 138 | 156 | 154 | 158 | 170 | 166 | 160 | 148 |  | 178 | 176 | 176 | 172 | 176 | 180 | 180 | 3715200
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 39 | 40 | 40 | 10 | 4 | 4 | 4 | 7 | 11 | 7 | 2 | 2 | 7 | 7 |  | 5 | 8 | 17 | 26 | 32 | 30 | 30 | 472320
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 22 | 22 | 22 | 21 | 19 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 471888
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 168120
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816800
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 498340
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 |  | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 473940
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 799800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 17 | 17 | 763900
73 | Ghorashal 108MW PP (Regent) | 93 | 93 | 93 | 93 | 93 | 93 | 91 | 91 | 91 | 91 | 91 | 91 | 92 | 95 | 92 | 93 | 88 | 45 |  | 97 | 97 | 97 | 99 | 99 | 99 | 99 | 2150500
| Feni Lanka Power | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 88 | 100 | 84 | 84 | 98 | 98 | 98 | 98 | 98 | 99 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2362080
| Chowmuhani 113 MW | 110 | 110 | 110 | 110 | 110 | 110 | 111 | 114 | 114 | 115 | 115 | 108 | 109 |  |  | 49 | 113 | 116 |  | 117 | 118 | 118 | 120 | 119 | 118 | 119 | 2485560
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 90 | 90 | 90 | 121 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 3353760
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 30 | 8 | 7 | 7 | 24 | 50 | 56 | 56 | 56 | 56 | 56 |  | 62 | 100 | 100 | 100 | 80 | 80 | 80 | 1638720
78 | Gazipur 52 MW PP | 33 | 42 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 13 | 26 | 32 | 38 | 41 | 41 |  | 38 | 38 | 38 | 41 | 41 | 42 | 41 | 846240
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3604800
80 | Jamalpur 95 MW PP(Powerpac) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 367680
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 1109381
| Gazipur 100 MW PP | 82 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 81 | 81 | 84 | 84 | 84 | 84 | 84 | 83 | 66 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1944000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 2 | 5 | 5 | 6 |  | 5 | 4 | 2 | 1 | 0 | [8 empty] | 27959
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1299168
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 85 | 85 | 92 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 55 | 90 | 88 | 91 | 91 | 91 | 91 | 2004762
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 87 | 87 | 86 | 50 | 0 |  |  |  | 13 | 50 | 52 | 79 | 78 | 84 | 73 | 72 | 71 | 36 |  | 59 | 73 | 73 | 80 | 85 | 85 | 85 | 1465997
86 | Meghnaghat CCPP ( Summit) | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 150 | 150 | 240 | 275 | 255 | 255 |  | 265 | 240 | 245 | 260 | 270 | 260 | 260 | 4489600
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 104 | 0 |  |  | 19 | 84 | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 85 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 2166720
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 90 | 90 | 80 | 80 | 80 | 80 | 80 | 20 | 80 | 80 |  | 100 | 100 | 100 | 100 | 100 | 90 | 90 | 2022000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 20 |  | 34 | 51 | 51 | 51 | 51 | 51 | 51 | 1183045
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 102 | 102 | 0 |  |  | 40 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2082672
95 | Patenga 50MW PP (Baraka) | 46 | 46 | 46 | 46 | 19 | 19 | 19 | 19 | 22 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 45 | 45 | 45 | 46 | 48 | 50 | 50 | 992640
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [5 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 15 | 15 | 15 | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1201721
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 35 | 0 |  |  |  | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1002266
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 163 | 163 | 163 | 130 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3607445
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 1 | 0 | 0 | 0 | [8 empty] | 12200
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 874800
104 | Keranigonj 300 MW PP (APR) | 304 | 106 | 52 | 0 | [7 empty] | 21 | 53 | 57 | 144 | 130 | 30 |  |  | 236 | 255 | 171 | 108 | 55 | 55 | 159 | 1724985
105 | Bramhangoan 100 MW PP (Aggreko) | 98 | 60 | 0 | [8 empty] | 38 | 50 | 50 | 100 | 100 |  |  |  | 90 | 97 | 98 | 100 | 100 | 100 | 98 | 1062298
106 | Mymensingh 200 MW PP (United) | 173 | 173 | 173 | 173 | 164 | 120 | 80 | 80 | 96 | 171 | 171 | 171 | 169 | 169 | 170 | 179 | 150 | 150 |  | 182 | 182 | 185 | 196 | 200 | 197 | 200 | 3921600
112 | Aurahati 100MW PP (Aggreko) | 103 | 63 | 0 | [8 empty] | 53 | 98 | 102 | 102 | 101 | 72 |  |  | 99 | 95 | 100 | 102 | 102 | 102 | 101 | 1255546
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 141 | 50 | 51 | 62 | 107 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 146 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3288960
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2415360
116 | Chandpur 200MW (Desh energy) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 92 | 92 | 95 | 90 | 95 | 95 | 90 |  | 95 | 105 | 100 | 100 | 100 | 100 | 100 | 2233920
117 | Ashuganj 150MW PP (Midland) | 147 | 150 | 150 | 150 | 147 | 142 | 143 | 143 | 143 | 142 | 142 | 140 | 138 | 138 | 100 | 100 | 100 | 100 |  | 100 | 100 | 97 | 132 | 135 | 137 | 142 | 3206618
118 | Bibiyana-III 400 MW CCPP | 403 | 403 | 403 | 403 | 403 | 401 | 402 | 403 | 405 | 404 | 405 | 405 | 406 | 406 | 403 | 402 | 405 | 405 |  | 385 | 368 | 366 | 365 | 402 | 403 | 373 | 9558000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2750400
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 63 | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 100 | 70 | 40 |  | 65 | 80 | 80 | 80 | 80 | 70 | 70 | 1631040
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 429055
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 887040
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 12 | 12 | 5 | 33 | 29 | 32 | 27 | 7 | 3 | 1 | 0 | [8 empty] | 177932
120 | Eastern Zone Total | 8647 | 8377 | 8170 | 8016 | 7855 | 7089 | 6981 | 6994 | 7278 | 7674 | 7725 | 7817 | 8067 | 8004 | 8233 | 8273 | 8041 | 7478 |  | 8495 | 8684 | 8618 | 8708 | 8786 | 8727 | 8801 | 194185240
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 83 | 99 | 93 | 83 | 86 | 99 | 83 |  | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 2233920
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 19 | 19 | 19 | 19 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 7 | 3 | 3 | 3 | 21 |  | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 248160
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 103 | 91 | 91 | 91 | 91 | 35 | 35 | 35 | 35 | 35 | 53 | 70 | 70 | 70 | 70 | 70 | 70 | 35 |  | 70 | 90 | 105 | 105 | 105 | 105 | 105 | 1813440
130
131
132 | United Payra Power Ltd. | 89 | 54 | 54 | 35 | 0 | [14 empty] | 3 | 17 | 17 | 17 | 22 | 73 | 100 | 520800
133 | Bhola Nutan Biddut BD LTD (GAS) | [9 empty] | 8 | 12 | 10 | 10 | 16 | 38 | 71 | 71 | 105 |  | 108 | 107 | 107 | 109 | 109 | 3 | 0 | 868145
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 110 | 110 | 110 | 110 | 16 | [9 empty] | 16 | 16 | 16 |  | 103 | 110 | 110 | 96 | 110 | 110 | 98 | 1312032
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 97 | 97 | 95 | 96 | 96 | 97 | 95 | 94 | 93 | 91 | 90 | 89 | 94 | 92 | 92 | 92 | 94 | 94 |  | 83 | 83 | 67 | 66 | 64 | 94 | 95 | 2172999
| Bhola 225 MW CCPP | 85 | 85 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 85 | 84 | 84 | 84 | 84 | 82 | 84 | 85 | 86 |  | 85 | 86 | 85 | 85 | 86 | 84 | 86 | 2057109
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 33 | 34 | 32 | 28 | 26 | 16 | 15 | 16 | 15 | 15 | 18 | 28 | 28 | 29 | 27 | 29 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 653585
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 60 | 20 | 0 | [14 empty] | 24 | 100 | 100 | 100 | 100 | 100 | 100 | 855360
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 829 | 829 | 829 | 829 | 829 | 829 | 829 | 829 | 829 | 829 | 832 | 832 | 832 | 831 | 821 | 820 | 821 | 821 |  | 820 | 820 | 821 | 820 | 820 | 831 | 830 | 19972363
147 | Bheramara 410 MW CCPP | 350 | 350 | 360 | 350 | 350 | 360 | 375 | 385 | 355 | 360 | 385 | 370 | 355 | 370 | 390 | 335 | 335 | 335 |  | 390 | 350 | 350 | 365 | 395 | 395 | 370 | 8978976
148 | Payra 1320 MW | 590 | 580 | 580 | 580 | 560 | 540 | 540 | 540 | 540 | 520 | 520 | 520 | 520 | 520 | 520 | 510 | 470 | 450 |  | 450 | 490 | 520 | 570 | 570 | 570 | 570 | 13744600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3676800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 0 | [5 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 902048
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 1 | 3 | 3 | 0 | 0 | 0 | [9 empty] | 16860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 185 | 184 | 185 | 185 | 188 | 178 | 170 | 177 | 184 | 179 | 189 | 186 | 173 | 164 | 176 | 157 | 130 | 130 |  | 139 | 168 | 175 | 187 | 196 | 201 | 199 | 4458491
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 213 | 215 | 214 | 214 | 214 | 192 | 180 | 180 | 180 | 180 | 198 | 201 | 161 | 177 | 187 | 167 | 130 | 130 |  | 144 | 181 | 183 | 189 | 197 | 203 | 202 | 4769300
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 382 | 397 | 412 | 417 | 373 | 401 | 400 | 413 | 415 | 412 | 412 | 390 | 410 | 405 | 409 | 336 | 334 | 329 |  | 335 | 321 | 326 | 420 | 413 | 416 | 416 | 9378145
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 16 | 22 | 8 | 8 | 5 | 0 | [11 empty] | 10 |  | 6 | 7 | 7 | 48 | 39 | 36 | 26 | 222533
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 17 | 21 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 483840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  | 11 | 11 | 11 | 11 |  | 5 | 5 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 209394
165 | Amnura 50 MW PP(Sinha) | 42 | 42 | 42 | 42 | 42 | 0 | [13 empty] | 42 | 42 | 42 | 24 | 24 | 24 | 24 | 402130
166 | Katakhali 50 MW PP (Northern) | 34 | 34 | 34 | 34 | 0 | [14 empty] | 16 | 34 | 34 | 34 | 34 | 34 | 34 | 317168
167 | Katakhali 50 MW Peaking PP | 31 | 31 | 31 | 31 | 31 | 0 | [6 empty] | 4 | 30 | 37 | 38 | 38 | 38 |  | 38 | 38 | 40 | 38 | 38 | 38 | 38 | 532168
168 | Santahar 50 MW Peaking PP | 35 | 33 | 0 | [16 empty] | 33 | 36 | 35 | 35 | 35 | 35 | 35 | 266660
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1162560
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 48 | 48 | 48 | 48 | 45 | 47 | 47 | 47 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 1743656
171 | Baghabari 200 MW PP (Paramount) | 200 | 150 | 70 | 0 | [15 empty] | 100 | 200 | 150 | 100 |  |  | 0 | 995022
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 70 | 0 |  |  | 20 | 102 | 113 | 113 | 113 | 113 | 70 | 70 | 35 |  | 53 | 102 | 108 | 113 | 113 | 113 | 113 | 2117856
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 0 |  |  |  | 25 | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 35 |  | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 2038656
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | [15 empty] | 12 | 15 | 15 | 15 | 10 | 0 | 0 | 57000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 0 |  |  |  | 40 | 106 | 113 | 113 | 113 | 113 | 34 | 34 | 34 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1944922
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 2 | 3 | 5 | 5 | 5 | 2 | 2 | 2 | 0 | [8 empty] | 38133
178
178