## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-02 | Wednesday
|  |  | Date (day): | 2021-06-02 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13959.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14766 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-01 | 2021-06-02 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 94 | 99 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | S/D for gas problem
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 130 | 156 | 200 | 200 | 160 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 250 | 260 | 280 | 280
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 30 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 10 | 85 | 85 |  | 15 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 22 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 185 | 181 | 200 | 200 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 60 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 180 | 227 | 220 | 220 |  | 115 | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 7 | 64 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 45 | 45 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 28 | 42 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 30 | 195 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 50 | 140 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 83 | 82 | 83 | 83 |  | 22 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 104 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 27 | 126 | 144 | 144 |  | 18 | Engine problem
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 9 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 1850 | 2684 | 3284 | 3504 | 489 | 1244
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 90 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 7 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 20 | 20 | 20 | 20 | 210 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 207 | 203 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 70 | 80
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 68 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 25 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 85 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 880 | 1030 | 1587 | 1604 | 588 | 123
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 125 | 125 | 125 | 125 | 4 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Machine problem.
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 221 | 221 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 240 | 370 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 0 | 0 |  |  | Under maint.
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 20 | 20 |  | 25 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 52 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 102 | 83 | 83 | 83 | 112 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 51 | 51 |  | 8 | Engine problem\
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 135 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 85 | 77 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 105 | 139 | 140 | 140 |  | 60 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 5 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 110 | 152 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 34 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 5 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 100 | 100 | 100 | 100
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 117 | 110 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1534 | 1779 | 1923 | 2103 | 385 | 198
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 132 | 135 | 157 | 157 | 45 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 17 | 20 | 20 |  | 2 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 16 | 16 | 16 |  | 79 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 192 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 107 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 13 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 322 | 491 | 581.6 | 530 | 45 | 81
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 44 | 44 |  | 26 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 163 | 163 | 163 |  | 160 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 49 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 2 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 63 | 56 | 56 |  | 10 | Engine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 81 | 80 | 80 |  | 6 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 219 | 210 | 210
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 290 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 380 | 363 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 7 | 7 | 7 |  | 3 | Engine prolem
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1890 | 1927 | 2002 | 2002 | 0 | 362
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 818 | 804 | 819 | 819
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 9 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 375 | 370 | 400 | 400
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  | 8 | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 31 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 105 | 90 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1246 | 1319 | 1539 | 1824 | 0 | 91
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 26 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 68 | 68 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 13 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 340 | 410 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 218 | 233 | 228 | 233 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 649 | 783 | 1176 | 1291 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 16 | 45 | 45 |  | 26 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 42 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 34 | 34 |  | 16 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 168 | 164 | 190 | 190 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 178 | 177 | 197 | 197 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 402 | 374 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 27 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 24 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 90 | 90
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 21 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 827 | 1336 | 1596 | 1625 | 381 | 82
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 153 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 9351 | 11612 | 13959.6 | 14766 | 2012 | 2477
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8879.1014 | 11026 | 13255.1283 | 14020.8333
| A. |  | 2021-06-01 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 11612 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7967 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11612 | MW
| 3 | Day peak Generation : |  |  | 9351 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11026 | MW
| 4 | Evening peak Generation : |  |  | 11612 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 235.9458 | MKWHr | By Solar | 0.30421 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 140.4657 | MKWHr |  | By Oil: | 59.9555 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.0551 | MKWHr |  | By Hydro: | 0.492 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2012 | MW | Dhaka | 3896 | 3896 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2477 | MW | Chittagong | 1106 | 1106 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4489 | MW | Khulna | 1254 | 1254 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1155.62 | MMCFD |  |  | Rajshahi | 1306 | 1306 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 150544647.162 | ii) Oil : | Taka | 454991284.39 | Comilla | 921 | 921 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 65488375 | Total | Taka | 671024306.552 | Mymensingh | 984 | 984 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.343 | MKWHr. | Sylhet | 447 | 447 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -180 | MW (E to W) at | 21:00 | hrs | Barisal | 300 | 300 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -236 | MW at | 20:00 | hrs | Rangpur | 812 | 812 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 30.1° C |  |  | Total | 11026 | 11026 |  | 0
| B. |  | 2021-06-02 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 34.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14766 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1766 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 264.1487 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8407 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.3389 | MKWHr. | ii) HVDC Flow at Peak Time |  | 804 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 1.3344 | MKWHr. | iii) Maximum HVDC Flow : |  | 818 | MW at | 7:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.51 |  | (b) Today: | 72.47 |  | (c) Rule Curve: |  | 76.26
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-01
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 57 |  | 0 | 280 | 230 | 0 | 0 | 30 | 222 | 0 | 150 | 80 | 64 | 150 | 10 | 0 | 0 | 0 | 35 | 17 | 55 | 20 | 25 | 22 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 18 | 22 | 38 | 0 | 80 | 0 | 260 | 270 | 222 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 158 | 144 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 80 | 0 | 101 | 0 | 100 | 119 | 140 | 366 | 107 | 82 | 105 | 0 | 0 | 54 | 110 | 100 | 111 | 10 | 400 | 90 | 0 | 126 | 17 | 0 | 17 | 0 |  | 790 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 33 | 80 | 0 | 0 | 0 | 50 | 0 | 88 | 34 | 0 | 0 | 52 | 28 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 95 | 60 | 192 | 0 | 396 | 70 | 0 | 113 | 0 | 74 | 0 | 0 | 113 | 500 | 0 | 0 | 0 | 0 |  | 7457 | 3569 | 11026 | 4302 | 790 | 1672 | 3033 | 650 | 20 | 401 | 158 | 0 | 0 | 72.52
2:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 57 |  | 0 | 280 | 235 | 0 | 0 | 15 | 222 | 0 | 150 | 50 | 7 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 20 | 25 | 22 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 200 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 18 | 22 | 16 | 0 | 80 | 0 | 260 | 270 | 220 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 21 | 8 | 33 | 21 | 154 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 36 | 0 | 98 | 0 | 100 | 116 | 143 | 367 | 108 | 82 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 10 | 400 | 25 | 0 | 108 | 17 | 0 | 17 | 0 |  | 790 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 32 | 80 | 0 | 0 | 0 | 50 | 0 | 88 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 183 | 0 | 95 | 30 | 188 | 0 | 408 | 105 | 0 | 113 | 0 | 15 | 0 | 0 | 70 | 500 | 0 | 0 | 0 | 0 |  | 6973 | 3424 | 10397 | 4305 | 790 | 1661 | 2480 | 649 | 20 | 338 | 154 | 0 | 0 | 75.52
3:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 185 |  | 0 | 280 | 240 | 0 | 0 | 0 | 222 | 0 | 120 | 32 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 20 | 25 | 19 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 0 | 22 | 23 | 0 | 80 | 0 | 265 | 270 | 219 | 8 | 85 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 12 | 150 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 162 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 36 | 0 | 80 | 0 | 100 | 104 | 142 | 366 | 108 | 81 | 105 | 0 | 0 | 54 | 110 | 100 | 111 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 |  | 790 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 32 | 48 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 192 | 0 | 408 | 70 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 |  | 6693 | 3224 | 9917 | 4319 | 790 | 1763 | 1976 | 660 | 20 | 239 | 150 | 0 | 0 | 72.52
4:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 293 |  | 0 | 280 | 230 | 0 | 0 | 0 | 224 | 0 | 120 | 32 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 20 | 25 | 19 | 20 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 0 | 22 | 30 | 0 | 80 | 0 | 260 | 270 | 220 | 8 | 84 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 0 | 12 | 144 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 161 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 46 | 0 | 100 | 104 | 142 | 367 | 108 | 81 | 105 | 0 | 0 | 54 | 110 | 100 | 111 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 |  | 790 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 32 | 48 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 95 | 0 | 169 | 0 | 330 | 70 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 |  | 6686 | 3107 | 9793 | 4241 | 790 | 1795 | 1904 | 660 | 20 | 239 | 144 | 0 | 0 | 72.51
5:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 207 |  | 0 | 280 | 235 | 0 | 0 | 0 | 223 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 21 | 20 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 22 | 30 | 0 | 80 | 0 | 260 | 220 | 220 | 8 | 84 | 20 | 5 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 12 | 136 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 161 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 60 | 108 | 100 | 366 | 75 | 64 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 |  | 791 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 16 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 96 | 0 | 155 | 0 | 340 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 510 | 0 | 0 | 0 | 0 |  | 6162 | 2890 | 9052 | 4208 | 791 | 1710 | 1477 | 660 | 20 | 50 | 136 | 0 | 0 | 72.51
6:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 207 |  | 0 | 280 | 240 | 0 | 0 | 0 | 221 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 21 | 20 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 207 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 39 | 0 | 80 | 0 | 275 | 100 | 219 | 0 | 85 | 20 | 15 | 0 | 0 | 0 | 0 | 35 | 19 | 8 | 33 | 12 | 122 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 162 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 100 | 10 | 375 | 8 | 0 | 105 | 0 | 0 | 54 | 85 | 100 | 111 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 |  | 790 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 73 | 0 | 157 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 0 | 0 | 0 | 0 |  | 5695 | 2733 | 8428 | 4084 | 790 | 1687 | 1113 | 610 | 20 | 0 | 122 | 2 | 0 | 72.51
7:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 191 |  | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 75 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 21 | 20 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 19 | 39 | 0 | 80 | 0 | 260 | 100 | 219 | 8 | 84 | 20 | 15 | 0 | 9 | 0 | 0 | 43 | 19 | 8 | 33 | 12 | 120 | 159 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 163 | 45 | 50 | 0 | 164 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 30 | 80 | 10 | 330 | 8 | 4 | 105 | 0 | 0 | 54 | 85 | 100 | 110 | 0 | 370 | 0 | 0 | 0 | 17 | 0 | 17 | 1 |  | 818 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 73 | 0 | 153 | 0 | 386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 16 | 0 | 0 | 0 |  | 5449 | 2760 | 8209 | 3904 | 818 | 1670 | 1104 | 570 | 20 | 0 | 120 | 3 | 0 | 72.5
8:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 131 |  | 0 | 280 | 235 | 0 | 0 | 0 | 150 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 20 | 25 | 11 | 20 | 8 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 0 | 1 | 19 | 8 | 0 | 80 | 0 | 260 | 10 | 220 | 8 | 82 | 20 | 15 | 0 | 30 | 0 | 0 | 43 | 19 | 8 | 33 | 0 | 120 | 157 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 130 | 162 | 45 | 50 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 30 | 80 | 10 | 333 | 24 | 49 | 105 | 1 | 0 | 37 | 85 | 100 | 111 | 0 | 330 | 0 | 2 | 0 | 17 | 0 | 17 | 0 |  | 817 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 55 | 0 | 161 | 0 | 362 | 53 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 430 | 41 | 0 | 0 | 0 |  | 5292 | 2796 | 8088 | 3699 | 817 | 1591 | 1258 | 580 | 20 | 0 | 120 | 3 | 0 | 72.5
9:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 145 |  | 0 | 280 | 140 | 0 | 0 | 0 | 150 | 0 | 120 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 20 | 0 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 215 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 0 | 7 | 19 | 3 | 0 | 90 | 0 | 320 | 0 | 199 | 8 | 85 | 20 | 30 | 0 | 43 | 0 | 0 | 43 | 19 | 8 | 33 | 0 | 128 | 135 | 16 | 20 | 1 | 42 | 42 | 50 | 0 | 130 | 162 | 45 | 50 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 7 | 30 | 90 | 6 | 384 | 24 | 49 | 105 | 1 | 0 | 35 | 85 | 100 | 110 | 0 | 330 | 0 | 4 | 0 | 17 | 0 | 9 | 1 |  | 818 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 32 | 0 | 155 | 0 | 338 | 51 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 400 | 41 | 0 | 0 | 0 |  | 5295 | 2672 | 7967 | 3758 | 818 | 1583 | 1093 | 550 | 20 | 0 | 128 | 17 | 0 | 72.5
10:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 151 |  | 0 | 280 | 130 | 0 | 0 | 0 | 180 | 0 | 150 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 17 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 229 | 0 | 0 | 0 |  | 1 | 0 | 0 | 80 | 0 | 11 | 19 | 2 | 0 | 135 | 0 | 340 | 0 | 201 | 70 | 84 | 20 | 30 | 0 | 43 | 0 | 0 | 43 | 21 | 8 | 33 | 0 | 94 | 136 | 16 | 20 | 1 | 42 | 42 | 47 | 0 | 163 | 163 | 57 | 78 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 7 | 55 | 99 | 15 | 399 | 32 | 55 | 105 | 2 | 0 | 35 | 91 | 100 | 111 | 10 | 384 | 0 | 16 | 0 | 17 | 0 | 14 | 6 |  | 818 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 32 | 0 | 189 | 0 | 337 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 100 | 0 | 0 | 0 |  | 5731 | 2766 | 8497 | 4069 | 818 | 1789 | 1155 | 520 | 20 | 0 | 94 | 32 | 0 | 72.5
11:00 | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 0 | 145 |  | 0 | 280 | 220 | 0 | 0 | 0 | 180 | 0 | 185 | 55 | 0 | 20 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 0 | 25 | 15 | 25 | 17 | 11 | 0 | 0 | 20 | 100 | 0 | 17 | 215 | 0 | 0 | 0 |  | 16 | 0 | 0 | 80 | 0 | 11 | 19 | 2 | 0 | 125 | 0 | 330 | 0 | 196 | 83 | 85 | 20 | 48 | 0 | 43 | 0 | 0 | 43 | 21 | 8 | 33 | 0 | 84 | 130 | 16 | 20 | 1 | 42 | 42 | 50 | 0 | 163 | 162 | 62 | 77 | 0 | 164 | 18 | 0 | 7 | 320 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 100 | 105 | 73 | 392 | 64 | 83 | 105 | 2 | 0 | 35 | 106 | 100 | 110 | 30 | 400 | 0 | 5 | 0 | 17 | 0 | 17 | 4 |  | 817 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 15 | 0 | 192 | 0 | 378 | 53 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 340 | 210 | 0 | 0 | 2 |  | 6216 | 2843 | 9059 | 4053 | 817 | 1961 | 1595 | 490 | 20 | 20 | 84 | 19 | 0 | 72.5
12:00 | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 0 | 130 |  | 0 | 280 | 250 | 0 | 0 | 0 | 180 | 0 | 185 | 60 | 7 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 25 | 20 | 25 | 17 | 28 | 0 | 0 | 20 | 100 | 0 | 17 | 207 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 11 | 19 | 2 | 0 | 125 | 0 | 240 | 0 | 221 | 102 | 85 | 20 | 52 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 25 | 5 | 106 | 132 | 16 | 20 | 2 | 42 | 42 | 50 | 0 | 163 | 157 | 62 | 77 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 50 | 7 | 100 | 105 | 128 | 380 | 115 | 83 | 105 | 0 | 0 | 35 | 110 | 100 | 117 | 50 | 400 | 0 | 13 | 27 | 17 | 0 | 17 | 9 |  | 818 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 178 | 0 | 402 | 53 | 0 | 21 | 0 | 0 | 0 | 3 | 0 | 340 | 218 | 0 | 0 | 2 |  | 6476 | 2875 | 9351 | 3934 | 818 | 1974 | 1858 | 490 | 20 | 115 | 106 | 36 | 0 | 72.5
13:00 | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 0 | 125 |  | 0 | 280 | 250 | 0 | 0 | 15 | 221 | 0 | 183 | 70 | 16 | 133 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 18 | 25 | 20 | 25 | 0 | 32 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 11 | 0 | 2 | 0 | 125 | 0 | 243 | 0 | 184 | 102 | 84 | 20 | 52 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 33 | 0 | 110 | 120 | 16 | 20 | 2 | 42 | 42 | 47 | 0 | 163 | 161 | 62 | 80 | 0 | 164 | 18 | 0 | 7 | 300 | 16 | 2 | 0 | 110 | 0 | 0 | 0 | 0 | 50 | 4 | 100 | 100 | 142 | 365 | 115 | 83 | 105 | 0 | 0 | 35 | 110 | 100 | 122 | 60 | 355 | 1 | 31 | 79 | 17 | 0 | 17 | 13 |  | 817 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 0 | 0 | 200 | 0 | 401 | 70 | 0 | 45 | 0 | 34 | 0 | 3 | 0 | 340 | 218 | 0 | 0 | 3 |  | 6616 | 2985 | 9601 | 3857 | 817 | 1945 | 2173 | 490 | 20 | 133 | 110 | 56 | 0 | 72.49
14:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 120 |  | 0 | 280 | 260 | 0 | 0 | 40 | 221 | 0 | 152 | 80 | 48 | 150 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 18 | 25 | 20 | 25 | 33 | 30 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 11 | 15 | 12 | 0 | 125 | 0 | 220 | 0 | 183 | 102 | 84 | 20 | 52 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 25 | 18 | 110 | 119 | 16 | 20 | 1 | 42 | 42 | 50 | 0 | 130 | 161 | 61 | 83 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 3 | 0 | 110 | 0 | 0 | 0 | 0 | 50 | 1 | 100 | 120 | 142 | 368 | 115 | 82 | 105 | 0 | 0 | 35 | 110 | 100 | 121 | 60 | 350 | 28 | 14 | 94 | 17 | 0 | 17 | 13 |  | 818 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 184 | 0 | 0 | 0 | 188 | 0 | 380 | 90 | 0 | 70 | 0 | 34 | 0 | 0 | 10 | 340 | 129 | 0 | 0 | 3 |  | 6751 | 2912 | 9663 | 3842 | 818 | 1802 | 2398 | 491 | 20 | 150 | 110 | 32 | 0 | 0
15:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 120 |  | 0 | 280 | 260 | 0 | 0 | 40 | 218 | 0 | 156 | 90 | 64 | 150 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 18 | 25 | 20 | 0 | 33 | 32 | 0 | 0 | 20 | 100 | 0 | 17 | 213 | 0 | 0 | 0 |  | 24 | 0 | 0 | 92 | 0 | 11 | 18 | 7 | 0 | 125 | 0 | 20 | 0 | 201 | 0 | 85 | 20 | 52 | 0 | 0 | 0 | 0 | 43 | 19 | 0 | 25 | 18 | 100 | 120 | 16 | 20 | 1 | 42 | 42 | 53 | 0 | 163 | 162 | 61 | 83 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 160 | 0 | 0 | 0 | 0 | 50 | 3 | 100 | 120 | 110 | 397 | 107 | 82 | 105 | 0 | 0 | 35 | 108 | 81 | 114 | 60 | 350 | 44 | 18 | 108 | 17 | 0 | 17 | 11 |  | 817 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 0 | 0 | 197 | 0 | 398 | 90 | 0 | 78 | 0 | 35 | 0 | 5 | 35 | 320 | 230 | 0 | 0 | 2 |  | 6583 | 3092 | 9675 | 3751 | 817 | 1823 | 2504 | 470 | 20 | 150 | 100 | 40 | 0 | 0
16:00 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 121 |  | 0 | 280 | 255 | 0 | 0 | 44 | 221 | 0 | 93 | 91 | 80 | 150 | 0 | 0 | 0 | 0 | 35 | 35 | 55 | 18 | 25 | 20 | 25 | 0 | 38 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 92 | 0 | 27 | 19 | 7 | 0 | 125 | 0 | 20 | 0 | 183 | 83 | 85 | 20 | 52 | 0 | 30 | 0 | 0 | 43 | 19 | 0 | 25 | 18 | 112 | 139 | 16 | 20 | 1 | 42 | 42 | 53 | 0 | 163 | 161 | 62 | 83 | 0 | 164 | 18 | 0 | 7 | 280 | 16 | 5 | 0 | 235 | 0 | 0 | 8 | 0 | 110 | 2 | 100 | 120 | 85 | 367 | 107 | 82 | 105 | 0 | 0 | 35 | 108 | 81 | 120 | 60 | 350 | 100 | 20 | 108 | 17 | 0 | 17 | 0 |  | 817 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 68 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 0 | 0 | 182 | 0 | 302 | 53 | 0 | 35 | 0 | 70 | 0 | 3 | 70 | 280 | 234 | 0 | 0 | 1 |  | 6799 | 2856 | 9655 | 3568 | 817 | 1823 | 2702 | 430 | 20 | 156 | 112 | 27 | 0 | 72.49
17:00 | 0 | 0 | 0 | 185 | 0 | 76 | 0 | 0 | 120 |  | 0 | 280 | 260 | 0 | 0 | 50 | 190 | 0 | 97 | 91 | 58 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 0 | 25 | 12 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 23 | 0 | 0 | 92 | 0 | 50 | 19 | 8 | 0 | 125 | 0 | 30 | 0 | 183 | 83 | 80 | 22 | 52 | 0 | 10 | 0 | 0 | 43 | 22 | 0 | 25 | 18 | 102 | 139 | 16 | 20 | 1 | 42 | 42 | 53 | 0 | 110 | 161 | 62 | 20 | 0 | 164 | 18 | 0 | 7 | 285 | 16 | 5 | 0 | 245 | 0 | 0 | 8 | 0 | 120 | 2 | 100 | 124 | 50 | 367 | 107 | 82 | 105 | 0 | 0 | 39 | 93 | 81 | 117 | 60 | 350 | 104 | 11 | 90 | 17 | 0 | 17 | 1 |  | 818 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 68 | 10 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 0 | 175 | 0 | 333 | 35 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 280 | 233 | 0 | 0 | 0 |  | 6527 | 2792 | 9319 | 3544 | 818 | 1701 | 2572 | 430 | 20 | 114 | 102 | 18 | 0 | 72.49
18:00 | 0 | 0 | 0 | 185 | 0 | 53 | 0 | 0 | 126 |  | 0 | 280 | 260 | 0 | 0 | 47 | 190 | 0 | 97 | 91 | 58 | 98 | 2 | 0 | 0 | 0 | 35 | 17 | 55 | 22 | 25 | 12 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 70 | 0 |  | 15 | 0 | 0 | 100 | 0 | 50 | 19 | 2 | 0 | 125 | 0 | 90 | 0 | 185 | 83 | 79 | 22 | 52 | 0 | 10 | 0 | 0 | 43 | 22 | 5 | 25 | 18 | 104 | 139 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 110 | 162 | 45 | 20 | 0 | 164 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 243 | 0 | 0 | 8 | 0 | 120 | 0 | 80 | 130 | 50 | 367 | 107 | 82 | 105 | 0 | 0 | 38 | 108 | 70 | 85 | 10 | 330 | 104 | 4 | 90 | 17 | 0 | 17 | 0 |  | 817 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 177 | 0 | 335 | 35 | 0 | 35 | 0 | 36 | 0 | 0 | 35 | 280 | 236 | 0 | 0 | 0 |  | 6516 | 2752 | 9268 | 3597 | 817 | 1705 | 2478 | 430 | 20 | 113 | 104 | 4 | 0 | 72.49
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 135 |  | 0 | 280 | 260 | 0 | 0 | 55 | 220 | 0 | 185 | 91 | 72 | 150 | 43 | 0 | 0 | 0 | 35 | 35 | 55 | 0 | 25 | 13 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 218 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 19 | 7 | 0 | 125 | 0 | 155 | 0 | 218 | 83 | 81 | 23 | 52 | 0 | 23 | 0 | 50 | 25 | 22 | 5 | 25 | 20 | 116 | 133 | 16 | 17 | 0 | 42 | 42 | 24 | 0 | 110 | 163 | 62 | 81 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 245 | 0 | 0 | 43 | 0 | 128 | 0 | 100 | 126 | 78 | 403 | 108 | 82 | 105 | 0 | 0 | 54 | 85 | 81 | 100 | 50 | 330 | 104 | 0 | 107 | 17 | 0 | 17 | 0 |  | 818 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 24 | 16 | 0 | 0 | 0 | 50 | 34 | 97 | 12 | 16 | 33 | 48 | 15 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 14 | 0 | 190 | 0 | 380 | 55 | 0 | 40 | 0 | 97 | 0 | 0 | 50 | 300 | 233 | 0 | 13 | 0 |  | 7273 | 3335 | 10608 | 3906 | 818 | 1882 | 2897 | 450 | 20 | 519 | 116 | 0 | 0 | 72.48
19:30 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 150 |  | 0 | 280 | 260 | 0 | 0 | 55 | 220 | 0 | 179 | 100 | 102 | 150 | 86 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 18 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 19 | 7 | 0 | 125 | 0 | 245 | 0 | 220 | 83 | 77 | 23 | 52 | 0 | 40 | 0 | 50 | 16 | 22 | 5 | 25 | 20 | 118 | 135 | 16 | 17 | 0 | 42 | 42 | 44 | 0 | 163 | 164 | 62 | 81 | 0 | 164 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 245 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 125 | 135 | 366 | 106 | 82 | 105 | 0 | 0 | 54 | 85 | 81 | 111 | 50 | 340 | 104 | 0 | 126 | 17 | 0 | 17 | 0 |  | 817 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 68 | 26 | 16 | 0 | 0 | 0 | 50 | 34 | 97 | 24 | 43 | 38 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 13 | 60 | 190 | 0 | 391 | 105 | 0 | 106 | 0 | 114 | 0 | 0 | 110 | 410 | 234 | 0 | 17 | 0 |  | 7765 | 3780 | 11545 | 3978 | 817 | 1971 | 3538 | 560 | 20 | 543 | 118 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 157 |  | 0 | 280 | 235 | 0 | 0 | 55 | 220 | 0 | 125 | 98 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 18 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 19 | 10 | 0 | 125 | 0 | 320 | 0 | 183 | 83 | 77 | 23 | 52 | 0 | 43 | 0 | 50 | 16 | 22 | 5 | 25 | 20 | 118 | 134 | 16 | 17 | 0 | 42 | 42 | 47 | 0 | 163 | 162 | 63 | 81 | 0 | 195 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 245 | 0 | 0 | 186 | 0 | 149 | 0 | 100 | 124 | 123 | 348 | 108 | 82 | 105 | 0 | 0 | 54 | 85 | 81 | 113 | 50 | 375 | 104 | 0 | 124 | 17 | 0 | 23 | 0 |  | 805 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 68 | 25 | 16 | 0 | 0 | 0 | 50 | 22 | 96 | 42 | 43 | 41 | 52 | 27 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 13 | 20 | 187 | 0 | 319 | 105 | 0 | 110 | 0 | 113 | 0 | 0 | 113 | 410 | 234 | 0 | 17 | 0 |  | 7784 | 3671 | 11455 | 4015 | 805 | 1914 | 3489 | 560 | 20 | 534 | 118 | 0 | 0 | 72.48
21:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 156 |  | 0 | 280 | 260 | 0 | 0 | 30 | 227 | 0 | 181 | 100 | 64 | 150 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 20 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 19 | 25 | 0 | 125 | 0 | 370 | 0 | 221 | 83 | 77 | 23 | 52 | 0 | 43 | 0 | 50 | 34 | 22 | 5 | 25 | 20 | 110 | 135 | 16 | 17 | 0 | 42 | 42 | 49 | 0 | 163 | 163 | 63 | 81 | 0 | 219 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 140 | 0 | 100 | 139 | 135 | 363 | 107 | 82 | 105 | 0 | 0 | 54 | 85 | 100 | 110 | 50 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 804 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 68 | 26 | 16 | 0 | 0 | 0 | 50 | 16 | 95 | 42 | 43 | 38 | 52 | 27 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 13 | 31 | 177 | 0 | 374 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 233 | 0 | 17 | 0 |  | 7911 | 3701 | 11612 | 4210 | 804 | 1995 | 3393 | 560 | 20 | 520 | 110 | 0 | 0 | 72.48
22:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 167 |  | 0 | 280 | 235 | 0 | 0 | 30 | 221 | 0 | 140 | 100 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 22 | 25 | 20 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 50 | 19 | 31 | 0 | 125 | 0 | 370 | 0 | 222 | 83 | 77 | 23 | 52 | 0 | 43 | 0 | 0 | 43 | 22 | 5 | 25 | 20 | 114 | 135 | 16 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 160 | 63 | 81 | 0 | 218 | 18 | 0 | 7 | 266 | 16 | 11 | 0 | 145 | 0 | 0 | 183 | 0 | 115 | 0 | 100 | 139 | 137 | 364 | 107 | 82 | 105 | 0 | 0 | 54 | 85 | 100 | 112 | 30 | 400 | 80 | 0 | 90 | 17 | 0 | 35 | 0 |  | 804 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 29 | 32 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 38 | 52 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 53 | 0 | 188 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 420 | 200 | 0 | 35 | 0 |  | 7438 | 3650 | 11088 | 4177 | 804 | 2015 | 3022 | 570 | 20 | 366 | 114 | 0 | 0 | 72.48
23:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 171 |  | 0 | 280 | 230 | 0 | 0 | 15 | 221 | 0 | 120 | 100 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 21 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 216 | 0 | 25 | 0 |  | 24 | 0 | 85 | 92 | 0 | 50 | 22 | 30 | 0 | 125 | 0 | 365 | 0 | 218 | 83 | 74 | 23 | 52 | 0 | 51 | 0 | 0 | 37 | 22 | 5 | 25 | 20 | 110 | 134 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 95 | 0 | 0 | 182 | 0 | 102 | 0 | 20 | 139 | 135 | 400 | 107 | 82 | 105 | 0 | 0 | 54 | 85 | 100 | 114 | 30 | 400 | 0 | 0 | 90 | 17 | 0 | 35 | 0 |  | 805 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 38 | 52 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 12 | 0 | 175 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 390 | 226 | 0 | 0 | 0 |  | 7251 | 3519 | 10770 | 4192 | 805 | 2049 | 2688 | 540 | 20 | 366 | 110 | 0 | 0 | 72.47
24:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 190 |  | 0 | 280 | 235 | 0 | 0 | 15 | 220 | 0 | 100 | 16 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 21 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 70 | 0 |  | 24 | 0 | 68 | 92 | 0 | 30 | 19 | 36 | 0 | 125 | 0 | 365 | 0 | 220 | 83 | 72 | 23 | 53 | 0 | 51 | 0 | 0 | 40 | 22 | 5 | 25 | 21 | 112 | 139 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 182 | 0 | 93 | 0 | 20 | 139 | 140 | 409 | 106 | 82 | 105 | 0 | 0 | 54 | 85 | 100 | 111 | 10 | 400 | 0 | 0 | 90 | 0 | 0 | 35 | 0 |  | 804 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 69 | 29 | 0 | 0 | 0 | 0 | 50 | 0 | 98 | 0 | 0 | 0 | 52 | 26 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 12 | 0 | 192 | 0 | 400 | 53 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 350 | 226 | 0 | 0 | 0 |  | 7064 | 3402 | 10466 | 4230 | 804 | 2074 | 2415 | 500 | 20 | 311 | 112 | 0 | 0 | 72.47
KWH | 0 | 0 | 0 | 4504500 | 0 | 2205909 | 0 | 0 | 3418000 |  | 0 | 6647750 | 5544087 | 0 | 0 | 557051 | 5098057 | 0 | 3514000 | 1491840 | 813168 | 1897440 | 201047 | 0 | 0 | 0 | 718956 | 361507 | 787274 | 360288 | 600000 | 399240 | 628500 | 728900 | 699926 | 0 | 0 | 492000 | 2300000 | 0 | 413818 | 5103443 | 0 | 102507 | 0 |  | 450240 | 0 | 816488 | 2175600 | 0 | 589440 | 430032 | 397440 | 0 | 2602385 | 0 | 6089500 | 1679000 | 5052000 | 1271272 | 1958400 | 459504 | 878880 | 0 | 983124 | 0 | 166944 | 957400 | 416304 | 119160 | 665900 | 314480 | 1334400 | 3215200 | 379200 | 401256 | 8750 | 1011000 | 1008000 | 1168200 | 0 | 3550990 | 3627000 | 1424160 | 1768320 | 0 | 4184860 | 407000 | 0 | 163620 | 7219000 | 357648 | 183100 | 0 | 2571817 | 0 | 0 | 1257600 | 0 | 1822460 | 47385 | 1933440 | 2746560 | 2363563 | 8951000 | 2100000 | 1745016 | 2581018 | 6602 | 0 | 1094967 | 2498207 | 2278860 | 2700600 | 688320 | 9030000 | 967680 | 131030 | 1563840 | 421527 | 0 | 510480 | 62719 |  | 19338909 | 0 | 9020736 | 0 | 0 | 0 | 0 | 0 | 43200 | 9088 | 0 | 1816856 | 517640 | 422784 | 0 | 0 | 0 | 495024 | 102174 | 1030704 | 168430 | 90405 | 197750 | 1005600 | 180195 | 492480 | 0 | 197136 | 0 | 0 | 3676200 | 0 | 0 | 0 | 0 | 4311173 | 0 | 942833 | 221760 | 4562855 | 0 | 8959127 | 1577568 | 0 | 1373568 | 0 | 1023120 | 0 | 34161 | 1057920 | 10378900 | 3046036 | 0 | 88800 | 13560 |  | 159549096 | 76396692 | 235945788 | 96835080 | 19338909 | 43630621 | 55016464 | 14055100 | 492000 | 4939007 | 1334400 | 304207 | 0
Fuel Cost | 0 | 0 | 0 | 6621615 | 0 | 2911799.88 | 0 | 0 | 3520540 |  | 0 | 7246047.5 | 6153936.57 | 0 | 0 | 4712651.46 | 5301979.28 | 0 | 6079220 | 11233555.2 | 7416092.16 | 18670809.6 | 1853653.34 | 0 | 0 | 0 | 5248378.8 | 2794449.11 | 7762521.64 | 270216 | 450000 | 0 | 0 | 0 | 6768284.42 | 0 | 0 | 132840 | 4163000 | 0 | 3844369.22 | 5562752.87 | 0 | 174261.9 | 0 |  | 0 | 0 | 7919933.6 | 20776980 | 0 | 4668364.8 | 541840.32 | 1180396.8 | 0 | 3851529.8 | 0 | 4506230 | 1679000 | 4647840 | 1639940.88 | 2252160 | 519239.52 | 1230432 | 0 | 1681142.04 | 0 | 1686134.4 | 9143170 | 528706.08 | 89370 | 1165325 | 235860 | 10008000 | 3408112 | 3443136 | 509595.12 | 139475 | 1658040 | 1612800 | 2079396 | 0 | 4048128.6 | 3772080 | 2805595.2 | 3377491.2 | 0 | 7239807.8 | 891330 | 0 | 333784.8 | 7291190 | 268236 | 139156 | 0 | 19442936.52 | 0 | 0 | 6539520 | 0 | 17933006.4 | 553930.65 | 15757536 | 29800176 | 16663119.15 | 8324430 | 19152000 | 16490401.2 | 22480666.78 | 0 | 0 | 9537162.57 | 21959239.53 | 22743022.8 | 23144142 | 4584211.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 111392115.84 | 0 | 9471772.8 | 0 | 0 | 0 | 0 | 0 | 453168 | 95242.24 | 0 | 2053047.28 | 802342 | 4126371.84 | 0 | 0 | 0 | 4871036.16 | 1038087.84 | 9121730.4 | 1296911 | 1222275.6 | 1916197.5 | 9744264 | 1747891.5 | 945561.6 | 0 | 149231.952 | 0 | 0 | 19925004 | 0 | 0 | 0 | 0 | 5690748.36 | 0 | 1414249.5 | 3772137.6 | 5338540.35 | 0 | 8869535.73 | 16469809.92 | 0 | 13035160.32 | 0 | 7939411.2 | 0 | 377479.05 | 7818028.8 | 45563371 | 0 | 0 | 0 | 0 |  | 496967423.71 | 296660723.382 | 793628147.092 | 101972668.632 | 111392115.84 | 48571978.53 | 407471053.15 | 65488375 | 132840 | 47520231.24 | 10008000 | 1070884.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 0 | 130 |  | 0 | 280 | 250 | 0 | 0 | 0 | 180 | 0 | 185 | 60 | 7 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 15 | 25 | 20 | 25 | 17 | 28 | 0 | 0 | 20 | 100 | 0 | 17 | 207 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 11 | 19 | 2 | 0 | 125 | 0 | 240 | 0 | 221 | 102 | 85 | 20 | 52 | 0 | 43 | 0 | 0 | 43 | 0 | 0 | 25 | 5 | 106 | 132 | 16 | 20 | 2 | 42 | 42 | 50 | 0 | 163 | 157 | 62 | 77 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 50 | 7 | 100 | 105 | 128 | 380 | 115 | 83 | 105 | 0 | 0 | 35 | 110 | 100 | 117 | 50 | 400 | 0 | 13 | 27 | 17 | 0 | 17 | 9 |  | 818 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 178 | 0 | 402 | 53 | 0 | 21 | 0 | 0 | 0 | 3 | 0 | 340 | 218 | 0 | 0 | 2 |  | 9351 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 156 | 0 | 0 | 280 | 260 | 0 | 0 | 30 | 227 | 0 | 181 | 100 | 64 | 150 | 10 | 0 | 0 | 0 | 35 | 35 | 55 | 22 | 25 | 20 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 100 | 0 | 50 | 19 | 25 | 0 | 125 | 0 | 370 | 0 | 221 | 83 | 77 | 23 | 52 | 0 | 43 | 0 | 50 | 34 | 22 | 5 | 25 | 20 | 110 | 135 | 16 | 17 | 0 | 42 | 42 | 49 | 0 | 163 | 163 | 63 | 81 | 0 | 219 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 192 | 0 | 140 | 0 | 100 | 139 | 135 | 363 | 107 | 82 | 105 | 0 | 0 | 54 | 85 | 100 | 110 | 50 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 804 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 68 | 26 | 16 | 0 | 0 | 0 | 50 | 16 | 95 | 42 | 43 | 38 | 52 | 27 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 13 | 31 | 177 | 0 | 374 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 410 | 233 | 0 | 17 | 0 |  | 11612 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 200 | 0 | 0 | 280 | 280 | 0 | 0 | 55 | 220 | 0 | 200 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 80 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 22 | 25 | 0 | 125 | 0 | 360 | 0 | 220 | 83 | 90 | 20 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 181 | 157 | 16 | 20 | 0 | 44 | 42 | 51 | 0 | 163 | 163 | 56 | 80 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 140 | 150 | 400 | 115 | 83 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 35 |  |  | 819 | 0 | 400 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 90 | 35 | 34 | 40 | 52 | 35 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 190 | 0 | 95 | 100 | 197 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 233 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 200 | 0 | 0 | 280 | 280 | 0 | 0 | 55 | 220 | 0 | 200 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 70 | 0 | 0 | 22 |  | 68 | 100 | 0 | 50 | 22 | 10 | 0 | 125 | 0 | 360 | 0 | 220 | 83 | 90 | 20 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 152 | 157 | 16 | 20 | 1.6 | 44 | 42 | 51 | 0 | 163 | 163 | 56 | 80 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 140 | 150 | 400 | 115 | 83 | 105 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 35 | 30 |  | 819 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 90 | 35 | 34 | 40 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 95 | 50 | 197 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 228 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 197 | 0 | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 155 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 25 |  | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 70 | 0 | 0 | 1 | 0 | 0 | 80 | 0 | 0 | 19 | 8 | 0 | 125 | 0 | 310 | 0 | 214 | 83 | 80 | 23 | 53 | 0 | 51 | 0 | 0 | 34 | 21 | 5 | 25 | 12 | 102 | 156 | 16 | 20 | 0 | 44 | 42 | 50 | 0 | 163 | 163 | 62 | 10 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10 | 25 | 2 | 329 | 84 | 83 | 72 | 1 | 0 | 54 | 17 | 100 | 105 | 0 | 400 | 0 | 12 | 0 | 0 | 0 | 35 | 14 | 0 | 809 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 12 | 0 | 197 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 280 | 228 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 7967 | 9:00
| Highest Generation |  | 11612 | 21:00
| Day Peak Generation |  | 9351 | 12:00
| Evening Peak Generation |  | 11612 | 21:00
| HVDC Max Flow |  | 818 | 7:00
| HVDC EvPeak Flow |  | 804 | 21:00
| Load factor L.F |  | 84.66%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-02
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-01 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9351 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8407 | MW
Evening Peak Generation : |  | 11612 | MW Hour : | 21:00 | Available Max Generation : |  | 14766 | MW
E.P. Demand (at gen end) : |  | 11612 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 11612 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1766 | MW
Total Gen. (MKWH) : |  | 235.9458 | System Load Factor : | 84.66% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -236 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-02
Actual : | 72.47 | Ft.(MSL) , | Rule curve : | 76.26 | Ft.( MSL )
Gas Consumed : | Total = | 1155.62 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 150544647.162
: |  | Coal : | 65488375 | Oil : | 454991284.39 | Total : | 671024306.552
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4587.9541 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1564.7984 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1402.8343 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1267.8727 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1145.5963 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 924.4674 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 510.9456 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.8675 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 713.0237 |  |  | 0 | 0%
Total | 0 |  | 12355.3601 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
7) Siddhirganj 335 MW ST
8) Bhola 225 MW GT-2
9) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chandraghona-Rangamati 132 kV Ckt-2 was under shut down from 10:58 to 11:46 for C/M.
b) Chandraghona-Rangamati 132 kV Ckt-1 was under shut down from 08:40 to 10:21 for C/M.
c) Rajshahi(N) 132 kV bus coupler breaker was under shut down from 11:02 to 11:39 for C/M.
d) Rajshahi(N) 230/132 kV T02 transformer was under shut down from 09:47 to 14:30 for C/M.
e) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 08:13 from both ends showing Dist RST,Z1 at Ashuganj end
& dist RST,Z1,SOTF at Sirajganj end and was switched on at 14:06 again tripped at 14:39 from
Sirajganj end showing dist Z1,general trip 135 km,dist RST and was switched on at 14:53.
f) Ghorashal-Ishordi 230 kV Ckt-1 was switched on at 14:55 .
g) Juldah 132/33 kV T-1 transformer tripped at 14:40 showing winding temperature high and was
switched on at 17:20.
i) Haripur-Bhulta 132 kV Ckt was under shut down from 16:28 to 17:58 due to sky wire removed at Haripur end.
j) Aminbazar 400/230 kV T-2 transformer was charged at 16:51 from 230 kV side.
k) Ashuganj-Sirajganj 230 kV Ckt-1 was under shut down from 17:00 to 18:31 to remove kite.
l) Sikalbaha 150 MW GT was synchronized at 17:34 and trip at 18:10 due shaft vibration again synchronized at 22:50.
m) Ashuganj (N) ST was synchronized at 17:48.
n) Haripur 230/132 kV T-1 transformer was charged at 18:15 .
o) Bakulia 132/33 kV T1 transformer was under shut down from 17:53 to 18:13 due to red hot maintenance |  |  |  |  | About 20 MW power interruption occurred under Bakulia S/S
at 33 kV bus isolator. |  |  |  |  | areas from 17:53 to 18:13.
p) Bhaluka 132/33 kV T2 transformer was under shut down from 15:23 to 16:17 due to red hot maintenance |  |  |  |  | About 25 MW power interruption occurred under Bhaluka S/S
at 33 kV B-phase isolator. |  |  |  |  | areas from 15:23 to 16:17.
q) Haripur-Siddhirganj 230 kV Ckt-2 was shut down from 20:40 to 22:02 for CVT changing.
r) Faridpur 33 kV bus section-2 was under shut down from 21:25 to 21:56 due to red hot maintenance at |  |  |  |  | About 12 MW power interruption occurred under Faridpur S/S
33 kV Y phase bus isolator PBS feeder. |  |  |  |  | areas from 21:25 to 21:56.
s) Barisal-Patuakhali 132 kV Ckt tripped at 22:14 from Barisal end showing dist relay and was switched |  |  |  |  | About 45 MW power interruption occurred under Patuakhali,Barguna
on at 22:30. |  |  |  |  | S/S areas from 22:14 to 22:30.
t) Sikalbaha 150 MW GT tripped at 02:02 due to excitation problem and was synchronized at 04:05(02-06-2021).
u) Dohazari-Cox's Bazar 132 kV Ckt-2 was shut down since 06:24(02-06-2021) for D/W.
v) Jamalpur-UMPL 132 kV Ckt-1 was shut down since 06:54(02-06-2021) for D/W.
w) Barisal(N) 132/33 kV T4 & T5 transformer were under shut down from 07:29 to 09:12(02-06-2021) for C/M. |  |  |  |  | About 18 MW power interruption occurred under Barisal(N) S/S
areas from 07:29 to 09:12.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-01 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4504500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2205909
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Shut down due to gas problem
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 156 | 3418000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6647750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 5544087 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 30 | 557051
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 10 | 201047 | Low demand
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 360288
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 181 | 3514000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1491840
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 227 | 5098057 | ST under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 64 | 813168 | Low demand
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 718956 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1897440
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 361507 | Engine problem
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 787274
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 999240 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 28 | 628500 | Engine problem
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 728900
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 699926 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 2571817 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 140 | 1822460
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 82 | 1745016 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 967680
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1563840 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 62719
| Dhaka area Total |  |  |  | 5919 | 2684 | 49910972
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 413818 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 47385
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 589440
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 492000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 5103443 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 102507 | Under maint.
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2581018
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 816488 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2175600
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1933440
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 430032
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 397440
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 6602
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1094967
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 85 | 2498207 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 688320 | Line O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 421527 | Line O/L
| Chattogram area Total |  |  |  | 2382 | 1030 | 22092234
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 125 | 2602385
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 221 | 5052000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 370 | 6089500 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 1679000 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 459504 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 878880
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 83 | 1271272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 983124 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 2363563
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 166944
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 77 | 1958400 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 139 | 2746560 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 416304
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 5 | 119160 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 1334400
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 665900 | Engine problem
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 957400 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 314480 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2278860 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 110 | 2700600
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 510480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1779 | 35548716
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 135 | 3215200 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 17 | 401256 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 379200 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8750
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 1257600
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 107 | 2100000
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 131030
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 450240
| Mymensingh Area Total |  |  |  | 709 | 491 | 7943276
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1011000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1008000 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3550990
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 163 | 3627000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 49 | 1168200
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 183100
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1424160
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1768320
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4184860
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 407000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 357648 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7219000 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 363 | 8951000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 163620 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9030000 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1927 | 44053898
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 804 | 19338909
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 9 | 43200 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 9088 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 370 | 9020736 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 31 | 221760 | Low demand
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1577568
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1319 | 30211261
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 422784 | Engine problem
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 26 | 517640 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1816856 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 13 | 942833 | Machine problem
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 410 | 10378900
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 233 | 3046036 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 88800 | Low demand
| Barisal Area Total |  |  |  | 1826 | 783 | 17213849
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 495024
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 16 | 102174
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 168430 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 90405 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 197750 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 164 | 4311173 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 177 | 4562855 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 374 | 8959127 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 27 | 180195 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 492480
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 197136
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1005600
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 1030704
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1373568
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1057920
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 13560
| Rajshahi Area Total |  |  |  | 2179 | 1336 | 24238101
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1023120
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34161
| Rangpur Area Total |  |  |  | 605 | 263 | 4733481
| Total |  |  |  | 21315 | 11612 | 235945788
| Eastern Grid Total |  |  |  | 14421 | 7911 | 159549096
| Western Grid Total |  |  |  | 6894 | 3701 | 76396692
| National Grid Total |  |  |  | 21315 | 11612 | 235945788
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-01
(a) ENTIRE EASTERN GRID : |  | 7354 | MW | (b) ENTIRE WESTERN GRID : |  | 3672 | MW
i) Dhaka area |  | 3896 | MW | i) Khulna area |  | 1254 | MW
ii) Chittagong area |  | 1106 | MW | ii) Rajshahi area |  | 1306 | MW
iii) Comilla area |  | 921 | MW | iii) Barisal area |  | 300 | MW
iv) Mymensingh area |  | 984 | MW | iv) Rangpur area |  | 812 | MW
v) Sylhet area |  | 447 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11026 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 10:00 | Kishoreganj | 130 | 21:00 | Jessore | 99 | 13:00
Munsiganj | 85 | 19:30 | Netrokona | 117 | 20:00 | Benapol | 62 | 21:00
Sonargaon | 66 | 18:00 | Jamalpur | 142 | 21:00 | Jhenida | 98 | 19:30
Shyampur | 192 | 0:00 | Sherpur | 120 | 22:00 | Bottail | 125 | 19:30
Bhulta | 202 | 0:00 | Srimongal | 47 | 21:00 | G.K Project | 57 | 20:00
Madanganj | 48 | 4:00 | Shahjibazar | 99 | 21:00 | Faridpur | 162 | 19:30
Shitalakhya | 102 | 15:00 | Fenchuganj | 40 | 19:00 | Madaripur | 87 | 21:00
Rahim steel | 23 | 12:00 | Kulawara | 36 | 1:00 | Sariatpur | 52 | 1:00
Matuail | 54 | 1:00 | Sylhet | 114 | 19:00 | Gopalganj | 83 | 21:00
Ghorasal | 68 | 1:00 | Chatak | 26 | 21:00 | Bagerhat | 90 | 19:30
Narsingdi | 157 | 1:00 | Sunamganj | 43 | 22:00 | Mongla | 38 | 10:00
Haripur (SBU) | 102 | 1:00 | Biani Bazar | 55 | 21:00 | Satkhira | 88 | 1:00
Sreenagar | 36 | 21:00 | Comilla (S) | 158 | 1:00 | Gallamari | 40 | 12:00
Ullon | 60 | 1:00 | Comilla(N) | 99 | 19:00 | Magura | 46 | 13:00
Hasnabad | 73 | 18:00 | Chandpur | 64 | 1:00 | Norail | 36 | 20:00
Magbazar | 85 | 14:00 | Feni | 91 | 1:00 | Chuadanga | 86 | 13:00
Maniknagar | 64 | 13:00 | Chowmuhani | 139 | 21:00 | Borguna | 16 | 1:00
Bangabhaban | 10 | 10:00 | Ashuganj | 42 | 1:00 | Barisal(N) | 37 | 20:00
Motijheel | 19 | 12:00 | Daudkandi | 122 | 20:00 | Barisal (S) | 94 | 20:00
Narinda | 50 | 15:00 | B.Baria | 129 | 1:00 | Patuakhali | 101 | 22:00
Kazla | 73 | 16:00 | Ramganj | 74 | 21:00 | Bhandaria | 43 | 1:00
Dhanmondi | 156 | 15:00 | Chaddagram | 38 | 21:00 | Borhan Uddin | 41 | 1:00
Lalbag | 84 | 16:00 | PHP | 9 | 17:00 | Ishurdi | 64 | 19:30
Madartek | 65 | 1:00 | Kochua | 54 | 1:00 | Ruppur Paromanobik | 3 | 21:00
Dhaka University | 35 | 13:00 | Madunaghat | 53 | 1:00 | Natore | 136 | 19:30
Aftabnagar | 9 | 13:00 | Hathazari | 76 | 1:00 | Bogra | 151 | 21:00
Fatullah | 56 | 1:00 | Khulshi | 205 | 13:00 | Noagaon | 117 | 21:00
Nawabganj | 45 | 21:00 | Halishahar | 115 | 13:00 | Rajshahi | 161 | 21:00
Keraniganj | 56 | 19:30 | Baraulia | 150 | 23:00 | Rajshahi New | 22 | 20:00
Mirpur | 106 | 19:00 | Sikalbaha | 32 | 1:00 | C.Nawabganj | 74 | 21:00
Kalyanpur | 93 | 14:00 | Dohazari | 84 | 1:00 | Amnura | 41 | 21:00
Gulshan | 118 | 13:00 | Cox'sbazar | 104 | 1:00 | Pabna | 94 | 20:00
Uttara | 80 | 16:00 | Chandraghona | 28 | 1:00 | Shahjadpur | 90 | 20:00
Uttara New | 31 | 13:00 | Kaptai | 3.8 | 13:00 | Serajganj | 95 | 20:00
Kamrangirchar | 84 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 71 | 21:00
Savar | 151 | 21:00 | Bakulia | 104 | 12:00 | Joypurhat | 61 | 21:00
Bhasantec | 138 | 19:00 | Julda | 18 | 1:00 | Sherpur(Bogura) | 56 | 21:00
Agargaon | 68 | 15:00 | TK chemical | 23 | 19:00 | Mohastangor | 62 | 21:00
Satmosjid | 82 | 14:00 | Modern Steel |  |  | Bhangura | 31 | 21:00
Tongi | 106 | 12:00 | Shahmirpur | 20.5 | 1:00 | Rangpur | 127 | 19:30
Kabirpur | 243 | 16:00 | Khagrachhari | 22 | 16:00 | Lalmonirhat | 43 | 20:00
Basundhara | 163 | 0:00 | Matarbari | 36 | 1:00 | Saidpur | 102 | 21:00
Manikganj | 68 | 21:00 | Baroiar Hat | 38 | 2:00 | Purbasadipur | 114 | 20:00
Joydevpur | 166 | 19:00 | Rangamati | 10 | 11:00 | Thakurgaon | 84 | 21:00
New Tongi | 95 | 12:00 | Abul Khair 230 | 11 | 20:00 | Palashbari | 111 | 21:00
Kodda | 261 | 15:00 | BSRM | 155 | 8:00 | Barapukuria | 53 | 21:00
Dhamrai | 126 | 0:00 | GPH Ispat | 84 | 3:00 | Panchagar | 53 | 20:00
Rajendrapur | 98 | 22:00 | Agrabad | 32 | 12:00 | Joldhaka | 60 | 21:00
Valuka | 130 | 19:00 | Goalpara | 27 | 13:00 | Kurigram | 57 | 19:30
Tangail | 190 | 21:00 | Central S/S | 78 | 19:00 | Mithapukur | 41 | 19:00
Mymensing | 190 | 22:00 | Noapara | 43 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-01 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 1:00 | 396 | 11:00 | Kaliakoir | 393 | 0.75 | 377 | 0.45833
| Bheramara | 401 | 7:00 | 395 | 13:00 | Bhulta | 382 | 0.041667 | 357 | 0.625
| Ashuganj(N) | 391 | 8:00 | 360 | 15:00 | Gopalganj | 402 | 0.625 | 388 | 0.125
| Payra | 407 | 20:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 225 | 17:00 | 218 | 10:00
| Ishurdi | 235 | 18:30 | 224 | 11:00 | Megnaghat | 232 | 19:30 | 224 | 12:00
| Ashuganj | 240 | 1:00 | 233 | 15:00 | Fenchuganj | 240 | 8:00 | 236 | 18:30
| Serajganj | 230 | 1:00 | 225 | 5:00 | Siddhirganj | 230 | 1:00 | 218 | 12:00
| Baghabari | 232 | 18:30 | 225 | 10:00 | Maniknagar | 228 | 1:00 | 217 | 12:00
| Barapukuria | 234 | 18:00 | 226 | 19:30 | Agargaon | 227 | 22:00 | 214 | 11:00
| Bogra | 225 | 18:30 | 215 | 11:00 | Barisal | 247 | 20:00 | 239 | 24:00
| Rajshahi | 236 | 18:30 | 221 | 11:00 | Bhola 225 MW | 249 | 7:00 | 240 | 10:00
| Khulna South | 229 | 18:00 | 207 | 7:00 | AKSML | 227 | 20:00 | 219 | 12:00
| Rampura | 229 | 1:00 | 219 | 11:00 | BSRM | 228 | 20:00 | 220 | 12:00
| Haripur | 226 | 1:00 | 218 | 11:00 | Bibiyana | 241 | 20:00 | 237 | 6:00
| Hasnabad | 226 | 8:00 | 215 | 12:00 | Bhulta | 230 | 8:00 | 218 | 12:00
| Shyampur | 227 | 20:00 | 220 | 12:00 | Ashuganj (S) | 237 | 1:00 | 219 | 15:00
| Aminbazar | 228 | 1:00 | 216 | 2:00 | Kaliakoir | 229 | 21:00 | 216 | 11:00
| Tongi | 226 | 19:30 | 213 | 9:00 | GPH | 227 | 20:00 | 220 | 1:00
| Comilla (N) | 231 | 20:00 | 224 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 132 | 1:00 | 124 | 12:00 | Kochua | 139 | 0.8125 | 136 | 0.041667
| Munsiganj | 134 | 9:00 | 125 | 12:00 | Madanhat | 136 | 0.66667 | 130 | 0.041667
| Sonargaon | 131 | 22:00 | 125 | 7:00 | Hathazari | 135 | 0.70833 | 130 | 0.041667
| Shyampur | 133 | 20:00 | 124 | 12:00 | Khulshi | 132 | 0.66667 | 126 | 0.375
| Bhulta | 131 | 9:00 | 112 | 17:00 | Halishahar | 132 | 0.70833 | 125 | 0.41667
| Madanganj | 132 | 1:00 | 123 | 12:00 | Baraulia | 134 | 0.66667 | 127 | 0.29167
| Shitalakhya | 138 | 19:30 | 124 | 12:00 | Sikalbaha | 135 | 0.66667 | 129 | 0.375
| Rahim steal | 133 | 9:00 | 124 | 12:00 | Dohazari | 135 | 0.83333 | 125 | 0.375
| Matuail | 132 | 1:00 | 124 | 12:00 | Cox'sbazar | 127 | 0.83333 | 114 | 0.25
| Ghorasal | 138 | 3:00 | 136 | 9:00 | Chandraghona | 134 | 0.70833 | 128 | 0.041667
| Narsinghdi | 136 | 8:00 | 118 | 17:00 | Kaptai | 132 | 0.75 | 128 | 0.29167
| Haripur (SBU) | 132 | 4:00 | 125 | 12:00 | A. Khaer Stl. | 133 | 0.70833 | 125 | 0.041667
| Sreenagar | 131 | 20:00 | 122 | 10:00 | Bakulia | 134 | 0.66667 | 126 | 0.41667
| Ullon | 137 | 1:00 | 126 | 12:00 | Julda | 138 | 0.79167 | 130 | 0.375
| Hasnabad | 136 | 19:30 | 125 | 12:00 | TK Chemical | 135 | 0.83333 | 129 | 0.25
| Magbazar | 135 | 1:00 | 125 | 15:00 | Modern Steel
| Maniknagar | 137 | 1:00 | 129 | 12:00 | Shahmirpur | 136 | 0.66667 | 130 | 0.375
| Bangabhaban | 137 | 1:00 | 129 | 12:00 | Khagrachhari | 133 | 0.66667 | 127 | 0
| Motijheel | 137 | 1:00 | 129 | 12:00 | Matarbari | 132 | 0.79167 | 117 | 0.041667
| Narinda | 137 | 1:00 | 129 | 12:00 | Baroiar Hat | 137 | 0.16667 | 131 | 0.041667
| Kazla | 137 | 1:00 | 129 | 12:00 | Rangamati | 133 | 16:00 | 128 | 9:00
| Dhanmondi | 133 | 5:00 | 124 | 12:00 | Agrabad | 132 | 16:00 | 126 | 10:00
| Lalbag | 136 | 20:00 | 123 | 12:00 | Goalpara S/S | 138 | 18:30 | 123 | 0.29167
| Madartek | 136 | 1:00 | 128 | 12:00 | Khulna Central S/S | 138 | 18:30 | 121 | 0.29167
| Dhaka University | 137 | 8:00 | 128 | 12:00 | Noapara | 136 | 18:00 | 120 | 0.45833
| Aftabnagar | 137 | 2:00 | 128 | 12:00 | Jessore | 134 | 18:00 | 116 | 0.5
| Fatullah | 133 | 1:00 | 124 | 12:00 | Benapol | 134 | 0.75 | 116 | 0.29167
| Nawabganj | 129 | 1:00 | 122 | 12:00 | Jhenida | 130 | 18:00 | 114 | 0.5
| Keraniganj | 131 | 20:00 | 122 | 12:00 | Bottail | 133 | 0.75 | 124 | 0.45833
| Mirpur | 136 | 1;00 | 128 | 14:00 | G.K Project | 139 | 0.70833 | 133 | 0.45833
| Kalyanpur | 137 | 1;00 | 128 | 12:00 | Faridpur | 135 | 0.77083 | 129 | 0.041667
| Gulshan | 136 | 16:00 | 128 | 12:00 | Madaripur | 134 | 0.75 | 133 | 0.95833
| Uttara | 137 | 1:00 | 126 | 11:00 | Shariyatpur S/S | 138 | 9:00 | 132 | 0.041667
| Uttara New | 140 | 8:00 | 126 | 11:00 | Gopalganj | 141 | 0.77083 | 133 | 0.041667
| Kamrangirchar | 138 | 1:00 | 127 | 10:00 | Bagerhat | 137 | 13:00 | 117 | 0.29167
| Savar | 136 | 1:00 | 125 | 12:00 | Mongla | 135 | 13:00 | 118 | 0.45833
| Bhasantec | 137 | 14:00 | 128 | 12:00 | Satkhira | 136 | 18:00 | 121 | 7:00
| Agargaon | 136 | 1:00 | 125 | 12:00 | Gallamari | 139 | 0.77083 | 124 | 7:00
| Satmosjid | 136 | 1:00 | 128 | 11:00 | Magura | 130 | 18:00 | 111 | 0.5
| Tongi | 139 | 20:00 | 130 | 9:00 | Narail | 128 | 0.75 | 112 | 0.5
| Kabirpur | 139 | 5:00 | 129 | 15:00 | Chuadanga | 126 | 18:00 | 104 | 0.041667
| Basundhara | 138 | 20:00 | 126 | 12:00 | Borguna | 140 | 14:00 | 132 | 0.041667
| Manikganj | 140 | 1:00 | 131 | 12:00 | Barisal(N) | 140 | 8:00 | 135 | 21:00
| Joydevpur | 139 | 1:00 | 129 | 10:00 | Barisal (S) | 139 | 0.91667 | 133 | 0.20833
| New Tongi | 138 | 1:00 | 132 | 15:00 | Patuakhali(S) | 140 | 0.625 | 129 | 0.041667
| Kodda | 138 | 1:00 | 124 | 12:00 | Bhandaria | 139 | 0.625 | 130 | 0.041667
| Dhamrai | 128 | 11:00 | 124 | 0:00 | Ishurdi | 136 | 18:00 | 130 | 11:00
| Rajendrapur | 135 | 21:00 | 123 | 15:00 | Ruppur Paromanobik | 135 | 18:00 | 131 | 12:00
| Valuka | 128 | 7:00 | 113 | 21:00 | Natore | 134 | 18:00 | 127 | 12:00
| Tangail | 136 | 7:00 | 123 | 21:00 | Bogra | 136 | 1:00 | 126 | 12:00
| Mymensing | 130 | 7:00 | 117 | 21:00 | Noagaon | 130 | 18:30 | 120 | 21:00
| Kishorganj | 133 | 7:00 | 123 | 21:00 | Rajshahi | 133 | 18:30 | 124 | 12:00
| Netrokona | 129 | 6:00 | 114 | 21:00 | Rajshahi New | 134 | 18:00 | 123 | 11:00
| Jamalpur | 133 | 1:00 | 124 | 17:00 | C.Nawabganj | 132 | 18:30 | 121 | 12:00
| Sherpur | 132 | 1:00 | 124 | 22:00 | Amnura | 133 | 18:30 | 121 | 12:00
| Srimongal | 140 | 7:00 | 136 | 23:00 | Pabna | 135 | 18:30 | 128 | 11:00
| Shahjibazar | 138 | 7:00 | 135 | 1:00 | Shahjadpur | 137 | 18:00 | 132 | 12:00
| Fenchuganj | 138 | 6:00 | 136 | 1:00 | Serajganj | 133 | 6:00 | 126 | 12:00
| Khulawara | 138 | 5:00 | 135 | 22:00 | Niyamatpur | 129 | 18:00 | 118 | 20:00
| Sylhet | 135 | 6:00 | 133 | 1:00 | Joypurhat | 130 | 18:30 | 118 | 21:00
| Chatak | 135 | 7:00 | 131 | 1:00 | Sherpur(Bogura) | 134 | 1:00 | 127 | 12:00
| Sunamganj | 135 | 8:00 | 129 | 22:00 | Mohastangor | 132 | 18:00 | 125 | 12:00
| Biani Bazar | 136 | 7:00 | 132 | 1:00 | Bangura | 136 | 18:30 | 130 | 12:00
| Comilla(s) | 131 | 5:00 | 126 | 8:00 | Rangpur | 127 | 18:00 | 117 | 20:00
| Comilla(n) | 139 | 19:30 | 135 | 14:00 | Lalmonirhat | 126 | 18:00 | 118 | 20:00
| Chandpur | 140 | 0:00 | 134 | 1:00 | Saidpur | 129 | 18:00 | 118 | 20:00
| Feni | 140 | 16:00 | 134 | 1:00 | Purbasadipur | 126 | 18:00 | 110 | 21:00
| Chowmuhani | 137 | 16:00 | 133 | 1:00 | Thakurgaon | 126 | 8:00 | 109 | 21:00
| Ashuganj | 140 | 7:00 | 138 | 21:00 | Palashbari | 129 | 18:30 | 120 | 12:00
| Daudkandi | 134 | 21:00 | 127 | 12:00 | Barapukuria | 134 | 18:00 | 126 | 21:00
| B.Baria | 137 | 8:00 | 132 | 22:00 | Panchagar | 127 | 8:00 | 105 | 20:00
| Ramganj | 139 | 17:00 | 134 | 1:00 | Joldhaka | 126 | 0.79167 | 111 | 0.875

## L-Curve
Date | 2021-06-01
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 116 | 7064 | 3402 | 10466 |  |  |  | QF-LDC-11
0:30 | 83 | 7260.5 | 3485.5 | 10746 | Date: | 2021-06-01
1:00 | 50 | 7457 | 3569 | 11026
1:30 | 65 | 7215 | 3496.5 | 10711.5
2:00 | 80 | 6973 | 3424 | 10397
2:30 | 85 | 6833 | 3324 | 10157 | [5 empty] | Gen. at Eve. Peak | 11612 | 11612 MW (21:00 )
3:00 | 90 | 6693 | 3224 | 9917 | [6 empty] | 21:00
3:30 | 47 | 6689.5 | 3165.5 | 9855 | [5 empty] | Gen. at Day Peak | 9351 | 9351 MW (12:00 )
4:00 | 4 | 6686 | 3107 | 9793 | [6 empty] | 12:00
4:30 | 22 | 6424 | 2998.5 | 9422.5 | [5 empty] | Highest Generation | 11612
5:00 | 40 | 6162 | 2890 | 9052 | [6 empty] | 21:00
5:30 | 40 | 5928.5 | 2811.5 | 8740
6:00 | 40 | 5695 | 2733 | 8428
6:30 | 50 | 5572 | 2746.5 | 8318.5
7:00 | 60 | 5449 | 2760 | 8209
7:30 | 70 | 5370.5 | 2778 | 8148.5
8:00 | 80 | 5292 | 2796 | 8088
8:30 | 50 | 5293.5 | 2734 | 8027.5
9:00 | 20 | 5295 | 2672 | 7967
9:30 | 15 | 5513 | 2719 | 8232
10:00 | 10 | 5731 | 2766 | 8497
10:30 | 32.5 | 5973.5 | 2804.5 | 8778
11:00 | 55 | 6216 | 2843 | 9059
11:30 | 47.5 | 6346 | 2859 | 9205
12:00 | 40 | 6476 | 2875 | 9351
12:30 | 30 | 6546 | 2930 | 9476
13:00 | 20 | 6616 | 2985 | 9601
13:30 | 30 | 6683.5 | 2948.5 | 9632
14:00 | 40 | 6751 | 2912 | 9663
14:30 | 118.5 | 6667 | 3002 | 9669
15:00 | 197 | 6583 | 3092 | 9675
15:30 | 100 | 6691 | 2974 | 9665
16:00 | 3 | 6799 | 2856 | 9655
16:30 | 63.5 | 6663 | 2824 | 9487
17:00 | 124 | 6527 | 2792 | 9319
17:30 | 106.5 | 6521.5 | 2772 | 9293.5
18:00 | 89 | 6516 | 2752 | 9268
18:30 | 49 | 6894.5 | 3043.5 | 9938
19:00 | 9 | 7273 | 3335 | 10608
19:30 | 32 | 7765 | 3780 | 11545
20:00 | 236 | 7784 | 3671 | 11455 |  |  |  | Executive Engineer
20:30 | 208 | 7847.5 | 3686 | 11533.5 |  |  |  | Network Operation Division
21:00 | 180 | 7911 | 3701 | 11612
21:30 | 101.5 | 7674.5 | 3675.5 | 11350
22:00 | 23 | 7438 | 3650 | 11088 |  |  |  |  | Page 6 of 7
22:30 | 49 | 7344.5 | 3584.5 | 10929
23:00 | 75 | 7251 | 3519 | 10770
23:30 | 95.5 | 7157.5 | 3460.5 | 10618
24:00 | 116 | 7064 | 3402 | 10466
11612 MW (21:00 )
9351 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-01 |  | Energy | 235945788
[11 empty] | 2021-06-01 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4230 | 804 | 2074 | 2688 | 500 | 20 | 311 | 0 | 112 | 0
0:30 | 4266 | 797 | 1873 | 2860.5 | 575 | 20 | 356 | 0 | 135 | 0 | Date: | 2021-06-01
1:00 | 4302 | 790 | 1672 | 3033 | 650 | 20 | 401 | 0 | 158 | 0
1:30 | 4303.5 | 790 | 1666.5 | 2756.5 | 649.5 | 20 | 369.5 | 0 | 156 | 0 | [7 empty] | Total Energy | 235.9458 | Total Energy Gen 235.946 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.946 MKWHr
2:00 | 4305 | 790 | 1661 | 2480 | 649 | 20 | 338 | 0 | 154 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4312 | 790 | 1712 | 2228 | 654.5 | 20 | 288.5 | 0 | 152 | 0 | [7 empty] | Energy Requirement | 235.9458
3:00 | 4319 | 790 | 1763 | 1976 | 660 | 20 | 239 | 0 | 150 | 0
3:30 | 4280 | 790 | 1779 | 1940 | 660 | 20 | 239 | 0 | 147 | 0 | [6 empty] | Shortage
4:00 | 4241 | 790 | 1795 | 1904 | 660 | 20 | 239 | 0 | 144 | 0
4:30 | 4224.5 | 790.5 | 1752.5 | 1690.5 | 660 | 20 | 144.5 | 0 | 140 | 0
5:00 | 4208 | 791 | 1710 | 1477 | 660 | 20 | 50 | 0 | 136 | 0
5:30 | 4146 | 790.5 | 1698.5 | 1295 | 635 | 20 | 25 | 0 | 129 | 1
6:00 | 4084 | 790 | 1687 | 1113 | 610 | 20 | 0 | 0 | 122 | 2
6:30 | 3994 | 804 | 1678.5 | 1108.5 | 590 | 20 | 0 | 0 | 121 | 2.5 |  |  |  |  | Coal
7:00 | 3904 | 818 | 1670 | 1104 | 570 | 20 | 0 | 0 | 120 | 3
7:30 | 3801.5 | 817.5 | 1630.5 | 1181 | 575 | 20 | 0 | 0 | 120 | 3 |  |  |  | Oil |  |  |  | ,
8:00 | 3699 | 817 | 1591 | 1258 | 580 | 20 | 0 | 0 | 120 | 3
8:30 | 3728.5 | 817.5 | 1587 | 1175.5 | 565 | 20 | 0 | 0 | 124 | 10
9:00 | 3758 | 818 | 1583 | 1093 | 550 | 20 | 0 | 0 | 128 | 17
9:30 | 3913.5 | 818 | 1686 | 1124 | 535 | 20 | 0 | 0 | 111 | 24.5
10:00 | 4069 | 818 | 1789 | 1155 | 520 | 20 | 0 | 0 | 94 | 32
10:30 | 4061 | 817.5 | 1875 | 1375 | 505 | 20 | 10 | 0 | 89 | 25.5
11:00 | 4053 | 817 | 1961 | 1595 | 490 | 20 | 20 | 0 | 84 | 19
11:30 | 3993.5 | 817.5 | 1967.5 | 1726.5 | 490 | 20 | 67.5 | 0 | 95 | 27.5
12:00 | 3934 | 818 | 1974 | 1858 | 490 | 20 | 115 | 0 | 106 | 36
12:30 | 3895.5 | 817.5 | 1959.5 | 2015.5 | 490 | 20 | 124 | 0 | 108 | 46
13:00 | 3857 | 817 | 1945 | 2173 | 490 | 20 | 133 | 0 | 110 | 56
13:30 | 3857 | 817 | 1945 | 2173 | 490 | 20 | 133 | 0 | 110 | 56
14:00 | 3857 | 817 | 1945 | 2173 | 490 | 20 | 133 | 0 | 110 | 56
14:30 | 3804 | 817 | 1884 | 2338.5 | 480 | 20 | 141.5 | 0 | 105 | 48
15:00 | 3751 | 817 | 1823 | 2504 | 470 | 20 | 150 | 0 | 100 | 40
15:30 | 3659.5 | 817 | 1823 | 2603 | 450 | 20 | 153 | 0 | 106 | 33.5
16:00 | 3568 | 817 | 1823 | 2702 | 430 | 20 | 156 | 0 | 112 | 27
16:30 | 3556 | 817.5 | 1762 | 2637 | 430 | 20 | 135 | 0 | 107 | 22.5
17:00 | 3544 | 818 | 1701 | 2572 | 430 | 20 | 114 | 0 | 102 | 18
17:30 | 3570.5 | 817.5 | 1703 | 2525 | 430 | 20 | 113.5 | 0 | 103 | 11
18:00 | 3597 | 817 | 1705 | 2478 | 430 | 20 | 113 | 0 | 104 | 4
18:30 | 3751.5 | 817.5 | 1793.5 | 2687.5 | 440 | 20 | 316 | 0 | 110 | 2
19:00 | 3906 | 818 | 1882 | 2897 | 450 | 20 | 519 | 0 | 116 | 0
19:30 | 3978 | 817 | 1971 | 3538 | 560 | 20 | 543 | 0 | 118 | 0
20:00 | 4015 | 805 | 1914 | 3489 | 560 | 20 | 534 | 0 | 118 | 0
20:30 | 4112.5 | 804.5 | 1954.5 | 3441 | 560 | 20 | 527 | 0 | 114 | 0
21:00 | 4210 | 804 | 1995 | 3393 | 560 | 20 | 520 | 0 | 110 | 0
21:30 | 4193.5 | 804 | 2005 | 3207.5 | 565 | 20 | 443 | 0 | 112 | 0
22:00 | 4177 | 804 | 2015 | 3022 | 570 | 20 | 366 | 0 | 114 | 0
22:30 | 4184.5 | 804.5 | 2032 | 2855 | 555 | 20 | 366 | 0 | 112 | 0
23:00 | 4192 | 805 | 2049 | 2688 | 540 | 20 | 366 | 0 | 110 | 0
23:30 | 4211 | 804.5 | 2061.5 | 2688 | 520 | 20 | 338.5 | 0 | 111 | 0 | Max Temp. in Dhaka |  | 30.1° C
24:00 | 4230 | 804 | 2074 | 2688 | 500 | 20 | 311 | 0 | 112 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 235.946 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.946 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-01
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 492000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 413818
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 2 |  | 7 | 7 |  | 7 | 4 | 1 | 3 | 2 | 2 | [9 empty] | 47385
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 200 | 202 | 204 | 204 | 207 | 204 | 204 | 215 | 229 | 215 | 207 | 203 | 203 | 213 | 203 | 203 | 203 |  | 218 | 203 | 203 | 203 | 203 | 216 | 203 | 5103443
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | [17 empty] | 70 | [6 empty] | 25 | 70 | 102507
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | [15 empty] | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 816488
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2581018
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 |  |  | 0 | 166944
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 150 | 150 | 120 | 120 | 120 | 120 | 75 | 120 | 120 | 150 | 185 | 185 | 183 | 152 | 156 | 93 | 97 | 97 |  | 185 | 179 | 125 | 181 | 140 | 120 | 100 | 3514000
17 | Siddhirganj 335 MW CCPP | 222 | 222 | 222 | 224 | 223 | 221 | 180 | 150 | 150 | 180 | 180 | 180 | 221 | 221 | 218 | 221 | 190 | 190 |  | 220 | 220 | 220 | 227 | 221 | 221 | 220 | 5098057
18 | Kodda 300 MW PP Unit-2 (Summit) | 195 | 15 | [9 empty] | 30 | 110 | 110 | 160 | 235 | 245 | 243 |  | 245 | 245 | 245 | 195 | 145 | 95 | 15 | 2571817
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 70 | 83 | 102 | 102 | 102 | 0 | 83 | 83 | 83 |  | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 1271272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4504500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 135 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2602385
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 22 | 22 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 459504
33 | Ashuganj 225 MW CCPP | 222 | 220 | 219 | 220 | 220 | 219 | 219 | 220 | 199 | 201 | 196 | 221 | 184 | 183 | 201 | 183 | 183 | 185 |  | 218 | 220 | 183 | 221 | 222 | 218 | 220 | 5052000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 220 | 100 | 100 | 10 | [17 empty] | 0 | 1679000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 265 | 260 | 260 | 275 | 260 | 260 | 320 | 340 | 330 | 240 | 243 | 220 | 20 | 20 | 30 | 90 |  | 155 | 245 | 320 | 370 | 370 | 365 | 365 | 6089500
35 | Ashuganj 55 MW PP (Precision) | 5 | 5 | 5 | 5 | 5 | 15 | 15 | 15 | 30 | 30 | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 53 | 878880
36 | Chandpur 150 MW CCPP | 85 | 85 | 85 | 84 | 84 | 85 | 84 | 82 | 85 | 84 | 85 | 85 | 84 | 84 | 85 | 85 | 80 | 79 |  | 81 | 77 | 77 | 77 | 77 | 74 | 72 | 1958400
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6647750
41 | Haripur 360MW CCPP(HPL) | 57 | 57 | 185 | 293 | 207 | 207 | 191 | 131 | 145 | 151 | 145 | 130 | 125 | 120 | 120 | 121 | 120 | 126 |  | 135 | 150 | 157 | 156 | 167 | 171 | 190 | 3418000
42 | RPCL 210MW CCPP | 144 | 157 | 157 | 157 | 157 | 157 | 159 | 157 | 135 | 136 | 130 | 132 | 120 | 119 | 120 | 139 | 139 | 139 |  | 133 | 135 | 134 | 135 | 135 | 134 | 139 | 3215200
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 2 | 4 | 16 | 5 | 13 | 31 | 14 | 18 | 20 | 11 | 4 | [8 empty] | 131030
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1011000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1008000
46 | Shajibazar 330 MW CCPP | 162 | 162 | 162 | 161 | 161 | 162 | 163 | 162 | 162 | 163 | 162 | 157 | 161 | 161 | 162 | 161 | 161 | 162 |  | 163 | 164 | 162 | 163 | 160 | 162 | 162 | 3627000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 45 | 45 | 45 | 57 | 62 | 62 | 62 | 61 | 61 | 62 | 62 | 45 |  | 62 | 62 | 63 | 63 | 63 | 62 | 62 | 1424160
48 | Shahjibazar 86MW PP (Shahjibazar) | 80 | 80 | 80 | 80 | 80 | 80 | 50 | 50 | 50 | 78 | 77 | 77 | 80 | 83 | 83 | 83 | 20 | 20 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1768320
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 | 164 |  | 164 | 164 | 195 | 219 | 218 | 218 | 218 | 4184860
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 407000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 163620
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 2 | 2 | 2 | 2 | 3 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 183100
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 47 | 50 | 50 | 47 | 50 | 53 | 53 | 53 | 53 |  | 24 | 44 | 47 | 49 | 50 | 53 | 53 | 1168200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 357648
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 290 | 285 | 280 | 290 | 280 | 290 | 290 | 310 | 320 | 310 | 300 | 290 | 310 | 280 | 285 | 300 |  | 310 | 280 | 280 | 290 | 266 | 290 | 290 | 7219000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 370 | 330 | 330 | 384 | 400 | 400 | 355 | 350 | 350 | 350 | 350 | 330 |  | 330 | 340 | 375 | 400 | 400 | 400 | 400 | 9030000
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | [6 empty] | 35 |  |  | 35 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 787274
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 |  |  |  |  | 1 | 16 | 24 | 24 | 24 | 24 | 23 | 23 | 15 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 450240
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 |  | 15 | 18 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 22 | 19 | 430032
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  |  | 15 | 18 | 18 | 18 | 18 | 0 | 22 |  | 0 | 19 | 22 | 22 | 22 | 22 | 22 | 360288
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 401256
63 | Impoprt (Tripura) | 158 | 154 | 150 | 144 | 136 | 122 | 120 | 120 | 128 | 94 | 84 | 106 | 110 | 110 | 100 | 112 | 102 | 104 |  | 116 | 118 | 118 | 110 | 114 | 110 | 112 | 1334400
64 | Malancha, Ctg. EPZ (United) | 38 | 16 | 23 | 30 | 30 | 39 | 39 | 8 | 3 | 2 | 2 | 2 | 2 | 12 | 7 | 7 | 8 | 2 |  | 7 | 7 | 10 | 25 | 31 | 30 | 36 | 397440
65 | Feni 22MW PP (Doreen) | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  |  |  | 19 | 19 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 416304
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [6 empty] | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 119160
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 665900
68 | Cumilla 25 MW PP (Summit) | 20 | 21 | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 5 |  | 18 | 18 | 18 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 314480
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 19 | 19 | 21 | 21 | 21 | 11 | 0 | 0 | 15 | 20 | 20 | 20 | 20 | 20 | 12 | 12 |  | 13 | 18 | 18 | 20 | 20 | 21 | 21 | 399240
71 | Maona 33 MW PP(Summit) | 33 | 33 | 25 | 20 | 20 | 20 | 20 | 20 | 20 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 |  | 25 | 25 | 28 | 28 | 28 | 28 | 28 | 628500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 |  | 17 | 17 | 17 |  | 33 | 33 |  | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 728900
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 94 | 94 | 94 | 95 | 95 | 96 | 76 | 53 |  | 98 | 99 | 99 | 99 | 99 | 99 | 99 | 2205909
| Feni Lanka Power | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 81 | 81 | 81 | 70 |  | 81 | 81 | 81 | 100 | 100 | 100 | 100 | 2278860
| Chowmuhani 113 MW | 111 | 110 | 111 | 111 | 110 | 111 | 110 | 111 | 110 | 111 | 110 | 117 | 122 | 121 | 114 | 120 | 117 | 85 |  | 100 | 111 | 113 | 110 | 112 | 114 | 111 | 2700600
| Manikgonj 162MW PP(MPGL) | 126 | 108 | [9 empty] | 27 | 79 | 94 | 108 | 108 | 90 | 90 |  | 107 | 126 | 124 | 126 | 90 | 90 | 90 | 1563840
77 | Siddhirganj 100 PP(Dutch Bangla) | 80 | 50 | 32 | 32 | 7 | 7 | 7 | 7 | 7 | 7 | 55 | 60 | 70 | 80 | 90 | 91 | 91 | 91 |  | 91 | 100 | 98 | 100 | 100 | 100 | 16 | 1491840
78 | Gazipur 52 MW PP | 42 | 42 | 42 | 42 | [6 empty] | 11 | 28 | 32 | 30 | 32 | 38 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 699926
79 | Kodda 150MW PP | 150 | 115 | 16 | 16 | [6 empty] | 20 | 115 | 133 | 150 | 150 | 150 | 98 | 98 |  | 150 | 150 | 150 | 150 | 64 | 64 | 64 | 1897440
80 | Jamalpur 95 MW PP(Powerpac) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 379200
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 35 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 25 | 16 | 16 | 34 | 43 | 37 | 40 | 957400
| Gazipur 100 MW PP | 82 | 82 | 81 | 81 | 64 |  | 4 | 49 | 49 | 55 | 83 | 83 | 83 | 82 | 82 | 82 | 82 | 82 |  | 82 | 82 | 82 | 82 | 82 | 82 | 82 | 1745016
| Kaptai 7 MW Solar PP | [6 empty] | 0 | 1 | 1 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 6602
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 37 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 39 | 38 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1094967
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 85 | 85 | 85 | 85 | 91 | 106 | 110 | 110 | 110 | 108 | 108 | 93 | 108 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 2498207
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 10 | [16 empty] | 2 |  | 43 | 86 | 85 | 10 |  |  | 0 | 201047
86 | Meghnaghat CCPP ( Summit) | 230 | 235 | 240 | 230 | 235 | 240 | 240 | 235 | 140 | 130 | 220 | 250 | 250 | 260 | 260 | 255 | 260 | 260 |  | 260 | 260 | 235 | 260 | 235 | 230 | 235 | 5544087
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 90 | 25 | [10 empty] | 1 | 28 | 44 | 100 | 104 | 104 |  | 104 | 104 | 104 | 104 | 80 |  | 0 | 967680
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 80 | 80 | 80 | 80 | 80 | 92 | 92 | 92 | 100 |  | 100 | 100 | 100 | 100 | 92 | 92 | 92 | 2175600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 |  | 9 | 30 | 43 | 43 | 43 | 43 | 43 | 43 |  | 30 | 10 | 10 |  | 23 | 40 | 43 | 43 | 43 | 51 | 51 | 983124
94 | Gagnagar 102 MW PP (Digital Power) | 64 | 7 | [9 empty] | 7 | 16 | 48 | 64 | 80 | 58 | 58 |  | 72 | 102 | 102 | 64 | 7 | 7 | 7 | 813168
95 | Patenga 50MW PP (Baraka) | 18 | 18 | [5 empty] | 1 | 7 | 11 | 11 | 11 | 11 | 11 | 11 | 27 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 30 | 589440
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 | 0 |  |  |  | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 30 | 15 | [10 empty] | 15 | 40 | 40 | 44 | 50 | 47 |  | 55 | 55 | 55 | 30 | 30 | 15 | 15 | 557051
100 | Manikganj 55 MW PP (Northern) | 17 | [11 empty] | 17 | 17 | 17 | 35 | 17 | 17 |  | 35 | 55 | 55 | 35 | 17 |  | 0 | 361507
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 110 | 110 |  | 110 | 163 | 163 | 163 | 163 | 163 | 163 | 3550990
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 8750
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 |  |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 718956
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 80 | 36 | 36 | 8 | [11 empty] | 8 | 8 | 8 |  | 43 | 186 | 186 | 192 | 183 | 182 | 182 | 1257600
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 101 | 98 | 80 | 46 | 11 |  |  | 25 | 52 | 50 | 50 | 50 | 50 | 50 | 50 | 110 | 120 | 120 |  | 128 | 149 | 149 | 140 | 115 | 102 | 93 | 1822460
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 60 | 30 | 30 | 30 | 30 | 55 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 80 |  | 100 | 100 | 100 | 100 | 100 | 20 | 20 | 1933440
116 | Chandpur 200MW (Desh energy) | 119 | 116 | 104 | 104 | 108 | 100 | 80 | 80 | 90 | 99 | 105 | 105 | 100 | 120 | 120 | 120 | 124 | 130 |  | 126 | 125 | 124 | 139 | 139 | 139 | 139 | 2746560
117 | Ashuganj 150MW PP (Midland) | 140 | 143 | 142 | 142 | 100 | 10 | 10 | 10 | 6 | 15 | 73 | 128 | 142 | 142 | 110 | 85 | 50 | 50 |  | 78 | 135 | 123 | 135 | 137 | 135 | 140 | 2363563
118 | Bibiyana-III 400 MW CCPP | 366 | 367 | 366 | 367 | 366 | 375 | 330 | 333 | 384 | 399 | 392 | 380 | 365 | 368 | 397 | 367 | 367 | 367 |  | 403 | 366 | 348 | 363 | 364 | 400 | 409 | 8951000
| Jamalpur 115 MW PP (United) | 107 | 108 | 108 | 108 | 75 | 8 | 8 | 24 | 24 | 32 | 64 | 115 | 115 | 115 | 107 | 107 | 107 | 107 |  | 108 | 106 | 108 | 107 | 107 | 107 | 106 | 2100000
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 10 | 10 | 10 | 10 | 10 |  |  |  |  | 10 | 30 | 50 | 60 | 60 | 60 | 60 | 60 | 10 |  | 50 | 50 | 50 | 50 | 30 | 30 | 10 | 688320
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 421527
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 9 | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 23 | 35 | 35 | 35 | 35 | 510480
| Spectra Solar Plant Ltd. | [6 empty] | 1 | 0 | 1 | 6 | 4 | 9 | 13 | 13 | 11 | 0 | 1 | 0 | [8 empty] | 62719
120 | Eastern Zone Total | 7457 | 6973 | 6693 | 6686 | 6162 | 5695 | 5449 | 5292 | 5295 | 5731 | 6216 | 6476 | 6616 | 6751 | 6583 | 6799 | 6527 | 6516 |  | 7273 | 7765 | 7784 | 7911 | 7438 | 7251 | 7064 | 159549096
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [17 empty] | 5 |  | 5 | 13 | 13 | 9 | 5 | 5 | 5 | 43200
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 105 | 70 | 70 | 17 |  |  | 53 | 51 | 53 | 53 | 53 | 70 | 90 | 90 | 53 | 35 | 35 |  | 55 | 105 | 105 | 105 | 105 | 105 | 53 | 1577568
130
131
132 | United Payra Power Ltd. | [19 empty] | 13 | 17 | 17 | 17 | 35 |  | 0 | 88800
133 | Bhola Nutan Biddut BD LTD (GAS) | [6 empty] | 16 | 41 | 41 | 100 | 210 | 218 | 218 | 129 | 230 | 234 | 233 | 236 |  | 233 | 234 | 234 | 233 | 200 | 226 | 226 | 3046036
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 80 | 80 | 48 | 48 | 16 | [14 empty] | 16 | 16 | 16 | 16 | 32 |  | 0 | 422784
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 95 | 95 | 95 | 95 | 96 | 73 | 73 | 55 | 32 | 32 | 15 | [8 empty] | 14 | 13 | 13 | 13 | 53 | 12 | 12 | 942833
| Bhola 225 MW CCPP | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 85 | 86 | 86 | 68 | 68 | 67 | 68 | 68 | 68 | 68 | 68 |  | 68 | 68 | 68 | 68 | 68 | 68 | 69 | 1816856
140 | Bhola 33 MW PP (Venture) | 33 | 32 | 32 | 32 | 27 | 27 | 17 | 15 | 20 | 23 | 25 | 23 | 10 | 8 | 5 | 11 | 10 | 17 |  | 24 | 26 | 25 | 26 | 29 | 30 | 29 | 517640
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 30 | [17 empty] | 0 | 60 | 20 | 31 |  |  | 0 | 221760
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 6 | 6 | [9 empty] | 9088
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 790 | 790 | 790 | 790 | 791 | 790 | 818 | 817 | 818 | 818 | 817 | 818 | 817 | 818 | 817 | 817 | 818 | 817 |  | 818 | 817 | 805 | 804 | 804 | 805 | 804 | 19338909
147 | Bheramara 410 MW CCPP | 350 | 350 | 405 | 410 | 410 | 380 | 410 | 355 | 385 | 395 | 370 | 375 | 355 | 355 | 390 | 350 | 350 | 300 |  | 375 | 380 | 380 | 370 | 360 | 350 | 350 | 9020736
148 | Payra 1320 MW | 500 | 500 | 510 | 510 | 510 | 460 | 420 | 430 | 400 | 370 | 340 | 340 | 340 | 340 | 320 | 280 | 280 | 280 |  | 300 | 410 | 410 | 410 | 420 | 390 | 350 | 10378900
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 151 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3676200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | [15 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 495024
| Sirajgonj 6.55 MW Solar | [9 empty] | 0 | 2 | 2 | 3 | 3 | 2 | 1 | 0 | 0 | [8 empty] | 13560
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 187 | 183 | 185 | 164 | 161 | 162 | 158 | 159 | 159 | 176 | 181 | 168 | 188 | 184 | 189 | 167 | 160 | 162 |  | 173 | 167 | 168 | 164 | 176 | 168 | 165 | 4311173
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 192 | 188 | 192 | 169 | 155 | 157 | 153 | 161 | 155 | 189 | 192 | 178 | 200 | 188 | 197 | 182 | 175 | 177 |  | 190 | 190 | 187 | 177 | 188 | 175 | 192 | 4562855
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 396 | 408 | 408 | 330 | 340 | 370 | 386 | 362 | 338 | 337 | 378 | 402 | 401 | 380 | 398 | 302 | 333 | 335 |  | 380 | 391 | 319 | 374 | 390 | 400 | 400 | 8959127
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 10 | 10 |  | 34 | 34 | 22 | 16 |  |  |  | 102174
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 492480
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 5 |  | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 197136
165 | Amnura 50 MW PP(Sinha) | 34 | 12 | [17 empty] | 12 | 24 | 42 | 42 |  |  | 0 | 168430
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 16 | 43 | 43 | 43 |  |  | 0 | 90405
167 | Katakhali 50 MW Peaking PP | [19 empty] | 33 | 38 | 41 | 38 | 38 | 38 | 0 | 197750
168 | Santahar 50 MW Peaking PP | 28 | [18 empty] | 15 | 26 | 27 | 27 | 26 | 26 | 26 | 180195
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 24 | 52 | 52 | 52 | 25 | 25 | 25 |  | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 1005600
170 | Chapainawabganj 100 MW Peaking PP | 88 | 88 | 88 | 88 | 50 | [14 empty] | 97 | 97 | 96 | 95 | 98 | 98 | 98 | 1030704
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 35 | 35 |  |  |  | 35 |  |  |  | 21 | 45 | 70 | 78 | 35 | 35 | 35 |  | 40 | 106 | 110 | 113 | 113 | 113 | 113 | 1373568
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 70 | [11 empty] | 10 | 35 | 70 | 35 | 35 |  | 50 | 110 | 113 | 113 | 113 | 113 | 113 | 1057920
173 | Rangpur 20 MW GTPP | 0 | [18 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 74 | 15 | [10 empty] | 34 | 34 | 35 | 70 | 34 | 36 |  | 97 | 114 | 113 | 113 | 113 | 113 | 113 | 1023120
177 | Sympa Solar Power 8MW | [8 empty] | 3 |  | 5 | 3 | 3 |  | 5 | 3 | 3 | [9 empty] | 34161
178
178