## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-03 | Thursday
|  |  | Date (day): | 2021-06-03 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14338.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15283 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-02 | 2021-06-03 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 99 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 |  |  | S/D for gas problem
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 172 | 212 | 280 | 300 | 60 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 300 | 260 | 280 | 300
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 35 | 74 | 85 | 85 |  | 15 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 181 | 177 | 200 | 200 |  |  | FGMO
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 42 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 25 | 0 | 250 | 300 |  | 35
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 84 | 102 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | Engine problem
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 45 | 45 | 45 |  | 35 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 33 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 195 | 245 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 302 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 100 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 102 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 122 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 83 | 84 | 83 | 83 |  | 22 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 84 | 104 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 126 | 144 | 144 |  | 18 | Engine problem
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 19 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2484 | 3214 | 3394 | 3704 | 389 | 1164
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 90 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 3 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 19 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 20 | 20 | 20 | 20 | 210 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 220 | 203 | 220 | 220
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 80 | 80 | 70 | 80
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 68 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 10 | 28
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 108 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 20 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 17 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 980 | 1110 | 1587 | 1607 | 588 | 123
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 125 | 125 | 125 | 125 | 4 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Machine problem.
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 164 | 217 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 355 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 0 | 300 | 360
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 25 | 49 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 82 | 68 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 70 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 80 | 72 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 120 | 120 | 140 | 140 |  | 60 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 124 | 154 | 152 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 100 | 100 | 100 | 100
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 115 | 119 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 35 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1635 | 1923 | 2151 | 2391 | 460 | 195
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 117 | 135 | 157 | 157 | 45 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20 |  | 2 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 16 | 16 | 16 | 16 |  | 79 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 31 | 193 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 1 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 343 | 503 | 581.6 | 530 | 45 | 81
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 44 | 44 |  | 26 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 161 | 160 | 163 | 163 |  | 160 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 56 | 56 |  | 10 | Engine problem
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 82 | 83 | 83 |  | 3 | Engine problem
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 191 | 218 | 210 | 210
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 320 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 410 | 366 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 7 | 7 | 7 |  | 3
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 370 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1866 | 1954 | 2005 | 2005 | 0 | 359
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 809 | 790 | 842 | 842
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 6 | 20 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 158 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 3 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 345 | 325 | 400 | 400
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  | 8 | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 2 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1165 | 1498 | 1577 | 1847 | 0 | 91
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 48 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 18 | 33 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 68 | 68 | 88 | 88 |  | 106 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 0 | 0 | 95 | 95
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 560 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 224 | 224 | 228 | 233 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 610 | 950 | 1176 | 1291 | 0 | 106
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 40 | 45 | 45 |  | 26 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 42 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 34 | 34 |  | 16 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 162 | 170 | 190 | 190 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 170 | 170 | 197 | 197 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 411 | 418 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 26 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 20 | 20
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 87 | 90 | 90
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 200 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 70 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1016 | 1591 | 1596 | 1625 | 381 | 82
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 8 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 56 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 212 | 271 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 10311 | 13014 | 14338.6 | 15283 | 1987 | 2391
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9808.6814 | 12380 | 13640.0698 | 14538.4617
| A. |  | 2021-06-02 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13014 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8407 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13014 | MW
| 3 | Day peak Generation : |  |  | 10311 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12380 | MW
| 4 | Evening peak Generation : |  |  | 13014 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 254.8772 | MKWHr | By Solar | 0.67795 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 146.1181 | MKWHr |  | By Oil: | 71.615 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.8041 | MKWHr |  | By Hydro: | 0.48 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1987 | MW | Dhaka | 4333 | 4333 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2391 | MW | Chittagong | 1190 | 1190 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4378 | MW | Khulna | 1569 | 1569 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1157.97 | MMCFD |  |  | Rajshahi | 1342 | 1342 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 154267642.558 | ii) Oil : | Taka | 590314489.29 | Comilla | 1240 | 1240 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 64366812 | Total | Taka | 808948943.848 | Mymensingh | 1013 | 1013 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.2995 | MKWHr. | Sylhet | 523 | 523 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -6 | MW (E to W) at | 21:00 | hrs | Barisal | 381 | 381 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -62 | MW at | 2:00 | hrs | Rangpur | 789 | 789 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.0° C |  |  | Total | 12380 | 12380 |  | 0
| B. |  | 2021-06-03 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15283 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11500 | MW
| 4 | Reserve(Generation end) |  |  |  | 1483 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 270.2709 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9686 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.2858 | MKWHr. | ii) HVDC Flow at Peak Time |  | 790 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8963 | MKWHr. | iii) Maximum HVDC Flow : |  | 809 | MW at | 6:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.47 |  | (b) Today: | 72.48 |  | (c) Rule Curve: |  | 76.52
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-02
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 251 |  | 0 | 280 | 230 | 0 | 0 | 15 | 220 | 0 | 100 | 0 | 7 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 21 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 94 | 0 |  | 24 | 0 | 68 | 92 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 315 | 0 | 220 | 83 | 75 | 23 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 25 | 21 | 112 | 156 | 16 | 20 | 0 | 44 | 42 | 53 | 0 | 130 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 160 | 0 | 92 | 0 | 20 | 139 | 142 | 409 | 107 | 83 | 105 | 0 | 0 | 54 | 51 | 100 | 111 | 10 | 400 | 0 | 0 | 54 | 0 | 0 | 35 | 0 |  | 782 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 69 | 29 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 168 | 0 | 12 | 0 | 197 | 0 | 424 | 17 | 0 | 70 | 0 | 38 | 0 | 0 | 70 | 350 | 227 | 0 | 0 | 0 |  | 6940 | 3178 | 10118 | 4232 | 782 | 2130 | 2066 | 499 | 20 | 277 | 112 | 0 | 0 | 72.47
2:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 262 |  | 0 | 280 | 235 | 0 | 0 | 0 | 221 | 0 | 100 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 21 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 216 | 0 | 135 | 0 |  | 24 | 0 | 51 | 92 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 310 | 0 | 220 | 83 | 76 | 23 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 25 | 21 | 98 | 156 | 16 | 20 | 0 | 44 | 42 | 50 | 0 | 130 | 163 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 62 | 0 | 20 | 139 | 142 | 407 | 107 | 83 | 105 | 0 | 0 | 54 | 51 | 100 | 110 | 10 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 783 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 69 | 27 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 0 | 199 | 0 | 402 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 350 | 227 | 0 | 0 | 0 |  | 6844 | 3031 | 9875 | 4282 | 783 | 2124 | 1809 | 499 | 20 | 260 | 98 | 0 | 0 | 72.47
3:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 276 |  | 0 | 280 | 230 | 0 | 0 | 0 | 221 | 0 | 100 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 0 | 0 |  | 24 | 0 | 51 | 92 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 345 | 0 | 219 | 83 | 76 | 23 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 25 | 21 | 96 | 156 | 16 | 20 | 0 | 44 | 42 | 50 | 0 | 163 | 163 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 46 | 0 | 20 | 123 | 100 | 408 | 107 | 83 | 105 | 0 | 0 | 54 | 51 | 100 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 782 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 69 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 0 | 199 | 0 | 418 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 228 | 0 | 0 | 0 |  | 6581 | 2957 | 9538 | 4176 | 782 | 2196 | 1525 | 499 | 20 | 244 | 96 | 0 | 0 | 72.47
4:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 287 |  | 0 | 280 | 235 | 0 | 0 | 0 | 220 | 0 | 100 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 0 | 216 | 0 | 0 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 340 | 0 | 219 | 83 | 75 | 23 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 25 | 21 | 96 | 155 | 16 | 20 | 0 | 44 | 42 | 50 | 0 | 163 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 40 | 0 | 10 | 123 | 10 | 408 | 108 | 83 | 105 | 0 | 0 | 54 | 51 | 100 | 112 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 783 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 199 | 0 | 422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 227 | 0 | 0 | 0 |  | 6304 | 2848 | 9152 | 4177 | 783 | 2198 | 1327 | 499 | 20 | 52 | 96 | 0 | 0 | 72.47
5:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 291 |  | 0 | 280 | 230 | 0 | 0 | 0 | 221 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 5 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 310 | 0 | 220 | 83 | 80 | 23 | 53 | 0 | 51 | 0 | 0 | 43 | 22 | 5 | 25 | 21 | 94 | 156 | 16 | 20 | 0 | 43 | 42 | 50 | 0 | 110 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 10 | 118 | 0 | 365 | 115 | 83 | 105 | 0 | 0 | 54 | 17 | 100 | 111 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 782 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 10 | 0 | 199 | 0 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 228 | 0 | 0 | 0 |  | 6125 | 2778 | 8903 | 4173 | 782 | 2113 | 1217 | 499 | 20 | 5 | 94 | 0 | 0 | 72.47
6:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 266 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 70 | 0 |  | 0 | 0 | 0 | 62 | 0 | 0 | 19 | 39 | 0 | 125 | 0 | 320 | 0 | 220 | 83 | 81 | 23 | 53 | 0 | 51 | 0 | 0 | 38 | 22 | 5 | 25 | 15 | 90 | 156 | 16 | 20 | 0 | 43 | 42 | 50 | 0 | 110 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 1 | 10 | 61 | 0 | 328 | 115 | 83 | 51 | 0 | 0 | 54 | 17 | 17 | 36 | 0 | 400 | 0 | 1 | 0 | 0 | 0 | 35 | 3 |  | 809 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 164 | 0 | 10 | 0 | 200 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 227 | 0 | 0 | 0 |  | 5716 | 2735 | 8451 | 4080 | 809 | 2063 | 930 | 449 | 20 | 5 | 90 | 5 | 0 | 72.47
7:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 226 |  | 0 | 280 | 235 | 0 | 0 | 0 | 180 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 21 | 25 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 217 | 0 | 70 | 0 |  | 0 | 0 | 0 | 66 | 0 | 0 | 19 | 40 | 0 | 125 | 0 | 345 | 0 | 218 | 83 | 80 | 23 | 53 | 0 | 51 | 0 | 0 | 25 | 22 | 5 | 25 | 15 | 92 | 156 | 16 | 20 | 1 | 44 | 42 | 50 | 0 | 110 | 164 | 62 | 78 | 0 | 164 | 18 | 0 | 7 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 10 | 17 | 0 | 364 | 75 | 83 | 51 | 0 | 0 | 54 | 17 | 17 | 40 | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 35 | 10 |  | 809 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 176 | 0 | 10 | 0 | 203 | 0 | 377 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 227 | 0 | 0 | 0 |  | 5657 | 2750 | 8407 | 4158 | 809 | 2030 | 825 | 449 | 20 | 5 | 92 | 19 | 0 | 72.47
8:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 197 |  | 0 | 280 | 240 | 0 | 0 | 0 | 180 | 0 | 155 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 25 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 70 | 0 |  | 1 | 0 | 0 | 80 | 0 | 0 | 19 | 8 | 0 | 125 | 0 | 310 | 0 | 214 | 83 | 80 | 23 | 53 | 0 | 51 | 0 | 0 | 34 | 21 | 5 | 25 | 12 | 102 | 156 | 16 | 20 | 0 | 44 | 42 | 50 | 0 | 163 | 163 | 62 | 10 | 0 | 164 | 18 | 0 | 7 | 310 | 16 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 10 | 25 | 2 | 329 | 84 | 83 | 72 | 1 | 0 | 54 | 17 | 100 | 105 | 0 | 400 | 0 | 12 | 0 | 0 | 0 | 35 | 14 |  | 809 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 12 | 0 | 197 | 0 | 417 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 280 | 228 | 0 | 0 | 1 |  | 5801 | 2807 | 8608 | 4085 | 809 | 2002 | 1125 | 430 | 20 | 5 | 102 | 30 | 0 | 72.47
9:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 186 |  | 0 | 280 | 255 | 0 | 0 | 15 | 217 | 0 | 155 | 8 | 2 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 21 | 25 | 33 | 5 | 0 | 0 | 20 | 100 | 0 | 17 | 207 | 0 | 70 | 0 |  | 6 | 0 | 0 | 92 | 0 | 0 | 19 | 5 | 0 | 125 | 0 | 325 | 0 | 187 | 83 | 80 | 23 | 52 | 0 | 51 | 0 | 0 | 43 | 21 | 5 | 25 | 12 | 96 | 147 | 16 | 20 | 1 | 44 | 42 | 50 | 0 | 163 | 162 | 62 | 0 | 0 | 164 | 17 | 0 | 7 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 2 | 100 | 85 | 56 | 375 | 107 | 83 | 105 | 2 | 0 | 54 | 35 | 100 | 110 | 50 | 400 | 0 | 23 | 2 | 0 | 0 | 35 | 24 |  | 809 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 12 | 0 | 197 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 280 | 229 | 0 | 0 | 1 |  | 6327 | 2810 | 9137 | 4144 | 809 | 1977 | 1568 | 430 | 20 | 37 | 96 | 56 | 0 | 72.48
10:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 172 |  | 0 | 280 | 265 | 0 | 0 | 30 | 212 | 0 | 185 | 30 | 7 | 115 | 6 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 21 | 25 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 217 | 0 | 70 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 3 | 0 | 125 | 0 | 345 | 0 | 177 | 82 | 80 | 20 | 51 | 0 | 43 | 0 | 0 | 43 | 21 | 8 | 25 | 18 | 112 | 132 | 16 | 0 | 2 | 44 | 42 | 47 | 0 | 163 | 163 | 61 | 0 | 0 | 164 | 17 | 0 | 7 | 320 | 16 | 5 | 0 | 15 | 0 | 0 | 5 | 0 | 74 | 2 | 100 | 100 | 122 | 402 | 115 | 83 | 105 | 1 | 0 | 54 | 100 | 100 | 110 | 60 | 397 | 11 | 38 | 32 | 8 | 0 | 35 | 22 |  | 808 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 186 | 0 | 409 | 0 | 0 | 4 | 0 | 0 | 0 | 3 | 0 | 280 | 226 | 0 | 0 | 3 |  | 6791 | 2793 | 9584 | 4155 | 808 | 1949 | 1899 | 430 | 20 | 140 | 112 | 71 | 0 | 72.48
11:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 172 |  | 0 | 280 | 275 | 0 | 0 | 50 | 215 | 0 | 182 | 32 | 70 | 150 | 30 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 80 | 0 |  | 0 | 0 | 0 | 80 | 0 | 1 | 19 | 2 | 0 | 125 | 0 | 310 | 0 | 160 | 82 | 80 | 20 | 25 | 0 | 43 | 0 | 0 | 43 | 21 | 8 | 25 | 18 | 112 | 131 | 16 | 0 | 2 | 42 | 42 | 50 | 0 | 130 | 163 | 61 | 0 | 0 | 164 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 145 | 0 | 0 | 24 | 0 | 112 | 3 | 100 | 120 | 123 | 367 | 115 | 83 | 105 | 3 | 0 | 54 | 108 | 100 | 117 | 30 | 380 | 54 | 48 | 98 | 17 | 0 | 35 | 23 |  | 808 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 68 | 19 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 12 | 0 | 170 | 0 | 378 | 0 | 0 | 60 | 0 | 34 | 0 | 3 | 0 | 280 | 224 | 0 | 0 | 2 |  | 7084 | 2852 | 9936 | 4017 | 808 | 1830 | 2429 | 430 | 20 | 206 | 112 | 84 | 0 | 72.48
12:00 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 172 |  | 0 | 280 | 300 | 0 | 0 | 55 | 25 | 0 | 181 | 42 | 84 | 150 | 35 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 80 | 0 |  | 1 | 0 | 0 | 80 | 0 | 19 | 21 | 2 | 0 | 125 | 0 | 350 | 0 | 164 | 82 | 80 | 20 | 25 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 124 | 117 | 16 | 17 | 3 | 42 | 42 | 50 | 0 | 130 | 161 | 61 | 78 | 0 | 191 | 18 | 0 | 0 | 300 | 8 | 5 | 0 | 195 | 0 | 0 | 31 | 0 | 122 | 3 | 100 | 120 | 132 | 410 | 106 | 83 | 105 | 4 | 0 | 54 | 108 | 100 | 115 | 30 | 370 | 84 | 52 | 108 | 17 | 0 | 35 | 19 |  | 809 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 170 | 0 | 411 | 2 | 0 | 70 | 0 | 56 | 0 | 6 | 70 | 300 | 224 | 0 | 0 | 2 |  | 7308 | 3003 | 10311 | 3946 | 809 | 1928 | 2736 | 450 | 20 | 209 | 124 | 89 | 0 | 72.48
13:00 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 172 |  | 0 | 280 | 285 | 0 | 0 | 55 | 0 | 0 | 183 | 50 | 102 | 150 | 50 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 211 | 0 | 80 | 0 |  | 22 | 0 | 0 | 80 | 0 | 41 | 21 | 2 | 0 | 125 | 0 | 315 | 0 | 163 | 82 | 80 | 20 | 25 | 0 | 51 | 0 | 41 | 43 | 21 | 8 | 25 | 20 | 122 | 117 | 16 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 161 | 61 | 76 | 0 | 205 | 18 | 0 | 0 | 310 | 8 | 5 | 0 | 210 | 0 | 0 | 80 | 0 | 146 | 5 | 100 | 120 | 135 | 380 | 106 | 83 | 105 | 3 | 0 | 54 | 110 | 100 | 116 | 30 | 391 | 104 | 47 | 117 | 17 | 0 | 35 | 32 |  | 806 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 3 | 4 | 0 | 68 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 170 | 0 | 408 | 30 | 0 | 95 | 0 | 70 | 0 | 5 | 113 | 330 | 224 | 0 | 0 | 2 |  | 7551 | 3139 | 10690 | 3872 | 806 | 1978 | 3068 | 480 | 20 | 248 | 122 | 96 | 0 | 72.49
14:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 172 |  | 0 | 280 | 285 | 0 | 0 | 55 | 0 | 0 | 152 | 50 | 102 | 147 | 50 | 0 | 0 | 0 | 35 | 55 | 35 | 19 | 25 | 19 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 80 | 0 |  | 24 | 0 | 0 | 92 | 0 | 42 | 21 | 2 | 0 | 125 | 0 | 310 | 0 | 176 | 88 | 80 | 23 | 25 | 0 | 51 | 0 | 41 | 43 | 21 | 8 | 25 | 20 | 136 | 116 | 16 | 17 | 1 | 42 | 42 | 50 | 0 | 163 | 161 | 60 | 79 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 227 | 0 | 0 | 70 | 0 | 149 | 7 | 100 | 120 | 134 | 371 | 115 | 83 | 105 | 2 | 0 | 54 | 108 | 100 | 115 | 30 | 393 | 104 | 46 | 126 | 17 | 0 | 35 | 27 |  | 805 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 42 | 16 | 0 | 52 | 0 | 20 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 170 | 0 | 406 | 60 | 0 | 95 | 0 | 105 | 0 | 6 | 113 | 340 | 224 | 0 | 0 | 3 |  | 7587 | 3249 | 10836 | 3845 | 805 | 1988 | 3218 | 490 | 20 | 242 | 136 | 92 | 0 | 72.49
15:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 186 |  | 0 | 280 | 290 | 0 | 0 | 55 | 0 | 0 | 181 | 70 | 102 | 150 | 62 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 19 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 80 | 0 |  | 24 | 0 | 0 | 92 | 0 | 46 | 21 | 2 | 0 | 110 | 0 | 340 | 0 | 184 | 88 | 81 | 23 | 25 | 0 | 51 | 0 | 41 | 43 | 21 | 8 | 25 | 20 | 136 | 115 | 8 | 17 | 1 | 42 | 42 | 47 | 0 | 163 | 160 | 54 | 79 | 0 | 219 | 18 | 0 | 7 | 310 | 16 | 8 | 0 | 227 | 74 | 0 | 70 | 0 | 149 | 9 | 100 | 120 | 132 | 397 | 115 | 0 | 105 | 2 | 0 | 54 | 108 | 100 | 116 | 50 | 389 | 104 | 16 | 126 | 17 | 0 | 35 | 21 |  | 805 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0 | 68 | 23 | 0 | 0 | 0 | 0 | 50 | 1 | 0 | 42 | 32 | 0 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 17 | 170 | 0 | 401 | 87 | 0 | 110 | 0 | 105 | 0 | 0 | 113 | 400 | 221 | 0 | 0 | 2 |  | 7704 | 3351 | 11055 | 3908 | 805 | 1997 | 3336 | 549 | 20 | 253 | 136 | 51 | 0 | 72.49
16:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 191 |  | 0 | 280 | 275 | 0 | 0 | 55 | 0 | 0 | 115 | 98 | 102 | 150 | 84 | 0 | 0 | 0 | 35 | 55 | 35 | 16 | 25 | 19 | 33 | 0 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 80 | 0 |  | 23 | 0 | 0 | 92 | 0 | 43 | 19 | 2 | 0 | 110 | 0 | 310 | 0 | 190 | 88 | 80 | 20 | 25 | 0 | 51 | 0 | 49 | 43 | 21 | 8 | 25 | 20 | 134 | 147 | 15 | 17 | 1 | 42 | 42 | 52 | 0 | 163 | 160 | 55 | 81 | 0 | 219 | 18 | 0 | 7 | 295 | 16 | 8 | 0 | 227 | 0 | 0 | 108 | 25 | 149 | 0 | 100 | 120 | 137 | 368 | 115 | 83 | 105 | 1 | 0 | 40 | 108 | 100 | 120 | 30 | 395 | 104 | 15 | 126 | 17 | 0 | 35 | 12 |  | 805 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 18 | 6 | 0 | 68 | 22 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 42 | 43 | 16 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 25 | 170 | 0 | 396 | 105 | 0 | 103 | 0 | 113 | 0 | 4 | 113 | 420 | 224 | 0 | 0 | 1 |  | 7644 | 3444 | 11088 | 3778 | 805 | 1993 | 3459 | 569 | 20 | 296 | 134 | 34 | 0 | 72.49
17:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 197 |  | 0 | 280 | 250 | 0 | 0 | 55 | 0 | 0 | 105 | 100 | 102 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 18 | 25 | 19 | 33 | 25 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 80 | 0 |  | 20 | 0 | 0 | 92 | 0 | 44 | 21 | 3 | 0 | 110 | 0 | 310 | 0 | 173 | 117 | 78 | 23 | 25 | 0 | 51 | 0 | 49 | 43 | 21 | 0 | 25 | 20 | 130 | 147 | 15 | 20 | 1 | 42 | 42 | 53 | 0 | 130 | 161 | 56 | 80 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 8 | 0 | 227 | 0 | 0 | 130 | 0 | 149 | 2 | 100 | 120 | 138 | 368 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 111 | 10 | 400 | 104 | 12 | 126 | 17 | 0 | 35 | 8 |  | 806 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 18 | 7 | 0 | 68 | 21 | 0 | 0 | 0 | 0 | 50 | 39 | 21 | 42 | 8 | 38 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 170 | 0 | 398 | 70 | 0 | 35 | 0 | 34 | 0 | 3 | 35 | 400 | 223 | 0 | 0 | 0 |  | 7607 | 3180 | 10787 | 3782 | 806 | 1991 | 3110 | 550 | 20 | 372 | 130 | 26 | 0 | 72.49
18:00 | 0 | 0 | 0 | 185 | 0 | 42 | 0 | 0 | 216 |  | 0 | 280 | 275 | 0 | 0 | 40 | 0 | 0 | 115 | 100 | 64 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 25 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 0 | 80 | 0 | 46 | 21 | 6 | 0 | 110 | 0 | 310 | 0 | 189 | 78 | 81 | 20 | 30 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 25 | 20 | 120 | 147 | 15 | 20 | 0 | 42 | 42 | 14 | 0 | 110 | 161 | 56 | 40 | 0 | 219 | 18 | 0 | 7 | 285 | 16 | 8 | 0 | 227 | 0 | 0 | 130 | 0 | 122 | 0 | 30 | 120 | 90 | 330 | 85 | 83 | 105 | 0 | 0 | 54 | 70 | 70 | 121 | 10 | 400 | 86 | 3 | 126 | 17 | 0 | 35 | 1 |  | 806 | 0 | 315 | 0 | 0 | 40 | 0 | 0 | 18 | 0 | 0 | 68 | 21 | 0 | 0 | 0 | 0 | 50 | 39 | 88 | 42 | 8 | 38 | 16 | 11 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 170 | 0 | 353 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 390 | 224 | 0 | 0 | 0 |  | 7081 | 3165 | 10246 | 3771 | 806 | 1777 | 2725 | 540 | 20 | 482 | 120 | 5 | 0 | 72.49
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 216 |  | 0 | 280 | 280 | 0 | 0 | 42 | 0 | 0 | 150 | 98 | 80 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 15 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 217 | 0 | 80 | 0 |  | 24 | 0 | 85 | 80 | 0 | 45 | 21 | 8 | 0 | 125 | 0 | 330 | 0 | 212 | 68 | 80 | 23 | 30 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 25 | 20 | 152 | 143 | 15 | 20 | 0 | 42 | 42 | 23 | 0 | 110 | 160 | 56 | 82 | 0 | 219 | 18 | 0 | 7 | 290 | 16 | 8 | 145 | 232 | 102 | 90 | 189 | 101 | 135 | 0 | 100 | 120 | 90 | 399 | 96 | 84 | 105 | 0 | 0 | 54 | 87 | 100 | 114 | 40 | 393 | 83 | 0 | 126 | 17 | 0 | 35 | 0 |  | 805 | 0 | 310 | 0 | 0 | 135 | 0 | 0 | 18 | 0 | 0 | 86 | 31 | 18 | 0 | 0 | 0 | 50 | 44 | 88 | 42 | 43 | 38 | 52 | 27 | 21 | 0 | 8 | 0 | 0 | 149 | 15 | 0 | 0 | 0 | 150 | 0 | 0 | 20 | 170 | 0 | 378 | 53 | 100 | 52 | 0 | 100 | 0 | 0 | 100 | 400 | 224 | 0 | 2 | 0 |  | 8166 | 3729 | 11895 | 3954 | 805 | 1914 | 3803 | 549 | 20 | 698 | 152 | 0 | 0 | 72.49
19:30 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 216 |  | 0 | 280 | 280 | 0 | 0 | 55 | 6 | 0 | 183 | 100 | 93 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 208 | 0 | 80 | 0 |  | 24 | 0 | 85 | 80 | 0 | 47 | 21 | 14 | 0 | 125 | 0 | 320 | 0 | 213 | 68 | 80 | 23 | 49 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 25 | 20 | 154 | 132 | 15 | 20 | 0 | 42 | 42 | 53 | 0 | 110 | 162 | 56 | 83 | 0 | 219 | 18 | 0 | 7 | 300 | 16 | 11 | 200 | 232 | 303 | 100 | 189 | 101 | 135 | 0 | 100 | 123 | 90 | 374 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 113 | 20 | 398 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 805 | 0 | 315 | 0 | 0 | 158 | 0 | 0 | 21 | 0 | 0 | 68 | 32 | 48 | 0 | 0 | 0 | 50 | 40 | 88 | 42 | 43 | 38 | 52 | 27 | 21 | 0 | 8 | 0 | 0 | 149 | 15 | 0 | 0 | 0 | 163 | 0 | 0 | 100 | 170 | 0 | 404 | 90 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 224 | 0 | 17 | 0 |  | 8577 | 4217 | 12794 | 3953 | 805 | 2010 | 4493 | 639 | 20 | 720 | 154 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 217 |  | 0 | 280 | 280 | 0 | 0 | 55 | 6 | 0 | 181 | 100 | 102 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 19 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 85 | 80 | 0 | 47 | 21 | 17 | 0 | 125 | 0 | 310 | 0 | 213 | 68 | 81 | 23 | 49 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 25 | 20 | 152 | 132 | 15 | 20 | 0 | 42 | 42 | 52 | 0 | 163 | 162 | 56 | 83 | 0 | 218 | 18 | 0 | 7 | 305 | 16 | 11 | 200 | 245 | 303 | 100 | 191 | 101 | 149 | 0 | 100 | 120 | 90 | 366 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 115 | 20 | 399 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 804 | 0 | 325 | 0 | 0 | 150 | 0 | 0 | 21 | 0 | 0 | 68 | 32 | 48 | 0 | 0 | 0 | 50 | 41 | 87 | 42 | 43 | 40 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 160 | 0 | 0 | 100 | 170 | 0 | 414 | 90 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 224 | 0 | 17 | 0 |  | 8649 | 4252 | 12901 | 3936 | 804 | 2081 | 4530 | 670 | 20 | 708 | 152 | 0 | 0 | 72.49
21:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 212 |  | 0 | 280 | 260 | 0 | 0 | 55 | 0 | 0 | 177 | 100 | 102 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 21 | 28 | 0 | 125 | 0 | 355 | 0 | 217 | 68 | 72 | 23 | 49 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 33 | 20 | 154 | 135 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 160 | 56 | 82 | 0 | 218 | 18 | 0 | 7 | 320 | 16 | 11 | 200 | 245 | 302 | 100 | 193 | 102 | 149 | 0 | 100 | 120 | 70 | 366 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 119 | 20 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 790 | 0 | 325 | 0 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 68 | 33 | 48 | 0 | 0 | 0 | 50 | 40 | 87 | 42 | 43 | 38 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 418 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 8704 | 4310 | 13014 | 3987 | 790 | 2108 | 4535 | 710 | 20 | 710 | 154 | 0 | 0 | 72.49
22:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 212 |  | 0 | 280 | 260 | 0 | 0 | 55 | 0 | 0 | 181 | 100 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 21 | 33 | 0 | 125 | 0 | 310 | 0 | 217 | 68 | 72 | 23 | 49 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 33 | 20 | 152 | 135 | 15 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 162 | 56 | 82 | 0 | 219 | 18 | 0 | 7 | 320 | 16 | 11 | 200 | 245 | 305 | 100 | 200 | 102 | 149 | 0 | 100 | 120 | 70 | 366 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 112 | 20 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 790 | 0 | 330 | 0 | 0 | 159 | 0 | 0 | 20 | 0 | 0 | 67 | 33 | 48 | 0 | 0 | 0 | 50 | 36 | 87 | 42 | 43 | 38 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 5 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 407 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 223 | 0 | 17 | 0 |  | 8670 | 4306 | 12976 | 3953 | 790 | 2101 | 4536 | 720 | 20 | 704 | 152 | 0 | 0 | 72.49
23:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 221 |  | 0 | 280 | 273 | 0 | 0 | 55 | 0 | 0 | 180 | 100 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 21 | 36 | 0 | 125 | 0 | 310 | 0 | 216 | 68 | 73 | 23 | 51 | 0 | 5 | 0 | 48 | 43 | 21 | 5 | 33 | 20 | 156 | 144 | 15 | 19 | 0 | 42 | 42 | 50 | 0 | 163 | 163 | 56 | 82 | 0 | 219 | 18 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 302 | 100 | 193 | 101 | 149 | 0 | 100 | 120 | 0 | 367 | 115 | 84 | 105 | 0 | 0 | 54 | 108 | 100 | 112 | 20 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 778 | 0 | 335 | 0 | 0 | 160 | 0 | 0 | 20 | 0 | 0 | 68 | 33 | 48 | 0 | 0 | 0 | 50 | 36 | 87 | 42 | 43 | 38 | 52 | 25 | 21 | 0 | 8 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 415 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 224 | 0 | 17 | 0 |  | 8572 | 4314 | 12886 | 3973 | 778 | 2055 | 4475 | 720 | 20 | 709 | 156 | 0 | 0 | 72.49
24:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 232 |  | 0 | 280 | 275 | 0 | 0 | 55 | 0 | 0 | 180 | 100 | 102 | 150 | 73 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 |  | 24 | 0 | 68 | 100 | 0 | 50 | 21 | 29 | 0 | 125 | 0 | 310 | 0 | 218 | 68 | 75 | 23 | 51 | 0 | 5 | 0 | 48 | 43 | 21 | 5 | 33 | 21 | 154 | 151 | 15 | 19 | 0 | 42 | 42 | 47 | 0 | 163 | 162 | 62 | 82 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 11 | 200 | 245 | 305 | 100 | 193 | 100 | 149 | 0 | 100 | 140 | 0 | 365 | 115 | 84 | 105 | 0 | 0 | 54 | 108 | 100 | 108 | 20 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 779 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 68 | 33 | 48 | 0 | 0 | 0 | 50 | 36 | 87 | 42 | 43 | 38 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 10 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 409 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 223 | 0 | 17 | 0 |  | 8588 | 4139 | 12727 | 3998 | 779 | 2049 | 4494 | 700 | 20 | 533 | 154 | 0 | 0 | 72.49
KWH | 0 | 0 | 0 | 4441500 | 0 | 2221590 | 0 | 0 | 5224000 |  | 0 | 6647750 | 6165673 | 0 | 0 | 822690 | 2581856 | 0 | 3723000 | 1230720 | 1357 | 2351040 | 956099 | 0 | 0 | 0 | 875520 | 759491 | 803240 | 425016 | 600000 | 476100 | 710300 | 794200 | 759360 | 0 | 0 | 480000 | 2400000 | 0 | 395377 | 4716777 | 0 | 1690085 | 0 |  | 396000 | 0 | 648241 | 2045760 | 0 | 586560 | 472224 | 472800 | 0 | 2948710 | 0 | 8172200 | 0 | 4844000 | 1973818 | 1855390 | 497952 | 1050720 | 0 | 1163285 | 0 | 546432 | 1023374 | 503244 | 104760 | 619100 | 472430 | 2896320 | 3295640 | 357120 | 374364 | 13500 | 1014000 | 997080 | 1146000 | 0 | 3556636 | 3593000 | 1432224 | 1540800 | 0 | 4818740 | 402000 | 0 | 149940 | 7408500 | 356328 | 210240 | 1033344 | 3184035 | 1571067 | 525088 | 2275200 | 583257 | 2521008 | 33750 | 1611840 | 2641920 | 2085890 | 9085000 | 2556000 | 2002800 | 2467272 | 25799 | 0 | 1286005 | 1985525 | 2225280 | 2608200 | 515520 | 9489500 | 1432320 | 327220 | 1882080 | 258436 | 0 | 889200 | 215038 |  | 19285818 | 0 | 8372736 | 0 | 0 | 822819 | 0 | 0 | 235630 | 23296 | 0 | 1654093 | 572671 | 250080 | 0 | 0 | 0 | 876139 | 291943 | 926784 | 445280 | 319808 | 283850 | 1027680 | 160658 | 480240 | 0 | 188964 | 0 | 0 | 3657100 | 52000 | 0 | 0 | 0 | 4215791 | 0 | 140350 | 636480 | 4726309 | 0 | 9675100 | 1046880 | 1068392 | 1503936 | 0 | 1278278 | 0 | 41520 | 1408512 | 10147000 | 5419009 | 0 | 91200 | 21120 |  | 173529767 | 81347466 | 254877233 | 97274853 | 19285818 | 48843209 | 64396154 | 13804100 | 480000 | 7218832 | 2896320 | 677947 | 0
Fuel Cost | 0 | 0 | 0 | 6529005 | 0 | 2932498.8 | 0 | 0 | 5380720 |  | 0 | 7246047.5 | 6843897.03 | 0 | 0 | 6959957.4 | 2685130.24 | 0 | 6440790 | 9267321.6 | 12375.84 | 23134233.6 | 8815232.78 | 0 | 0 | 0 | 6391296 | 5870865.43 | 7919946.4 | 318762 | 450000 | 0 | 0 | 0 | 7343011.2 | 0 | 0 | 129600 | 4344000 | 0 | 3673052.33 | 5141286.93 | 0 | 2873144.5 | 0 |  | 0 | 0 | 6287937.7 | 19537008 | 0 | 4645555.2 | 595002.24 | 1404216 | 0 | 4364090.8 | 0 | 6047428 | 0 | 4456480 | 2546225.22 | 2133698.5 | 562685.76 | 1471008 | 0 | 1989217.35 | 0 | 5518963.2 | 9773221.7 | 639119.88 | 78570 | 1083425 | 354322.5 | 21722400 | 3493378.4 | 3242649.6 | 475442.28 | 215190 | 1662960 | 1595328 | 2039880 | 0 | 4054565.04 | 3736720 | 2821481.28 | 2942928 | 0 | 8336420.2 | 880380 | 0 | 305877.6 | 7482585 | 267246 | 159782.4 | 17577181.44 | 24071304.6 | 26676717.66 | 8779471.36 | 11831040 | 9752057.04 | 24806718.72 | 394537.5 | 13136496 | 28664832 | 14705524.5 | 8449050 | 23310720 | 18926460 | 21489939.12 | 0 | 0 | 11201103.55 | 17452764.75 | 22208294.4 | 22352274 | 3433363.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 111086311.68 | 0 | 8791372.8 | 0 | 0 | 11404271.34 | 0 | 0 | 2471758.7 | 244142.08 | 0 | 1869125.09 | 887640.05 | 2440780.8 | 0 | 0 | 0 | 8621207.76 | 2966140.88 | 8202038.4 | 3428656 | 4323804.16 | 2750506.5 | 9958219.2 | 1558382.6 | 922060.8 | 0 | 143045.748 | 0 | 0 | 19821482 | 1801800 | 0 | 0 | 0 | 5564844.12 | 0 | 210525 | 10826524.8 | 5529781.53 | 0 | 9578349 | 10929427.2 | 18173347.92 | 14272352.64 | 0 | 9919437.28 | 0 | 458796 | 10408903.68 | 44545330 | 0 | 0 | 0 | 0 |  | 598845413.27 | 344110365.758 | 942955779.028 | 102873299.198 | 111086311.68 | 51394343.36 | 515353106.53 | 64366812 | 129600 | 74961382.76 | 21722400 | 1068523.5 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 172 |  | 0 | 280 | 300 | 0 | 0 | 55 | 25 | 0 | 181 | 42 | 84 | 150 | 35 | 0 | 0 | 0 | 35 | 55 | 17 | 19 | 25 | 21 | 25 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 80 | 0 |  | 1 | 0 | 0 | 80 | 0 | 19 | 21 | 2 | 0 | 125 | 0 | 350 | 0 | 164 | 82 | 80 | 20 | 25 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 20 | 124 | 117 | 16 | 17 | 3 | 42 | 42 | 50 | 0 | 130 | 161 | 61 | 78 | 0 | 191 | 18 | 0 | 0 | 300 | 8 | 5 | 0 | 195 | 0 | 0 | 31 | 0 | 122 | 3 | 100 | 120 | 132 | 410 | 106 | 83 | 105 | 4 | 0 | 54 | 108 | 100 | 115 | 30 | 370 | 84 | 52 | 108 | 17 | 0 | 35 | 19 |  | 809 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 6 | 3 | 0 | 68 | 18 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 170 | 0 | 411 | 2 | 0 | 70 | 0 | 56 | 0 | 6 | 70 | 300 | 224 | 0 | 0 | 2 |  | 10311 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 212 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 0 | 0 | 177 | 100 | 102 | 150 | 74 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 80 | 0 | 0 | 24 | 0 | 85 | 100 | 0 | 50 | 21 | 28 | 0 | 125 | 0 | 355 | 0 | 217 | 68 | 72 | 23 | 49 | 0 | 51 | 0 | 48 | 43 | 21 | 0 | 33 | 20 | 154 | 135 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 160 | 56 | 82 | 0 | 218 | 18 | 0 | 7 | 320 | 16 | 11 | 200 | 245 | 302 | 100 | 193 | 102 | 149 | 0 | 100 | 120 | 70 | 366 | 115 | 84 | 105 | 0 | 0 | 54 | 110 | 100 | 119 | 20 | 400 | 104 | 0 | 126 | 17 | 0 | 35 | 0 |  | 790 | 0 | 325 | 0 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 68 | 33 | 48 | 0 | 0 | 0 | 50 | 40 | 87 | 42 | 43 | 38 | 52 | 26 | 21 | 0 | 8 | 0 | 0 | 150 | 8 | 0 | 0 | 0 | 170 | 0 | 0 | 100 | 170 | 0 | 418 | 105 | 200 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 224 | 0 | 17 | 0 |  | 13014 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 300 | 0 | 0 | 280 | 300 | 0 | 0 | 55 | 300 | 0 | 200 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 80 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 22 | 28 | 0 | 125 | 0 | 360 | 360 | 220 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 181 | 157 | 16 | 20 | 0 | 44 | 42 | 51 | 0 | 163 | 163 | 56 | 83 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 140 | 150 | 400 | 115 | 83 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 144 | 116 | 0 | 35 |  |  | 842 | 0 | 400 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 90 | 35 | 34 | 40 | 52 | 35 | 20 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 190 | 0 | 95 | 100 | 197 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 233 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 280 | 0 | 0 | 280 | 280 | 0 | 0 | 55 | 250 | 0 | 200 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 70 | 0 | 0 | 22 |  | 68 | 100 | 0 | 50 | 22 | 10 | 0 | 125 | 0 | 360 | 300 | 220 | 8 | 90 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 152 | 157 | 16 | 20 | 1.6 | 44 | 42 | 51 | 0 | 163 | 163 | 56 | 83 | 0 | 210 | 18 | 0 | 7 | 341 | 16 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 140 | 150 | 400 | 115 | 83 | 105 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 50 | 144 | 116 | 0 | 35 | 30 |  | 842 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 45 | 90 | 35 | 34 | 40 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 95 | 50 | 197 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 228 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 273 | 0 | 0 | 280 | 280 | 0 | 0 | 40 | 0 | 0 | 120 | 50 | 16 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 20 | 25 | 21 | 33 |  | 30 | 0 | 0 | 20 | 100 | 0 | 17 | 204 | 0 | 80 | 0 | 0 | 24 | 0 | 51 | 92 | 0 | 23 | 21 | 7 | 0 | 125 | 0 | 275 | 75 | 184 | 8 | 51 | 23 | 53 | 0 | 5 | 0 | 0 | 43 | 21 | 5 | 33 | 21 | 110 | 153 | 16 | 19 | 1 | 43 | 42 | 47 | 0 | 110 | 162 | 56 | 83 | 0 | 218 | 18 | 0 | 7 | 285 | 16 | 8 | 0 | 109 | 0 | 0 | 45 | 0 | 104 | 10 | 40 | 121 | 0 | 307 | 115 | 82 | 105 | 3 | 0 | 54 | 110 | 100 | 111 | 10 | 370 | 53 | 9 | 89 | 17 | 0 | 35 | 7 | 0 | 827 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 12 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 0 | 0 | 179 | 0 | 310 | 105 | 0 | 65 | 0 | 34 | 0 | 2 | 35 | 400 | 225 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8407 | 7:00
| Highest Generation |  | 13014 | 21:00
| Day Peak Generation |  | 10311 | 12:00
| Evening Peak Generation |  | 13014 | 21:00
| HVDC Max Flow |  | 809 | 6:00
| HVDC EvPeak Flow |  | 790 | 21:00
| Load factor L.F |  | 81.6%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-03
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-02 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10311 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9686 | MW
Evening Peak Generation : |  | 13014 | MW Hour : | 21:00 | Available Max Generation : |  | 15283 | MW
E.P. Demand (at gen end) : |  | 13014 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 13014 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1483 | MW
Total Gen. (MKWH) : |  | 254.8772 | System Load Factor : | 81.6% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -62 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-03
Actual : | 72.48 | Ft.(MSL) , | Rule curve : | 76.52 | Ft.( MSL )
Gas Consumed : | Total = | 1157.97 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 154267642.558
: |  | Coal : | 64366812 | Oil : | 590314489.29 | Total : | 808948943.848
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4875.7448 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1664.7497 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1492.7591 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1349.2593 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1219.0715 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 983.7645 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 541.4166 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 253.0638 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 758.7694 |  |  | 0 | 0%
Total | 0 |  | 13138.5988 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3
4) Kaptai-2
5) Raozan #1,2
6) Sylhet-225 MW ST
7) Bhola 225 MW GT-2
8) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Meghnaghat 230 kV Ckt-2 was under shut down from 10:29 to 19:27 for C/M.
b) Kishoreganj 132/33 kV T1 transformer was under shut down from 08:32 to 15:28 for C/M.
c) Rampura-Bhulta 230 kV Ckt-3 was under shut down from 08:27 to 15:16 for C/M.
d) Tangail 132/33 kV T1 transformer was under shut down from 12:22 to 12:28 for harmonic test .
e) Tangail 132/33 kV T3 transformer was under shut down from 13:25 to 14:10 for harmonic test .
f) Chandraghona-Rangamati 132 kV Ckt-2 was under shut down from 14:32 to 16:47 for protection test.
g) Dohazari-Cox's Bazar 132 kV Ckt-2 was switched on test 16:37.
h) Ramganj 132/33 kV T2 transformer was under shut down from 16:07 to 17:31 for red hot maintenance |  |  |  |  | About 40MW power interruption occurred under Ramganj S/S areas
at 33 kV PBS feeder . |  |  |  |  | from 16:07 to 17:31
i) Chandraghona 132 kV bus coupler was switched on at 16:38.
j) Siddhirganj 335 MW GT was synchronized at 19:20.
k) Mongla 132/33 kV T2 transformer was under shut down from 14:21 to 15:38 for C/M. |  |  |  |  | About 15 MW power interruption occurred under Mongla S/S areas
from 14:21 to 15:38
l) Dhamrai-Kaliakoir 132 kV Ckt-2 was under shut down since at 06:05(03-06-2021) for D/W.
m) Ghorasal 230 kV bus coupler-2 was under shut down since 06:47 for C/M.
n) Hathazari 132/33 kV T2 transformer was under shut down since 06:28(03-06-2021) for C/M.
o) Ghorasal-Joydevpur 132 kV Ckt-1 tripped at 06:35 from Joydevpur end due to DC MCB fail and was |  |  |  |  | About 30 MW power interruption occurred under Joydevpur S/S areas
switched on at 06:38. |  |  |  |  | from 06:35 to 06:38
p) Joydevpur-Kodda 132 kV Ckt-1,2 was under shut down since 06:13 due to red hot maintenance at
different points.
q) Ashuganj south GT was synchronized at 04:26(03-06-2021).
r) Mongla 132/33 kV T1,T2 transformer tripped at 04:00 from 33 kV side showing instantaneous E/F relay |  |  |  |  | About 36 MW power interruption occurred under Mongla S/S areas
and were switched on at 04:57(3-6-2021) |  |  |  |  | from 04:00 to 04:57
s) Dohazari-Cox's Bazar 132 kV Ckt-1 was under shut down since 07:09(03-06-2021) for D/W.
t) Jamalpur-UMPL 132 kV Ckt-2 was under shut down since 07:13(03-06-2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-02 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4441500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 2221590
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Gas shortage
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 212 | 5224000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6647750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6165673 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 822690
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 74 | 956099 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 425016
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 177 | 3723000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1230720
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 0 | 2581856 | Under Maint.
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1357
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 875520 | Engine problem
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2351040
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 759491
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 803240
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 45 | 1076100 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 710300
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 794200
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 33 | 759360 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 245 | 3184035 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 302 | 1571067
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 525088
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 102 | 583257
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 2521008
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 84 | 2002800 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1432320
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1882080 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 215038
| Dhaka area Total |  |  |  | 5919 | 3214 | 56487195
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 395377 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 33750
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 586560
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 480000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4716777 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 80 | 1690085
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2467272
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 648241 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2045760
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1611840
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 472224
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 472800
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 25799
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1286005
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1985525
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 20 | 515520 | Line O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 258436 | Line O/L
| Chattogram area Total |  |  |  | 2382 | 1110 | 22091971
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 125 | 2948710
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 217 | 4844000
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 355 | 8172200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 0 | 0 | Under maint.
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 497952 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 1050720
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 68 | 1973818 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1163285
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 70 | 2085890 | 230 kV line red hot.
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 546432
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 72 | 1855390 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 120 | 2641920 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 503244
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 104760 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 154 | 2896320
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 619100
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1023374 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 472430 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1033344
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2225280 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 119 | 2608200
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 889200 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1923 | 40155569
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 135 | 3295640 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 374364
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 357120 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13500
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 2275200
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2556000
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 327220
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 396000
| Mymensingh Area Total |  |  |  | 709 | 503 | 9595044
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1014000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 997080 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3556636
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3593000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1146000
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210240
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1432224
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 82 | 1540800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4818740
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 402000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 356328 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7408500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 366 | 9085000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 149940 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9489500 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1954 | 45199988
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 790 | 19285818
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 235630 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 158 | 822819 | Low demand
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 23296 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 325 | 8372736 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 636480
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1046880
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1498 | 30423659
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 48 | 250080 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 572671
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 68 | 1654093 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 0 | 140350 | Machine problem
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 560 | 10147000
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 224 | 5419009 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 91200 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 950 | 18274403
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 876139
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 291943
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 42 | 445280 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 319808 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 283850 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4215791 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 4726309 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 418 | 9675100 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 26 | 160658 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 480240
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 188964 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1027680
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 926784 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 200 | 1068392
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1503936
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1408512
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 21120
| Rajshahi Area Total |  |  |  | 2179 | 1591 | 27620506
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3657100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 8 | 52000 | Machine problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1278278
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41520
| Rangpur Area Total |  |  |  | 605 | 271 | 5028898
| Total |  |  |  | 21315 | 13014 | 254877233
| Eastern Grid Total |  |  |  | 14421 | 8704 | 173529767
| Western Grid Total |  |  |  | 6894 | 4310 | 81347466
| National Grid Total |  |  |  | 21315 | 13014 | 254877233
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-02
(a) ENTIRE EASTERN GRID : |  | 8299 | MW | (b) ENTIRE WESTERN GRID : |  | 4081 | MW
i) Dhaka area |  | 4333 | MW | i) Khulna area |  | 1569 | MW
ii) Chittagong area |  | 1190 | MW | ii) Rajshahi area |  | 1342 | MW
iii) Comilla area |  | 1240 | MW | iii) Barisal area |  | 381 | MW
iv) Mymensingh area |  | 1013 | MW | iv) Rangpur area |  | 789 | MW
v) Sylhet area |  | 523 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12380 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 19:00 | Kishoreganj | 130 | 20:00 | Jessore | 110 | 20:00
Munsiganj | 94 | 21:00 | Netrokona | 114 | 24:00 | Benapol | 60 | 20:00
Sonargaon | 60 | 21:00 | Jamalpur | 151 | 20:00 | Jhenida | 112 | 21:00
Shyampur | 196 | 15:00 | Sherpur | 130 | 23:00 | Bottail | 142 | 19:30
Bhulta | 215 | 0:00 | Srimongal | 55 | 21:00 | G.K Project | 63 | 21:00
Madanganj | 56 | 16:00 | Shahjibazar | 122 | 22:00 | Faridpur | 203 | 22:00
Shitalakhya | 111 | 17:00 | Fenchuganj | 47 | 19:00 | Madaripur | 102 | 22:00
Rahim steel | 22 | 7:00 | Kulawara | 46 | 19:00 | Sariatpur | 68 | 21:00
Matuail | 60 | 10:00 | Sylhet | 124 | 19:00 | Gopalganj | 98 | 20:00
Ghorasal | 78 | 23:00 | Chatak | 29 | 19:30 | Bagerhat | 106 | 21:00
Narsingdi | 178 | 23:00 | Sunamganj | 51 | 21:00 | Mongla | 36 | 19:30
Haripur (SBU) | 116 | 12:00 | Biani Bazar | 63 | 19:00 | Satkhira | 112 | 20:00
Sreenagar | 42 | 21:00 | Comilla (S) | 156 | 23:00 | Gallamari | 36 | 20:00
Ullon | 66 | 23:00 | Comilla(N) | 153 | 21:00 | Magura | 58 | 19:30
Hasnabad | 79 | 19:30 | Chandpur | 80 | 22:00 | Norail | 47 | 19:30
Magbazar | 99 | 15:00 | Feni | 129 | 19:30 | Chuadanga | 91 | 21:00
Maniknagar | 70 | 13:00 | Chowmuhani | 186 | 23:00 | Borguna | 18 | 22:00
Bangabhaban | 12 | 10:00 | Ashuganj | 31 | 0:00 | Barisal(N) | 50 | 22:00
Motijheel | 22 | 13:00 | Daudkandi | 156 | 21:00 | Barisal (S) | 112 | 21:00
Narinda | 54 | 13:00 | B.Baria | 167 | 22:00 | Patuakhali | 111 | 22:00
Kazla | 79 | 19:30 | Ramganj | 96 | 23:00 | Bhandaria | 52 | 21:00
Dhanmondi | 188 | 13:00 | Chaddagram | 48 | 22:00 | Borhan Uddin | 46 | 21:00
Lalbag | 86 | 13:00 | PHP | 9 | 18:00 | Ishurdi | 71 | 22:00
Madartek | 72 | 21:00 | Kochua | 66 | 21:00 | Ruppur Paromanobik | 4 | 19:00
Dhaka University | 42 | 12:00 | Madunaghat | 56 | 14:00 | Natore | 132 | 22:00
Aftabnagar | 10 | 19:30 | Hathazari | 85 | 22:00 | Bogra | 166 | 22:00
Fatullah | 62 | 24:00 | Khulshi | 204 | 16:00 | Noagaon | 123 | 21:00
Nawabganj | 54 | 21:00 | Halishahar | 115 | 13:00 | Rajshahi | 160 | 23:00
Keraniganj | 70 | 19:30 | Baraulia | 150 | 23:00 | Rajshahi New | 22 | 22:00
Mirpur | 115 | 19:00 | Sikalbaha | 31 | 15:00 | C.Nawabganj | 59 | 23:00
Kalyanpur | 87 | 19:00 | Dohazari | 82 | 20:00 | Amnura | 50 | 22:00
Gulshan | 134 | 15:00 | Cox'sbazar | 95 | 23:00 | Pabna | 109 | 24:00
Uttara | 86 | 19:00 | Chandraghona | 28 | 19:30 | Shahjadpur | 102 | 20:00
Uttara New | 29 | 19:00 | Kaptai | 4.1 | 20:00 | Serajganj | 99 | 21:00
Kamrangirchar | 92 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 70 | 22:00
Savar | 180 | 19:30 | Bakulia | 104 | 15:00 | Joypurhat | 62 | 21:00
Bhasantec | 152 | 19:00 | Julda | 24 | 12:00 | Sherpur(Bogura) | 58 | 22:00
Agargaon | 77 | 16:00 | TK chemical | 26.7 | 20:00 | Mohastangor | 66 | 24:00
Satmosjid | 92 | 21:00 | Modern Steel |  |  | Bhangura | 34 | 21:00
Tongi | 104 | 21:00 | Shahmirpur | 24 | 0:00 | Rangpur | 120 | 24:00
Kabirpur | 237 | 19:00 | Khagrachhari | 20 | 1:00 | Lalmonirhat | 45 | 22:00
Basundhara | 165 | 15:00 | Matarbari | 37 | 21:00 | Saidpur | 103 | 20:00
Manikganj | 78 | 21:00 | Baroiar Hat | 42 | 22:00 | Purbasadipur | 110 | 21:00
Joydevpur | 177 | 19:30 | Rangamati | 12 | 19:00 | Thakurgaon | 84 | 23:00
New Tongi | 108 | 15:00 | Abul Khair 230 | 7 | 3:00 | Palashbari | 120 | 20:00
Kodda | 272 | 16:00 | BSRM | 153 | 22:00 | Barapukuria | 56 | 21:00
Dhamrai | 118 | 15:00 | GPH Ispat | 89 | 19:30 | Panchagar | 50 | 19:30
Rajendrapur | 110 | 21:00 | Agrabad | 36 | 16:00 | Joldhaka | 56 | 19:30
Valuka | 124 | 16:00 | Goalpara | 28 | 21:00 | Kurigram | 60 | 22:00
Tangail | 219 | 21:00 | Central S/S | 93 | 21:00 | Mithapukur | 46 | 19:30
Mymensing | 194 | 22:00 | Noapara | 61 | 22:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-02 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 24:00 | 394 | 10:00 | Kaliakoir | 384 | 0.25 | 373 | 0.375
| Bheramara | 399 | 24:00 | 394 | 19:30 | Bhulta | 376 | 24:00 | 358 | 0.41667
| Ashuganj(N) | 382 | 5:00 | 364 | 10:00 | Gopalganj | 402 | 0.625 | 383 | 0.83333
| Payra | 408 | 24:00 | 395 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 220 | 19:30 | 215 | 10:00
| Ishurdi | 234 | 18:30 | 225 | 23:00 | Megnaghat | 232 | 7:00 | 220 | 10:00
| Ashuganj | 240 | 17:00 | 235 | 4:00 | Fenchuganj | 240 | 23:00 | 235 | 17:00
| Serajganj | 229 | 14:00 | 225 | 3:00 | Siddhirganj | 227 | 21:00 | 216 | 10:00
| Baghabari | 232 | 15:00 | 226 | 10:00 | Maniknagar | 224 | 21:00 | 213 | 10:00
| Barapukuria | 233 | 5:00 | 224 | 19:30 | Agargaon | 225 | 6:00 | 212 | 10:00
| Bogra | 226 | 19:00 | 214 | 21:00 | Barisal | 245 | 1:00 | 236 | 23:00
| Rajshahi | 237 | 18:30 | 224 | 12:00 | Bhola 225 MW | 248 | 6:00 | 242 | 23:00
| Khulna South | 227 | 18:00 | 206 | 24:00 | AKSML | 222 | 1:00 | 216 | 7:00
| Rampura | 225 | 24:00 | 214 | 10:00 | BSRM | 223 | 1:00 | 218 | 7:00
| Haripur | 224 | 22:00 | 215 | 11:00 | Bibiyana | 238 | 1:00 | 234 | 9:00
| Hasnabad | 226 | 20:00 | 215 | 10:00 | Bhulta | 227 | 24:00 | 215 | 10:00
| Shyampur | 225 | 24:00 | 220 | 10:00 | Ashuganj (S) | 229 | 23:00 | 219 | 10:00
| Aminbazar | 226 | 1:00 | 213 | 2:00 | Kaliakoir | 222 | 1:00 | 213 | 9:00
| Tongi | 224 | 23:00 | 212 | 9:00 | GPH | 223 | 1:00 | 216 | 10:00
| Comilla (N) | 227 | 1:00 | 221 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 130 | 19:30 | 123 | 11:00 | Kochua | 139 | 0.16667 | 133 | 0.25
| Munsiganj | 131 | 20:00 | 122 | 10:00 | Madanhat | 132 | 0.83333 | 128 | 0.45833
| Sonargaon | 133 | 19:30 | 124 | 9:00 | Hathazari | 131 | 0.041667 | 129 | 0.41667
| Shyampur | 134 | 22:00 | 122 | 10:00 | Khulshi | 128 | 0.125 | 124 | 0.41667
| Bhulta | 125 | 19:00 | 118 | 10:00 | Halishahar | 128 | 0.041667 | 124 | 0.29167
| Madanganj | 130 | 21:00 | 121 | 10:00 | Baraulia | 130 | 0.041667 | 125 | 0.70833
| Shitalakhya | 141 | 23:00 | 126 | 10:00 | Sikalbaha | 132 | 0.875 | 125 | 0.83333
| Rahim steal | 130 | 19:00 | 123 | 11:00 | Dohazari | 130 | 0.875 | 125 | 0.041667
| Matuail | 130 | 19:30 | 123 | 11:00 | Cox'sbazar | 122 | 0.875 | 108 | 0.54167
| Ghorasal | 138 | 7:00 | 136 | 3:00 | Chandraghona | 130 | 0.083333 | 126 | 0.66667
| Narsinghdi | 134 | 6:00 | 126 | 22:00 | Kaptai | 130 | 0.041667 | 128 | 0.20833
| Haripur (SBU) | 131 | 19:30 | 123 | 10:00 | A. Khaer Stl. | 132 | 0.041667 | 126 | 0.33333
| Sreenagar | 130 | 19:30 | 121 | 9:00 | Bakulia | 131 | 0.875 | 127 | 0.25
| Ullon | 133 | 24:00 | 124 | 11:00 | Julda | 133 | 0.33333 | 130 | 0.125
| Hasnabad | 137 | 19:30 | 126 | 10:00 | TK Chemical | 131 | 0.041667 | 129 | 0.20833
| Magbazar | 132 | 3:00 | 122 | 12:00 | Modern Steel
| Maniknagar | 135 | 22:00 | 127 | 9:00 | Shahmirpur | 135 | 0.125 | 130 | 0.33333
| Bangabhaban | 135 | 22:00 | 127 | 9:00 | Khagrachhari | 129 | 0.041667 | 127 | 0.45833
| Motijheel | 135 | 22:00 | 127 | 9:00 | Matarbari | 126 | 0.77083 | 116 | 0.58333
| Narinda | 135 | 22:00 | 127 | 9:00 | Baroiar Hat | 135 | 0.33333 | 129 | 0.29167
| Kazla | 135 | 22:00 | 127 | 9:00 | Rangamati | 129 | 1:00 | 126 | 15:00
| Dhanmondi | 131 | 23:00 | 122 | 10:00 | Agrabad | 129 | 21:00 | 125 | 12:00
| Lalbag | 138 | 24:00 | 125 | 10:00 | Goalpara S/S | 136 | 18:30 | 123 | 0
| Madartek | 133 | 5:00 | 123 | 10:00 | Khulna Central S/S | 134 | 15:00 | 122 | 0
| Dhaka University | 133 | 6:00 | 124 | 11:00 | Noapara | 134 | 19:00 | 119 | 0
| Aftabnagar | 133 | 22:00 | 124 | 12:00 | Jessore | 128 | 18:30 | 119 | 0.5
| Fatullah | 134 | 22:00 | 122 | 10:00 | Benapol | 130 | 0.75 | 112 | 0
| Nawabganj | 130 | 24:00 | 121 | 9:00 | Jhenida | 126 | 18:30 | 107 | 0
| Keraniganj | 131 | 22:00 | 121 | 10:00 | Bottail | 130 | 0.77083 | 119 | 0
| Mirpur | 135 | 23:00 | 127 | 9:00 | G.K Project | 138 | 0.66667 | 133 | 0.91667
| Kalyanpur | 136 | 23:00 | 127 | 9:00 | Faridpur | 134 | 0.25 | 126 | 0.83333
| Gulshan | 132 | 2:00 | 124 | 10:00 | Madaripur | 137 | 0.20833 | 129 | 0.83333
| Uttara | 135 | 22:00 | 125 | 10:00 | Shariyatpur S/S | 138 | 6:00 | 129 | 0.83333
| Uttara New | 135 | 24:00 | 125 | 9:00 | Gopalganj | 142 | 0.25 | 130 | 0.83333
| Kamrangirchar | 137 | 22:00 | 124 | 9:00 | Bagerhat | 136 | 15:00 | 118 | 0
| Savar | 137 | 0:00 | 124 | 9:00 | Mongla | 132 | 15:00 | 121 | 0.45833
| Bhasantec | 134 | 0:00 | 125 | 10:00 | Satkhira | 136 | 16:00 | 119 | 0:00
| Agargaon | 135 | 0:00 | 126 | 10:00 | Gallamari | 137 | 0.75 | 124 | 0:00
| Satmosjid | 134 | 6:00 | 126 | 10:00 | Magura | 125 | 5:00 | 106 | 0
| Tongi | 137 | 23:00 | 129 | 10:00 | Narail | 122 | 0.20833 | 108 | 0.83333
| Kabirpur | 133 | 2:00 | 127 | 16:00 | Chuadanga | 120 | 6:00 | 97 | 0
| Basundhara | 134 | 0:00 | 126 | 10:00 | Borguna | 135 | 7:00 | 127 | 0.91667
| Manikganj | 138 | 0:00 | 131 | 10:00 | Barisal(N) | 139 | 6:00 | 131 | 23:00
| Joydevpur | 139 | 0:00 | 129 | 9:00 | Barisal (S) | 139 | 0.25 | 130 | 0.91667
| New Tongi | 136 | 0:00 | 127 | 9:00 | Patuakhali(S) | 136 | 0.33333 | 126 | 0.91667
| Kodda | 131 | 22:00 | 126 | 16:00 | Bhandaria | 137 | 0.20833 | 125 | 0.83333
| Dhamrai | 131 | 2:00 | 125 | 21:00 | Ishurdi | 135 | 16:00 | 130 | 24:00
| Rajendrapur | 133 | 22:00 | 122 | 10:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 20:00
| Valuka | 122 | 2:00 | 109 | 21:00 | Natore | 135 | 18:30 | 128 | 22:00
| Tangail | 130 | 4:00 | 120 | 21:00 | Bogra | 135 | 16:00 | 126 | 23:00
| Mymensing | 126 | 10:00 | 114 | 21:00 | Noagaon | 130 | 19:00 | 117 | 23:00
| Kishorganj | 130 | 6:00 | 120 | 21:00 | Rajshahi | 133 | 18:00 | 126 | 12:00
| Netrokona | 125 | 18:30 | 109 | 22:00 | Rajshahi New | 135 | 18:00 | 126 | 13:00
| Jamalpur | 136 | 16:00 | 124 | 4:00 | C.Nawabganj | 134 | 18:00 | 124 | 11:00
| Sherpur | 136 | 16:00 | 121 | 24:00 | Amnura | 136 | 18:30 | 123 | 12:00
| Srimongal | 138 | 4:00 | 134 | 21:00 | Pabna | 134 | 18:00 | 128 | 24:00
| Shahjibazar | 138 | 6:00 | 132 | 20:00 | Shahjadpur | 136 | 18:00 | 133 | 8:00
| Fenchuganj | 139 | 6:00 | 134 | 21:00 | Serajganj | 133 | 19:00 | 125 | 2:00
| Khulawara | 137 | 4:00 | 133 | 22:00 | Niyamatpur | 129 | 18:30 | 114 | 23:00
| Sylhet | 135 | 4:00 | 132 | 19:00 | Joypurhat | 130 | 19:00 | 115 | 23:00
| Chatak | 136 | 7:00 | 129 | 23:00 | Sherpur(Bogura) | 134 | 16:00 | 125 | 22:00
| Sunamganj | 135 | 8:00 | 124 | 19:00 | Mohastangor | 132 | 16:00 | 123 | 22:00
| Biani Bazar | 135 | 6:00 | 129 | 20:00 | Bangura | 136 | 18:30 | 131 | 20:00
| Comilla(s) | 130 | 1:00 | 123 | 19:30 | Rangpur | 127 | 17:00 | 114 | 23:00
| Comilla(n) | 137 | 20:00 | 134 | 15:00 | Lalmonirhat | 126 | 14:00 | 115 | 19:30
| Chandpur | 140 | 17:00 | 134 | 6:00 | Saidpur | 127 | 6:00 | 111 | 23:00
| Feni | 137 | 8:00 | 130 | 0:00 | Purbasadipur | 125 | 6:00 | 106 | 22:00
| Chowmuhani | 135 | 17:00 | 129 | 23:00 | Thakurgaon | 123 | 5:00 | 105 | 22:00
| Ashuganj | 140 | 5:00 | 135 | 20:00 | Palashbari | 127 | 6:00 | 115 | 22:00
| Daudkandi | 137 | 19:30 | 124 | 9:00 | Barapukuria | 133 | 5:00 | 124 | 20:00
| B.Baria | 135 | 5:00 | 128 | 22:00 | Panchagar | 125 | 6:00 | 103 | 22:00
| Ramganj | 136 | 17:00 | 130 | 23:00 | Joldhaka | 125 | 0.20833 | 108 | 0.91667

## L-Curve
Date | 2021-06-02
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 44 | 8588 | 4139 | 12727 |  |  |  | QF-LDC-11
0:30 | 42 | 7764 | 3658.5 | 11422.5 | Date: | 2021-06-02
1:00 | 40 | 6940 | 3178 | 10118
1:30 | 51 | 6892 | 3104.5 | 9996.5
2:00 | 62 | 6844 | 3031 | 9875
2:30 | 59.5 | 6712.5 | 2994 | 9706.5 | [5 empty] | Gen. at Eve. Peak | 13014 | 13014 MW (21:00 )
3:00 | 57 | 6581 | 2957 | 9538 | [6 empty] | 21:00
3:30 | 42 | 6442.5 | 2902.5 | 9345 | [5 empty] | Gen. at Day Peak | 10311 | 10311 MW (12:00 )
4:00 | 27 | 6304 | 2848 | 9152 | [6 empty] | 12:00
4:30 | 50.5 | 6214.5 | 2813 | 9027.5 | [5 empty] | Highest Generation | 13014
5:00 | 74 | 6125 | 2778 | 8903 | [6 empty] | 21:00
5:30 | 129.5 | 5920.5 | 2756.5 | 8677
6:00 | 185 | 5716 | 2735 | 8451
6:30 | 182 | 5686.5 | 2742.5 | 8429
7:00 | 179 | 5657 | 2750 | 8407
7:30 | 204.5 | 5729 | 2778.5 | 8507.5
8:00 | 230 | 5801 | 2807 | 8608
8:30 | 226.5 | 6064 | 2808.5 | 8872.5
9:00 | 223 | 6327 | 2810 | 9137
9:30 | 190 | 6559 | 2801.5 | 9360.5
10:00 | 157 | 6791 | 2793 | 9584
10:30 | 145.5 | 6937.5 | 2822.5 | 9760
11:00 | 134 | 7084 | 2852 | 9936
11:30 | 141.5 | 7196 | 2927.5 | 10123.5
12:00 | 149 | 7308 | 3003 | 10311
12:30 | 93.5 | 7429.5 | 3071 | 10500.5
13:00 | 38 | 7551 | 3139 | 10690
13:30 | 68.5 | 7569 | 3194 | 10763
14:00 | 99 | 7587 | 3249 | 10836
14:30 | 145.5 | 7645.5 | 3300 | 10945.5
15:00 | 192 | 7704 | 3351 | 11055
15:30 | 210 | 7674 | 3397.5 | 11071.5
16:00 | 228 | 7644 | 3444 | 11088
16:30 | 161.5 | 7625.5 | 3312 | 10937.5
17:00 | 95 | 7607 | 3180 | 10787
17:30 | 197.5 | 7344 | 3172.5 | 10516.5
18:00 | 300 | 7081 | 3165 | 10246
18:30 | 247.5 | 7623.5 | 3447 | 11070.5
19:00 | 195 | 8166 | 3729 | 11895
19:30 | 18 | 8577 | 4217 | 12794
20:00 | 2 | 8649 | 4252 | 12901 |  |  |  | Executive Engineer
20:30 | 4 | 8676.5 | 4281 | 12957.5 |  |  |  | Network Operation Division
21:00 | 6 | 8704 | 4310 | 13014
21:30 | 7 | 8687 | 4308 | 12995
22:00 | 8 | 8670 | 4306 | 12976 |  |  |  |  | Page 6 of 7
22:30 | 17 | 8621 | 4310 | 12931
23:00 | 26 | 8572 | 4314 | 12886
23:30 | 35 | 8580 | 4226.5 | 12806.5
24:00 | 44 | 8588 | 4139 | 12727
13014 MW (21:00 )
10311 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-02 |  | Energy | 254877233
[11 empty] | 2021-06-02 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3998 | 779 | 2049 | 4475 | 700 | 20 | 533 | 0 | 154 | 0
0:30 | 4115 | 780.5 | 2089.5 | 3270.5 | 599.5 | 20 | 405 | 0 | 133 | 0 | Date: | 2021-06-02
1:00 | 4232 | 782 | 2130 | 2066 | 499 | 20 | 277 | 0 | 112 | 0
1:30 | 4257 | 782.5 | 2127 | 1937.5 | 499 | 20 | 268.5 | 0 | 105 | 0 | [7 empty] | Total Energy | 254.8772 | Total Energy Gen 254.877 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.877 MKWHr
2:00 | 4282 | 783 | 2124 | 1809 | 499 | 20 | 260 | 0 | 98 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4229 | 782.5 | 2160 | 1667 | 499 | 20 | 252 | 0 | 97 | 0 | [7 empty] | Energy Requirement | 254.8772
3:00 | 4176 | 782 | 2196 | 1525 | 499 | 20 | 244 | 0 | 96 | 0
3:30 | 4176.5 | 782.5 | 2197 | 1426 | 499 | 20 | 148 | 0 | 96 | 0 | [6 empty] | Shortage
4:00 | 4177 | 783 | 2198 | 1327 | 499 | 20 | 52 | 0 | 96 | 0
4:30 | 4175 | 782.5 | 2155.5 | 1272 | 499 | 20 | 28.5 | 0 | 95 | 0
5:00 | 4173 | 782 | 2113 | 1217 | 499 | 20 | 5 | 0 | 94 | 0
5:30 | 4126.5 | 795.5 | 2088 | 1073.5 | 474 | 20 | 5 | 0 | 92 | 2.5
6:00 | 4080 | 809 | 2063 | 930 | 449 | 20 | 5 | 0 | 90 | 5
6:30 | 4119 | 809 | 2046.5 | 877.5 | 449 | 20 | 5 | 0 | 91 | 12 |  |  |  |  | Coal
7:00 | 4158 | 809 | 2030 | 825 | 449 | 20 | 5 | 0 | 92 | 19
7:30 | 4121.5 | 809 | 2016 | 975 | 439.5 | 20 | 5 | 0 | 97 | 24.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4085 | 809 | 2002 | 1125 | 430 | 20 | 5 | 0 | 102 | 30
8:30 | 4114.5 | 809 | 1989.5 | 1346.5 | 430 | 20 | 21 | 0 | 99 | 43
9:00 | 4144 | 809 | 1977 | 1568 | 430 | 20 | 37 | 0 | 96 | 56
9:30 | 4149.5 | 808.5 | 1963 | 1733.5 | 430 | 20 | 88.5 | 0 | 104 | 63.5
10:00 | 4155 | 808 | 1949 | 1899 | 430 | 20 | 140 | 0 | 112 | 71
10:30 | 4086 | 808 | 1889.5 | 2164 | 430 | 20 | 173 | 0 | 112 | 77.5
11:00 | 4017 | 808 | 1830 | 2429 | 430 | 20 | 206 | 0 | 112 | 84
11:30 | 3981.5 | 808.5 | 1879 | 2582.5 | 440 | 20 | 207.5 | 0 | 118 | 86.5
12:00 | 3946 | 809 | 1928 | 2736 | 450 | 20 | 209 | 0 | 124 | 89
12:30 | 3909 | 807.5 | 1953 | 2902 | 465 | 20 | 228.5 | 0 | 123 | 92.5
13:00 | 3872 | 806 | 1978 | 3068 | 480 | 20 | 248 | 0 | 122 | 96
13:30 | 3872 | 806 | 1978 | 3068 | 480 | 20 | 248 | 0 | 122 | 96
14:00 | 3872 | 806 | 1978 | 3068 | 480 | 20 | 248 | 0 | 122 | 96
14:30 | 3890 | 805.5 | 1987.5 | 3202 | 514.5 | 20 | 250.5 | 0 | 129 | 73.5
15:00 | 3908 | 805 | 1997 | 3336 | 549 | 20 | 253 | 0 | 136 | 51
15:30 | 3843 | 805 | 1995 | 3397.5 | 559 | 20 | 274.5 | 0 | 135 | 42.5
16:00 | 3778 | 805 | 1993 | 3459 | 569 | 20 | 296 | 0 | 134 | 34
16:30 | 3780 | 805.5 | 1992 | 3284.5 | 559.5 | 20 | 334 | 0 | 132 | 30
17:00 | 3782 | 806 | 1991 | 3110 | 550 | 20 | 372 | 0 | 130 | 26
17:30 | 3776.5 | 806 | 1884 | 2917.5 | 545 | 20 | 427 | 0 | 125 | 15.5
18:00 | 3771 | 806 | 1777 | 2725 | 540 | 20 | 482 | 0 | 120 | 5
18:30 | 3862.5 | 805.5 | 1845.5 | 3264 | 544.5 | 20 | 590 | 0 | 136 | 2.5
19:00 | 3954 | 805 | 1914 | 3803 | 549 | 20 | 698 | 0 | 152 | 0
19:30 | 3953 | 805 | 2010 | 4493 | 639 | 20 | 720 | 0 | 154 | 0
20:00 | 3936 | 804 | 2081 | 4530 | 670 | 20 | 708 | 0 | 152 | 0
20:30 | 3961.5 | 797 | 2094.5 | 4532.5 | 690 | 20 | 709 | 0 | 153 | 0
21:00 | 3987 | 790 | 2108 | 4535 | 710 | 20 | 710 | 0 | 154 | 0
21:30 | 3970 | 790 | 2104.5 | 4535.5 | 715 | 20 | 707 | 0 | 153 | 0
22:00 | 3953 | 790 | 2101 | 4536 | 720 | 20 | 704 | 0 | 152 | 0
22:30 | 3963 | 784 | 2078 | 4505.5 | 720 | 20 | 706.5 | 0 | 154 | 0
23:00 | 3973 | 778 | 2055 | 4475 | 720 | 20 | 709 | 0 | 156 | 0
23:30 | 3985.5 | 778.5 | 2052 | 4475 | 710 | 20 | 621 | 0 | 155 | 0 | Max Temp. in Dhaka |  | 34.0° C
24:00 | 3998 | 779 | 2049 | 4475 | 700 | 20 | 533 | 0 | 154 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 254.877 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 254.877 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-02
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 480000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 0 | 5 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 395377
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 0 | 2 | 2 | 3 | 3 | 5 | 7 | 9 |  | 2 | 0 | [8 empty] | 33750
6 | Sikalbaha 225MW CCPP (Gas) | 204 | 216 | 204 | 216 | 203 | 203 | 217 | 203 | 207 | 217 | 204 | 220 | 211 | 204 | 220 | 204 | 204 | 203 |  | 217 | 208 | 203 | 203 | 203 | 203 | 203 | 4716777
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 94 | 135 | 0 | 0 | 70 | 70 | 70 | 70 | 70 | 70 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1690085
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 51 | 51 | 0 | [15 empty] | 85 | 85 | 85 | 85 | 85 | 85 | 68 | 648241
12 | Hathazari 100 MW peaking PP | [25 empty] | 0
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 51 | 51 | 72 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2467272
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 145 | 200 | 200 | 200 | 200 | 200 | 200 | 1033344
14 | Titas 50 MW Peaking PP | [12 empty] | 41 | 41 | 41 | 49 | 49 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 546432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 100 | 100 | 100 | 100 | 100 | 75 | 120 | 155 | 155 | 185 | 182 | 181 | 183 | 152 | 181 | 115 | 105 | 115 |  | 150 | 183 | 181 | 177 | 181 | 180 | 180 | 3723000
17 | Siddhirganj 335 MW CCPP | 220 | 221 | 221 | 220 | 221 | 180 | 180 | 180 | 217 | 212 | 215 | 25 | [8 empty] | 6 | 6 | 0 | 0 | 0 | 0 | 2581856
18 | Kodda 300 MW PP Unit-2 (Summit) | [9 empty] | 15 | 145 | 195 | 210 | 227 | 227 | 227 | 227 | 227 |  | 232 | 232 | 245 | 245 | 245 | 245 | 245 | 3184035
19 | Ashuganj 195MW PP (APSCL-United) | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 82 | 82 | 82 | 82 | 88 | 88 | 88 | 117 | 78 |  | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 1973818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4441500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 110 | 110 | 110 | 110 |  | 125 | 125 | 125 | 125 | 125 | 125 | 125 | 2948710
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 23 | 23 | 20 | 23 | 20 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 497952
33 | Ashuganj 225 MW CCPP | 220 | 220 | 219 | 219 | 220 | 220 | 218 | 214 | 187 | 177 | 160 | 164 | 163 | 176 | 184 | 190 | 173 | 189 |  | 212 | 213 | 213 | 217 | 217 | 216 | 218 | 4844000
34 | Ashuganj 450 MW CCPP(South)
| Ashuganj 450 MW CCPP(North) | 315 | 310 | 345 | 340 | 310 | 320 | 345 | 310 | 325 | 345 | 310 | 350 | 315 | 310 | 340 | 310 | 310 | 310 |  | 330 | 320 | 310 | 355 | 310 | 310 | 310 | 8172200
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 52 | 51 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 30 |  | 30 | 49 | 49 | 49 | 49 | 51 | 51 | 1050720
36 | Chandpur 150 MW CCPP | 75 | 76 | 76 | 75 | 80 | 81 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 81 | 80 | 78 | 81 |  | 80 | 80 | 81 | 72 | 72 | 73 | 75 | 1855390
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6647750
41 | Haripur 360MW CCPP(HPL) | 251 | 262 | 276 | 287 | 291 | 266 | 226 | 197 | 186 | 172 | 172 | 172 | 172 | 172 | 186 | 191 | 197 | 216 |  | 216 | 216 | 217 | 212 | 212 | 221 | 232 | 5224000
42 | RPCL 210MW CCPP | 156 | 156 | 156 | 155 | 156 | 156 | 156 | 156 | 147 | 132 | 131 | 117 | 117 | 116 | 115 | 147 | 147 | 147 |  | 143 | 132 | 132 | 135 | 135 | 144 | 151 | 3295640
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 12 | 23 | 38 | 48 | 52 | 47 | 46 | 16 | 15 | 12 | 3 | [8 empty] | 327220
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 43 | 43 | 44 | 44 | 44 | 44 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1014000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 997080
46 | Shajibazar 330 MW CCPP | 162 | 163 | 163 | 162 | 162 | 162 | 164 | 163 | 162 | 163 | 163 | 161 | 161 | 161 | 160 | 160 | 161 | 161 |  | 160 | 162 | 162 | 160 | 162 | 163 | 162 | 3593000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 61 | 61 | 60 | 54 | 55 | 56 | 56 |  | 56 | 56 | 56 | 56 | 56 | 56 | 62 | 1432224
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 10 |  |  |  | 78 | 76 | 79 | 79 | 81 | 80 | 40 |  | 82 | 83 | 83 | 82 | 82 | 82 | 82 | 1540800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 164 | 164 | 164 | 164 | 164 | 191 | 205 | 218 | 219 | 219 | 218 | 219 |  | 219 | 219 | 218 | 218 | 219 | 219 | 218 | 4818740
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 402000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  |  | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 149940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 210240
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 53 | 50 | 47 | 52 | 53 | 14 |  | 23 | 53 | 52 | 53 | 53 | 50 | 47 | 1146000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 356328
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 310 | 300 | 290 | 290 | 300 | 310 | 310 | 320 | 290 | 300 | 310 | 300 | 310 | 295 | 290 | 285 |  | 290 | 300 | 305 | 320 | 320 | 300 | 300 | 7408500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 397 | 380 | 370 | 391 | 393 | 389 | 395 | 400 | 400 |  | 393 | 398 | 399 | 400 | 400 | 400 | 400 | 9489500
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 17 | 0 |  |  |  | 35 | 35 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 803240
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 0 |  |  |  | 1 | 6 |  |  | 1 | 22 | 24 | 24 | 23 | 20 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 396000
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 472224
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 18 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 425016
62 | Tangail 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 17 | 17 | 17 | 17 | 17 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 374364
63 | Impoprt (Tripura) | 112 | 98 | 96 | 96 | 94 | 90 | 92 | 102 | 96 | 112 | 112 | 124 | 122 | 136 | 136 | 134 | 130 | 120 |  | 152 | 154 | 152 | 154 | 152 | 156 | 154 | 2896320
64 | Malancha, Ctg. EPZ (United) | 39 | 39 | 39 | 39 | 39 | 39 | 40 | 8 | 5 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 6 |  | 8 | 14 | 17 | 28 | 33 | 36 | 29 | 472800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 503244
66 | Feni 11 MW PP (Doreen) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 11 | 8 | 8 | 8 | 8 | [8 empty] | 5 | 5 | 104760
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 619100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 15 | 15 | 12 | 12 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 472430
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 |  | 15 | 19 | 19 | 20 | 20 | 20 | 20 | 476100
71 | Maona 33 MW PP(Summit) | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 28 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 710300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 794200
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 95 | 91 | 95 | 95 | 92 | 92 | 98 | 95 | 97 | 97 | 42 |  | 95 | 98 | 98 | 99 | 99 | 99 | 99 | 2221590
| Feni Lanka Power | 100 | 100 | 100 | 100 | 100 | 17 | 17 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2225280
| Chowmuhani 113 MW | 111 | 110 | 110 | 112 | 111 | 36 | 40 | 105 | 110 | 110 | 117 | 115 | 116 | 115 | 116 | 120 | 111 | 121 |  | 114 | 113 | 115 | 119 | 112 | 112 | 108 | 2608200
| Manikgonj 162MW PP(MPGL) | 54 | 0 | [6 empty] | 2 | 32 | 98 | 108 | 117 | 126 | 126 | 126 | 126 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 1882080
77 | Siddhirganj 100 PP(Dutch Bangla) | [7 empty] | 4 | 8 | 30 | 32 | 42 | 50 | 50 | 70 | 98 | 100 | 100 |  | 98 | 100 | 100 | 100 | 100 | 100 | 100 | 1230720
78 | Gazipur 52 MW PP | 42 | 42 | 42 | 42 | 0 |  |  |  | 5 | 33 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 16 |  | 33 | 33 | 33 | 33 | 33 | 42 | 41 | 759360
79 | Kodda 150MW PP | 64 | 64 | 48 | 16 | 0 |  |  |  | 32 | 115 | 150 | 150 | 150 | 147 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2351040
80 | Jamalpur 95 MW PP(Powerpac) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 15 | 15 | 15 |  | 15 | 15 | 15 | 16 | 15 | 15 | 15 | 357120
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 38 | 25 | 34 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1023374
| Gazipur 100 MW PP | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 84 | 83 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 2002800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 1 | 3 | 4 | 3 | 2 | 2 | 1 | 0 | [9 empty] | 25799
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 40 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1286005
| Karnaphuli Power Ltd. | 51 | 51 | 51 | 51 | 17 | 17 | 17 | 17 | 35 | 100 | 108 | 108 | 110 | 108 | 108 | 108 | 110 | 70 |  | 87 | 110 | 110 | 110 | 110 | 108 | 108 | 1985525
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [9 empty] | 6 | 30 | 35 | 50 | 50 | 62 | 84 | 74 | 74 |  | 74 | 74 | 74 | 74 | 73 | 73 | 73 | 956099
86 | Meghnaghat CCPP ( Summit) | 230 | 235 | 230 | 235 | 230 | 235 | 235 | 240 | 255 | 265 | 275 | 300 | 285 | 285 | 290 | 275 | 250 | 275 |  | 280 | 280 | 280 | 260 | 260 | 273 | 275 | 6165673
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [9 empty] | 11 | 54 | 84 | 104 | 104 | 104 | 104 | 104 | 86 |  | 83 | 104 | 104 | 104 | 104 | 104 | 104 | 1432320
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 62 | 66 | 80 | 92 | 80 | 80 | 80 | 80 | 92 | 92 | 92 | 92 | 80 |  | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 2045760
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 43 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 5 | 5 | 1163285
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 0 | [6 empty] | 2 | 7 | 70 | 84 | 102 | 102 | 102 | 102 | 102 | 64 |  | 80 | 93 | 102 | 102 | 102 | 102 | 102 | 1357
95 | Patenga 50MW PP (Baraka) | [10 empty] | 1 | 19 | 41 | 42 | 46 | 43 | 44 | 46 |  | 45 | 47 | 47 | 50 | 50 | 50 | 50 | 586560
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 0 | [6 empty] | 15 | 30 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 40 |  | 42 | 55 | 55 | 55 | 55 | 55 | 55 | 822690
100 | Manikganj 55 MW PP (Northern) | [9 empty] | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 759491
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 163 | 163 | 110 | 110 | 110 | 163 | 163 | 163 | 130 | 130 | 163 | 163 | 163 | 163 | 130 | 110 |  | 110 | 110 | 163 | 163 | 163 | 163 | 163 | 3556636
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 0 | 1 | 2 | 2 | 3 | 2 | 1 | 1 | 1 | 1 | 0 | [8 empty] | 13500
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 875520
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 74 |  |  |  |  | 102 | 303 | 303 | 302 | 305 | 302 | 305 | 1571067
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 525088
106 | Mymensingh 200 MW PP (United) | 160 | 130 | 50 | 8 | 0 |  |  |  |  | 5 | 24 | 31 | 80 | 70 | 70 | 108 | 130 | 130 |  | 189 | 189 | 191 | 193 | 200 | 193 | 193 | 2275200
112 | Aurahati 100MW PP (Aggreko) | [15 empty] | 25 |  |  |  | 101 | 101 | 101 | 102 | 102 | 101 | 100 | 583257
114 | Kodda 149 MW PP Unit-1 (Summit) | 92 | 62 | 46 | 40 | 40 | 40 | 24 | 24 | 65 | 74 | 112 | 122 | 146 | 149 | 149 | 149 | 149 | 122 |  | 135 | 135 | 149 | 149 | 149 | 149 | 149 | 2521008
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 30 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1611840
116 | Chandpur 200MW (Desh energy) | 139 | 139 | 123 | 123 | 118 | 61 | 17 | 25 | 85 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 123 | 120 | 120 | 120 | 120 | 140 | 2641920
117 | Ashuganj 150MW PP (Midland) | 142 | 142 | 100 | 10 | 0 |  |  | 2 | 56 | 122 | 123 | 132 | 135 | 134 | 132 | 137 | 138 | 90 |  | 90 | 90 | 90 | 70 | 70 |  |  | 2085890
118 | Bibiyana-III 400 MW CCPP | 409 | 407 | 408 | 408 | 365 | 328 | 364 | 329 | 375 | 402 | 367 | 410 | 380 | 371 | 397 | 368 | 368 | 330 |  | 399 | 374 | 366 | 366 | 366 | 367 | 365 | 9085000
| Jamalpur 115 MW PP (United) | 107 | 107 | 107 | 108 | 115 | 115 | 75 | 84 | 107 | 115 | 115 | 106 | 106 | 115 | 115 | 115 | 115 | 85 |  | 96 | 115 | 115 | 115 | 115 | 115 | 115 | 2556000
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | 10 | 10 | 0 | [5 empty] | 50 | 60 | 30 | 30 | 30 | 30 | 50 | 30 | 10 | 10 |  | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 515520
| Anlima Energy Ltd. | [9 empty] | 8 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 258436
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 889200
| Spectra Solar Plant Ltd. | [5 empty] | 3 | 10 | 14 | 24 | 22 | 23 | 19 | 32 | 27 | 21 | 12 | 8 | 1 | [8 empty] | 215038
120 | Eastern Zone Total | 6940 | 6844 | 6581 | 6304 | 6125 | 5716 | 5657 | 5801 | 6327 | 6791 | 7084 | 7308 | 7551 | 7587 | 7704 | 7644 | 7607 | 7081 |  | 8166 | 8577 | 8649 | 8704 | 8670 | 8572 | 8588 | 173529767
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 3 | 3 | 5 | 18 | 18 | 18 |  | 18 | 21 | 21 | 20 | 20 | 20 | 20 | 235630
| Khulna 225 MW CCPP | [17 empty] | 40 |  | 135 | 158 | 150 | 158 | 159 | 160 | 0 | 822819
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | 0 | [9 empty] | 2 | 30 | 60 | 87 | 105 | 70 | 35 |  | 53 | 90 | 90 | 105 | 105 | 105 | 105 | 1046880
130
131
132 | United Payra Power Ltd. | [19 empty] | 2 | 17 | 17 | 17 | 17 | 17 | 17 | 91200
133 | Bhola Nutan Biddut BD LTD (GAS) | 227 | 227 | 228 | 227 | 228 | 227 | 227 | 228 | 229 | 226 | 224 | 224 | 224 | 224 | 221 | 224 | 223 | 224 |  | 224 | 224 | 224 | 224 | 223 | 224 | 223 | 5419009
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 18 | 48 | 48 | 48 | 48 | 48 | 48 | 250080
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 11 | 11 | 10 | 10 | 10 | 12 | 12 | 12 | 12 | 0 | [14 empty] | 140350
| Bhola 225 MW CCPP | 69 | 69 | 69 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 |  | 86 | 68 | 68 | 68 | 67 | 68 | 68 | 1654093
140 | Bhola 33 MW PP (Venture) | 29 | 27 | 26 | 24 | 23 | 20 | 18 | 17 | 17 | 18 | 19 | 18 | 20 | 23 | 23 | 22 | 21 | 21 |  | 31 | 32 | 32 | 33 | 33 | 33 | 33 | 572671
141 | Noapara 100 MW PP (Bangla Trac) | [14 empty] | 17 | 25 |  |  |  | 20 | 100 | 100 | 100 | 100 | 100 | 100 | 636480
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 3 | 4 | 1 | 6 | 6 | 7 | [9 empty] | 23296
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 782 | 783 | 782 | 783 | 782 | 809 | 809 | 809 | 809 | 808 | 808 | 809 | 806 | 805 | 805 | 805 | 806 | 806 |  | 805 | 805 | 804 | 790 | 790 | 778 | 779 | 19285818
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 355 | 365 | 370 | 370 | 365 | 360 | 350 | 345 | 345 | 340 | 330 | 315 | 315 | 315 | 315 |  | 310 | 315 | 325 | 325 | 330 | 335 | 345 | 8372736
148 | Payra 1320 MW | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 280 | 280 | 280 | 280 | 300 | 330 | 340 | 400 | 420 | 400 | 390 |  | 400 | 490 | 520 | 560 | 570 | 570 | 550 | 10147000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 150 | 150 |  | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 3657100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 0 | [5 empty] | 20 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 876139
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 3 | 2 | 2 | 2 | 3 | 2 | 1 | 0 | 0 | [8 empty] | 21120
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 168 | 167 | 176 | 170 | 165 | 164 | 176 | 175 | 178 | 170 | 162 | 162 | 162 | 162 | 150 | 150 | 150 | 150 |  | 150 | 163 | 160 | 170 | 170 | 170 | 170 | 4215791
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 197 | 199 | 199 | 199 | 199 | 200 | 203 | 197 | 197 | 186 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4726309
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 424 | 402 | 418 | 422 | 397 | 376 | 377 | 417 | 420 | 409 | 378 | 411 | 408 | 406 | 401 | 396 | 398 | 353 |  | 378 | 404 | 414 | 418 | 407 | 415 | 409 | 9675100
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [14 empty] | 1 | 7 | 39 | 39 |  | 44 | 40 | 41 | 40 | 36 | 36 | 36 | 291943
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 19 | 19 | 19 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 480240
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 188964
165 | Amnura 50 MW PP(Sinha) | [12 empty] | 12 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 445280
166 | Katakhali 50 MW PP (Northern) | [13 empty] | 16 | 32 | 43 | 8 | 8 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 319808
167 | Katakhali 50 MW Peaking PP | [15 empty] | 16 | 38 | 38 |  | 38 | 38 | 40 | 38 | 38 | 38 | 38 | 283850
168 | Santahar 50 MW Peaking PP | [17 empty] | 11 |  | 27 | 27 | 26 | 26 | 26 | 25 | 26 | 160658
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 25 | 25 | 8 | 8 | 8 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 16 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1027680
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 90 | 31 | 0 | [11 empty] | 21 | 88 |  | 88 | 88 | 87 | 87 | 87 | 87 | 87 | 926784
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 100 | 200 | 200 | 200 | 200 | 200 | 200 | 1068392
| Bagura 113 MW PP (Confidence)-2 | 70 | 70 | 0 | [6 empty] | 4 | 60 | 70 | 95 | 95 | 110 | 103 | 35 | 35 |  | 52 | 113 | 113 | 113 | 113 | 113 | 113 | 1503936
172 | Confidence Power Bogura Unit-1 113 MW | 70 | 0 | [9 empty] | 70 | 113 | 113 | 113 | 113 | 35 | 35 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1408512
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | [14 empty] | 15 | 15 | 10 | 8 | 5 | 10 | 10 | 52000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 38 | 0 | [8 empty] | 34 | 56 | 70 | 105 | 105 | 113 | 34 | 34 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1278278
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 3 | 3 | 6 | 5 | 6 |  | 4 | 3 | 1 | [8 empty] | 41520
178
178