## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:March 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-04-01 |  | 2021-03-01 |  | 2020-04-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13792 | 2021-04-27 | 10790 | 18/03/20 | 10344 | 14/04/20 | 13792 | 2021-04-27
|  |  | 20:00 |  | 19:30 |  | 21:00 |  | 20:00
2 | Minimum Generation (MW) | 4853 | 2021-04-17 | 5676.1 | 03/03/20 | 4292.2 | 25/04/20 | - | -
|  |  | 7:00 |  | 5:00 |  | 6:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13792 | 2021-04-27 | 10790 | 18/03/20 | 10344 | 14/04/20 | 13792 | 2021-04-27
|  |  | 20:00 |  | 19:30 |  | 21:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 11773 | 2021-04-28 | 9428.9 | 18/03/20 | 8389.7 | 05/04/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 14097 | 2021-04-27 | 10790 | 18/03/20 | 10344 | 14/04/20 | 14097 | 2021-04-27
|  |  | 19:00 |  | 19:30 |  | 21:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 12676.7 |  | 9878.5806 |  | 8896.9333 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10379.6667 |  | 8156.329 |  | 7031.8517 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 933 | 2021-04-29 18:00 | 943 | 23/03/2020 | 949 | 09/04/2020 | 956 | 27/3/2019
|  |  | 18:00 |  | 20:00 |  | 22:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 187 | 2021-04-18 | 152 | 15/03/2020 | 142 | 14/04/2020 | 194 | 12/06/19
|  |  | 18:00 |  | 18:30 |  | 20:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 275 | 2021-04-27 | - | - | - | - | 1459 | 04/05/2010
|  |  | 20:00 | [5 empty] | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | 13792 | 2021-04-27 | - | - | - | - | 13792 | 2021-04-27
|  |  | 20:00 | [5 empty] | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | - | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 1 |  | - |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1830.3371 |  | 3442.7368 |  | 3300.8626 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 184.6566 |  | 103.8241 |  | 99.2395
22 | Net Generation of BPDB (MKWH) | 1645.6805 |  | 3338.9126 |  | 3201.6231
23 | Net Generation of IPP (MKWH) | 4706.4414 |  | 1608.1902 |  | 134.1374
24 | Net Generation of REB (MKWH) | 133.246 |  | 135.7736 |  | 101.3435
24 | Net Generation of Rental Power Plant (MKWH) | 587.4025 |  | 297.8023 |  | 202.4975
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7072.7704 |  | 5380.6788 |  | 3639.6015 |  | 6596.69 | Oct'20
26 | Energy Generation by Gas (MKWH) | 4613.3508 |  | 4372.4084 |  | 3983.5017 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 295.1848 |  | 137.8528 |  | 102.8552 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1657.9757 |  | 556.2721 |  | 295.0235 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 41.547 |  | 49.3088 |  | 24.8805 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 21.9287 |  | 6.9723 |  | 5.7632 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 627.4399 |  | 361.6886 |  | 416.1569 |  | 509.8908 | Oct'20
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 658.1569 |  | 453.512 |  | 403.908 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 77.1406 |  | 73.9685 |  | 70.2513 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:April' 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13792 | 2021-04-27 | 20:00
Generation Period
| Dhaka | MW | 4543
| Chattogram | MW | 1348
| Cumilla | MW | 1288
| Mymensingh | MW | 1089
| Sylhet | MW | 545
a) | Total supply in East zone | MW | 8813
| Khulna | MW | 1653
| Barisal | MW | 392
| Rajshahi | MW | 1447
| Rangpur | MW | 791
b) | Total supply in West zone | MW | 4283
c) | Total supply in both zone ( a+b) | MW | 13096
Ref: | 27.21.0000.603.16.087.20.400 | Date: 18/04/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:April' 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 590 | 2021-04-04 | 22:00
| b) Ishurdi end | MW | 264 | 2021-04-24 | 10:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 550 | 2021-04-22 | 16:00
| b) Ishurdi end | MW | 208 | 2021-04-03 | 21:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 17.33
| b) Ishurdi end | MKWH | 28.46
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 27.51
| b) Ishurdi end | MKWH | 16.82
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 490 | 2021-04-03 | 21:00
| b)Serajganj end | MW | 440 | 2021-04-11 | 11:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 430 | 2021-04-21 | 21:00
| b)Sirajganj end | MW | 460 | 2021-04-03 | 21:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 4.732 | 2021-04-02
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 4.74 | 2021-04-02
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 42.36
| b)Sirajganj end | MKWH | 46.11
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 44.28
| b)Sirajganj end | MKWH | 42.69
30 | Transmission loss of EWI /NO-2 | % | 1.704
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month: April 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2021-04-01 20:48 | 2021-04-01 20:53 | 0:05 | T | Tripped showing O/C relay | 140 | 11.6667 | Power interruption
Dhamrai | 132/33 kV transformer T-1 | 2021-04-04 06:22 | 2021-04-04 08:33 | 2:11 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-04-05 11:22 | 2021-04-05 11:41 | 0:19 | E/O | Due to fire originated from marshaling box | 140 | 44.3333 | Power interruption
| 132/33 kV Transformer-T2 | 2021-04-05 11:22 | 2021-04-05 18:03 | 6:41 | E/O | Due to fire originated from marshaling box | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T-3 | 2021-04-07 20:20 | 2021-04-07 21:01 | 0:41 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kishoreganj | 132/33 kV Transformers-T3 & T4, 33 kV Bus | 2021-04-12 12:02 | 2021-04-12 14:05 | 2:03 | E/O | Due to red-hot maintenance | 25 | 51.25 | Power interruption
Savar | 132/33 kV Transformers-T2 | 2021-04-12 16:14 | 2021-04-12 19:58 | 3:44 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformers-T3 | 2021-04-12 16:14 | 2021-04-12 16:25 | 0:11 | T | Tripped showing O/C relay | 159 | 29.15 | Power interruption
Mymensingh | 132/33 kV Transformers- T-1 & T-2 | 2021-04-19 04:48 | 2021-04-19 04:55 | 0:07 | T | Due to Shambhuganj feeder fault | 36 | 4.2 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-04-29 06:30 | 2021-04-29 07:39 | 1:09 | E/O | Due to red-hot maintenance | 15 | 17.25 | Power interruption
|  |  | Total : | 17:11 |  | Unserved Energy: |  | 157.85
Dhaka (South) Grid Circle :
Ashuganj | 230/132 kV transformer OAT-12 | 2021-04-03 04:36 | 2021-04-03 06:08 | 1:32 | T | Tripped showing master trip, E/F relay | 0 | 0 | No interruption
Siddhirganj | 132/33 kV Transformer-T2 | 2021-04-09 07:21 | 2021-04-09 09:26 | 2:05 | E/O | Due to red-hot maintenance | 20 | 41.6667 | Power interruption
Sonargaon | 132/33 kV Transformer-T2 | 2021-04-08 06:30 | 2021-04-08 07:28 | 0:58 | E/O | Due to high temperature | 15 | 14.5 | Power interruption
|  |  | Total : | 4:35 |  | Unserved Energy: |  | 56.1667
Chattogram Grid Circle :
Halishahar | 132/33 kV Transformer-T2 | 2021-04-06 23:08 | 2021-04-07 | 0:52 | T | Tripped showing Diff O/C relay | 25 | 21.6667 | Power interruption
Dohazari | 132/33 kV Transformer-T-1,T2 | 2021-04-14 10:32 | 2021-04-14 10:48 | 0:16 | E/O | Due to fire at 33 kV Chandonish feeder | 60 | 16 | Power interruption
Halishahar | 132/33 kV Transformer-T2 | 2021-04-17 06:44 | 2021-04-17 06:51 | 0:07 | T | Due to feeder fault | 15 | 1.75 | Power interruption
|  |  | Total : | 1:15 |  | Unserved Energy: |  | 39.4167
Cumilla Grid Circle :
Chowmuhani | 132/33 kV Transformer-T2 | 2021-04-04 06:42 | 2021-04-04 10:20 | 3:38 | E/O | Due to red-hot maintenance | 40 | 145.3333 | Power interruption
Feni | 132/33 kV Transformer-T1 | 2021-04-04 20:47 | 2021-04-04 22:40 | 1:53 | E/O | Due to CT burst | 0 | 0 | No interruption
| Feni 132 kV bus | 2021-04-04 20:47 | 2021-04-04 22:40 | 1:53 | E/O | Due to CT burst | 0 | 0 | No interruption
Cumilla(S) | 132/33 kV transformers T-3 & T-4 | 2021-04-06 14:19 | 2021-04-06 14:48 | 0:29 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Kachua | 132/33 kV transformer T-2 | 2021-04-07 07:20 | 2021-04-07 08:05 | 0:45 | E/O | Due to red-hot maintenance at 33 kV feeder | 26 | 19.5 | Power interruption
Chatak | 132/33 kV transformer T-2 | 2021-04-11 06:44 | 2021-04-11 07:02 | 0:18 | T | Due to 33 kV Sunamganj feeder fault | 0 | 0 | No interruption
| 132/33 kV transformer T-3 | 2021-04-16 18:06 | 2021-04-16 18:33 | 0:27 | T | Due to 33 kV Sunamganj feeder fault | 0 | 0 | No interruption
Sylhet | 132/33 kV transformer T-1 | 2021-04-17 01:50 | 2021-04-17 02:22 | 0:32 | T | Tripped showing differential relay. | 7 | 3.7333 | Power interruption
B.Baria | 132/33 kV transformer T-1 | 2021-04-17 10:18 | 2021-04-17 11:09 | 0:51 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
B.Baria | 132/33 kV transformer T-2 | 2021-04-21 11:35 | 2021-04-21 12:44 | 1:09 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2021-04-22 09:15 | 2021-04-22 10:25 | 1:10 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Feni | 132/33 kV Transformer-T1 | 2021-04-23 09:20 | 2021-04-23 10:50 | 1:30 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Fenchuganj | 132/33 kV Transformer-T2 | 2021-04-24 10:05 | 2021-04-24 10:39 | 0:34 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sreemangal | 132/33 kV Transformer- T2 & T3 | 2021-04-27 14:57 | 2021-04-27 15:02 | 0:05 | T | Due to 33 kV REB feeder fault | 26 | 2.1667 | Power interruption
|  |  | Total : | 15:14 |  |  |  | 170.7333
Khulna Grid Circle :
Bhandaria | 132/33 kV transformers T-2 & T-3 | 2021-04-06 08:35 | 2021-04-06 09:05 | 0:30 | T | Tripped showing O/C and E/F relay | 16 | 8 | Power interruption
Gallamari | 132/33 kV transformers T-1 & T-2 | 2021-04-07 05:42 | 2021-04-07 05:54 | 0:12 | T | Tripped showing O/C relay | 26 | 5.2 | Power interruption
Patuakhali | 132/33 kV transformers T-1 & T-2 | 2021-04-08 10:58 | 2021-04-08 11:36 | 0:38 | T | Tripped showing O/C and E/F relay | 39 | 24.7 | Power interruption
Bottail | 132/33 kV Transformer-T-2 and 33 kV Bus | 2021-04-09 07:29 | 2021-04-09 12:12 | 4:43 | E/O | Due to 33 kV feeder fault. | 65 | 306.5833 | Power interruption
Madaripur | 132/33 kV Transformer-T-3 | 2021-04-11 13:30 | 2021-04-11 13:46 | 0:16 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Faridpur | 33 kV Bus-2 | 2021-04-16 08:40 | 2021-04-16 09:43 | 1:03 | E/O | Due to red-hot maintenance | 14 | 14.7 | Power interruption
Madaripur | 132/33 kV Transformer-T-1 | 2021-04-17 05:47 | 2021-04-17 07:27 | 1:40 | E/O | Due to over voltage | 0 | 0 | No interruption
|  |  | Total : | 9:02 |  | Unserved Energy: |  | 359.1833
HVDC Grid Circle : Nil
Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
Naogaon | 132/33 kV transformer T-2 | 2021-04-05 07:55 | 2021-04-05 08:08 | 0:13 | T | Tripped showing O/C and E/F relay | 10 | 2.1667 | Power interruption
Mohasthangarh | 132/33 kV transformer T-1 and 33 kV Breaker | 2021-04-08 05:46 | 2021-04-08 05:46 | 0:00 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mahastangar | 132/33 kV Transformer-T-1 | 2021-04-08 12:50 | 2021-04-08 14:34 | 1:44 | E/O | Due to red-hot maintenance | 11 | 19.0667 | Power interruption
| 132/33 kV Transformer-T-2 | 2021-04-08 12:50 | 2021-04-08 14:34 | 1:44 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 230/132 kV Transformer-T-1 | 2021-04-08 00:50 | 2021-04-08 01:05 | 0:15 | T | Tripped showing no relay | 0 | 0 | No interruption
Sherpur (Bogura) | 132/33 kV Transformer-T-2 | 2021-04-11 09:08 | 2021-04-11 10:39 | 1:31 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Pabna | 33 kV Bus | 2021-04-11 08:26 | 2021-04-11 10:11 | 1:45 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Sherpur (Bogura) | 132/33 kV Transformer-T-1 | 2021-04-11 10:50 | 2021-04-11 11:54 | 1:04 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV Transformer-T-1 | 2021-04-11 18:40 | 2021-04-11 19:37 | 0:57 | E/O | Due to red-hot maintenance | 110 | 104.5 | No interruption
| 132/33 kV Transformer-T-2 | 2021-04-11 18:40 | 2021-04-11 19:42 | 1:02 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
| 132/33 kV Transformer-T-3 | 2021-04-11 18:40 | 2021-04-11 19:55 | 1:15 | E/O | Due to flashing from LA of 33 kV bus | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T-1 | 2021-04-12 14:33 | 2021-04-12 15:40 | 1:07 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Bogura | 132/33 kV Transformer-T-3 & T-4 | 2021-04-12 18:50 | 2021-04-12 18:55 | 0:05 | T | Tripped showing Inst O/C relay | 60 | 5 | Power interruption
Naogaon | 132/33 kV Transformer-T-1 | 2021-04-16 15:25 | 2021-04-16 17:20 | 1:55 | E/O | Due to red-hot maintenance | 35 | 67.0833 | Power interruption
Bogura | 132/33 kV Transformer-T-3 & T-4 | 2021-04-17 16:37 | 2021-04-17 16:50 | 0:13 | T | Tripped showing O/C and E/F relay | 50 | 10.8333 | Power interruption
| 132/33 kV Transformer- T-4 & 33 kV extension Bus | 2021-04-17 16:50 | 2021-04-17 18:21 | 1:31 | E/O | Due to jumper cable down | 24 | 36.4 | Power interruption
Barapukuria | 132/33 kV Transformer-T-4 | 2021-04-20 13:54 | 2021-04-20 14:05 | 0:11 | T | Due to mechanical fault | 0 | 0 | No interruption
| 132/33 kV Transformer-T-4 | 2021-04-20 19:58 | 2021-04-20 21:38 | 1:40 | T | Due to mechanical fault | 47 | 78.3333 | Power interruption
Rajshahi(O) | 132/33 kV Transformer-T-2 | 2021-04-21 18:34 | 2021-04-21 19:57 | 1:23 | T | Tripped showing O/C relay | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-04-21 18:34 | 2021-04-21 18:34 | 0:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T1 | 2021-04-22 12:15 | 2021-04-22 16:30 | 4:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T4 & 33 kV Bus | 2021-04-22 16:07 | 2021-04-22 16:53 | 0:46 | E/O | Due to red-hot maintenance | 26 | 19.9333 | Power interruption
Bogura | 132/33 kV Transformer-T1 & 33 kV Bus | 2021-04-22 14:30 | 2021-04-22 15:53 | 1:23 | E/O | Due to red-hot maintenance | 60 | 83 | Power interruption
Mithapukur | 132/33 kV Transformer-T1 | 2021-04-22 14:02 | 2021-04-22 14:37 | 0:35 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 and its Bus | 2021-04-23 07:17 | 2021-04-23 08:52 | 1:35 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Kurigram | 132/33 kV Transformer-T1 | 2021-04-23 21:15 | 2021-04-23 22:51 | 1:36 | E/O | Due to red-hot maintenance | 10 | 16 | Power interruption
Mithapukur | 132/33 kV Transformer-T2 | 2021-04-24 06:55 | 2021-04-24 07:30 | 0:35 | T | Tripped showing O/C, E/F relay | 10 | 5.8333 | Power interruption
Sherpur(Bogura) | 132/33 kV Transformer-T2 | 2021-04-24 10:57 | 2021-04-24 12:12 | 1:15 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mithapukur | 132/33 kV Transformer-T2 | 2021-04-26 07:38 | 2021-04-26 08:17 | 0:39 | T | Tripped showing O/C, E/F relay | 4 | 2.6 | Power interruption
Barapukuria | 230/132 kV Transformer TR-1 | 2021-04-27 12:03 | 2021-04-27 13:37 | 1:34 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Mithapukur | 132/33 kV Transformer-T1 | 2021-04-28 17:53 | 2021-04-28 18:20 | 0:27 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T1 | 2021-04-29 00:04 | 2021-04-29 00:05 | 0:01 | E/O | Due to fall of sky wire on a 33 kV feeder | 0 | 0 | No interruption
Ishurdi | 132/33 kV Transformer-T1 and 33 kV bus | 2021-04-30 07:30 | 2021-04-30 08:15 | 0:45 | E/O | Due to red-hot maintenance | 18 | 13.5 | Power interruption
|  |  | Total : | 35:01 |  |  |  | 464.25
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 82:18 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:April 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | 230/132 kV Transformer-T03 | 2021-04-01 12:59 | 2021-04-01 13:50 | 0:51 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T2 | 2021-04-01 11:37 | 2021-04-01 14:07 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV Transformer-T3 | 2021-04-01 11:37 | 2021-04-01 14:07 | 2:30 | S/O | Due to SAS work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T3 | 2021-04-02 06:40 | 2021-04-02 06:40 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 |  | 2021-04-02 14:35 |  | S/O | After parallel | 0 | 0 | No interruption
Madanganj | Madanganj 132/33 kV transformer GT-1 | 2021-04-03 10:02 | 2021-04-03 19:36 | 9:34 | S/O | Due to 33 kV bus maintenance | 0 | 0 | No interruption
Netrokona | Netrokona 132/33 kV Transformer T-4 | 2021-04-02 09:04 | 2021-04-02 11:59 | 2:55 | S/O | Due to oil filling | 0 | 0 | No interruption
Rampura | Rampura-busber-2 | 2021-04-03 10:03 | 2021-04-03 16:55 | 6:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2021-04-03 09:36 | 2021-04-03 13:22 | 3:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishoreganj | 132/33 kV transformer T-3 | 2021-04-04 07:39 | 2021-04-04 12:50 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132 kV main Bus-1 | 2021-04-07 09:23 | 2021-04-07 17:12 | 7:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | j 230/132 kV transformer ATR-01 | 2021-04-07 10:52 | 2021-04-07 10:52 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kadda | 132 kV main Bus-2 | 2021-04-08 07:11 | 2021-04-08 13:49 | 6:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Mogbazar | 133 kV reserve Bus | 2021-04-08 08:25 | 2021-04-08 08:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132 kV Bus-1 & 2 | 2021-04-09 06:26 | 2021-04-09 12:32 | 6:06 | S/O | Due to D/W work | 165 | 1006.5 | Power interruption
Jamalpur | 132/33 kV Transformer-T1 | 2021-04-10 14:28 | 2021-04-10 16:54 | 2:26 | S/O | Due to C/M work | 4 | 9.7333 | Power interruption
Netrokona | 132/33 kV transformer T-1 , T2 | 2021-04-10 09:35 | 2021-04-10 11:35 | 2:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Moghbazar | 132 kV main Bus | 2021-04-11 08:28 | 2021-04-11 18:06 | 9:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T1 | 2021-04-11 09:07 | 2021-04-11 15:43 | 6:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-04-11 09:01 | 2021-04-11 10:20 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-04-11 11:40 | 2021-04-11 12:24 | 0:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | 230/132 kV ATR-01 Transformer |  | 2021-04-12 11:10 |  | S/O | After maintenance work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T1 | 2021-04-12 09:26 | 2021-04-12 17:50 | 8:24 | S/O | Due to SCADA work | 0 | 0 | No interruption
Aminbazar | 132 kV main Bus-1 | 2021-04-12 14:48 | 2021-04-12 19:59 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2021-04-13 08:31 | 2021-04-13 18:36 | 10:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Mirpur | 132/33 kV Transformer-T3 | 2021-04-13 08:16 | 2021-04-13 22:05 | 13:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | 132/33 kV Transformer-T1 | 2021-04-15 09:45 | 2021-04-15 16:01 | 6:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj | 230/132 kV T-01 Transformer | 2021-04-20 13:09 | 2021-04-20 14:02 | 0:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj (new) | 230/132 kV T-02 Transformer | 2021-04-21 12:01 | 2021-04-21 12:01 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132 kV Bus-1 | 2021-04-22 10:22 | 2021-04-22 15:47 | 5:25 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 33 kV bus-A | 2021-04-24 09:54 | 2021-04-24 13:53 | 3:59 | S/O | Due to PBS work | 0 | 0 | No interruption
Tongi | 132 kV Bus-2 | 2021-04-24 10:07 | 2021-04-24 14:45 | 4:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 132 kV Bus-2 | 2021-04-27 07:14 | 2021-04-27 07:14 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T2 | 2021-04-29 09:14 | 2021-04-29 17:05 | 7:51 | S/O | Due to maintenance work | 0 | 0 | No interruption
Keraniganj | 230/132 kV T-2 Transformer |  | 2021-04-29 14:25 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 143:56 |  | Unserved Energy: |  | 1016.2333
Dhaka (South) Grid Circle :
Rampura | 132 kV mai Bus-2 | 2021-04-01 08:29 | 2021-04-01 18:33 | 10:04 | S/O | Due to maintenance work | 0 | 0 | No interruption
Hasnabad | 230/132 kVTransformer-T1 |  | 2021-04-05 00:29 |  | S/O | After maintenance work | 0 | 0 | No interruption
Keraniganj | 132/33 Kv transformer T1 | 2021-04-09 16:18 | 2021-04-09 17:25 | 1:07 | S/O | Due to 33 kV bus section maint. | 0 | 0 | No interruption
Satmosjid | 132/33 Kv transformer T2 | 2021-04-10 09:35 | 2021-04-10 17:55 | 8:20 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 19:31 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Halishahar | Halishahar 132/33 kV transformer T-2 | 2021-04-03 07:50 | 2021-04-03 10:59 | 3:09 | S/O | Due to C/M work | 10 | 31.5 | Power interruption
Julda | Julda 132/33 kV transformers T-1 & T-2 | 2021-04-03 08:23 | 2021-04-03 17:31 | 9:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(Old) | 132/33 kV transformers T-3 & T-4 | 2021-04-05 08:40 | 2021-04-05 10:35 | 1:55 | S/O | Due to C/M work | 10 | 19.1667 | Power interruption
Madunaghat | 132/33 kV Transformer-T2 | 2021-04-09 08:43 | 2021-04-09 14:25 | 5:42 | S/O | Due to project work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2021-04-10 09:54 | 2021-04-10 16:26 | 6:32 | S/O | Due to D/W work | 0 | 0 | No interruption
Madunaghat | 132/33 kV Transformer-T2 | 2021-04-10 09:54 | 2021-04-10 16:26 | 6:32 | S/O | Due to D/W work | 2 | 13.0667 | Power interruption
Chowmuhani | 132/33 kV Transformer-T1 | 2021-04-12 07:03 | 2021-04-12 09:15 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Cox'sbazar | 132/33 kV Transformer-T1 | 2021-04-13 06:50 | 2021-04-13 08:40 | 1:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV GIS Bus-1 | 2021-04-19 09:52 | 2021-04-19 16:50 | 6:58 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV GIS Bus-2 | 2021-04-21 10:19 | 2021-04-21 16:36 | 6:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 230/132 kV Transformer-T-03 | 2021-04-22 10:06 | 2021-04-22 10:32 | 0:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132 kV Bus-2 | 2021-04-22 09:26 | 2021-04-22 12:16 | 2:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | 132/33 kV Transformer-T1 and 33 kV Bus | 2021-04-22 11:13 | 2021-04-22 12:08 | 0:55 | S/O | Due to C/M work | 20 | 18.3333 | Power interruption
Sikalbaha | 230/132 kV Transformer-TR1 | 2021-04-24 10:15 | 2021-04-24 14:21 | 4:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | 230/132 kV Transformer-T2 | 2021-04-25 10:47 | 2021-04-25 13:05 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 60:50 |  | Unserved Energy : |  | 82.0667
Cumilla Grid Circle :
Shahjibazar | 132/33 kV transformers T-4 & T-6 | 2021-04-02 08:35 | 2021-04-02 10:54 | 2:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kVtransformer T-4 | 2021-04-06 10:08 | 2021-04-06 16:02 | 5:54 | S/O | Due to CT replacement | 0 | 0 | No interruption
Sunamgan | 132/33 kV transformer T-2 | 2021-04-06 07:26 | 2021-04-06 08:12 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kVtransformer T-2 | 2021-04-07 08:34 | 2021-04-07 18:27 | 9:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj 132 kV Bus-2 | 2021-04-08 07:36 | 2021-04-08 07:36 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kVtransformer T-2 | 2021-04-08 10:08 | 2021-04-08 18:24 | 8:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kV Transformer-T1 and 33 kV Bus | 2021-04-08 07:55 | 2021-04-08 09:55 | 6:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj 132 kV Bus-1 | 2021-04-08 12:49 | 2021-04-08 17:17 | 4:28 | S/O | Due to maintenance work. | 0 | 0 | No interruption
Ramganj | 132/33 kV transformer T-2 | 2021-04-09 08:07 | 2021-04-09 09:41 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV transformer T-3 | 2021-04-10 08:31 | 2021-04-10 10:42 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| 132/33 kV transformer T-4 | 2021-04-10 12:07 | 2021-04-10 12:55 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj 230 kV GIS Bus | 2021-04-11 08:58 | 2021-04-11 17:18 | 8:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-1 | 2021-04-13 09:31 | 2021-04-13 14:25 | 4:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | 132/33 kV transformer T-1 | 2021-04-15 11:17 | 2021-04-15 12:20 | 1:03 | S/O | Due to auxiliary X-former maint. | 0 | 0 | No interruption
Shahjibazar | 132/33 kV transformer T-2 | 2021-04-18 09:05 | 2021-04-18 15:15 | 6:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T-2 | 2021-04-20 07:34 | 2021-04-20 09:21 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Fenchuganj | 230/132 kV transformer AT-2 | 2021-04-24 07:27 | 2021-04-24 09:59 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Chattak | 132/33 kV transformer T-2 | 2021-04-28 10:00 | 2021-04-28 10:45 | 0:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Sunamganj | 132/33 kV transformer T-1 | 2021-04-28 10:01 | 2021-04-28 11:19 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Biyanibazar | 132/33 kV transformer T-2 | 2021-04-30 15:48 | 2021-04-30 16:51 | 1:03 | S/O | Due to C/M work | 20 | 21 | Power interruption
|  |  | Total : | 70:51 |  | Unserved Energy : |  | 21
Khulna Grid Circle :
Bagerhat | Bagerhat 132/33 kV transformer T3 | 2021-04-02 07:15 | 2021-04-02 07:15 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2021-04-02 07:04 | 2021-04-02 07:04 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria | Bhandaria 132/33 kV transformer T-1 | 2021-04-02 07:41 | 2021-04-02 07:41 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bhandaria 132/33 kV transformer T-1 | 2021-04-03 06:57 | 2021-04-03 18:15 | 11:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj Old 132/33 kV transformer T-1 | 2021-04-03 07:03 | 2021-04-03 12:42 | 5:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | Madaripur 132/33 kV transformer T-2 | 2021-04-03 07:30 | 2021-04-03 11:52 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 transformers T1, T2 and T3 | 2021-04-03 07:42 | 2021-04-03 08:14 | 0:32 | S/O | Due to C/M work | 70 | 37.3333 | Power interruption
Faridpur | Faridpur 132 kV Bus-A | 2021-04-03 09:32 | 2021-04-03 18:32 | 9:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhandaria | Bhandaria 132/33 kV transformer T-1 | 2021-04-04 12:30 | 2021-04-04 16:44 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur 132/33 kV transformer T3 | 2021-04-05 07:38 | 2021-04-05 18:20 | 10:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur 132/33 kV transformer T3 | 2021-04-06 08:10 | 2021-04-06 12:55 | 4:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T-3 and 33 kv | 2021-04-07 16:08 | 2021-04-07 17:20 | 1:12 | S/O | Due to 33 kV feeder maint | 11 | 13.2 | Power interruption
bus section
Faridpur | Faridpur 132/33 kV transformer T3 | 2021-04-09 09:52 | 2021-04-09 10:10 | 0:18 | S/O | Due to 33 kV auxiliary transformer maint | 45 | 13.5 | Power interruption
Madaripur | 132/33 kV transformer T3 | 2021-04-09 08:18 | 2021-04-09 13:12 | 4:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 | 2021-04-10 08:33 | 2021-04-10 10:09 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-B | 2021-04-11 10:37 | 2021-04-11 12:58 | 2:21 | S/O | Due to bus PT work | 0 | 0 | No interruption
Khulna© | 132/33 kV transformer T1 and 33 kV Bus | 2021-04-12 07:05 | 2021-04-12 09:12 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Goalpara | 132/33 kV transformer T6 | 2021-04-13 07:31 | 2021-04-13 09:27 | 1:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 | 2021-04-13 07:37 | 2021-04-13 09:08 | 1:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 | 2021-04-13 09:50 | 2021-04-13 12:48 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV transformer T2 | 2021-04-17 07:30 | 2021-04-17 07:30 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132 kV Bus-1 | 2021-04-18 08:57 | 2021-04-18 14:14 | 5:17 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-2 | 2021-04-18 10:20 | 2021-04-18 11:58 | 1:38 | S/O | Due to D/W work | 0 | 0 | No interruption
| 133 kV Bus | 2021-04-19 09:40 | 2021-04-19 14:09 | 4:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T1 | 2021-04-21 09:44 | 2021-04-21 12:35 | 2:51 | S/O | Due to CT loop replacement | 0 | 0 | No interruption
Faridpur | 132/33 kV transformer T2 | 2021-04-21 09:44 | 2021-04-21 13:16 | 3:32 | S/O | Due to CT loop replacement | 7 | 24.7333 | Power interruption 09:44 to 13:16
Barishal(S) | 132/33 kV transformer T2 | 2021-04-22 07:01 | 2021-04-22 07:34 | 0:33 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(S) | 132/33 kV transformer T1 | 2021-04-22 07:36 | 2021-04-22 08:08 | 0:32 | S/O | Due to C/M work | 14 | 15.6333 | Power interruption 7:01 to 8:08
Khulna | 132/33 kV transformer T3 | 2021-04-23 08:36 | 2021-04-23 11:20 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(c) | 132/33 kV transformer T3 | 2021-04-23 15:15 | 2021-04-23 15:42 | 0:27 | S/O | Due to C/M work | 15 | 6.75 | Power interruption
Gallamari | 132/33 kV transformer T1 | 2021-04-28 08:13 | 2021-04-29 16:06 | 31:53 | S/O | Due to D/W work | 0 | 0 | No interruption
| 132 kV Bus-1 | 2021-04-28 08:16 | 2021-04-29 15:56 | 31:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T2 | 2021-04-28 08:02 | 2021-04-28 09:29 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132 kV Bus-2 | 2021-04-30 08:24 | 2021-04-30 15:41 | 7:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Gallamari | 132/33 kV transformer T1 | 2021-04-30 08:31 | 2021-04-30 15:16 | 6:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Goalpara | 132 kV Bus-A | 2021-04-30 10:15 | 2021-04-30 14:10 | 3:55 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 174:25 |  | Unserved Energy : |  | 111.15
Page: 4/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
HVDC Grid Circle :Nil
Nil
|  |  | Total : | 0:00 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Mahastangar | 132/33 kV Transformer-T-2 | 2021-04-02 15:08 | 2021-04-02 16:16 | 1:08 | S/O | Due to 33 kV feeder maint. | 22 | 24.9822 | Power interruption
| 33 kV Bus section-2 | 2021-04-02 15:08 | 2021-04-02 16:16 | 1:08 | S/O | Due to 33 kV feeder maint. | 0 | 0
Sherpur | 132/33 kV transformer T-3 | 2021-04-04 09:18 | 2021-04-04 16:42 | 7:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV T-3 transformer and 33 kV Bus | 2021-04-06 09:14 | 2021-04-06 17:04 | 7:50 | S/O | Due to C/M work | 25 | 195.8333 | Power interruption
Sherpur | 132/33 kV transformer T-3 | 2021-04-06 10:45 | 2021-04-06 16:40 | 5:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Kurigram | 132/33 kV transformer T-1 and 33 kV Bus | 2021-04-06 12:09 | 2021-04-06 12:57 | 0:48 | S/O | Due to 33 kV maintenance | 18 | 14.4 | Power interruption
Purbasadipur | 132/33 kV transformer T-3 | 2021-04-07 11:20 | 2021-04-07 12:28 | 1:08 | S/O | Due to C/M work | 25 | 28.3333 | Power interruption
Purbasadipur | 132/33 kV transformer T1 | 2021-04-08 09:31 | 2021-04-08 18:06 | 8:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T4 | 2021-04-09 11:02 | 2021-04-09 14:58 | 3:56 | S/O | Due to sky wire work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformer T3 | 2021-04-09 11:08 | 2021-04-09 14:50 | 3:42 | S/O | Due to 33 kV bus maint. | 17 | 62.9 | Power interruption
Chapainawabganj | 132/33 kV transformer T3 & T4 | 2021-04-10 09:48 | 2021-04-10 17:52 | 8:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Purbasadipur | 132/33 kV transformer T-3 | 2021-04-10 09:15 | 2021-04-10 16:33 | 7:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Mohasthangarh | 132/33 kV transformers T-1 & T-2 | 2021-04-13 09:46 | 2021-04-13 12:10 | 2:24 | S/O | Due to 33 kV Bus maint | 45 | 108 | Power interruption
Sherpur | 132/33 kV transformers T-3 | 2021-04-13 09:55 | 2021-04-13 11:40 | 1:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhangura | 132/33 kV transformers T-1 | 2021-04-13 12:33 | 2021-04-13 17:01 | 4:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhangura | 132/33 kV transformers T-1 | 2021-04-15 10:35 | 2021-04-15 17:56 | 7:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | 132/33 kV transformers T-3 & its 33 kV Bus section | 2021-04-18 11:16 | 2021-04-18 14:22 | 3:06 | S/O | Due to C/M work | 25 | 77.5 | Power interruption
Barapukuria | 132 kV Bus-1 | 2021-04-19 09:44 | 2021-04-19 13:38 | 3:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV transformers T-3 | 2021-04-20 09:10 | 2021-04-20 13:09 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV transformers T-1 | 2021-04-21 07:05 | 2021-04-21 10:34 | 3:29 | S/O | Due to C/M work | 40 | 139.3333 | Power interruption
Barapukuria | 230/132 kV transformers T-1 | 2021-04-23 11:49 | 2021-04-23 13:54 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV transformers TR-2 | 2021-04-28 07:37 | 2021-04-28 07:37 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 89:27 |  | Unserved Energy : |  | 651.2822
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 559:00 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:April 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Bhaluka | Bhaluka-Mymensingh 132 kV line-1 | 2021-04-01 09:39 | 2021-04-01 20:38 | 10:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Mogbazar 132 kV line-1 | 2021-04-02 08:37 | 2021-04-02 21:53 | 13:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-1 | 2021-04-03 07:35 | 2021-04-03 18:11 | 10:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-04-03 09:21 | 2021-04-03 18:31 | 9:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Jamalpur 132 kV line-1 | 2021-04-03 07:35 | 2021-04-03 18:11 | 10:36 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2021-04-03 08:40 | 2021-04-03 18:06 | 9:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV line-2 | 2021-04-04 08:58 | 2021-04-04 15:07 | 6:09 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Mirpur 132 kV line-2 | 2021-04-04 09:24 | 2021-04-04 17:40 | 8:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensigh-Kishoreganj 132 kV line-1 | 2021-04-04 09:45 | 2021-04-04 22:40 | 12:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV line-1 | 2021-04-04 09:54 | 2021-04-04 12:12 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensigh | Mymensing-Jamalpur 132 kV line-1 | 2021-04-05 08:27 | 2021-04-05 16:39 | 8:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 132 kV line-2 | 2021-04-05 16:53 | 2021-04-05 17:18 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2021-04-07 09:59 | 2021-04-07 15:59 | 6:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Mogbazar 132 kV line-1 | 2021-04-07 08:37 | 2021-04-07 19:59 | 11:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-2 | 2021-04-07 16:16 | 2021-04-07 17:03 | 0:47 | S/O | Due to protection test | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-1 | 2021-04-07 16:15 | 2021-04-07 16:22 | 0:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2021-04-08 07:43 | 2021-04-08 16:39 | 8:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV line-2 | 2021-04-08 12:19 | 2021-04-08 16:36 | 4:17 | S/O | Due to protection test. | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-2 | 2021-04-09 07:03 | 2021-04-09 16:36 | 9:33 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensigh | Mymensingh-Netrakona 132 kV line-1 | 2021-04-09 16:44 | 2021-04-09 18:14 | 1:30 | S/O | Due to removing kite. | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-2 | 2021-04-10 07:28 | 2021-04-10 17:23 | 9:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | Savar-Manikganj-162 MW 132 kV line-2 | 2021-04-11 08:54 | 2021-04-11 18:05 | 9:11 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | Mymensing-Kishorganj 132 kV line-2 | 2021-04-11 11:09 | 2021-04-11 12:01 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Jamalpur 132 kVline-1 | 2021-04-11 12:07 | 2021-04-11 12:57 | 0:50 | S/O | Due to D/W work. | 0 | 0 | No interruption
| Mymensing-Mymensing RPCL 132 kV line-1 | 2021-04-11 14:18 | 2021-04-11 15:56 | 1:38 | S/O | Due to protection test | 0 | 0 | No interruption
| Mymensing-Mymensing RPCL 132 kV line-2 | 2021-04-11 15:57 | 2021-04-11 16:25 | 0:28 | S/O | Due to protection test | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-04-12 07:18 | 2021-04-12 07:18 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar- | Aminbazar-Kaliakoir 230 kV line-1 | 2021-04-13 07:41 | 2021-04-13 15:31 | 7:50 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Kaliakoir 230 kV line-2 | 2021-04-13 15:41 | 2021-04-13 21:23 | 5:42 | S/O | Due to C/M work | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-1 | 2021-04-14 08:25 | 2021-04-14 08:25 | 0:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-1 | 2021-04-15 08:21 | 2021-04-15 16:18 | 7:57 | S/O | Due to D/W work. | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-2 | 2021-04-15 08:22 | 2021-04-15 16:28 | 8:06 | S/O | Due to D/W work. | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-2 | 2021-04-16 08:17 | 2021-04-16 16:39 | 8:22 | S/O | Due to D/W work. | 0 | 0 | No interruption
| Aminbazar-Keraniganj 230 kV line-1 | 2021-04-16 08:17 | 2021-04-16 16:25 | 8:08 | S/O | Due to D/W work. | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kabirpur 132 kV line-2 | 2021-04-18 13:11 | 2021-04-18 14:05 | 0:54 | S/O | Due to protection test | 0 | 0 | No interruption
Rampura- | Rampura-Bhulta 230 kV line-3 | 2021-04-19 08:38 | 2021-04-19 14:05 | 5:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar- | Aminbazar-Mirpur 132 kV line-1 | 2021-04-19 09:08 | 2021-04-19 15:13 | 6:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV line-1 | 2021-04-20 09:23 | 2021-04-20 13:52 | 4:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Moghbazar 132 kV line-1 | 2021-04-20 11:46 | 2021-04-20 16:24 | 4:38 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-04-20 10:06 | 2021-04-20 14:56 | 4:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-04-21 10:12 | 2021-04-21 12:58 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-2 | 2021-04-22 10:07 | 2021-04-22 14:35 | 4:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Mirpur | Mirpur-Aminbazar 132 kV line-1 | 2021-04-22 14:40 | 2021-04-22 14:48 | 0:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV line-1 | 2021-04-23 09:04 | 2021-04-23 11:38 | 2:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Agargaon 230 kV line-1 | 2021-04-28 11:11 | 2021-04-28 14:11 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Sreenagar 132 kV line--1 & 2 |  | 2021-04-28 16:34 |  | S/O | After maintenance work | 0 | 0 | No interruption
Keraniganj | Keraniganj-Aurahati 132 kV line |  | 2021-04-28 16:39 |  | S/O | After maintenance work | 0 | 0 | No interruption
|  |  | Total : | 253:08 |  | Unserved Energy: |  | 0
Page: 2/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (South) Grid Circle :
Ghorashal | Ghorasal-Norsingdi 132 kV line-3 |  | 2021-04-05 00:01 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Aurahati 132 kV line | 2021-04-08 04:39 | 2021-04-08 04:39 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Kamrangirchar-Aurahati 132 kV line |  | 2021-04-09 20:37 |  | S/O | After maintenance work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj GT-1 P/P 132 kV line-1 | 2021-04-10 09:22 | 2021-04-10 17:26 | 8:04 | S/O | Due to relay change | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shyampur 230 kV line-1 | 2021-04-12 08:24 | 2021-04-12 10:27 | 2:03 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbag 132 kV line | 2021-04-23 04:34 | 2021-04-23 08:49 | 4:15 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hasnabad-Kamrangirchar 132 kV line | 2021-04-23 04:56 | 2021-04-23 11:01 | 6:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-2 | 2021-04-24 09:25 | 2021-04-24 17:40 | 8:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensing-RPCL 132 kV Ckt-2 | 2021-04-25 06:59 | 2021-04-25 16:44 | 9:45 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 38:27 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-04-01 07:03 | 2021-04-01 17:18 | 10:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-04-02 09:09 | 2021-04-02 13:28 | 4:19 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-(Matarbari)-Cox'sbazar 132 kV line-1 | 2021-04-03 06:24 | 2021-04-03 20:50 | 14:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2021-04-03 08:50 | 2021-04-03 12:50 | 4:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-04-03 10:44 | 2021-04-03 14:06 | 3:22 | S/O | Due to D/W work | 0 | 0 | No interruption
| Hathazari-Baraulia 132 kV line-2 | 2021-04-04 07:49 | 2021-04-04 07:49 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2021-04-04 09:03 | 2021-04-04 13:18 | 4:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-2 | 2021-04-05 08:53 | 2021-04-05 13:30 | 4:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV line-2 | 2021-04-06 08:52 | 2021-04-06 12:45 | 3:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroirhat 132 kV line-1 | 2021-04-07 10:04 | 2021-04-07 11:13 | 1:09 | S/O | Due to tree trimming | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-2 | 2021-04-08 09:29 | 2021-04-08 09:29 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(N) | Sikalbaha(N)-Madunaghat 132 kV line | 2021-04-10 10:11 | 2021-04-10 16:50 | 6:39 | S/O | Due to project work. | 0 | 0 | No interruption
| Sikalbaha(N)-Shahmirpur 132 kV line-1 | 2021-04-10 09:58 | 2021-04-10 17:00 | 7:02 | S/O | Due to project work. | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-04-12 09:28 | 2021-04-12 11:47 | 2:19 | S/O | Due to tree trimming | 0 | 0 | No interruption
Baroaulia | Baroaulia-Hathazari 132 kV line-2 | 2021-04-13 07:10 | 2021-04-13 10:02 | 2:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Shahmirpur 132 kV line-2 | 2021-04-15 09:00 | 2021-04-15 15:40 | 6:40 | S/O | Due to D/W work | 0 | 0 | No interruption
Julda | Julda-Sikalbaha 132 kV line | 2021-04-16 09:24 | 2021-04-16 14:53 | 5:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha GIS-Sikalbaha 132 kV line-1 | 2021-04-17 09:26 | 2021-04-17 15:50 | 6:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | Hathazari-Baraulia 132 kV line-2 | 2021-04-17 13:40 | 2021-04-17 16:16 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha(New) | Sikalbaha(New)-Sikalbaha(Old) 132 kV line | 2021-04-18 09:24 | 2021-04-18 15:53 | 6:29 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line | 2021-04-23 06:36 | 2021-04-23 09:32 | 2:56 | S/O | Due to D/W work | 20 | 58.6667 | Power interruption
Hathazari | Hathazari-Madunaghat 132 kV line | 2021-04-23 08:42 | 2021-04-23 16:48 | 8:06 | S/O | Due to project work | 0 | 0 | No interruption
Dohazari | Dohazari-Matarbari-Cox'sbazar 132 kV line | 2021-04-23 14:03 | 2021-04-23 15:45 | 1:42 | S/O | Due to D/W work | 30 | 51 | Power interruption
Hathazari | Hathazari-Madunaghat 132 kV line | 2021-04-24 10:33 | 2021-04-24 17:03 | 6:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-TK Chemical 132 kV line | 2021-04-26 09:03 | 2021-04-26 13:33 | 4:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha GIS-Dohazari 132 kV line-2 | 2021-04-27 09:39 | 2021-04-27 16:42 | 7:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Dohazari 132 kV line-1 | 2021-04-29 09:00 | 2021-04-29 13:14 | 4:14 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangamati | Rangamati-Khagrachari 132 kV line-2 | 2021-04-30 10:43 | 2021-04-30 11:10 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 132:14 |  | Unserved Energy: |  | 109.6667
Cumilla Grid Circle :
Sreemongal | Sreemongal-Shahjibazar 132 kV line-1 | 2021-04-01 09:49 | 2021-04-01 11:31 | 1:42 | S/O | Due to Tree trimming | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV line | 2021-04-01 07:23 | 2021-04-01 18:00 | 10:37 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV line | 2021-04-02 07:47 | 2021-04-02 17:53 | 10:06 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV line | 2021-04-03 07:26 | 2021-04-03 07:26 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV line-1 | 2021-04-04 08:31 | 2021-04-04 17:36 | 9:05 | S/O | Due to D/W work | 0 | 0 | No interruption
| Baroierhat-PHP 132 kV line | 2021-04-06 08:45 | 2021-04-06 08:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2021-04-06 09:41 | 2021-04-06 20:58 | 11:17 | S/O | Due to protection test | 0 | 0 | No interruption
B.Baria- | B.Baria-Shahjibazar 132 kV line-2 | 2021-04-07 13:15 | 2021-04-07 14:35 | 1:20 | S/O | Due to Tree trimming | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-1 | 2021-04-08 07:56 | 2021-04-08 10:02 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-04-08 13:01 | 2021-04-08 17:27 | 4:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj- | Ramganj-Chandpur Desh P/P 132 kV line-1 | 2021-04-10 08:25 | 2021-04-10 09:48 | 1:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahmirpur 132 kV line-3 | 2021-04-10 08:17 | 2021-04-10 15:11 | 6:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2021-04-11 10:52 | 2021-04-11 15:59 | 5:07 | S/O | Due to protection test | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2021-04-11 16:01 | 2021-04-11 17:54 | 1:53 | S/O | Due to protection test | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-2 | 2021-04-12 06:40 | 2021-04-12 14:06 | 7:26 | S/O | Due to C/M work | 0 | 0 | No interruption
Baroierhat | Baroierhat-PHP 132 kV line |  | 2021-04-12 16:24 |  | S/O | After maintenance | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV line-1 | 2021-04-13 10:22 | 2021-04-13 12:30 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV line | 2021-04-13 08:10 | 2021-04-13 08:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chattak | Chattak-Sylhet 132 kV line-2 |  | 2021-04-13 15:20 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2021-04-17 12:08 | 2021-04-17 15:15 | 3:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj- | Ashuganj-Kishoreganj 132 kV line-2 | 2021-04-18 12:09 | 2021-04-18 17:31 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2021-04-18 13:17 | 2021-04-18 14:16 | 0:59 | S/O | Due to protection test | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-04-19 08:32 | 2021-04-19 16:21 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chowmuhoni 132 kV line-1,2 | 2021-04-19 11:04 | 2021-04-19 12:36 | 1:32 | S/O | Due to tree trimming. | 0 | 0 | No interruption
Ashuganj | Ashuganj -Modular P.P. 230 kV line | 2021-04-22 12:54 | 2021-04-22 19:41 | 6:47 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-PHP 132 kV line |  | 2021-04-24 12:02 |  | S/O | After maintenance | 0 | 0 | No interruption
Feni | Feni-Baroiarhat 132 kV line | 2021-04-24 13:00 | 2021-04-24 15:12 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj- | Ashuganj-Sirajganj 230 kV Ckt-1 |  | 2021-04-29 10:05 |  | S/O | After maintenance | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishoreganj 132 kV line-2 | 2021-04-29 11:16 | 2021-04-29 17:04 | 5:48 | S/O | Due to OPGW work | 0 | 0 | No interruption
|  |  | Total : | 109:06 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna© | Khulna©-Satkhira 132 kV line-2 | 2021-04-02 07:52 | 2021-04-02 12:02 | 4:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj New 400 kV line-2 | 2021-04-02 08:18 | 2021-04-02 08:39 | 0:21 | S/O | Due to Gopalganj(New) ATR-02 S/D | 0 | 0 | No interruption
Gopalganj | Gopalganj New 400/132 kV transformer ATR-02 | 2021-04-02 08:22 | 2021-04-02 16:16 | 7:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | Gopalganj-Madaripur 132 kV line-3 | 2021-04-02 15:32 | 2021-04-02 17:40 | 2:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhandaria- | Bhandaria-Barishal 132 kV line-1 | 2021-04-10 10:59 | 2021-04-10 11:42 | 0:43 | S/O | Due to clearing right of way | 0 | 0 | No interruption
Gopalganj(N) | Gopalganj(N)-Madaripur 132 kV line-3 | 2021-04-10 08:17 | 2021-04-10 15:11 | 6:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-04-12 07:25 | 2021-04-12 07:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Khulna(C) 132 kV line-1 | 2021-04-13 08:39 | 2021-04-13 10:10 | 1:31 | S/O | Due to D/W work | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV line-1 | 2021-04-30 11:22 | 2021-04-30 15:09 | 3:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 27:28 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
Bheramara | Bheramara-Faridpur 132 kV line-1 | 2021-04-02 08:55 | 2021-04-02 19:43 | 10:48 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2021-04-03 07:18 | 2021-04-03 07:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-1 | 2021-04-04 07:25 | 2021-04-04 07:25 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
| Bheramara-Faridpur 132 kV line-2 | 2021-04-05 06:56 | 2021-04-05 06:56 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
| Bheramara HVDC Block-1 | 2021-04-08 07:03 | 2021-04-08 08:20 | 1:17 | S/O | Due to maintenance | 0 | 0 | No interruption
| HVDC Bheramara-Bahrampur 400 kV line-2 | 2021-04-08 10:21 | 2021-04-08 19:12 | 8:51 | S/O | Due to D/W work | 0 | 0 | No interruption
| HVDC Bheramara-Bahrampur 400 kV line-1 | 2021-04-10 09:59 | 2021-04-10 17:50 | 7:51 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | Bheramara-Faridpur 132 kV line-2 | 2021-04-12 09:05 | 2021-04-12 09:57 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-HVDC 230 kV line-1 | 2021-04-21 08:46 | 2021-04-21 14:05 | 5:19 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | HVDC-Bheramara 400 kV line |  | 2021-04-22 13:48 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 34:58 |  | Unserved Energy: |  | 0:00
Page: 5/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:March 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Bogura Grid Circle :
Bogura | Bogura-Barapukuria S/S 230 kV line-1 | 2021-04-02 11:36 | 2021-04-02 14:16 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line-1 | 2021-04-03 10:18 | 2021-04-03 17:23 | 7:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Barapukuria 230 kV line-1 | 2021-04-03 09:51 | 2021-04-03 12:55 | 3:04 | S/O | Due to Protection test | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV line-2 |  | 2021-04-03 13:55 |  | S/O | After maintenance | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line-1 | 2021-04-04 09:42 | 2021-04-04 17:50 | 8:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(old) | Rajshahi(old)-Natore 132 kV line-1 | 2021-04-04 11:11 | 2021-04-04 16:54 | 5:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Bhangura | Baghabari-Bhangura 132 kV line | 2021-04-06 11:17 | 2021-04-06 17:34 | 6:17 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line-1 | 2021-04-07 10:16 | 2021-04-07 18:04 | 7:48 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(N) | Rajshahi(N)-Rajshahi(O) 132 kV line-1 | 2021-04-10 11:57 | 2021-04-11 17:43 | 29:46 | S/O | Due to breaker maintenance | 0 | 0 | No interruption
Bhangura | Bhangura-Baghabari-71 MW 132 kV line | 2021-04-11 10:47 | 2021-04-11 17:01 | 6:14 | S/O | Due to SAS maintenance | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line | 2021-04-12 08:40 | 2021-04-12 09:07 | 0:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line-1 |  | 2021-04-12 19:08 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur Confidence 132 kV line-1 | 2021-04-13 08:46 | 2021-04-13 11:57 | 3:11 | S/O | Due to C/M work | 0 | 0 | No interruption
| Rangpur S/S-Rangpur Confidence 132 kV line-2 | 2021-04-13 12:40 | 2021-04-13 15:17 | 2:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line-2 |  | 2021-04-13 19:01 |  |  | new connection | 0 | 0 | No interruption
Rajshahi(Old) | Rajshahi(Old)-Rajshahi(New) 132 kV line-1 | 2021-04-14 07:12 | 2021-04-14 07:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Saidpur 132 kV line-1,2 | 2021-04-14 08:16 | 2021-04-14 14:19 | 6:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | Sherpur-UMPL 132 kV line-1 | 2021-04-17 10:09 | 2021-04-17 11:13 | 1:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line | 2021-04-18 10:01 | 2021-04-18 17:22 | 7:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Katakhali P.P | Katakhali P.P.-Katakhali S/S 132 kV line | 2021-04-18 10:34 | 2021-04-18 13:30 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | Barapukuria-Rangpur 132 kV line-2 | 2021-04-19 09:14 | 2021-04-19 12:28 | 3:14 | S/O | Due to C/M work | 0 | 0 | No interruption
| Barapukuria-Rangpur 132 kV line-1 | 2021-04-19 12:32 | 2021-04-19 13:45 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Chapainawabganj | Chapainawabganj-Amnura 132 kV line |  | 2021-04-20 13:45 |  | S/O | After maintenance | 0 | 0 | No interruption
Barapukuria | Barapukuria S/S-Barapukuria P/S 230 kV line-1 | 2021-04-23 08:30 | 2021-04-23 11:30 | 3:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi(N) 132 kV line | 2021-04-27 07:29 | 2021-04-27 07:29 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -1 | 2021-04-27 11:04 | 2021-04-27 18:22 | 7:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Rajshahi(O) | Rajshahi(O)-Rajshahi(N) 132 kV line-2 | 2021-04-28 07:10 | 2021-04-28 07:10 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -1 | 2021-04-28 09:18 | 2021-04-28 17:40 | 8:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-04-29 08:02 | 2021-04-29 15:22 | 7:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Baghabari | Baghabari-Bhangura 132 kV line -2 | 2021-04-29 12:41 | 2021-04-29 12:57 | 0:16 | S/O | Due to D/W work | 0 | 0 | No interruption
Bagura | Bagura-Sherpur 132 kV line -2 | 2021-04-30 08:32 | 2021-04-30 17:20 | 8:48 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 139:55 |  | Unserved Energy: |  | 0
Others :
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 735:16 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:April' 2021
| Area | Previous Month (March 2021) |  |  |  | Current Month (April' 2021)
SL No. |  | Total number of |  |  |  | Total number of |  |  |  | 82
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 20 | 5 | 8 | 33 | 26 | 9 | 82 | 117
2 | Dhaka (South) Grid Circle. | 7 | 8 | 45 | 60 | 10 | 3 | 13 | 26
3 | Chattogram Grid Circle. | 6 | 9 | 84 | 99 | 12 | 3 | 43 | 58
4 | Cumilla Grid Circle. | 24 | 10 | 67 | 101 | 28 | 13 | 49 | 90
5 | Khulna Grid Circle. | 7 | 6 | 21 | 34 | 6 | 6 | 45 | 57
6 | HVDC Grid Circle | 5 | 2 | 15 | 22 | 2 | 0 | 10 | 12
7 | Bogura Grid Circle. | 7 | 12 | 36 | 55 | 28 | 24 | 52 | 104
8 | Others | Total number of T: 1; Total number of S/O: 1; Total number of Total: 2; Total number of Total: 0
9 | Total | 77 | 52 | 277 | 406 | 112 | 58 | 294 | 464
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:April' 2021 | [10 empty] | 555.*8
| Area | Previous Month (March 2021) |  |  |  | Current Month (April' 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to |  |  |  | T | E | S/D
|  | T | E/O | S/O | Total | T | E/O | S/O | Total | 592.5167
1 | Dhaka (North) Grid Circle. | 1161 | 213 | 587.5 | 1961.5 | 116.97 | 112.83 | 1016.2333 | 1246.0333 | 68.75 |  |  | 15.8333 | 8.4
2 | Dhaka (South) Grid Circle. | 205.83 | 16.43 | 253 | 475.26 | 46.33 | 56.1667 | 0 | 102.4967 | 136.8 |  |  | 40 | 16.2
3 | Chattogram Grid Circle. | 58.6 | 29.5 |  | 88.1 | 23.42 | 16 | 191.74 | 231.16 | 2 | T |  | 150 | 11.0833
4 | Cumilla Grid Circle. | 133.15 | 222.43 | 90.17 | 445.75 | 182.87 | 164.83 | 21 | 368.7 | 14.6667 | 6.75 | 58.7667 | 205.8333 | 22.9167
5 | Khulna Grid Circle. |  | 167.68 | 14.17 | 181.85 | 37.9 | 321.28 | 111.15 | 470.33 | 23.4667 | 21.6667 | 37.3333 | 12.9167 | 58.6
6 | HVDC Grid Circle | 129 | 15.83 | 18.33 | 163.16 | 0 | 0 | 0 | 0 | 18.9 | 1.6333 | 50 |  |  | 127.67 | 51.6
7 | Bogura Grid Circle. | 22.87 | 622.73 | 167.83 | 813.43 | 147.09 | 359.48 | 651.2822 | 1157.8522 | 75 | 23.4 | 28.3333 |  |  | 179.27
8 | Others |  |  |  | 0 | 0 | 0 | 0 | 0 | 65 | 49.5 | 48
9 | Total | 1710.45 | 1287.6 | 1131 | 4129.05 | 554.58 | 1030.5867 | 1991.4056 | 3576.5722 | 153.9 | 8.8667 | 222.4333
[10 empty] | 1151 | 8.6667
12.6667
133.15
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:April' 2021
A) Power Interruption | [10 empty] | 10 |  | 3
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks |  |  |  | 116.34
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 6 | 2 | 8 | 5 | 1 | 4 | 1174.07 |  |  | 3240.35 |  | 1742.6
2 | Dhaka (South) | 5031.6 | 2 | - | 2 | - | 1 | 1 | 56.17 |  |  | 279.9167 |  | 129
3 | Chattogram | 2042 | 3 | 4 | 7 | 2 | 2 | 3 | 121.49 |  |  | 235.2833 |  | 88.1
4 | Khulna | 2434 | 5 | 7 | 12 | 2 | 3 | 4 | 470.33 |  |  | 93 |  | 181.85
5 | HVDC | 5954.3 | - | - | - | - | - | - | - |  |  | 235.3833 |  | 34.16 | 58.03
6 | Bogura | 3145.6 | 14 | 8 | 22 | 3 | 6 | 13 | 1115.53 |  |  | 940.25 |  | 651.73
7 | Cumilla | 2981 | 4 | 1 | 5 | 1 | 1 | 2 | 191.73 |  |  | 129.3333 |  | 342.65
8 | Others | - | - | - | - | - | - | - | 0 |  |  |  |  | 3170.09
| Total | 30390.1 | [6 empty] | 3129.32
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.97%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.99%
4 | Khulna | 99.95%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.88% | [6 empty] | Information Management Division
7 | Cumilla | 99.95% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:April' 2021 | [11 empty] | 2043.54
4646.17
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | - | 3 | 3 | - | - | 71.95
2 | Dhaka (South) | 990.29 |  | 3 | - | 3 | 3 | - | - | 46.3333
3 | Chattogram | 917 | - | - | 2 | 2 | - | - | 2 | 109.6667
4 | Khulna | 1238.4 | - | - | - | - | - | - | - | - | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 2 | - | 2 | 2 | - | - | 42.3333
7 | Cumilla | 1648.16 | - | 3 | - | 3 | 2 | 1 | - | 176.9667
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | [7 empty] | 447.25
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.98%
3 | Chattogram | 99.84%
4 | Khulna | 99.97%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.97% | [7 empty] | Information Management Division
7 | Cumilla | 99.97% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month::April' 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-04-18 | 28 | - | 15 | 19hr12 min |  |  | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
19hr12 min
Kachua

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:March' 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Kishoreganj | 2 | 0:05 | 140 | 11.6667 | Due to tripping of 132/33 kV Transformers-T1 & T2 |  |  | 10 | 0:00 | #REF!
|  | 2:03 | 25 | 51.25 | Due to red-hot maintenance of 132/33 kV Transformers-T3 & T4 |  |  | 68.75 | 0:00
Savar | 1 | 0:11 | 159 | 29.15 | Due to tripping of 132/33 kV Transformers-T3 |  |  | 136.8 | 0:00 | -107.65
Mymensingh | 1 | 0:07 | 36 | 4.2 | Due to tripping of 132/33 kV Transformers-T1 & T2 |  |  | 2 | 0:00
Kabirpur | 3 | 0:19 | 140 | 44.3333 | Due to fire originated from marshaling box |  |  | 14.6667
|  | 1:09 | 15 | 17.25 | Due to red-hot maintenance of 132/33 kV Trasformer T1 |  |  | 23.4667
|  | 0:05 | 411 | 34.25 | Due to tripping of Tongi-Kabirpur 132 kV line-1 & 2 |  |  | 99 |  |  | 34.8
Tongi | 1 | 0:12 | 76 | 15.2 | Due to tripping of Tongi-Kabirpur 132 kV line -2
Moghbazar | 1 | 0:30 | 45 | 22.5 | Due to tripping of Rampura-Moghbazar 132 kV line-1
Jamalpur | 1 | 2:26 | 4 | 9.7333 | Due to S/D of 132/33 kV Transformer T1
Kodda | 1 | 6:06 | 165 | 1006.5 | Due to S/D of 132 kV Bus-1 & 2
Siddhirganj | 2 | 2:05 | 20 | 41.6667 | Due to red-hot maintenance of 132/33 kV Trasformer T2
|  | 0:08 | 48 | 6.4 | Due to tripping of Siddhirganj-Matuail 132 kV line
Sonargaon | 1 | 0:58 | 15 | 14.5 | Due to high temperature of 132/33 kV Trasformer T2
Aurahati | 1 | 0:28 | 65 | 30.3333 | Due to tripping of Aurahati-Kamrangirchar 132 kV line
Haripur | 1 | 0:24 | 24 | 9.6 | Due to tripping of Haripur-Rahim Steel 132 kV line
Halishahar | 3 | 0:52 | 25 | 21.6667 | Due to tripping of 132/33 kV Transformer-T2
|  | 0:07 | 15 | 1.75 | Due to 33 kV Feeder fault
|  | 3:09 | 10 | 31.5 | Due to S/D of 132/33 kV Transformer T2
Dohazari | 4 | 0:16 | 60 | 16 | Due to fire at 33 kV Chandonish feeder
|  | 0:55 | 20 | 18.3333 | Due to S/D of 132/33 kV Transformer T1 and 33 kV Bus
|  | 2:56 | 20 | 58.6667 | Due to S/D of Dohazari-Cox's Bazar 132 kV line
|  | 1:42 | 30 | 51 | Due to S/D of Dohazari-Matarbari-Cox'sbazar 132 kV line
Sikalbaha(Old) | 1 | 1:55 | 10 | 19.1667 | Due to S/D of 132/33 kV Transformer T3 and T4
Madunaghat | 1 | 6:32 | 2 | 13.0667 | Due to S/D of 132/33 kV Transformer T2
Chowmuhani | 1 | 3:38 | 40 | 145.3333 | Due to red-hot maintenance
Kachua | 1 | 0:45 | 26 | 19.5 | Due to red-hot maintenance
Sylhet | 1 | 0:32 | 7 | 3.7333 | Due to tripping of 132/33 kV Transformers-T1 |  | 41.6667
Sreemangal | 1 | 0:05 | 26 | 2.1667 | Due to 33 kV REB feeder fault |  | 14.5
Cumilla(S) | 2 | 0:51 | 134 | 113.9 | Due to tripping of Cumilla(S)-Tripura 132 kV line-1 & 2
|  | 0:28 | 130 | 60.6667 | Due to tripping of Cumilla(S)-Surjamoninagar 230 kV line-1 & 2 | 60.6667
Chattak | 1 | 0:12 | 12 | 2.4 | Due to tripping of Chattak-Sunamganj 132 kV line | 1006.5 | Power interruption
Biyanibazar | 1 | 1:03 | 20 | 21 | Due to S/D of 132/33 kV Transformers-T1
Bhandaria | 1 | 0:30 | 16 | 8 | Due to tripping of 132/33 kV transformers T-2 & T-3
Gallamari | 1 | 0:12 | 26 | 5.2 | Due to tripping of 132/33 kV transformers T-1 & T-2
Patuakhali | 1 | 0:38 | 39 | 24.7 | Due to tripping of 132/33 kV transformers T-1 & T-3
Bottail | 1 | 4:43 | 65 | 306.5833 | Due to 33 kV feeder fault
Faridpur |  | 1:03 | 14 | 14.7 | Due to red-hot maintenance
| 3 | 0:18 | 45 | 13.5 | Due to 33 kV auxiliary transformer maint
|  | 3:36 | 7 | 24.7333 | Due to CT loop replacement
Satkhira | 1 | 0:32 | 70 | 37.3333 | Due to S/D of 132/33 transformers T1, T2 and T3
Khulna(c) | 1 | 0:27 | 15 | 6.75 | Due to S/D of 132/33 transformers T3
Madaripur | 1 | 1:12 | 11 | 13.2 | Due to 33 kV feeder maint
Barishal(S) | 1 | 0:32 | 14 | 15.6333 | Due to S/D of 132/33 kV Transformers-T1
Naogaon | 4 | 0:13 | 10 | 2.1667 | Due to tripping of 132/33 kV transformers T-2
|  | 1:55 | 35 | 67.0833 | Due to red-hot maintenance
|  | 0:24 | 60 | 24 | Due to tripping of Naogaon-Joypurhat 132 kV line
|  | 3:29 | 40 | 139.3333 | Due to S/D of 132/33 kV Transformers-T1
Mahastangar | 3 | 1:44 | 11 | 19.0667 | Due to red-hot maintenance
|  | 1:08 | 22 | 24.9822 | Due to 33 kV feeder maint.
|  | 2:24 | 45 | 108 | Due to 33 kV bus maint.
Rajshahi(O) | 1 | 0:57 | 110 | 104.5 | Due to red-hot maintenance
Bogura | 5 | 0:05 | 60 | 5 | Due to tripping of 132/33 kV transformers -T-3 & T-4
|  | 1:31 | 24 | 36.4 | Due to jumper cable down
|  | 0:13 | 50 | 10.8333 | Due to tripping of 132/33 kV transformers -T-3 & T-4
|  | 1:23 | 60 | 83 | Due to red-hot maintenance
|  | 3:06 | 25 | 77.5 | Due to S/D of 132/33 kV transformers T-3 & its 33 kV Bus section
Barapukuria | 2 | 1:40 | 47 | 78.3333 | Due to mechanical fault
|  | 3:42 | 17 | 62.9 | Due to 33 kV bus maint.
Sirajganj | 1 | 0:46 | 26 | 19.9333 | Due to red-hot maintenance |  |  | 114
Kurigram | 1 | 1:36 | 10 | 16 | Due to red-hot maintenance
Mithapukur | 2 | 0:35 | 10 | 5.8333 | Due to tripping of 132/33 kV transformers T-2
|  | 0:39 | 4 | 2.6 | Due to tripping of 132/33 kV transformers T-3
Ishurdi | 1 | 0:45 | 18 | 13.5 | Due to red-hot maintenance
Saidpur | 1 | 0:10 | 110 | 18.3333 | Due to tripping of Saidpur-Purbasadipur 132 kV line-2
Purbasadipur | 3 | 7:50 | 25 | 195.8333 | Due to S/D of 132/33 kV Transformer T3 and 33 kV Bus
|  | 0:48 | 18 | 14.4 | Due to red-hot maintenance
|  | 1:08 | 25 | 28.3333 | Due to S/D of 132/33 kV Transformer T3
| Total Unserved energy : |  |  | 3576.5822 | MWH | #REF! |  |  | #REF!
3242.7956
[5 empty] | Executive Engineer | 3226.32
[5 empty] | Information Management Division | 16.4756
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month:April'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 136 | 26 | 2021-04-01 | 10:00
2 | Munsiganj | 149 | 26 | 2021-04-01 | 21:00
3 | Sonargaon | 104 | 8 | 2021-04-01 | 19:30
4 | Shyampur | 226 | 8 | 2021-04-01 | 0:00
5 | Bhulta | 221 | 29 | 2021-04-01 | 23:00
6 | Madanganj | 136 | 19 | 2021-04-01 | 19:30
7 | Shitalakhya | 133 | 12 | 2021-04-01 | 15:00
8 | Rahim steel | 125 | 3 | 2021-04-01 | 17:00
9 | Matuail | 130 | 21 | 2021-04-01 | 7:00
10 | Ghorasal | 97 | 1 | 2021-04-01 | 18:00
11 | Narsingdi | 180 | 28 | 2021-04-01 | 23:00
12 | Haripur (SBU) | 132 | 3 | 2021-04-01 | 21:00
13 | Sreenagar | 44 | 30 | 2021-04-01 | 21:00
14 | Ullon | 102 | 20 | 2021-04-01 | 22:00
15 | Hasnabad | 118 | 21 | 2021-04-01 | 19:30
16 | Magbazar | 101 | 28 | 2021-04-01 | 15:00
17 | Maniknagar | 108 | 29 | 2021-04-01 | 13:00
18 | Bangabhaban | 24 | 1 | 2021-04-01 | 10:00
19 | Narinda | 90 | 1 | 2021-04-01 | 19:00
20 | Dhanmondi | 217 | 4 | 2021-04-01 | 13:00
21 | Lalbag | 90 | 4 | 2021-04-01 | 13:00
22 | Madartek | 756 | 3 | 2021-04-01 | 24:00
23 | Dhaka University | 43 | 4 | 2021-04-01 | 12:00
24 | Aftabnagar | 11 | 1 | 2021-04-01 | 24:00
25 | Fatullah | 66 | 11 | 2021-04-01 | 10:00
26 | Nawabganj | 61 | 29 | 2021-04-01 | 21:00
27 | Mirpur | 123 | 27 | 2021-04-01 | 18:00
28 | Kalyanpur | 138 | 28 | 2021-04-01 | 19:00
29 | Gulshan | 150 | 1 | 2021-04-01 | 12:00
30 | Uttara | 108 | 13 | 2021-04-01 | 15:00
31 | Uttara(new) | 34 | 28 | 2021-04-01 | 14:00
32 | Kamrangirchar | 93 | 11 | 2021-04-01 | 19:00
33 | Savar | 219 | 1 | 2021-04-01 | 12:00
34 | Bhasantec | 171 | 27 | 2021-04-01 | 19:00
35 | Agargaon | 77 | 1 | 2021-04-01 | 12:00
36 | Satmosjid | 111 | 27 | 2021-04-01 | 19:00
37 | Tongi | 132 | 27 | 2021-04-01 | 10:00
38 | Kabirpur | 270 | 28 | 2021-04-01 | 15:00
39 | Basundhara | 179 | 28 | 2021-04-01 | 13:00
40 | Manikganj | 2253 | 28 | 2021-04-01 | 12:00
41 | Joydevpur | 180 | 28 | 2021-04-01 | 14:00
42 | New Tongi | 121 | 1 | 2021-04-01 | 12:00
43 | Kodda | 294 | 21 | 2021-04-01 | 16:00
44 | Dhamrai | 126 | 27 | 2021-04-01 | 15:00
45 | Rajendrapur | 112 | 12 | 2021-04-01 | 19:00
46 | Valuka | 142 | 15 | 2021-04-01 | 14:00
47 | Tangail | 250 | 14 | 2021-04-01 | 20:00
48 | Mymensing | 231 | 27 | 2021-04-01 | 21:00
49 | Kishorganj | 158 | 16 | 2021-04-01 | 22:00
50 | Netrokona | 131 | 21 | 2021-04-01 | 22:00
51 | Jamalpur | 170 | 20 | 2021-04-01 | 22:00
52 | Sherpur | 148 | 27 | 2021-04-01 | 21:00
53 | Srimongal | 59 | 28 | 2021-04-01 | 21:00
54 | Shahjibazar | 136 | 11 | 2021-04-01 | 20:00
56 | Fenchuganj | 52 | 26 | 2021-04-01 | 21:00
57 | Kulawara | 50 | 27 | 2021-04-01 | 22:00
58 | Sylhet | 129 | 29 | 2021-04-01 | 19:00
59 | Chatak | 34 | 22 | 2021-04-01 | 21:00
60 | Sunamganj | 52 | 29 | 2021-04-01 | 21:00
61 | Bianibazar | 75 | 29 | 2021-04-01 | 19:00
62 | Cumilla (S) | 178 | 15 | 2021-04-01 | 21:00
63 | Cumilla(N) | 177 | 24 | 2021-04-01 | 20:00
64 | Chandpur | 86 | 28 | 2021-04-01 | 21:00
65 | Feni | 142 | 27 | 2021-04-01 | 23:00
66 | Chowmuhani | 202 | 21 | 2021-04-01 | 21:00
67 | Ashuganj | 60 | 11 | 2021-04-01 | 23:00
68 | Daudkandi | 176 | 25 | 2021-04-01 | 21:00
69 | B.Baria | 178 | 13 | 2021-04-01 | 20:00
70 | Ramganj | 104 | 29 | 2021-04-01 | 21:00
71 | Chaddagram | 61 | 22 | 2021-04-01 | 13:00
72 | PHP | 12 | 21 | 2021-04-01 | 19:00
73 | Kochua | 79 | 29 | 2021-04-01 | 21:00
74 | Madanhat | 149 | 21 | 2021-04-01 | 4:00
75 | Hathazari | 99 | 29 | 2021-04-01 | 21:00
76 | Khulshi | 231 | 28 | 2021-04-01 | 11:00
77 | Halishahar | 152 | 26 | 2021-04-01 | 9:00
78 | Baraulia | 171 | 20 | 2021-04-01 | 0:00
79 | Sikalbaha | 40 | 28 | 2021-04-01 | 12:00
80 | Dohazari | 104 | 26 | 2021-04-01 | 21:00
81 | Cox'sbazar | 111 | 2 | 2021-04-01 | 18:30
82 | Chandraghona | 34 | 19 | 2021-04-01 | 19:30
83 | Kaptai | 6 | 9 | 2021-04-01 | 19:00
84 | A. Khaer Stl. | 12 | 1 | 2021-04-01 | 19:00
85 | Bakulia | 113 | 11 | 2021-04-01 | 15:00
86 | Julda | 26 | 11 | 2021-04-01 | 13:00
87 | TK chemical | 34 | 29 | 2021-04-01 | 19:30
88 | Modern Steel | 0 | 1 | 2021-04-01 | #N/A
89 | Shahmirpur | 30 | 25 | 2021-04-01 | 0:00
90 | Khagrachhari | 26 | 7 | 2021-04-01 | 13:00
91 | Matarbari | 43 | 30 | 2021-04-01 | 21:00
92 | Baroiar Hat | 64 | 12 | 2021-04-01 | 19:00
93 | Rangamati | 14 | 1 | 2021-04-01 | 19:00
94 | Abul Khair 230 | 175 | 21 | 2021-04-01 | 15:00
95 | BSRM | 161 | 28 | 2021-04-01 | 11:00
96 | GPH Ispat | 95 | 21 | 2021-04-01 | 15:00
97 | Goalpara | 35 | 1 | 2021-04-01 | 23:00
98 | Central s/s | 108 | 29 | 2021-04-01 | 21:00
99 | Noapara | 73 | 29 | 2021-04-01 | 20:00
100 | Jashore | 152 | 21 | 2021-04-01 | 21:00
101 | Benapol | 74 | 10 | 2021-04-01 | 14:00
101 | Jhenidah | 127 | 21 | 2021-04-01 | 19:30
102 | Bottail | 144 | 28 | 2021-04-01 | 21:00
103 | G.K Project | 69 | 14 | 2021-04-01 | 1:00
104 | Faridpur | 220 | 28 | 2021-04-01 | 20:00
105 | Madaripur | 116 | 27 | 2021-04-01 | 23:00
106 | Sariatpur | 76 | 28 | 2021-04-01 | 21:00
107 | Gopalganj | 106 | 28 | 2021-04-01 | 22:00
108 | Bagerhat | 112 | 27 | 2021-04-01 | 21:00
109 | Mongla | 46 | 12 | 2021-04-01 | 12:00
110 | Satkhira | 132 | 28 | 2021-04-01 | 22:00
111 | Gallamari | 45 | 28 | 2021-04-01 | 19:30
112 | Magura | 66 | 21 | 2021-04-01 | 21:00
113 | Norail | 48 | 21 | 2021-04-01 | 21:00
114 | Chuadanga | 96 | 27 | 2021-04-01 | 23:00
115 | Borguna | 98 | 16 | 2021-04-01 | 20:00
116 | Barsal(N) | 52 | 29 | 2021-04-01 | 21:00
117 | Barsal(S) | 139 | 10 | 2021-04-01 | 5:00
118 | Patuakhali | 125 | 28 | 2021-04-01 | 21:00
119 | Bhandaria | 61 | 29 | 2021-04-01 | 21:00
120 | Borhan Uddin | 47 | 28 | 2021-04-01 | 21:00
121 | Ishurdi | 72 | 28 | 2021-04-01 | 21:00
122 | Ruppur Paromanobik | 4 | 1 | 2021-04-01 | 11:00
123 | Natore | 149 | 26 | 2021-04-01 | 21:00
124 | Bogura | 182 | 14 | 2021-04-01 | 22:00
125 | Naogaon | 139 | 14 | 2021-04-01 | 21:00
126 | Rajshahi | 176 | 27 | 2021-04-01 | 21:00
127 | Rajshahi New | 26 | 26 | 2021-04-01 | 21:00
128 | C.Nawabganj | 86 | 11 | 2021-04-01 | 20:00
129 | Amnura | 73 | 14 | 2021-04-01 | 23:00
130 | Pabna | 130 | 12 | 2021-04-01 | 20:00
131 | Shahjadpur | 119 | 14 | 2021-04-01 | 19:30
132 | Serajganj | 116 | 7 | 2021-04-01 | 19:30
133 | Niyamatpur | 96 | 15 | 2021-04-01 | 20:00
134 | Joypurhat | 65 | 20 | 2021-04-01 | 24:00
135 | Sherpur(Bogura) | 66 | 21 | 2021-04-01 | 3:00
136 | Mohastangar | 76 | 15 | 2021-04-01 | 20:00
137 | Bangura | 43 | 28 | 2021-04-01 | 21:00
138 | Rangpur | 137 | 13 | 2021-04-01 | 23:00
139 | Lalmonirhat | 50 | 12 | 2021-04-01 | 18:30
140 | Saidpur | 122 | 13 | 2021-04-01 | 19:30
141 | Purbasadipur | 114 | 28 | 2021-04-01 | 15:00
142 | Thakurgaon | 88 | 4 | 2021-04-01 | 19:00
143 | Palshbari | 129 | 14 | 2021-04-01 | 19:30
144 | Barapukuria | 59 | 24 | 2021-04-01 | 22:00
145 | Panchugar | 54 | 27 | 2021-04-01 | 21:00
146 | Joldhaka | 67 | 27 | 2021-04-01 | 21:00
147 | Kurigram | 62 | 13 | 2021-04-01 | 21:00
148 | Mitha Pukur | 41 | 11 | 2021-04-01 | 20:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:April' 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4804 | 03.04.2021 | 24:00 |  |  | 4527 | 3865 | 28/02/21
Chattogram | 1529 | 26.04.2021 | 15:00 |  |  | 1396 | 1138 | 27/02/21
Khulna | 1737 | 28.04.2021 | 21:00 |  |  | 1579 | 1303 | 28/02/21
Rajshahi | 1488 | 20.04.2021 | 21:00 |  |  | 1363 | 1088 | 28/02/21
Cumilla | 1349 | 28.04.2021 | 21:00 |  |  | 1268 | 951 | 28/02/21
Mymensingh | 1118 | 16.04.2021 | 22:00 |  |  | 1017 | 894 | 27/02/21
Sylhet | 562 | 27.04.2021 | 21:00 |  |  | 551 | 443 | 15/02/21
Barisal | 422 | 28.04.2021 | 21:00 |  |  | 437 | 288 | 28/02/21
Rangpur | 979 | 14.04.2021 | 19:00 |  |  | 817 | 699 | 44379
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 415 | 4 | 2021-04-01 | 21:00 | 395 | 10 | 2021-04-01 | 11:00
2 | Bheramara | 400 | 407 | 17 | 2021-04-01 | 6:00 | 388 | 7 | 2021-04-01 | 20:00
3 | Ashuganj(N) | 400 | 394 | 4 | 2021-04-01 | 20:00 | 361 | 10 | 2021-04-01 | 11:00
4 | Payra | 400 | 422 | 4 | 2021-04-01 | 21:00 | 394 | 20 | 2021-04-01 | 1:00
5 | Kaliakoir | 400 | 413 | 4 | 2021-04-01 | 21:00 | 369 | 18 | 2021-04-01 | 12:00
6 | Bhulta | 400 | 391 | 4 | 2021-04-01 | 19:30 | 345 | 22 | 2021-04-01 | 15:00
7 | Gopalganj | 400 | 422 | 4 | 2021-04-01 | 15:00 | 376 | 3 | 2021-04-01 | 19:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 236 | 14 | 2021-04-01 | 3:00 | 220 | 10 | 2021-04-01 | 10:00
2 | Ishurdi | 230 | 244 | 4 | 2021-04-01 | 19:00 | 223 | 11 | 2021-04-01 | 24:00
3 | Ashuganj | 230 | 240 | 4 | 2021-04-01 | 19:30 | 221 | 10 | 2021-04-01 | 11:00
4 | Serajganj | 230 | 236 | 4 | 2021-04-01 | 19:00 | 222 | 7 | 2021-04-01 | 19:00
5 | Baghabari | 230 | 238 | 4 | 2021-04-01 | 19:30 | 217 | 1 | 2021-04-01 | 13:00
6 | Barapukuria | 230 | 242 | 28 | 2021-04-01 | 19:30 | 0 | 1 | 2021-04-01 | 8:00
7 | Bogura | 230 | 232 | 4 | 2021-04-01 | 18:00 | 209 | 1 | 2021-04-01 | 10:00
8 | Rajshahi | 230 | 243 | 4 | 2021-04-01 | 17:00 | 216 | 13 | 2021-04-01 | 12:00
9 | Khulna South | 230 | 256 | 4 | 2021-04-01 | 19:30 | 195 | 15 | 2021-04-01 | 13:00
10 | Rampura | 230 | 232 | 4 | 2021-04-01 | 20:00 | 211 | 8 | 2021-04-01 | 11:00
11 | Haripur | 230 | 236 | 4 | 2021-04-01 | 21:00 | 210 | 10 | 2021-04-01 | 12:00
12 | Hasnabad | 230 | 238 | 4 | 2021-04-01 | 21:00 | 210 | 10 | 2021-04-01 | 10:00
13 | Shyampur | 230 | 229 | 4 | 2021-04-01 | 21:00 | 220 | 1 | 2021-04-01 | 9:00
14 | Aminbazar | 230 | 235 | 4 | 2021-04-01 | 1:00 | 208 | 10 | 2021-04-01 | 2:00
15 | Tongi | 230 | 235 | 4 | 2021-04-01 | 19:00 | 205 | 10 | 2021-04-01 | 11:00
16 | Comilla (N) | 230 | 235 | 4 | 2021-04-01 | 21:00 | 214 | 10 | 2021-04-01 | 11:00
17 | Hathazari | 230 | 231 | 4 | 2021-04-01 | 22:00 | 206 | 25 | 2021-04-01 | 6:00
18 | Megnaghat | 230 | 240 | 4 | 2021-04-01 | 19:00 | 216 | 10 | 2021-04-01 | 13:00
19 | Fenchuganj | 230 | 245 | 17 | 2021-04-01 | 6:00 | 234 | 2 | 2021-04-01 | 15:00
20 | Siddhirganj | 230 | 237 | 4 | 2021-04-01 | 21:00 | 210 | 10 | 2021-04-01 | 6:00 |  |  | 7345
21 | Maniknagar | 230 | 236 | 4 | 2021-04-01 | 21:00 | 22 | 10 | 2021-04-01 | 8:00
22 | Old Airport | 230 | 260 | 4 | 2021-04-01 | 21:00 | 205 | 10 | 2021-04-01 | 11:00
23 | Barisal | 230 | 251 | 23 | 2021-04-01 | 2:00 | 229 | 17 | 2021-04-01 | 12:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-04-01 | 3:00 | 0 | 4 | 2021-04-01 | 21:00
25 | AKSML | 230 | 232 | 4 | 2021-04-01 | 22:00 | 206 | 25 | 2021-04-01 | 11:00
26 | BSRM | 230 | 233 | 4 | 2021-04-01 | 22:00 | 207 | 26 | 2021-04-01 | 15:00
27 | Bibiyana | 230 | 245 | 4 | 2021-04-01 | 19:30 | 232 | 11 | 2021-04-01 | 15:00
28 | Bhulta | 230 | 237 | 4 | 2021-04-01 | 21:00 | 211 | 10 | 2021-04-01 | 11:00
29 | Ashuganj (S) | 230 | 232 | 6 | 2021-04-01 | 18:30 | 220 | 10 | 2021-04-01 | 11:00
30 | Kaliakoir | 230 | 238 | 4 | 2021-04-01 | 21:00 | 210 | 10 | 2021-04-01 | 11:00
31 | GPH | 230 | 232 | 17 | 2021-04-01 | 7:00 | 205 | 26 | 2021-04-01 | 15:00
132 kV Substation
1 | Siddhirganj | 132 | 141 | 4 | 2021-04-01 | 0.83333 | 123 | 10 | 2021-04-01 | 0.45833
2 | Munsiganj | 132 | 141 | 4 | 2021-04-01 | 0.83333 | 123 | 10 | 2021-04-01 | 0.45833
3 | Sonargaon | 132 | 140 | 4 | 2021-04-01 | 0.875 | 125 | 10 | 2021-04-01 | 0.45833
4 | Shyampur | 132 | 141 | 4 | 2021-04-01 | 0.83333 | 129 | 3 | 2021-04-01 | 0.45833
5 | Bhulta | 132 | 138 | 4 | 2021-04-01 | 0.875 | 116 | 10 | 2021-04-01 | 0.45833
6 | Madanganj | 132 | 140 | 4 | 2021-04-01 | 0.83333 | 121 | 18 | 2021-04-01 | 0.5
7 | Shitalakhya | 132 | 144 | 4 | 2021-04-01 | 0.875 | 119 | 10 | 2021-04-01 | 0.45833
8 | Rahim Steal | 132 | 141 | 4 | 2021-04-01 | 0.875 | 124 | 10 | 2021-04-01 | 0.5
9 | Matuail | 132 | 141 | 4 | 2021-04-01 | 0.83333 | 123 | 10 | 2021-04-01 | 0.45833
10 | Ghorasal | 132 | 142 | 4 | 2021-04-01 | 0.95833 | 128 | 10 | 2021-04-01 | 0.45833
11 | Narsinghdi | 132 | 141 | 4 | 2021-04-01 | 0.79167 | 119 | 10 | 2021-04-01 | 0.875
12 | Haripur (SBU) | 132 | 140 | 4 | 2021-04-01 | 0.8125 | 123 | 10 | 2021-04-01 | 0.45833
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 139 | 17 | 2021-04-01 | 0.125 | 122 | 10 | 2021-04-01 | 0.45833
15 | Hasnabad | 132 | 140 | 4 | 2021-04-01 | 0.79167 | 122 | 10 | 2021-04-01 | 0.5
16 | Magbazar | 132 | 138 | 4 | 2021-04-01 | 0.875 | 120 | 10 | 2021-04-01 | 0.5
17 | Maniknagar | 132 | 142 | 4 | 2021-04-01 | 0.875 | 124 | 10 | 2021-04-01 | 0.45833
18 | Bangabhaban | 132 | 142 | 4 | 2021-04-01 | 0.875 | 124 | 10 | 2021-04-01 | 0.45833
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2021
|  | Rated | Maxm | Date |  |  | Minm | Date |  |  |  | 7
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks | 8
No. | 132 KV Substation | kV | kV |  |  |  | kV |  |  |  |  | 9
19 | Narinda | 132 | 142 | 4 | 2021-04-01 | 0.875 | 124 | 10 | 2021-04-01 | 0.45833 |  | 13
20 | Dhanmondi | 132 | 139 | 17 | 2021-04-01 | 0.125 | 122 | 10 | 2021-04-01 | 0.45833 |  | 14
21 | Lalbag | 132 | 142 | 4 | 2021-04-01 | 0.875 | 117 | 10 | 2021-04-01 | 0.45833 |  | 15
22 | Madartek | 132 | 138 | 4 | 2021-04-01 | 0.8125 | 122 | 10 | 2021-04-01 | 0.45833 |  | 16
23 | Dhaka University | 132 | - | - | - | - | - | - | - | - |  | 17
24 | Aftabnagar | 132 | 138 | 4 | 2021-04-01 | 0.79167 | 123 | 10 | 2021-04-01 | 0.45833 |  | 18
25 | Fatullah | 132 | 141 | 4 | 2021-04-01 | 0.8125 | 123 | 10 | 2021-04-01 | 0.41667 |  | 19
26 | Nawabganj | 133 | 137 | 4 | 2021-04-01 | 0.8125 | 118 | 10 | 2021-04-01 | 0.45833
27 | Mirpur | 132 | 141 | 4 | 2021-04-01 | 0.875 | 122 | 10 | 2021-04-01 | 0.41667 |  | 20
28 | Kalyanpur | 132 | 142 | 4 | 2021-04-01 | 0.875 | 123 | 10 | 2021-04-01 | 0.5 |  | 21
29 | Gulshan | 132 | 138 | 21 | 2021-04-01 | 0.95833 | 122 | 10 | 2021-04-01 | 0.5 |  | 22
30 | Uttara | 132 | 141 | 4 | 2021-04-01 | 0.875 | 121 | 10 | 2021-04-01 | 0.45833 |  | 23
31 | Uttara(New) | 132 | 141 | 4 | 2021-04-01 | 0.875 | 110 | 28 | 2021-04-01 | 0.5 |  | 24
32 | Kamrangirchar | 132 | 141 | 4 | 2021-04-01 | 0.875 | 117 | 10 | 2021-04-01 | 0.5 |  | 25
33 | Savar | 132 | 142 | 4 | 2021-04-01 | 0.875 | 122 | 18 | 2021-04-01 | 0.5 |  | 26
34 | Bhasantec | 132 | 143 | 4 | 2021-04-01 | 0.875 | 121 | 10 | 2021-04-01 | 0.45833 |  | 27
35 | Agargaon | 132 | 143 | 4 | 2021-04-01 | 0.875 | 122 | 10 | 2021-04-01 | 0.45833 |  | 28
36 | Satmosjid | 132 | 142 | 4 | 2021-04-01 | 0.875 | 124 | 6 | 2021-04-01 | 0.45833 |  | 29
37 | Tongi | 132 | 147 | 4 | 2021-04-01 | 0.79167 | 123 | 10 | 2021-04-01 | 0.45833 |  | 30
38 | Kabirpur | 132 | 142 | 4 | 2021-04-01 | 0.8125 | 124 | 22 | 2021-04-01 | 0.625 |  | 31
39 | Basundhara | 132 | 145 | 4 | 2021-04-01 | 0.79167 | 121 | 10 | 2021-04-01 | 0.45833 |  | 32
40 | Manikganj | 132 | 145 | 21 | 2021-04-01 | 0.95833 | 123 | 10 | 2021-04-01 | 0.45833 |  | 33
41 | Joydevpur | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 122 | 10 | 2021-04-01 | 0.45833 |  | 34
42 | New Tongi | 132 | 146 | 4 | 2021-04-01 | 0.875 | 121 | 10 | 2021-04-01 | 0.45833 |  | 35
43 | Kodda | 132 | 145 | 4 | 2021-04-01 | 0.77083 | 118 | 6 | 2021-04-01 | 0.45833 |  | 36
44 | Dhamrai | 132 | 142 | 4 | 2021-04-01 | 0.77083 | 123 | 22 | 2021-04-01 | 0.58333 |  | 37
45 | Rajendrapur | 132 | 145 | 4 | 2021-04-01 | 0.8125 | 116 | 5 | 2021-04-01 | 0.66667 |  | 38
46 | Valuka | 132 | 142 | 4 | 2021-04-01 | 0.79167 | 104 | 1 | 2021-04-01 | 0.77083 |  | 39
47 | Tangail | 132 | 143 | 4 | 2021-04-01 | 0.8125 | 118 | 21 | 2021-04-01 | 0.75 |  | 40
48 | Mymensing | 132 | 143 | 4 | 2021-04-01 | 0.8125 | 112 | 11 | 2021-04-01 | 0.83333 |  | 41
49 | Kishorganj | 132 | 142 | 4 | 2021-04-01 | 0.79167 | 112 | 3 | 2021-04-01 | 0.83333 |  | 42
50 | Netrokona | 132 | 143 | 4 | 2021-04-01 | 0.8125 | 108 | 11 | 2021-04-01 | 0.83333 |  | 43
51 | Jamalpur | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 113 | 9 | 2021-04-01 | 0.5 |  | 44
52 | Sherpur | 132 | 143 | 4 | 2021-04-01 | 0.79167 | 112 | 9 | 2021-04-01 | 0.5 |  | 45
53 | Srimongal | 132 | 141 | 4 | 2021-04-01 | 0.79167 | 128 | 10 | 2021-04-01 | 0.91667 |  | 46
54 | Shahjibazar | 132 | 141 | 4 | 2021-04-01 | 0.79167 | 125 | 10 | 2021-04-01 | 0.75 |  | 47
55 | Fenchuganj | 132 | 140 | 4 | 2021-04-01 | 0.77083 | 130 | 24 | 2021-04-01 | 0.33333 |  | 48
56 | Khulawara | 132 | 140 | 4 | 2021-04-01 | 0.79167 | 130 | 24 | 2021-04-01 | 0.375 |  | 49
57 | Sylhet | 132 | 138 | 4 | 2021-04-01 | 0.79167 | 128 | 23 | 2021-04-01 | 0.58333 |  | 50
58 | Chattak | 132 | 138 | 4 | 2021-04-01 | 0.79167 | 123 | 9 | 2021-04-01 | 0.83333 |  | 51
59 | Sunamganj | 132 | 138 | 4 | 2021-04-01 | 0.79167 | 123 | 9 | 2021-04-01 | 0.83333 |  | 52
60 | Biani Bazar | 132 | 139 | 4 | 2021-04-01 | 0.79167 | 125 | 9 | 2021-04-01 | 0.75 |  | 53
61 | Comilla(South) | 132 | 137 | 17 | 2021-04-01 | 0.20833 | 117 | 24 | 2021-04-01 | 0.58333 |  | 54
62 | Comilla (North) | 132 | 144 | 4 | 2021-04-01 | 0.875 | 129 | 10 | 2021-04-01 | 0.58333 |  | ok
63 | Chandpur | 132 | 145 | 10 | 2021-04-01 | 0.29167 | 125 | 4 | 2021-04-01 | 0.79167 |  | 56
64 | Feni | 132 | 138 | 8 | 2021-04-01 | 0.83333 | 121 | 23 | 2021-04-01 | 0.5 |  | 57
65 | Chowmuhani | 132 | 142 | 4 | 2021-04-01 | 0.875 | 122 | 4 | 2021-04-01 | 0.77083 |  | 58
66 | Ashuganj | 132 | 145 | 4 | 2021-04-01 | 0.79167 | 128 | 10 | 2021-04-01 | 0.83333 |  | 59
67 | Daudkandi | 132 | 142 | 4 | 2021-04-01 | 0.875 | 122 | 21 | 2021-04-01 | 0.91667 |  | 60
68 | Brahminbaria | 132 | 141 | 4 | 2021-04-01 | 0.79167 | 121 | 10 | 2021-04-01 | 0.875 |  | 61
69 | Ramganj | 132 | 140 | 4 | 2021-04-01 | 0.875 | 121 | 4 | 2021-04-01 | 0.77083 |  | 62
70 | Chaddagram | 132 | 142 | 4 | 2021-04-01 | 0.875 | 123 | 23 | 2021-04-01 | 0.5 |  | 63
71 | PHP | 132 | 140 | 7 | 2021-04-01 | 0.75 | 122 | 4 | 2021-04-01 | 0.79167 |  | 64
72 | Kochua | 132 | 142 | 4 | 2021-04-01 | 0.875 | 127 | 1 | 2021-04-01 | 0.8125
73 | Madanhat | 132 | 141 | 4 | 2021-04-01 | 0.91667 | 126 | 25 | 2021-04-01 | 0.29167 |  | 65
74 | Hathazari | 132 | 137 | 4 | 2021-04-01 | 0.91667 | 123 | 25 | 2021-04-01 | 0.25 |  | 66
75 | Khulshi | 132 | 139 | 5 | 2021-04-01 | 0.75 | 122 | 24 | 2021-04-01 | 0.41667 |  | 67
76 | Halishahar | 132 | 139 | 4 | 2021-04-01 | 0.91667 | 122 | 25 | 2021-04-01 | 0.29167 |  | 68
77 | Baraulia | 132 | 140 | 4 | 2021-04-01 | 0.91667 | 122 | 24 | 2021-04-01 | 0.41667 |  | 11
78 | Sikalbaha | 132 | 139 | 3 | 2021-04-01 | 0.875 | 119 | 2 | 2021-04-01 | 0.5 |  | 12
79 | Dohazari | 132 | 137 | 4 | 2021-04-01 | 0 | 115 | 27 | 2021-04-01 | 0.41667 |  | 13
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: April'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 135 | 4 | 2021-04-01 | 0 | 104 | 4 | 2021-04-01 | 0.58333
81 | Chandraghona | 132 | 140 | 4 | 2021-04-01 | 0.91667 | 123 | 25 | 2021-04-01 | 0.45833
82 | Kaptai | 132 | 135 | 1 | 2021-04-01 | 0.041667 | 125 | 26 | 2021-04-01 | 0.29167
83 | A. Khaer Stl. | 132 | 135 | 8 | 2021-04-01 | 0.83333 | 123 | 25 | 2021-04-01 | 0.45833
84 | Bakulia | 132 | 139 | 4 | 2021-04-01 | 0.91667 | 123 | 25 | 2021-04-01 | 0.45833
85 | Julda | 132 | 139 | 10 | 2021-04-01 | 0.29167 | 123 | 30 | 2021-04-01 | 0.29167
86 | TK Chemical | 132 | 137 | 4 | 2021-04-01 | 0.91667 | 124 | 25 | 2021-04-01 | 0.45833
87 | Modern Steel | - | - | - | - | - | - | - | - | -
88 | Shahmirpur | 132 | 139 | 1 | 2021-04-01 | 0.79167 | 123 | 30 | 2021-04-01 | 0.29167
89 | Khagrachhari | 132 | 139 | 4 | 2021-04-01 | 0.91667 | 122 | 25 | 2021-04-01 | 0.29167
90 | Matarbari | 132 | 139 | 4 | 2021-04-01 | 0 | 100 | 23 | 2021-04-01 | 0.45833
91 | Baroiar Hat | 132 | 138 | 4 | 2021-04-01 | 0.91667 | 120 | 23 | 2021-04-01 | 0.625
92 | Rangamati | 132 | 139 | 4 | 2021-04-01 | 0.91667 | 122 | 25 | 2021-04-01 | 0.25
93 | Goalpara | 132 | 148 | 4 | 2021-04-01 | 0.8125 | 120 | 21 | 2021-04-01 | 0.54167
94 | Khulna Central | 132 | 147 | 4 | 2021-04-01 | 0.8125 | 119 | 15 | 2021-04-01 | 0.41667
95 | Noapara | 132 | 147 | 4 | 2021-04-01 | 0.8125 | 116 | 15 | 2021-04-01 | 0.41667
96 | Jessore | 132 | 142 | 4 | 2021-04-01 | 0.79167 | 108 | 13 | 2021-04-01 | 0.91667
97 | Benapol | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 106 | 13 | 2021-04-01 | 0.875
98 | Jhenida | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 102 | 13 | 2021-04-01 | 0.83333
99 | Bottail | 132 | 146 | 4 | 2021-04-01 | 0.8125 | 117 | 13 | 2021-04-01 | 0.91667
100 | G.K Project | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 130 | 13 | 2021-04-01 | 0.5
101 | Faridpur | 132 | 144 | 4 | 2021-04-01 | 0.79167 | 124 | 4 | 2021-04-01 | 0.45833
102 | Madaripur | 132 | 152 | 4 | 2021-04-01 | 0.875 | 128 | 29 | 2021-04-01 | 0.54167
103 | Sariatpur | 132 | 151 | 4 | 2021-04-01 | 0.875 | 126 | 3 | 2021-04-01 | 0.79167
104 | Gopalganj | 132 | 150 | 4 | 2021-04-01 | 0.8125 | 128 | 10 | 2021-04-01 | 0.77083
105 | Bagerhat | 132 | 148 | 4 | 2021-04-01 | 0.8125 | 115 | 15 | 2021-04-01 | 0.41667
106 | Mongla | 132 | 146 | 4 | 2021-04-01 | 0.8125 | 113 | 15 | 2021-04-01 | 0.54167
107 | Satkhira | 132 | 147 | 4 | 2021-04-01 | 0.8125 | 116 | 13 | 2021-04-01 | 0.91667
108 | Gallamari | 132 | 148 | 4 | 2021-04-01 | 0.8125 | 120 | 15 | 2021-04-01 | 0.41667
109 | Magura | 132 | 146 | 4 | 2021-04-01 | 0.8125 | 98 | 13 | 2021-04-01 | 0.91667
110 | Norail | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 98 | 13 | 2021-04-01 | 0.91667
111 | Chuadanga | 132 | 145 | 4 | 2021-04-01 | 0.79167 | 90 | 26 | 2021-04-01 | 0.91667
112 | Borguna | 132 | 149 | 4 | 2021-04-01 | 0.91667 | 124 | 30 | 2021-04-01 | 0.58333
113 | Barisal(N) | 132 | 155 | 4 | 2021-04-01 | 0.875 | 128 | 16 | 2021-04-01 | 0.25
114 | Barisal(S) | 132 | 153 | 4 | 2021-04-01 | 0.875 | 127 | 11 | 2021-04-01 | 0.66667
115 | Patuakhali | 132 | 147 | 17 | 2021-04-01 | 0.25 | 116 | 23 | 2021-04-01 | 0.58333
116 | Bhandaria | 132 | 148 | 17 | 2021-04-01 | 0.25 | 120 | 12 | 2021-04-01 | 0.66667
117 | Ishurdi | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 125 | 26 | 2021-04-01 | 0.041667
118 | Ruppur paromanobik | 132 | 144 | 4 | 2021-04-01 | 0.8125 | 129 | 13 | 2021-04-01 | 0.875
118 | Natore | 132 | 142 | 4 | 2021-04-01 | 0.75 | 126 | 4 | 2021-04-01 | 0.29167
119 | Bogra | 132 | 141 | 4 | 2021-04-01 | 0.8125 | 123 | 3 | 2021-04-01 | 0.83333
120 | Noagaon | 132 | 139 | 8 | 2021-04-01 | 0 | 113 | 16 | 2021-04-01 | 0.875
121 | Rajshahi | 132 | 142 | 4 | 2021-04-01 | 0.79167 | 124 | 16 | 2021-04-01 | 0.875
122 | Rajshahi New | 132 | 145 | 4 | 2021-04-01 | 0.70833 | 124 | 25 | 2021-04-01 | 0.875
123 | C.Nawabganj | 132 | 142 | 4 | 2021-04-01 | 0.70833 | 120 | 21 | 2021-04-01 | 0.58333
124 | Amnura | 132 | 143 | 21 | 2021-04-01 | 0.8125 | 119 | 21 | 2021-04-01 | 0.58333
125 | Pabna | 132 | 143 | 4 | 2021-04-01 | 0.83333 | 125 | 19 | 2021-04-01 | 0.16667
126 | Shahjadpur | 132 | 143 | 4 | 2021-04-01 | 0.70833 | 130 | 13 | 2021-04-01 | 0.375
127 | Serajganj | 132 | 138 | 4 | 2021-04-01 | 0.75 | 124 | 3 | 2021-04-01 | 0.83333
128 | Niyamatpur | 132 | 142 | 8 | 2021-04-01 | 0 | 104 | 20 | 2021-04-01 | 0.875
129 | Joypurhat | 132 | 143 | 8 | 2021-04-01 | 0 | 108 | 20 | 2021-04-01 | 0.875
130 | Sherpur(Bogura) | 132 | 141 | 4 | 2021-04-01 | 0.79167 | 121 | 22 | 2021-04-01 | 0.083333
132 | Mohastangor | 132 | 139 | 4 | 2021-04-01 | 0.75 | 121 | 3 | 2021-04-01 | 0.83333
133 | Bangura | 132 | 143 | 4 | 2021-04-01 | 0.79167 | 129 | 3 | 2021-04-01 | 0.79167
134 | Rangpur | 132 | 140 | 28 | 2021-04-01 | 0.8125 | 112 | 25 | 2021-04-01 | 0.83333
135 | Lalmonirhat | 132 | 138 | 17 | 2021-04-01 | 0.041667 | 112 | 13 | 2021-04-01 | 0.79167
136 | Saidpur | 132 | 139 | 1 | 2021-04-01 | 0.33333 | 110 | 1 | 2021-04-01 | 0.54167
137 | Purbasadipur | 132 | 137 | 1 | 2021-04-01 | 0.33333 | 102 | 30 | 2021-04-01 | 0.875
138 | Thakurgaon | 132 | 139 | 1 | 2021-04-01 | 0.33333 | 100 | 26 | 2021-04-01 | 0.79167
139 | Palashbari | 132 | 138 | 28 | 2021-04-01 | 0.77083 | 115 | 1 | 2021-04-01 | 0.41667
140 | Barapukuria | 132 | 142 | 28 | 2021-04-01 | 0.8125 | 117 | 1 | 2021-04-01 | 0.54167
141 | Panchagar | 132 | 138 | 1 | 2021-04-01 | 0.33333 | 97 | 27 | 2021-04-01 | 0.54167
142 | Joldhaka | 132 | 140 | 1 | 2021-04-01 | 0.33333 | 103 | 1 | 2021-04-01 | 0.54167
143 | Kurigram | 132 | 139 | 28 | 2021-04-01 | 0.77083 | 107 | 13 | 2021-04-01 | 0.8125
144 | Mithapukur | 132 | 140 | 28 | 2021-04-01 | 0.79167 | 116 | 1 | 2021-04-01 | 0.41667
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:April' 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 100 | 275
Hasnabad | TR2 | 225 | 100 | 275 | 26/04/21 | 7:00
| TR3 | 225 | 100 | 275
| TR1 | 225 | 170 | 510
Tongi | TR2 | 225 | 170 | 510 | 13/04/21 | 9:00
| TR3 | 225 | 170 | 510
Haripur | TR1 | 225 | 112 | 280
| TR2 | 225 | 112 | 280 | 23/04/21 | 7:00
| TR3 | 225 | 112 | 280
| TR1 | 225 | 184 | 510
Rampura | TR2 | 225 | 184 | 510 | 28/04/21 | 13:00
| TR3 | 225 | 184 | 510
Keraniganj | ATR1 | 300 | 68.32 | 178.9 | 28/04/21 | 13:59
| ATR2 | 300 | 75.29 | 196.7
| ATR3 | 300 | 80.34 | 210.3
| ATR4 | 300 | 76.07 | 199.2
| TR1 | 225 | 153 | 450
Aminbazar | TR2 | 225 | 153 | 450 | 2021-09-04 | 12:00
| TR3 | 225 | 160 | 468
Agargaon | TR1 | 300 | 281 | 832 | 2021-03-31 | 9:00
| TR2 | 300 | 269 | 804 | 2021-03-29 | 9:00
Maniknagar | TR1 | 300 | 116 | 350 | 29/04/21 | 13:00
| TR2 | 300 | 116 | 350
Cumilla (N) | TR1 | 225 | 210 | 588 | 2021-04-04 | 18:30
| TR2 | 225 | 208 | 588
Fenchuganj | AT2 | 300 | 256 | 690 | 2021-09-04 | 20:00
| MT1 | 150 | 82 | 220 | 2021-04-04
Hathazari | MT2 | 150 | 82 | 220
| MT3 | 150 | 82 | 220 |  | 19:00
| MT4 | 150 | 82 | 220
| TR1 | 225 | 110 | 294
Ishurdi | TR2 | 225 | 110 | 294 | 14/04/21 | 21:00
| TR3 | 225 | 110 | 294
Khulna(S) | TR1 | 225 | 122 | 337
| TR2 | 225 | 122 | 337 | 16/04//21 | 4:00
| TR3 | 300 | 156 | 430
Bogura | TR1 | 225 | 133 | 405
| TR2 | 225 | 133 | 405 | 21/04/21 | 18:00
| TR3 | 225 | 182 | 533
Baghabari | TR1 | 300 | 183 | 570
| TR2 | 225 | 129 | 350 | 16/04/21 | 21:00
Rajshahi | ATR-01 | 300 | 126 | 350 | 2021-07-04 | 23:00
| ATR-02 | 300 | 126 | 350
Barapukuria | TR1 | 225 | 158 | 780 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 169 | 800 | 27/04/21 | 22:00 | 132 kV current is being provided
| TR6 | 300 | 217 | 1085
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:April' 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 277.8 | 432 | 2021-12-03 | 14:45
| TR2(400/230 kV) | 520 | 281.3 | 435
| TR1(400/132 kV) | 325 | 277 | 465 | 2021-01-03 | 18:15
| TR2(400/132 kV) | 325 | 277 | 468
Bibiyana | ICT1(400/230 kV) | 520 | 161 | 239 | 21/03/21 | 18:00
| ICT2(400/230kV) | 520 | 157 | 232
Bhulta | ATR1(400/230 kV) | 520 | 213 | 397 | 2021-11-03 | 3:15
| ATR2(400/230kV) | 520 | 213 | 397
Ashuganj(N) | GSUT1 | 567 | 380.6 | 636 | 2021-11-03 | 3:16
Gopalganj | ATR1(400/138 kV) | 325 | 309 | 466 | 29/03/21 | 21:00
| ATR2(400/138kV) | 325 | 309 | 466
Payra | GSUT1 | 270 | 208 | 305 | 29/03/21 | 21:00
| GSUT2 | 270 | 208 | 305
| GSUT3 | 270 | 208 | 305
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
270

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:April' 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:April' 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-04-01 | 12893 | 12893 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-01 | 11079 | 11079 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-02 | 11995 | 11995 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-02 | 9745 | 9745 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-03 | 13018 | 13018 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-03 | 10126 | 10126 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-04 | 8524 | 8524 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-04 | 11262 | 11262 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-05 | 11347 | 11347 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-05 | 8996 | 8996 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-06 | 11958 | 11958 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-06 | 9994 | 9994 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-07 | 12651 | 12651 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-07 | 10450 | 10450 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-08 | 12854 | 12854 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-08 | 10322 | 10322 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-09 | 11655 | 11655 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-09 | 8629 | 8629 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-10 | 13064 | 13064 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-10 | 9503 | 9503 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-11 | 12798 | 12798 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-11 | 11266 | 11266 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-12 | 13377 | 13377 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-12 | 10900 | 10900 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-13 | 13308 | 13308 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-13 | 11347 | 11347 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-14 | 13058 | 13058 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-14 | 10094 | 10094 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-15 | 13380 | 13380 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-15 | 10902 | 10902 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-16 | 12705 | 12705 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-16 | 9873 | 9873 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-17 | 11940 | 11940 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-17 | 8237 | 8237 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-18 | 12661 | 12661 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-18 | 9873 | 9873 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-19 | 12961 | 12961 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-19 | 10158 | 10158 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-20 | 13228 | 13228 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-20 | 10747 | 10747 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-21 | 12542 | 12542 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-21 | 11129 | 11129 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-22 | 12409 | 12409 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-22 | 9864 | 9864 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-23 | 11853 | 11853 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-23 | 9072 | 9072 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-24 | 13007 | 13007 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-24 | 10005 | 10005 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-25 | 13520 | 13520 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-25 | 11145 | 11145 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-26 | 13777 | 13777 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-26 | 11508 | 11508 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-27 | 13792 | 14097 | 275 | - | - | - | - | - | - | - | - | - | - | - | 2021-04-27 | 11614 | 11614 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-28 | 12949 | 12949 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-28 | 11773 | 11773 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-29 | 13788 | 13788 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-29 | 11323 | 11323 | - | - | - | - | - | - | - | - | - | - | - | -
2021-04-30 | 13289 | 13289 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-04-30 | 10454 | 10454 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | -305 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | 0 | 0 | 29
[15 empty] | 0 | 0 | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:April' 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13792 | 2021-04-27 | 20:00
2 | Maximum Day Peak Genaration | MW | 11773 | 2021-04-28 | 12:00
3 | Maximum Evening Peak Demand | MW | 14097 | 44313 | 19:00
4 | Minimum Generation | MW | 4853 | 2021-04-17 | 7:00
5 | Average of the daily evening peak Genaration | MW | 12676.7
6 | Average of the daily day peak Genaration | MW | 10379.6667
7 | Maximum load shed | MW | 275 | 2021-04-27 | 20:00
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 1
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 9.1667
11 | Total Generation | MkWh | 7915.5838
12 | Total Generation by BPDB | MkWh | 1830.3371 | % of total Gen. | 23.12%
13 | Total Generation by IPP | MkWh | 2364.6922 | '' | 29.87%
14 | A) Total Generation by Generation Companies | MkWh | 2341.7491 | '' | 29.58%
| B) Total Generation by REB | MkWh | 133.246 | " | 1.683%
| C) Total Generation by RENTAL | MkWh | 587.4025 | " | 7.421%
| D) Total Imported from India (BIPTC) | MkWh | 563.0526 | " | 7.113%
| E) Total Imported from Tripura, India (A.C) | MkWh | 95.1043 | " | 1.201%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4613.3508 | % of total Gen. | 58.28%
| B) Oil | MkWh | 1953.1605 | '' | 24.67%
| C) Hydro | MkWh | 41.547 | '' | 0.5249%
| D) Solar | MkWh | 21.9287 | '' | 0.277%
| E) Coal | MkWh | 627.4399 | '' | 7.927%
| F) BIPTC (Import from India) | MkWh | 563.0526 | '' | 7.113%
| G) A.C (Import from Tripura, India) | MkWh | 95.1043 | '' | 1.201%
16 | Maximun of the daily total Generation . | MkWh | 348.9198 | 2021-04-23
17 | Monthly Load factor | % | 77.1406
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 26846.2371
| A) Gas | M.Taka | 4833.4655
| B) Liquid fuel | M.Taka | 15508.3095
| C) Coal | M.Taka | 2919.6113
| D) BIPTC (Import from India) | M.Taka | 2871.5683
| E) Tripura(Import from India) | M.Taka | 713.2824
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1058.5806 | 24/03/2021
| A) Gas | M.Taka | 174.2531 | 28/03/2021
| B) Liquid fuel | M.Taka | 786.9735 | 24/03/2021
| C) Coal | M.Taka | 549.0231 | 02/03/2021
| D) BIPTC (Import from India) | M.Taka | 103.8879 | 2021-04-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.5485
| B) Excluding Hydro & Solar | Taka/kWhR | 3.5768
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 82.2 | 30/4/2021 | 06:00
b) | Actual | FT (MSL) | 76.93 | 30/4/2021 | 06:00
22 | Peak Genaration of March 2020 | MW | 10790 | 18/03/20 | 19:30
23 | Peak Demand of March 2020 | MW | 10790 | 18/03/20 | 19:30
24 | Maximum peak Generation recorded upto 31/03/2021 | MW | 12893 | 29/05/19 | 21:00
25 | Maximum peak Demand recorded upto 31/03/2021 | MW | 12893 | 29/05/19 | 21:00
26 | Maximum load shed recorded upto 31/03/2021 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.