## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-07 | Monday
|  |  | Date (day): | 2021-06-07 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13979.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15246 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-06 | 2021-06-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 101 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 314 | 296 | 310 | 315 |  |  | Gas shortage
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 181 | 170 | 180 | 180 | 180 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 230 | 260 | 280 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 10 | 40 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 87 | 87 |  | 13 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 21 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 24 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 272 | 270 | 300 | 320
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 16 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 53 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 82 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 0 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 50 | 17 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 52 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 41 | 42 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 38 | 15 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 117 | 116 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 85 | 85 | 85 | 85 |  | 20 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 0 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 115 | 54 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2517 | 2245 | 3505 | 3770 | 719 | 1078
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 3 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 1 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 11 | 25 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 20 | 20 | 20 | 20 | 210 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 71 | 196 | 220 | 220 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 120 | 120 | 120
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 55 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 85 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 10 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 28 | 7 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 6 | 6 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 10 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 7 | 17 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 40 | 10 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 17 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 442 | 909 | 1657 | 1650 | 572 | 123
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 125 | 100 | 100 | 129 | 0
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Machine problem.
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 98 | 221 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 275 | 320 | 340 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 295 | 320 | 350 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 49 | 53 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 43 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 50 | 143 | 143 |  | 7 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 91 | 30 | 90 |  | 73 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 177 | 51 | 185 | 185 |  | 15 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 110 | 152 | 181
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 5 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 104 | 52 | 100 | 100
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 115 | 55 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 29 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1576 | 1591 | 2087 | 2406 | 456 | 146
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 134 | 135 | 153 | 153 | 49 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 0 | 20 | 20 |  | 2 | Engine problem
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 16 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 58 | 120 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 33 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 391 | 410 | 569.6 | 518 | 49 | 89
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 111 | 110 | 0 | 160 |  | 170 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 53 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 62 | 61 | 61
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 80 | 83 | 80 | 80
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 191 | 191 | 205 | 205
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 15 | 16 | 15 | 15 |  | 10 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 377 | 376 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 5 | 7 | 7 | 7 |  | 3
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 399 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1864 | 1863 | 1836 | 1996 | 0 | 359
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 917 | 914 | 836 | 933
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 0 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 340 | 260 | 260 | 150 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  | 8 | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 0 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 80 | 0 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1306 | 1254 | 1431 | 1798 | 150 | 91
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 13 | 23 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 64 | 65 | 65 | 65 |  | 129 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 10 | 12 | 12 | 12 | 65 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 450 | 330 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 148 | 133 | 228 | 233 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 685 | 563 | 1070 | 1185 | 65 | 129
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 51 | 51 |  | 20 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 34 | 0 | 34 | 34 |  | 16 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 34 | 34 |  | 16 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 106 | 108 | 80 | 80 | 130 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 157 | 138 | 130 | 130 | 90 |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 168 | 185 | 185 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 354 | 359 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 43 | 34 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 88 | 50 | 90
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 101 | 35 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 100 | 35 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1098 | 1129 | 1553 | 1640 | 391 | 77
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 111 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 262 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 10141 | 10227 | 13979.6 | 15246 | 2526 | 2282
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9808.8171 | 9892 | 13521.6782 | 14746.5955
| A. |  | 2021-06-06 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 10906 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8658 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10227 | MW
| 3 | Day peak Generation : |  |  | 10141 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9892 | MW
| 4 | Evening peak Generation : |  |  | 10227 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 247.1049 | MKWHr | By Solar | 0.53968 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 152.4599 | MKWHr |  | By Oil: | 55.1368 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.9431 | MKWHr |  | By Hydro: | 0.488 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2526 | MW | Dhaka | 3728 | 3728 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2282 | MW | Chittagong | 1026 | 1026 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4808 | MW | Khulna | 927 | 927 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1207.1 | MMCFD |  |  | Rajshahi | 1104 | 1104 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 159712539.018 | ii) Oil : | Taka | 414106475.66 | Comilla | 962 | 962 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 64987116 | Total | Taka | 638806130.678 | Mymensingh | 826 | 826 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.2265 | MKWHr. | Sylhet | 446 | 446 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 240 | MW (E to W) at | 21:00 | hrs | Barisal | 181 | 181 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -62 | MW at | 3:00 | hrs | Rangpur | 692 | 692 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 9892 | 9892 |  | 0
| B. |  | 2021-06-07 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 38.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15246 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
| 4 | Reserve(Generation end) |  |  |  | 2046 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 299.0817 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8378 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 22.1345 | MKWHr. | ii) HVDC Flow at Peak Time |  | 914 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.4029 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 72.46 |  | (b) Today: | 72.81 |  | (c) Rule Curve: |  | 77.56
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 310 | 243 |  | 0 | 280 | 220 | 0 | 0 | 15 | 334 | 0 | 0 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 85 | 92 | 0 | 19 | 22 | 21 | 0 | 100 | 0 | 260 | 300 | 183 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 120 | 157 | 8 | 19 | 0 | 42 | 42 | 53 | 0 | 163 | 111 | 62 | 83 | 0 | 225 | 18 | 0 | 7 | 285 | 8 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 95 | 0 | 20 | 170 | 132 | 366 | 107 | 84 | 105 | 0 | 0 | 54 | 34 | 114 | 114 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 |  | 918 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 52 | 34 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 175 | 0 | 13 | 100 | 190 | 0 | 390 | 105 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 450 | 225 | 0 | 0 | 0 |  | 7286 | 3620 | 10906 | 4736 | 918 | 2031 | 2203 | 600 | 20 | 278 | 120 | 0 | 0 | 72.46
2:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 310 | 244 |  | 0 | 280 | 220 | 0 | 0 | 15 | 335 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 120 | 0 |  | 22 | 0 | 85 | 92 | 0 | 0 | 22 | 29 | 0 | 100 | 0 | 260 | 300 | 183 | 8 | 89 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 19 | 116 | 156 | 8 | 19 | 0 | 42 | 42 | 53 | 0 | 130 | 110 | 62 | 83 | 0 | 225 | 18 | 0 | 7 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 72 | 0 | 20 | 80 | 10 | 366 | 115 | 84 | 105 | 0 | 0 | 54 | 34 | 114 | 111 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 |  | 918 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 43 | 34 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 119 | 0 | 183 | 0 | 12 | 100 | 190 | 0 | 400 | 105 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 450 | 225 | 0 | 0 | 0 |  | 6954 | 3467 | 10421 | 4742 | 918 | 2025 | 1827 | 600 | 20 | 173 | 116 | 0 | 0 | 72.46
3:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 310 | 263 |  | 0 | 280 | 220 | 0 | 0 | 0 | 333 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 30 | 24 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 120 | 0 |  | 24 | 0 | 85 | 92 | 0 | 0 | 22 | 29 | 0 | 100 | 0 | 260 | 300 | 184 | 8 | 91 | 26 | 56 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 20 | 116 | 155 | 8 | 19 | 0 | 42 | 42 | 53 | 0 | 130 | 110 | 62 | 83 | 0 | 225 | 18 | 0 | 7 | 295 | 8 | 11 | 0 | 0 | 0 | 0 | 35 | 0 | 61 | 0 | 20 | 17 | 0 | 364 | 115 | 84 | 105 | 0 | 0 | 54 | 34 | 114 | 111 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 |  | 918 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 25 | 34 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 188 | 0 | 12 | 80 | 190 | 0 | 319 | 70 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 420 | 226 | 0 | 0 | 0 |  | 6831 | 3294 | 10125 | 4743 | 918 | 1964 | 1621 | 570 | 20 | 173 | 116 | 0 | 0 | 72.46
4:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 310 | 263 |  | 0 | 280 | 220 | 0 | 0 | 0 | 332 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 85 | 92 | 0 | 0 | 22 | 29 | 0 | 100 | 0 | 260 | 300 | 0 | 8 | 90 | 0 | 0 | 0 | 51 | 0 | 0 | 43 | 19 | 8 | 33 | 20 | 110 | 156 | 8 | 19 | 0 | 42 | 42 | 53 | 0 | 130 | 112 | 63 | 83 | 0 | 225 | 18 | 0 | 5 | 295 | 8 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 42 | 0 | 20 | 17 | 0 | 367 | 115 | 0 | 105 | 0 | 0 | 54 | 34 | 34 | 111 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 25 | 0 |  | 918 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 25 | 34 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 120 | 0 | 189 | 0 | 12 | 40 | 190 | 0 | 394 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 420 | 225 | 0 | 0 | 0 |  | 6262 | 3237 | 9499 | 4548 | 918 | 1978 | 1207 | 570 | 20 | 148 | 110 | 0 | 0 | 72.46
5:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 309 | 283 |  | 0 | 280 | 220 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 20 | 33 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 51 | 92 | 0 | 0 | 22 | 36 | 0 | 100 | 0 | 260 | 300 | 0 | 8 | 87 | 16 | 0 | 0 | 10 | 0 | 0 | 43 | 19 | 8 | 33 | 20 | 100 | 194 | 8 | 19 | 0 | 42 | 42 | 53 | 0 | 130 | 112 | 63 | 20 | 0 | 225 | 18 | 0 | 7 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 66 | 0 | 20 | 17 | 0 | 366 | 115 | 56 | 105 | 0 | 0 | 54 | 34 | 17 | 65 | 0 | 400 | 0 | 0 | 0 | 17 | 0 | 17 | 0 |  | 917 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 25 | 34 | 22 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 120 | 0 | 187 | 0 | 12 | 40 | 190 | 0 | 383 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 380 | 216 | 0 | 0 | 0 |  | 6148 | 3174 | 9322 | 4581 | 917 | 1869 | 1192 | 529 | 20 | 114 | 100 | 0 | 0 | 72.46
6:00 | 0 | 0 | 0 | 185 | 0 | 23 | 0 | 309 | 293 |  | 0 | 280 | 220 | 0 | 0 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 33 | 33 | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 51 | 60 | 0 | 0 | 22 | 40 | 0 | 100 | 0 | 260 | 300 | 0 | 8 | 87 | 0 | 20 | 0 | 10 | 0 | 0 | 43 | 19 | 8 | 15 | 0 | 88 | 168 | 8 | 19 | 0 | 42 | 42 | 11 | 0 | 130 | 111 | 63 | 20 | 0 | 225 | 18 | 0 | 7 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 23 | 2 | 20 | 17 | 0 | 367 | 115 | 85 | 68 | 0 | 0 | 54 | 34 | 17 | 36 | 0 | 400 | 0 | 1 | 0 | 17 | 0 | 17 | 2 |  | 918 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 50 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 187 | 0 | 12 | 0 | 190 | 0 | 380 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 211 | 0 | 0 | 0 |  | 5816 | 3011 | 8827 | 4485 | 918 | 1771 | 960 | 500 | 20 | 80 | 88 | 5 | 0 | 72.46
7:00 | 0 | 0 | 0 | 185 | 0 | 23 | 0 | 309 | 274 |  | 0 | 280 | 220 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 20 | 33 | 33 | 13 | 0 | 0 | 20 | 100 | 0 | 17 | 209 | 0 | 120 | 0 |  | 25 | 0 | 51 | 60 | 0 | 0 | 22 | 35 | 0 | 100 | 0 | 280 | 320 | 0 | 8 | 90 | 16 | 12 | 0 | 10 | 0 | 0 | 43 | 19 | 8 | 0 | 0 | 54 | 168 | 8 | 19 | 0 | 42 | 42 | 11 | 0 | 100 | 111 | 62 | 20 | 0 | 165 | 18 | 0 | 7 | 280 | 8 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 6 | 20 | 17 | 0 | 313 | 115 | 85 | 68 | 1 | 0 | 54 | 34 | 17 | 36 | 0 | 398 | 0 | 4 | 0 | 17 | 0 | 17 | 4 |  | 918 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 50 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 187 | 0 | 12 | 0 | 190 | 0 | 347 | 35 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 223 | 0 | 0 | 0 |  | 5696 | 2962 | 8658 | 4427 | 918 | 1684 | 968 | 500 | 20 | 71 | 54 | 16 | 0 | 72.46
8:00 | 0 | 0 | 0 | 185 | 0 | 90 | 0 | 310 | 253 |  | 0 | 280 | 220 | 0 | 0 | 0 | 336 | 0 | 0 | 4 | 2 | 16 | 0 | 0 | 0 | 0 | 40 | 17 | 17 | 0 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 115 | 0 |  | 22 | 0 | 6 | 92 | 0 | 0 | 22 | 10 | 0 | 100 | 0 | 260 | 300 | 0 | 8 | 85 | 0 | 30 | 0 | 22 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 60 | 155 | 8 | 19 | 1 | 42 | 42 | 53 | 0 | 130 | 109 | 63 | 40 | 0 | 204 | 18 | 0 | 7 | 280 | 8 | 5 | 0 | 0 | 0 | 0 | 26 | 0 | 18 | 8 | 20 | 17 | 0 | 400 | 115 | 85 | 68 | 2 | 0 | 54 | 34 | 52 | 70 | 0 | 400 | 0 | 9 | 0 | 17 | 0 | 17 | 11 |  | 917 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 50 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 119 | 0 | 183 | 0 | 12 | 0 | 190 | 0 | 310 | 35 | 0 | 13 | 0 | 0 | 0 | 1 | 0 | 380 | 221 | 0 | 0 | 1 |  | 6029 | 2980 | 9009 | 4463 | 917 | 1784 | 1173 | 530 | 20 | 29 | 60 | 33 | 0 | 72.46
9:00 | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 309 | 250 |  | 0 | 280 | 220 | 0 | 0 | 0 | 336 | 0 | 0 | 45 | 16 | 16 | 0 | 0 | 0 | 0 | 53 | 55 | 55 | 0 | 25 | 26 | 33 | 33 | 25 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 115 | 0 |  | 22 | 0 | 0 | 92 | 0 | 0 | 22 | 4 | 0 | 100 | 0 | 260 | 300 | 30 | 8 | 90 | 20 | 30 | 0 | 51 | 0 | 0 | 43 | 0 | 0 | 33 | 3 | 76 | 139 | 8 | 19 | 1 | 42 | 42 | 53 | 0 | 110 | 112 | 62 | 40 | 0 | 191 | 18 | 0 | 7 | 270 | 8 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 19 | 19 | 20 | 17 | 0 | 376 | 115 | 85 | 68 | 0 | 0 | 54 | 34 | 52 | 110 | 0 | 400 | 0 | 20 | 0 | 17 | 0 | 17 | 24 |  | 917 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 50 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 125 | 0 | 181 | 0 | 12 | 0 | 190 | 0 | 352 | 35 | 0 | 35 | 0 | 0 | 0 | 2 | 0 | 400 | 130 | 0 | 0 | 1 |  | 6304 | 2977 | 9281 | 4506 | 917 | 1731 | 1394 | 550 | 20 | 20 | 76 | 67 | 0 | 72.47
10:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 311 | 205 |  | 0 | 280 | 250 | 0 | 0 | 0 | 334 | 0 | 0 | 50 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 16 | 25 | 26 | 33 | 33 | 37 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 115 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 22 | 4 | 0 | 120 | 0 | 270 | 290 | 38 | 24 | 86 | 23 | 40 | 0 | 43 | 0 | 0 | 20 | 0 | 0 | 33 | 3 | 86 | 124 | 8 | 19 | 1 | 42 | 42 | 53 | 0 | 163 | 111 | 62 | 80 | 0 | 191 | 18 | 0 | 7 | 300 | 15 | 5 | 0 | 0 | 0 | 0 | 40 | 0 | 53 | 5 | 60 | 28 | 0 | 376 | 115 | 85 | 80 | 0 | 0 | 54 | 51 | 80 | 112 | 0 | 400 | 0 | 18 | 0 | 17 | 0 | 17 | 29 |  | 918 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 121 | 0 | 175 | 0 | 12 | 0 | 190 | 0 | 384 | 35 | 0 | 38 | 0 | 6 | 0 | 2 | 0 | 410 | 148 | 0 | 0 | 2 |  | 6588 | 3049 | 9637 | 4536 | 918 | 1881 | 1543 | 560 | 20 | 36 | 86 | 57 | 0 | 72.47
11:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 314 | 195 |  | 0 | 280 | 275 | 0 | 0 | 0 | 270 | 0 | 0 | 70 | 16 | 82 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 16 | 25 | 28 | 33 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 125 | 0 | 335 | 340 | 56 | 0 | 89 | 26 | 45 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 33 | 5 | 100 | 134 | 8 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 111 | 61 | 80 | 0 | 191 | 18 | 0 | 5 | 280 | 15 | 5 | 0 | 3 | 0 | 0 | 40 | 0 | 104 | 0 | 0 | 111 | 0 | 377 | 115 | 85 | 0 | 0 | 0 | 0 | 0 | 114 | 116 | 0 | 394 | 0 | 31 | 52 | 0 | 0 | 17 | 30 |  | 918 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 168 | 0 | 12 | 0 | 190 | 0 | 402 | 70 | 0 | 71 | 0 | 34 | 0 | 2 | 35 | 450 | 149 | 0 | 0 | 3 |  | 6253 | 3206 | 9459 | 4239 | 918 | 1798 | 1630 | 600 | 20 | 86 | 100 | 68 | 0 | 72.47
12:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 314 | 181 |  | 0 | 280 | 230 | 0 | 0 | 10 | 272 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 50 | 0 | 25 | 28 | 0 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 3 | 71 | 0 | 0 | 0 |  | 24 | 0 | 0 | 60 | 0 | 11 | 22 | 2 | 0 | 125 | 0 | 270 | 300 | 98 | 0 | 90 | 26 | 49 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 33 | 5 | 104 | 134 | 8 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 111 | 62 | 80 | 0 | 191 | 18 | 0 | 5 | 300 | 15 | 5 | 0 | 38 | 0 | 0 | 58 | 0 | 117 | 1 | 40 | 177 | 0 | 377 | 115 | 85 | 55 | 0 | 0 | 10 | 7 | 104 | 115 | 40 | 400 | 17 | 33 | 115 | 0 | 0 | 29 | 33 |  | 917 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 25 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 157 | 0 | 10 | 0 | 190 | 0 | 354 | 80 | 0 | 101 | 0 | 111 | 0 | 1 | 100 | 450 | 148 | 0 | 0 | 3 |  | 6790 | 3351 | 10141 | 4237 | 917 | 1750 | 2286 | 600 | 20 | 154 | 104 | 73 | 0 | 72.48
13:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 313 | 171 |  | 0 | 280 | 260 | 0 | 0 | 40 | 270 | 0 | 0 | 100 | 92 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 54 | 19 | 25 | 28 | 33 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 17 | 82 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 46 | 22 | 12 | 0 | 135 | 0 | 270 | 300 | 194 | 0 | 84 | 26 | 48 | 0 | 0 | 0 | 0 | 43 | 19 | 8 | 33 | 6 | 90 | 133 | 8 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 110 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 280 | 15 | 5 | 0 | 110 | 0 | 0 | 70 | 0 | 131 | 0 | 40 | 145 | 0 | 376 | 115 | 85 | 105 | 0 | 0 | 36 | 70 | 70 | 75 | 40 | 400 | 53 | 22 | 126 | 25 | 0 | 35 | 32 |  | 917 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 63 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 45 | 34 | 0 | 0 | 16 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 115 | 0 | 157 | 0 | 10 | 0 | 190 | 0 | 355 | 88 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 440 | 147 | 0 | 0 | 1 |  | 7337 | 3468 | 10805 | 4417 | 917 | 1741 | 2722 | 590 | 20 | 249 | 90 | 59 | 0 | 72.48
14:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 312 | 168 |  | 0 | 280 | 245 | 0 | 0 | 30 | 270 | 0 | 0 | 100 | 102 | 98 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 28 | 33 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 0 | 84 | 0 | 70 | 0 |  | 24 | 0 | 0 | 92 | 5 | 47 | 22 | 3 | 0 | 135 | 0 | 270 | 295 | 184 | 0 | 90 | 26 | 49 | 0 | 0 | 0 | 0 | 43 | 19 | 8 | 33 | 6 | 104 | 133 | 8 | 19 | 2 | 42 | 42 | 53 | 0 | 130 | 112 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 275 | 8 | 5 | 0 | 145 | 0 | 0 | 70 | 0 | 112 | 0 | 10 | 51 | 0 | 376 | 115 | 85 | 105 | 0 | 0 | 49 | 100 | 52 | 55 | 10 | 400 | 40 | 19 | 126 | 17 | 0 | 35 | 29 |  | 918 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 64 | 12 | 0 | 0 | 0 | 0 | 50 | 0 | 47 | 34 | 0 | 0 | 16 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 109 | 0 | 156 | 0 | 12 | 68 | 190 | 0 | 296 | 90 | 0 | 70 | 0 | 70 | 0 | 3 | 70 | 440 | 150 | 0 | 0 | 2 |  | 7081 | 3345 | 10426 | 4465 | 918 | 1635 | 2441 | 590 | 20 | 198 | 104 | 55 | 0 | 72.48
15:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 311 | 168 |  | 0 | 280 | 265 | 0 | 0 | 15 | 270 | 0 | 0 | 100 | 64 | 98 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 19 | 25 | 28 | 33 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 7 | 80 | 0 | 120 | 0 |  | 24 | 0 | 0 | 92 | 5 | 50 | 22 | 3 | 0 | 135 | 0 | 270 | 280 | 186 | 0 | 91 | 26 | 49 | 0 | 0 | 0 | 0 | 43 | 19 | 0 | 33 | 5 | 94 | 132 | 8 | 19 | 1 | 42 | 42 | 53 | 0 | 130 | 111 | 61 | 83 | 0 | 190 | 18 | 0 | 7 | 285 | 14 | 5 | 0 | 95 | 0 | 0 | 30 | 0 | 100 | 0 | 10 | 17 | 0 | 377 | 115 | 72 | 105 | 0 | 0 | 54 | 17 | 52 | 17 | 10 | 400 | 17 | 14 | 72 | 17 | 0 | 35 | 21 |  | 917 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 1 | 0 | 0 | 0 | 0 | 50 | 0 | 48 | 12 | 0 | 0 | 16 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 151 | 0 | 11 | 30 | 190 | 0 | 334 | 90 | 0 | 35 | 0 | 45 | 0 | 0 | 35 | 350 | 110 | 0 | 0 | 1 |  | 6709 | 3071 | 9780 | 4482 | 917 | 1630 | 1901 | 500 | 20 | 199 | 94 | 37 | 0 | 72.49
16:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 312 | 169 |  | 0 | 280 | 285 | 0 | 0 | 15 | 270 | 0 | 0 | 70 | 32 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 83 | 0 | 120 | 0 |  | 24 | 0 | 0 | 60 | 3 | 24 | 22 | 3 | 0 | 135 | 0 | 270 | 320 | 202 | 0 | 91 | 26 | 51 | 0 | 0 | 0 | 0 | 43 | 19 | 8 | 33 | 5 | 98 | 133 | 8 | 19 | 1 | 42 | 42 | 53 | 0 | 130 | 109 | 61 | 83 | 0 | 190 | 18 | 0 | 7 | 270 | 14 | 0 | 0 | 45 | 0 | 0 | 8 | 0 | 100 | 0 | 10 | 17 | 0 | 377 | 65 | 68 | 17 | 1 | 0 | 35 | 17 | 17 | 17 | 10 | 394 | 0 | 17 | 17 | 17 | 0 | 35 | 10 |  | 917 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 48 | 0 | 0 | 0 | 16 | 0 | 18 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 105 | 0 | 146 | 0 | 11 | 0 | 140 | 0 | 333 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 340 | 95 | 0 | 0 | 0 |  | 6268 | 2769 | 9037 | 4471 | 917 | 1606 | 1239 | 490 | 20 | 165 | 98 | 31 | 0 | 72.52
17:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 312 | 170 |  | 0 | 280 | 260 | 0 | 0 | 15 | 270 | 0 | 0 | 24 | 32 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 81 | 0 | 120 | 0 |  | 24 | 0 | 0 | 60 | 2 | 25 | 22 | 3 | 0 | 135 | 0 | 270 | 280 | 184 | 0 | 91 | 26 | 52 | 0 | 0 | 0 | 0 | 34 | 19 | 8 | 33 | 6 | 92 | 152 | 8 | 0 | 0 | 42 | 42 | 53 | 0 | 130 | 111 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 290 | 14 | 0 | 0 | 45 | 0 | 0 | 8 | 0 | 100 | 1 | 10 | 17 | 0 | 376 | 65 | 85 | 17 | 0 | 0 | 35 | 17 | 17 | 17 | 10 | 399 | 0 | 2 | 17 | 17 | 0 | 35 | 0 |  | 917 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 8 | 0 | 31 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 60 | 0 | 134 | 0 | 12 | 0 | 140 | 0 | 236 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 280 | 90 | 0 | 0 | 0 |  | 6160 | 2388 | 8548 | 4302 | 917 | 1518 | 1159 | 430 | 20 | 106 | 92 | 4 | 0 | 72.55
18:00 | 0 | 0 | 0 | 160 | 0 | 101 | 0 | 312 | 170 |  | 0 | 280 | 270 | 0 | 0 | 15 | 270 | 0 | 0 | 24 | 32 | 64 | 0 | 0 | 0 | 0 | 35 | 35 | 17 | 19 | 25 | 18 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 140 | 0 | 120 | 0 |  | 0 | 0 | 0 | 60 | 6 | 25 | 22 | 3 | 0 | 115 | 0 | 260 | 270 | 184 | 8 | 90 | 26 | 54 | 0 | 0 | 0 | 0 | 43 | 19 | 8 | 33 | 6 | 102 | 146 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 130 | 110 | 40 | 83 | 0 | 177 | 18 | 0 | 7 | 290 | 14 | 0 | 0 | 52 | 0 | 0 | 8 | 0 | 100 | 0 | 10 | 17 | 0 | 377 | 65 | 85 | 17 | 0 | 0 | 35 | 17 | 17 | 17 | 10 | 367 | 1 | 1 | 17 | 17 | 0 | 35 | 0 |  | 914 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 0 | 0 | 0 | 8 | 7 | 31 | 0 | 8 | 0 | 2 | 0 | 5 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 12 | 0 | 140 | 0 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 90 | 0 | 0 | 0 |  | 6114 | 2378 | 8492 | 4216 | 914 | 1532 | 1167 | 430 | 20 | 110 | 102 | 1 | 0 | 72.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 101 | 0 | 278 | 170 |  | 0 | 280 | 265 | 0 | 0 | 42 | 250 | 0 | 0 | 24 | 48 | 64 | 8 | 0 | 0 | 0 | 53 | 35 | 17 | 21 | 25 | 18 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 195 | 0 | 90 | 0 |  | 12 | 0 | 85 | 100 | 6 | 26 | 22 | 5 | 0 | 100 | 0 | 260 | 265 | 186 | 8 | 85 | 26 | 54 | 0 | 1 | 0 | 50 | 43 | 19 | 11 | 33 | 6 | 112 | 146 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 130 | 110 | 63 | 83 | 0 | 171 | 18 | 0 | 0 | 270 | 0 | 11 | 0 | 102 | 0 | 0 | 8 | 0 | 113 | 0 | 10 | 26 | 0 | 372 | 90 | 85 | 46 | 0 | 0 | 45 | 17 | 52 | 39 | 10 | 363 | 15 | 0 | 20 | 17 | 0 | 35 | 0 |  | 915 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 0 | 0 | 50 | 31 | 88 | 12 | 8 | 31 | 8 | 21 | 5 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 12 | 0 | 140 | 0 | 334 | 0 | 0 | 32 | 0 | 105 | 0 | 0 | 25 | 280 | 90 | 0 | 0 | 0 |  | 6529 | 2848 | 9377 | 4189 | 915 | 1617 | 1674 | 430 | 20 | 420 | 112 | 0 | 0 | 72.66
19:30 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 274 | 170 |  | 0 | 280 | 270 | 0 | 0 | 55 | 250 | 0 | 0 | 24 | 64 | 98 | 0 | 0 | 0 | 0 | 53 | 35 | 17 | 21 | 25 | 18 | 28 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 195 | 0 | 90 | 0 |  | 24 | 0 | 85 | 100 | 6 | 25 | 22 | 7 | 0 | 100 | 0 | 260 | 265 | 221 | 8 | 85 | 26 | 54 | 0 | 7 | 0 | 50 | 43 | 19 | 11 | 33 | 6 | 114 | 135 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 130 | 112 | 62 | 80 | 0 | 191 | 18 | 0 | 0 | 270 | 0 | 11 | 0 | 45 | 0 | 0 | 100 | 0 | 149 | 0 | 10 | 51 | 26 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 400 | 17 | 0 | 54 | 17 | 0 | 35 | 0 |  | 914 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 50 | 34 | 88 | 12 | 0 | 38 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 60 | 0 | 130 | 0 | 12 | 0 | 140 | 0 | 292 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 340 | 90 | 0 | 0 | 0 |  | 6971 | 3061 | 10032 | 4427 | 914 | 1598 | 1991 | 491 | 20 | 477 | 114 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 273 | 170 |  | 0 | 280 | 250 | 0 | 0 | 55 | 250 | 0 | 0 | 24 | 32 | 98 | 0 | 0 | 0 | 0 | 53 | 17 | 17 | 21 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 25 | 22 | 7 | 0 | 100 | 0 | 260 | 265 | 221 | 8 | 90 | 26 | 54 | 0 | 18 | 0 | 25 | 43 | 19 | 11 | 33 | 6 | 110 | 134 | 16 | 19 | 0 | 42 | 42 | 53 | 0 | 163 | 111 | 62 | 80 | 0 | 191 | 18 | 0 | 0 | 280 | 0 | 11 | 0 | 45 | 0 | 0 | 86 | 0 | 140 | 0 | 10 | 51 | 21 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 400 | 17 | 0 | 54 | 17 | 0 | 35 | 0 |  | 913 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 12 | 0 | 40 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 60 | 0 | 130 | 0 | 12 | 0 | 140 | 0 | 299 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 330 | 90 | 0 | 0 | 0 |  | 6951 | 3001 | 9952 | 4461 | 913 | 1661 | 1887 | 480 | 20 | 420 | 110 | 0 | 0 | 72.64
21:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 296 | 170 |  | 0 | 280 | 260 | 0 | 0 | 40 | 270 | 0 | 0 | 24 | 16 | 82 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 21 | 25 | 27 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 68 | 100 | 0 | 25 | 22 | 28 | 0 | 100 | 0 | 275 | 295 | 221 | 8 | 91 | 26 | 53 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 110 | 135 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 163 | 110 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 116 | 0 | 10 | 51 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 399 | 0 | 0 | 54 | 17 | 0 | 35 | 0 |  | 914 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 38 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 138 | 0 | 12 | 0 | 168 | 0 | 359 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 330 | 133 | 0 | 0 | 0 |  | 7018 | 3209 | 10227 | 4651 | 914 | 1828 | 1864 | 480 | 20 | 360 | 110 | 0 | 0 | 72.66
22:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 312 | 170 |  | 0 | 280 | 270 | 0 | 0 | 30 | 270 | 0 | 0 | 24 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 68 | 100 | 0 | 0 | 22 | 28 | 0 | 100 | 0 | 280 | 290 | 219 | 8 | 89 | 26 | 54 | 0 | 45 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 108 | 134 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 163 | 109 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 275 | 14 | 11 | 0 | 0 | 0 | 0 | 120 | 0 | 92 | 0 | 10 | 51 | 20 | 377 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 399 | 0 | 0 | 17 | 17 | 0 | 35 | 0 |  | 915 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 186 | 0 | 12 | 0 | 210 | 0 | 400 | 15 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 340 | 133 | 0 | 0 | 0 |  | 6868 | 3336 | 10204 | 4804 | 915 | 1857 | 1706 | 490 | 20 | 304 | 108 | 0 | 0 | 72.68
23:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 312 | 172 |  | 0 | 280 | 295 | 0 | 0 | 15 | 270 | 0 | 0 | 24 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 212 | 0 | 110 | 0 |  | 24 | 0 | 68 | 92 | 0 | 0 | 22 | 28 | 0 | 100 | 0 | 320 | 330 | 217 | 8 | 92 | 26 | 54 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 112 | 147 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 163 | 110 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 290 | 7 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 10 | 0 | 0 | 377 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 |  | 914 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 43 | 33 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 144 | 0 | 160 | 0 | 12 | 0 | 206 | 0 | 420 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 400 | 133 | 0 | 0 | 0 |  | 6824 | 3280 | 10104 | 4850 | 914 | 1900 | 1488 | 549 | 20 | 271 | 112 | 0 | 0 | 72.7
24:00 | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 312 | 191 |  | 0 | 280 | 290 | 0 | 0 | 15 | 270 | 0 | 0 | 24 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 199 | 0 | 110 | 0 |  | 24 | 0 | 68 | 92 | 0 | 0 | 22 | 29 | 0 | 100 | 0 | 300 | 320 | 218 | 8 | 92 | 23 | 55 | 0 | 51 | 0 | 0 | 43 | 19 | 11 | 33 | 19 | 112 | 148 | 16 | 20 | 0 | 42 | 42 | 53 | 0 | 163 | 110 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 310 | 14 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 81 | 0 | 10 | 0 | 0 | 377 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 400 | 0 | 0 | 0 | 17 | 0 | 35 | 0 |  | 914 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 43 | 33 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 160 | 0 | 12 | 0 | 201 | 0 | 421 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 400 | 133 | 0 | 0 | 0 |  | 6843 | 3256 | 10099 | 4807 | 914 | 1942 | 1483 | 550 | 20 | 271 | 112 | 0 | 0 | 72.72
KWH | 0 | 0 | 0 | 4252500 | 0 | 2152590 | 0 | 7535646 | 5012000 |  | 0 | 6641000 | 6045236 | 0 | 0 | 420700 | 7163667 | 0 | 0 | 1233600 | 633024 | 1292640 | 13257 | 0 | 0 | 0 | 1061640 | 563370 | 449918 | 235584 | 600000 | 635580 | 672600 | 835800 | 789600 | 0 | 0 | 488000 | 2400000 | 0 | 363749 | 3789174 | 0 | 2328371 | 0 |  | 550560 | 0 | 913076 | 1954440 | 32640 | 377760 | 503712 | 367680 | 0 | 2651860 | 0 | 6860000 | 7252000 | 3218000 | 167272 | 2111980 | 501624 | 1052640 | 0 | 607810 | 0 | 57344 | 1003550 | 358020 | 162180 | 708700 | 261580 | 2402880 | 3406520 | 245760 | 332928 | 13400 | 1007000 | 1003800 | 1166400 | 0 | 3532173 | 2473000 | 1422928 | 1705920 | 0 | 4740620 | 404000 | 0 | 141300 | 7052000 | 213576 | 149376 | 0 | 878181 | 0 | 0 | 1440000 | 0 | 1994690 | 34020 | 446400 | 1413120 | 607810 | 8948000 | 2613600 | 1897200 | 2054945 | 4561 | 0 | 1164091 | 863123 | 1452360 | 1796760 | 237120 | 9457000 | 192960 | 231820 | 848160 | 421527 | 0 | 740880 | 217369 |  | 22134545 | 0 | 7549920 | 0 | 0 | 0 | 0 | 0 | 61440 | 0 | 0 | 1401000 | 454451 | 0 | 0 | 0 | 0 | 546816 | 36916 | 1008560 | 161320 | 9656 | 89724 | 604320 | 362084 | 432000 | 0 | 179154 | 0 | 0 | 3666900 | 0 | 0 | 2727600 | 0 | 4210355 | 0 | 294116 | 579840 | 4718573 | 0 | 8495364 | 1182240 | 0 | 986688 | 0 | 9834720 | 0 | 19975 | 607680 | 10276200 | 3801273 | 0 | 0 | 18540 |  | 160652952 | 86451970 | 247104922 | 109383928 | 22134545 | 43075989 | 50768195 | 13943100 | 488000 | 4368600 | 2402880 | 539685 | 0
Fuel Cost | 0 | 0 | 0 | 6251175 | 0 | 2841418.8 | 0 | 7611002.46 | 5162360 |  | 0 | 7238690 | 6710211.96 | 0 | 0 | 3559122 | 7450213.68 | 0 | 0 | 9289008 | 5773178.88 | 12719577.6 | 122229.54 | 0 | 0 | 0 | 7749972 | 4354850.1 | 4436191.48 | 176688 | 450000 | 0 | 0 | 0 | 7635432 | 0 | 0 | 131760 | 4344000 | 0 | 3379228.21 | 4130199.66 | 0 | 3958230.7 | 0 |  | 0 | 0 | 8856837.2 | 18664902 | 283968 | 2991859.2 | 634677.12 | 1092009.6 | 0 | 3924752.8 | 0 | 5076400 | 7252000 | 2960560 | 215780.88 | 2428777 | 566835.12 | 1473696 | 0 | 1039355.1 | 0 | 579174.4 | 9583902.5 | 454685.4 | 121635 | 1240225 | 196185 | 18021600 | 3610911.2 | 2231500.8 | 422818.56 | 213596 | 1651480 | 1606080 | 2076192 | 0 | 4026677.22 | 2571920 | 2803168.16 | 3258307.2 | 0 | 8201272.6 | 884760 | 0 | 288252 | 7122520 | 160182 | 113525.76 | 0 | 6639048.36 | 0 | 0 | 7488000 | 0 | 19627749.6 | 397693.8 | 3638160 | 15332352 | 4285060.5 | 8321640 | 23836032 | 17928540 | 17898570.95 | 0 | 0 | 10139232.61 | 7586851.17 | 14494552.8 | 15398233.2 | 1579219.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 127494979.2 | 0 | 7927416 | 0 | 0 | 0 | 0 | 0 | 644505.6 | 0 | 0 | 1583130 | 704399.05 | 0 | 0 | 0 | 0 | 5380669.44 | 375066.56 | 8925756 | 1242164 | 130549.12 | 869425.56 | 5855860.8 | 3512214.8 | 829440 | 0 | 135619.578 | 0 | 0 | 19874598 | 0 | 0 | 3191292 | 0 | 5557668.6 | 0 | 441174 | 9863078.4 | 5520730.41 | 0 | 8410410.36 | 12342585.6 | 0 | 9363669.12 | 0 | 76317427.2 | 0 | 220723.75 | 4490755.2 | 45112518 | 0 | 0 | 0 | 0 |  | 418968657.08 | 366317826.348 | 785286483.428 | 113491856.808 | 127494979.2 | 46220682.21 | 372243248.5 | 64987116 | 131760 | 41863227.16 | 18021600 | 832013.55 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 314 | 181 |  | 0 | 280 | 230 | 0 | 0 | 10 | 272 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 50 | 0 | 25 | 28 | 0 | 33 | 41 | 0 | 0 | 20 | 100 | 0 | 3 | 71 | 0 | 0 | 0 |  | 24 | 0 | 0 | 60 | 0 | 11 | 22 | 2 | 0 | 125 | 0 | 270 | 300 | 98 | 0 | 90 | 26 | 49 | 0 | 0 | 0 | 0 | 43 | 0 | 8 | 33 | 5 | 104 | 134 | 8 | 17 | 2 | 42 | 42 | 53 | 0 | 163 | 111 | 62 | 80 | 0 | 191 | 18 | 0 | 5 | 300 | 15 | 5 | 0 | 38 | 0 | 0 | 58 | 0 | 117 | 1 | 40 | 177 | 0 | 377 | 115 | 85 | 55 | 0 | 0 | 10 | 7 | 104 | 115 | 40 | 400 | 17 | 33 | 115 | 0 | 0 | 29 | 33 |  | 917 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 25 | 0 | 17 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 157 | 0 | 10 | 0 | 190 | 0 | 354 | 80 | 0 | 101 | 0 | 111 | 0 | 1 | 100 | 450 | 148 | 0 | 0 | 3 |  | 10141 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 296 | 170 | 0 | 0 | 280 | 260 | 0 | 0 | 40 | 270 | 0 | 0 | 24 | 16 | 82 | 0 | 0 | 0 | 0 | 53 | 0 | 17 | 21 | 25 | 27 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 | 0 | 24 | 0 | 68 | 100 | 0 | 25 | 22 | 28 | 0 | 100 | 0 | 275 | 295 | 221 | 8 | 91 | 26 | 53 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 110 | 135 | 16 | 0 | 0 | 42 | 42 | 53 | 0 | 163 | 110 | 62 | 83 | 0 | 191 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 116 | 0 | 10 | 51 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 17 | 52 | 55 | 10 | 399 | 0 | 0 | 54 | 17 | 0 | 35 | 0 |  | 914 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 38 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 138 | 0 | 12 | 0 | 168 | 0 | 359 | 0 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 330 | 133 | 0 | 0 | 0 |  | 10227 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 315 | 180 | 0 | 0 | 280 | 300 | 0 | 0 | 55 | 320 | 0 | 0 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 25 | 0 | 129 | 0 | 340 | 350 | 220 | 8 | 90 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 181 | 153 | 8 | 20 | 0 | 42 | 42 | 51 | 0 | 163 | 160 | 61 | 80 | 0 | 205 | 18 | 0 | 7 | 341 | 15 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 35 |  |  | 933 | 0 | 260 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 90 | 34 | 34 | 40 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 80 | 0 | 130 | 0 | 12 | 100 | 185 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 233 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 310 | 180 | 0 | 0 | 280 | 280 | 0 | 0 | 55 | 300 | 0 | 0 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 7 | 0 | 100 | 0 | 320 | 320 | 220 | 8 | 30 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 152 | 153 | 8 | 20 | 1.6 | 42 | 42 | 51 | 0 | 163 | 0 | 61 | 80 | 0 | 205 | 18 | 0 | 7 | 341 | 15 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 35 | 30 |  | 836 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 50 | 34 | 34 | 40 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 80 | 0 | 130 | 0 | 12 | 50 | 185 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 228 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 296 | 203 | 0 | 0 | 280 | 275 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 29 | 33 |  | 0 | 0 | 0 | 20 | 100 | 0 | 17 | 200 | 0 | 120 | 0 | 0 | 25 | 0 | 0 | 60 | 0 | 0 | 22 | 7 | 0 | 100 | 0 | 300 | 320 | 189 | 8 | 30 | 20 | 25 | 0 | 51 | 0 | 0 | 12 | 19 | 8 | 33 | 12 | 100 | 153 | 8 | 20 | 1 | 42 | 42 | 50 | 0 | 130 | 112 | 61 | 80 | 0 | 205 | 0 | 0 | 7 | 310 | 15 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 10 | 10 | 0 | 0 | 377 | 75 | 87 | 105 | 2 | 0 | 54 | 17 | 52 | 63 | 0 | 350 | 0 | 15 | 0 | 17 | 0 | 35 | 10 | 0 | 629 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 12 | 0 | 192 | 0 | 412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 134 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 8658 | 7:00
| Highest Generation |  | 10906 | 1:00
| Day Peak Generation |  | 10141 | 12:00
| Evening Peak Generation |  | 10227 | 21:00
| HVDC Max Flow |  | 918 | 1:00
| HVDC EvPeak Flow |  | 914 | 21:00
| Load factor L.F |  | 94.41%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10141 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8378 | MW
Evening Peak Generation : |  | 10227 | MW Hour : | 21:00 | Available Max Generation : |  | 15246 | MW
E.P. Demand (at gen end) : |  | 10227 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 10906 | MW Hour : | 1:00 | Reserve(Generation end) |  | 2046 | MW
Total Gen. (MKWH) : |  | 247.1049 | System Load Factor : | 94.41% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -62 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-07
Actual : | 72.81 | Ft.(MSL) , | Rule curve : | 77.56 | Ft.( MSL )
Gas Consumed : | Total = | 1207.1 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 159712539.018
: |  | Coal : | 64987116 | Oil : | 414106475.66 | Total : | 638806130.678
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4741.9805 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1618.2926 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1450.9623 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1311.4311 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1184.9204 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 956.2034 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 527.2538 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 246.0006 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 737.507 |  |  | 0 | 0%
Total | 0 |  | 12774.5517 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kodda-Kabirpur 132 kV Ckt-2 was under shut down from 09:02 to 13:11 for C/M.
b) Mithapukur 132/33 kV T-1 transformer was under shut down from 09:48 to 13:47 for C/M.
c) Savar 132/33 kV T-3 transformer was under shut down from 08:35 to 17:01 for D/W.
d) Siddhirganj-Haripur 132 kV Ckt-2 was under shut down from 08:45 to 13:13 for R/H maintenance.
e) Ashuganj 230 kV GIS Bus was under shut down from 12:27 to 17:32 for C/M.
f) Ashuganj 225 MW GT was synchronized at 11:12 and STG was synchronized at 11:44.
g) Bheramara HVDC 20DF41 filter was under shut down from 11:23 to 13:04 for C/M.
h) Sikalbaha-Madunaghat 132 kV both Ckts tripped at 10:37 showing E/F relay at Sikalbaha end and was |  |  |  |  | About 270 MW power interruption occurred under Cox'sbazar,Dohazari,
switched on at 10:54. |  |  |  |  | Shamirpur,Juldah,Sikalbaha,Bakulia S/S areas from 10:37 to 10:54.
At the same time Bakulia-Khulshi 132 kV both Ckts tripped from Khulshi end and Sikalbaha 225 MW,Sikalbaha
150 MW,Juldah all units, Baraka Sikalbaha,Jodiac,Patia,Anlima and Karnaphuli also tripped.
i) Sikalbaha 225 MW GT was synchronized at 11:12 and ST was synchronized at 17:17.
j) Sikalbaha 150 MW GT was synchronized at 13:40.
k) GPH 230 kV Bus-2 was shut down at 12:27 for testing work.
l) Keraniganj-Srinagar 132 kV Ckt-2 tripped at 13:18 showing Dist. Z1,R at Keraniganj end and was switched
on at 13:56.
m) Aminbazar-Meghnaghat 230 kV Ckt-2 tripped at 14:51 showing Dist. Z1,Y at Aminbazar end and Dist. Z1,Y
auto reclosure at Meghnaghat end and was switched on at 15:03.
n) Aminbazar-Mirpur 132 kV Ckt-1 was under shut down from 15:07 to 15:35 for C/M.
o) Halishahar 132/33 kV T-1 and T-3 transformers 33 kV side tripped showing O/C relay at T-1 transformer |  |  |  |  | About 48 MW power interruption occurred under Halishahar S/S area
and Inst. O/C relay at T-3 transformer and was switched on at 15:13. |  |  |  |  | from 14:42 15:13.
p) Ashuganj-Sirajganj 230 kV Ckt-2 tripped at 16:17 showing auto reclosure block at Ashuganj end and was
switched on at 16:39.
q) Pabna-Shahjadpur 132 kV Ckt tripped at 16:01 showing Dist. Z1,R at Pabna end and Dist. Z1,R at
Shahjadpur end and was switched on at 16:56.
r) Ghorashal-Ishurdi 230 kV Ckt-2 was switched on at 17:19.
s) Orion Rupsha-Goalpara 132 kV Ckt tripped at 17:44 showing Dist. Z1 at Orion Rupsha end and Dist. Z1,C
at Goalpara end and was switched on at 17:58.
t) Madanganj 132/33 kV T-1 transformer tripped at 01:50(07/6/2021) from both ends showing backup protection |  |  |  |  | About 25 MW power interruption occurred under Madanganj S/S area
trip at 132 kV side & O/C relay at 33 kV Side due to 33 kV ,premier cement protection and was switched on at 02:34. |  |  |  |  | from 01:50(07/6/2021) to 02:34.
u) Sylhet-Chatak 132 kV Ckt-2 tripped at 05:10(07/6/2021) from Sylhet end showing Dist. Z1 and was switched |  |  |  |  | About 25 MW power interruption occurred under Sunamganj S/S area
on at 05:21. |  |  |  |  | from 05:10(07/6/2021) to 05:21.
v) Chuadanga 132/33 kV T-2 transformer was shut down at 06:30(07/6/2021) for D/W. |  |  |  |  | About 20 MW power interruption occurred under Chuadanga S/S area
since 06:30(07/6/2021) to till now.
w) Mohasthangarh 33 kV Bus & 132/33 kV T-1 transformer was shut down at 07:06(07/6/2021) for R/H maint. |  |  |  |  | About 10 MW power interruption occurred under Mohasthangarh S/S area
at 33 kV incomer Bus isolator and was switched on at 09:17. |  |  |  |  | from 07:06(07/6/2021) to 09:17.
x) Jamalpur 132/33 kV T-1 transformer was shut down at 07:18(07/6/2021) for replacing 132 kV CT.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4252500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 2152590
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 296 | 7535646 | Gas shortage
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 170 | 5012000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6641000 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6045236 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 420700 | Low demand
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 13257 | Reserve.
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 235584
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 24 | 1233600 | Low demand
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 7163667 | Gas shortage
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 16 | 633024 | Low demand
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 53 | 1061640
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 82 | 1292640 | Low demand
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 563370 | Reserve.
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 449918 | Low demand
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 52 | 1235580 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 672600
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 835800
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 789600 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 878181 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 116 | 1994690
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 85 | 1897200 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 192960 | Reserve.
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 848160 | Low demand
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 217369
| Dhaka area Total |  |  |  | 5919 | 2245 | 54268512
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 363749 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 34020
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 25 | 377760 | Low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 488000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 196 | 3789174 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2328371 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2054945
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 913076 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1954440
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 446400 | Line O/L
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 503712
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 367680
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 32640 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 4561
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1164091
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 17 | 863123 | Transformer O/L
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 237120 | Line O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 17 | 421527 | Line O/L
| Chattogram area Total |  |  |  | 2382 | 909 | 18744389
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 100 | 2651860
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 221 | 3218000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 275 | 6860000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7252000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 501624 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 53 | 1052640
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 167272 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 607810 | Ashuganj 230 kV Bus S/D
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 607810 | Ashuganj 230 kV Bus S/D
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 57344
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 91 | 2111980 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 51 | 1413120 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 358020
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 162180 | Engine problem
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 110 | 2402880
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 708700
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1003550 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 261580 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1452360 | High voltage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 55 | 1796760 | Low demand
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 740880 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1591 | 35388370
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 135 | 3406520 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 332928 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 16 | 245760 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13400
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 1440000 | Low demand
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2613600
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 231820
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 550560
| Mymensingh Area Total |  |  |  | 709 | 410 | 8834588
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 1007000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1003800 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3532173
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2473000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1166400
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 149376
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1422928
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1705920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 191 | 4740620
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 404000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 213576 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7052000 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 376 | 8948000
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 7 | 141300 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 399 | 9457000
| Sylhet Area Total |  |  |  | 2377 | 1863 | 43417093
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 914 | 22134545
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 61440 | Reserve.
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 340 | 7549920 | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 0 | 579840 | Reserve.
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 0 | 1182240 | Reserve.
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1254 | 31507985
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 23 | 454451
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1401000 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 294116 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 330 | 10276200
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 133 | 3801273 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 563 | 16227040
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 546816
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 36916 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 161320 | Reserve.
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 9656 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 89724 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 108 | 2727600 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 138 | 4210355 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 168 | 4718573 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 359 | 8495364 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 362084 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 432000
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 179154
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 604320 | Low demand
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 1008560 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 986688 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 35 | 607680 | Low demand
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 18540
| Rajshahi Area Total |  |  |  | 2179 | 1129 | 25195350
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3666900 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 9834720
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 19975
| Rangpur Area Total |  |  |  | 605 | 263 | 13521595
| Total |  |  |  | 21315 | 10227 | 247104922
| Eastern Grid Total |  |  |  | 14421 | 7018 | 160652952
| Western Grid Total |  |  |  | 6894 | 3209 | 86451970
| National Grid Total |  |  |  | 21315 | 10227 | 247104922
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-06
(a) ENTIRE EASTERN GRID : |  | 6988 | MW | (b) ENTIRE WESTERN GRID : |  | 2904 | MW
i) Dhaka area |  | 3728 | MW | i) Khulna area |  | 927 | MW
ii) Chittagong area |  | 1026 | MW | ii) Rajshahi area |  | 1104 | MW
iii) Comilla area |  | 962 | MW | iii) Barisal area |  | 181 | MW
iv) Mymensingh area |  | 826 | MW | iv) Rangpur area |  | 692 | MW
v) Sylhet area |  | 446 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9892 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 124 | 11:00 | Kishoreganj | 124 | 21:00 | Jessore | 121 | 14:00
Munsiganj | 82 | 1:00 | Netrokona | 107 | 19:30 | Benapol | 46 | 1:00
Sonargaon | 68 | 21:00 | Jamalpur | 117 | 1:00 | Jhenida | 102 | 1:00
Shyampur | 198 | 10:00 | Sherpur | 108 | 19:30 | Bottail | 136 | 19:30
Bhulta | 209 | 12:00 | Srimongal | 44 | 19:30 | G.K Project | 54 | 19:30
Madanganj | 44 | 12:00 | Shahjibazar | 100 | 21:00 | Faridpur | 160 | 13:00
Shitalakhya | 121 | 12:00 | Fenchuganj | 38 | 19:30 | Madaripur | 80 | 1:00
Rahim steel | 26 | 11:00 | Kulawara | 40 | 19:30 | Sariatpur | 48 | 1:00
Matuail | 54 | 14:00 | Sylhet | 110 | 21:00 | Gopalganj | 76 | 1:00
Ghorasal | 71 | 15:00 | Chatak | 24 | 19:30 | Bagerhat | 90 | 1:00
Narsingdi | 162 | 15:00 | Sunamganj | 42 | 21:00 | Mongla | 42 | 12:00
Haripur (SBU) | 119 | 15:00 | Biani Bazar | 52 | 19:00 | Satkhira | 104 | 14:00
Sreenagar | 32 | 1:00 | Comilla (S) | 120 | 1:00 | Gallamari | 36 | 13:00
Ullon | 63 | 14:00 | Comilla(N) | 113 | 19:30 | Magura | 46 | 1:00
Hasnabad | 83 | 11:00 | Chandpur | 62 | 1:00 | Norail | 32 | 1:00
Magbazar | 101 | 13:00 | Feni | 90 | 1:0 | Chuadanga | 89 | 1:00
Maniknagar | 74 | 13:00 | Chowmuhani | 152 | 2:00 | Borguna | 16 | 1:00
Bangabhaban | 12 | 10:00 | Ashuganj | 28 | 11:00 | Barisal(N) | 32 | 1:00
Motijheel | 21 | 12:00 | Daudkandi | 122 | 22:00 | Barisal (S) | 104 | 13:00
Narinda | 56 | 13:00 | B.Baria | 126 | 22:00 | Patuakhali | 98 | 1:00
Kazla | 78 | 11:00 | Ramganj | 64 | 23:00 | Bhandaria | 42 | 1:00
Dhanmondi | 204 | 13:00 | Chaddagram | 32 | 22:00 | Borhan Uddin | 28 | 22:00
Lalbag | 86 | 13:00 | PHP | 9 | 22:00 | Ishurdi | 61 | 1:00
Madartek | 66 | 19:00 | Kochua | 48 | 22:00 | Ruppur Paromanobik | 4 | 17:00
Dhaka University | 46 | 13:00 | Madunaghat | 46 | 1:00 | Natore | 118 | 14:00
Aftabnagar | 10 | 12:00 | Hathazari | 74 | 1:00 | Bogra | 128 | 2:00
Fatullah | 60 | 10:00 | Khulshi | 172 | 1:00 | Noagaon | 110 | 1:00
Nawabganj | 41 | 21:00 | Halishahar | 95 | 8:00 | Rajshahi | 141 | 21:00
Keraniganj | 52 | 22:00 | Baraulia | 164 | 1:00 | Rajshahi New | 20 | 1:00
Mirpur | 170 | 13:00 | Sikalbaha | 27 | 1:00 | C.Nawabganj | 60 | 13:00
Kalyanpur | 105 | 13:00 | Dohazari | 86 | 1:00 | Amnura | 46 | 21:00
Gulshan | 138 | 13:00 | Cox'sbazar | 97 | 21:00 | Pabna | 96 | 20:00
Uttara | 82 | 13:00 | Chandraghona | 24 | 1:00 | Shahjadpur | 79 | 14:00
Uttara New | 30 | 13:00 | Kaptai | 4.5 | 19:00 | Serajganj | 83 | 20:00
Kamrangirchar | 96 | 14:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 70 | 21:00
Savar | 150 | 12:00 | Bakulia | 85 | 12:00 | Joypurhat | 54 | 21:00
Bhasantec | 161 | 13: | Julda | 19 | 1:00 | Sherpur(Bogura) | 48 | 13:00
Agargaon | 83 | 13:00 | TK chemical | 22.5 | 19:30 | Mohastangor | 50 | 1:00
Satmosjid | 97 | 13:00 | Modern Steel |  |  | Bhangura | 26 | 13:00
Tongi | 129 | 14:00 | Shahmirpur | 22.5 | 9:00 | Rangpur | 120 | 20:00
Kabirpur | 245 | 14:00 | Khagrachhari | 18 | 12:00 | Lalmonirhat | 36 | 21:00
Basundhara | 170 | 13:00 | Matarbari | 27.5 | 1:00 | Saidpur | 92 | 21:00
Manikganj | 74 | 1:00 | Baroiar Hat | 30 | 1:00 | Purbasadipur | 117 | 20:00
Joydevpur | 167 | 15:00 | Rangamati | 10 | 19:00 | Thakurgaon | 73 | 19:30
New Tongi | 113 | 12:00 | Abul Khair 230 | 132 | 5:00 | Palashbari | 105 | 21:00
Kodda | 284 | 14:00 | BSRM | 151 | 13:00 | Barapukuria | 53 | 21:00
Dhamrai | 124 | 12:00 | GPH Ispat | 83 | 7:00 | Panchagar | 49 | 19:00
Rajendrapur | 92 | 13:00 | Agrabad | 26 | 16:00 | Joldhaka | 54 | 19:30
Valuka | 108 | 12:00 | Goalpara | 27 | 1:00 | Kurigram | 51 | 21:00
Tangail | 170 | 13:00 | Central S/S | 96 | 1:00 | Mithapukur | 25 | 21:00
Mymensing | 180 | 1:00 | Noapara | 49 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 20:00 | 395 | 10:00 | Kaliakoir | 387 | 0.75 | 374 | 0.41667
| Bheramara | 394 | 1:00 | 388 | 24:00 | Bhulta | 380 | 0.20833 | 367 | 0.45833
| Ashuganj(N) | 387 | 18:00 | 374 | 10:00 | Gopalganj | 411 | 0.625 | 391 | 0.54167
| Payra | 413 | 5:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 226 | 13:00 | 217 | 17:00
| Ishurdi | 235 | 17:00 | 225 | 13:00 | Megnaghat | 230 | 8:00 | 223 | 11:00
| Ashuganj | 236 | 20:00 | 230 | 10:00 | Fenchuganj | 239 | 3:00 | 233 | 7:00
| Serajganj | 230 | 1:00 | 225 | 9:00 | Siddhirganj | 227 | 5:00 | 220 | 10:00
| Baghabari | 233 | 17:00 | 226 | 24:00 | Maniknagar | 225 | 5:00 | 218 | 10:00
| Barapukuria | 235 | 18:30 | 229 | 10:00 | Agargaon | 223 | 18:00 | 213 | 10:00
| Bogra | 225 | 19:00 | 216 | 10:00 | Barisal | 246 | 13:00 | 232 | 1:00
| Rajshahi | 234 | 18:30 | 224 | 24:00 | Bhola 225 MW | 248 | 20:00 | 237 | 1:00
| Khulna South | 229 | 18:30 | 202 | 13:00 | AKSML | 224 | 13:00 | 216 | 8:00
| Rampura | 225 | 5:00 | 220 | 10:00 | BSRM | 225 | 14:00 | 218 | 8:00
| Haripur | 224 | 19:00 | 218 | 9:00 | Bibiyana | 239 | 5:00 | 234 | 11:00
| Hasnabad | 224 | 19:00 | 215 | 9:00 | Bhulta | 228 | 18:30 | 220 | 11:00
| Shyampur | 222 | 5:00 | 220 | 10:00 | Ashuganj (S) | 233 | 19:00 | 227 | 10:00
| Aminbazar | 224 | 1:00 | 216 | 2:00 | Kaliakoir | 225 | 19:00 | 215 | 10:00
| Tongi | 223 | 19:00 | 212 | 10:00 | GPH | 225 | 13:00 | 217 | 8:00
| Comilla (N) | 227 | 14:00 | 222 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 19:00 | 125 | 10:00 | Kochua | 138 | 0.5 | 131 | 0.95833
| Munsiganj | 133 | 19:00 | 125 | 11:00 | Madanhat | 135 | 0.5 | 129 | 0.45833
| Sonargaon | 130 | 19:00 | 124 | 11:00 | Hathazari | 135 | 0.5 | 130 | 0.083333
| Shyampur | 133 | 19:00 | 127 | 10:00 | Khulshi | 132 | 0.5 | 126 | 0.45833
| Bhulta | 124 | 18:30 | 118 | 10:00 | Halishahar | 132 | 0.5 | 126 | 0.29167
| Madanganj | 131 | 19:30 | 124 | 10:00 | Baraulia | 132 | 0.5 | 128 | 0.125
| Shitalakhya | 134 | 14:00 | 125 | 11:00 | Sikalbaha | 136 | 0.5 | 129 | 0.70833
| Rahim steal | 131 | 19:00 | 126 | 9:00 | Dohazari | 135 | 0.45833 | 126 | 0.16667
| Matuail | 131 | 19:00 | 125 | 10:00 | Cox'sbazar | 128 | 0.45833 | 110 | 0.79167
| Ghorasal | 138 | 9:00 | 137 | 1:00 | Chandraghona | 135 | 0.5 | 129 | 0.041667
| Narsinghdi | 135 | 18:00 | 128 | 1:00 | Kaptai | 133 | 0.54167 | 128 | 0.041667
| Haripur (SBU) | 131 | 4:00 | 126 | 11:00 | A. Khaer Stl. | 132 | 0.45833 | 126 | 0.083333
| Sreenagar | 127 | 19:00 | 122 | 9:00 | Bakulia | 135 | 0.54167 | 128 | 0.125
| Ullon | 137 | 4:00 | 128 | 12:00 | Julda | 135 | 0.5 | 129 | 0.45833
| Hasnabad | 133 | 19:00 | 126 | 11:00 | TK Chemical | 134 | 0.5 | 127 | 0.45833
| Magbazar | 135 | 1:00 | 127 | 11:00 | Modern Steel
| Maniknagar | 135 | 3:00 | 129 | 11:00 | Shahmirpur | 137 | 0.54167 | 127 | 0.45833
| Bangabhaban | 135 | 3:00 | 129 | 11:00 | Khagrachhari | 134 | 0.5 | 128 | 0.041667
| Motijheel | 135 | 3:00 | 129 | 11:00 | Matarbari | 131 | 0.45833 | 109 | 0.77083
| Narinda | 135 | 3:00 | 129 | 11:00 | Baroiar Hat | 137 | 0.5 | 130 | 0.25
| Kazla | 135 | 3:00 | 129 | 11:00 | Rangamati | 134 | 12:00 | 128 | 1:00
| Dhanmondi | 131 | 3:00 | 125 | 11:00 | Agrabad | 133 | 13:00 | 126 | 11:00
| Lalbag | 133 | 5:00 | 124 | 10:00 | Goalpara S/S | 141 | 18:00 | 122 | 0.54167
| Madartek | 136 | 3:00 | 128 | 12:00 | Khulna Central S/S | 139 | 18:00 | 123 | 0.66667
| Dhaka University | 136 | 1:00 | 128 | 11:00 | Noapara | 136 | 18:00 | 121 | 0.54167
| Aftabnagar | 137 | 5:00 | 128 | 11:00 | Jessore | 132 | 17:00 | 113 | 0.54167
| Fatullah | 133 | 5:00 | 127 | 11:00 | Benapol | 132 | 0.75 | 116 | 0.66667
| Nawabganj | 127 | 18:30 | 121 | 11:00 | Jhenida | 131 | 18:30 | 112 | 0.041667
| Keraniganj | 128 | 19:00 | 122 | 10:00 | Bottail | 133 | 0.77083 | 123 | 0.54167
| Mirpur | 134 | 5:00 | 127 | 10:00 | G.K Project | 139 | 0.70833 | 133 | 0.95833
| Kalyanpur | 134 | 6:00 | 120 | 10:00 | Faridpur | 138 | 0.75 | 130 | 0.45833
| Gulshan | 137 | 5:00 | 129 | 11:00 | Madaripur | 143 | 0.70833 | 134 | 0.041667
| Uttara | 133 | 6:00 | 127 | 11:00 | Shariyatpur S/S | 143 | 17:00 | 132 | 0.041667
| Uttara New | 133 | 3:00 | 127 | 11:00 | Gopalganj | 146 | 0.70833 | 135 | 0.54167
| Kamrangirchar | 132 | 4:00 | 127 | 10:00 | Bagerhat | 140 | 18:00 | 120 | 0.20833
| Savar | 135 | 15:00 | 126 | 10:00 | Mongla | 139 | 18:30 | 114 | 0.54167
| Bhasantec | 133 | 5:00 | 126 | 11:00 | Satkhira | 142 | 18:00 | 121 | 13:00
| Agargaon | 135 | 5:00 | 127 | 11:00 | Gallamari | 141 | 0.77083 | 121 | 13:00
| Satmosjid | 134 | 6:00 | 127 | 12:00 | Magura | 131 | 18:30 | 110 | 0.041667
| Tongi | 137 | 19:00 | 128 | 10:00 | Narail | 129 | 0.77083 | 109 | 0.041667
| Kabirpur | 134 | 18:00 | 125 | 14:00 | Chuadanga | 128 | 18:30 | 102 | 0.041667
| Basundhara | 134 | 19:30 | 125 | 10:00 | Borguna | 143 | 20:00 | 126 | 0.041667
| Manikganj | 140 | 18:00 | 130 | 13:00 | Barisal(N) | 144 | 17:00 | 132 | 1:00
| Joydevpur | 138 | 18:00 | 130 | 9:00 | Barisal (S) | 142 | 0.83333 | 131 | 0.041667
| New Tongi | 136 | 23:00 | 127 | 15:00 | Patuakhali(S) | 143 | 0.66667 | 126 | 0.041667
| Kodda | 134 | 18:00 | 123 | 9:00 | Bhandaria | 143 | 0.8125 | 127 | 0.041667
| Dhamrai | 134 | 18:00 | 123 | 15:00 | Ishurdi | 136 | 18:30 | 131 | 13:00
| Rajendrapur | 135 | 18:30 | 120 | 10:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 1:00
| Valuka | 129 | 18:00 | 115 | 15:00 | Natore | 134 | 19:00 | 129 | 13:00
| Tangail | 135 | 18:00 | 123 | 14:00 | Bogra | 133 | 18:30 | 128 | 2:00
| Mymensing | 129 | 18:00 | 120 | 1:00 | Noagaon | 131 | 18:30 | 121 | 1:00
| Kishorganj | 130 | 17:00 | 123 | 0:00 | Rajshahi | 131 | 19:00 | 127 | 13:00
| Netrokona | 129 | 18:00 | 117 | 0:00 | Rajshahi New | 134 | 18:30 | 127 | 1:00
| Jamalpur | 134 | 20:00 | 124 | 16:00 | C.Nawabganj | 133 | 18:30 | 124 | 2:00
| Sherpur | 133 | 20:00 | 121 | 16:00 | Amnura | 133 | 19:00 | 124 | 1:00
| Srimongal | 138 | 17:00 | 134 | 4:00 | Pabna | 135 | 18:00 | 130 | 11:00
| Shahjibazar | 136 | 18:30 | 129 | 4:00 | Shahjadpur | 138 | 18:00 | 134 | 11:00
| Fenchuganj | 138 | 7:00 | 135 | 1:00 | Serajganj | 134 | 17:00 | 128 | 15:00
| Khulawara | 136 | 8:00 | 134 | 23:00 | Niyamatpur | 127 | 11:00 | 118 | 1:00
| Sylhet | 134 | 18:00 | 132 | 19:30 | Joypurhat | 131 | 19:30 | 120 | 1:00
| Chatak | 134 | 4:00 | 130 | 23:00 | Sherpur(Bogura) | 134 | 19:00 | 128 | 2:00
| Sunamganj | 133 | 7:00 | 128 | 22:00 | Mohastangor | 133 | 19:00 | 127 | 1:00
| Biani Bazar | 134 | 8:00 | 130 | 23:00 | Bangura | 136 | 19:00 | 131 | 13:00
| Comilla(s) | 130 | 6:00 | 124 | 14:00 | Rangpur | 130 | 18:30 | 121 | 10:00
| Comilla(n) | 138 | 13:00 | 134 | 23:00 | Lalmonirhat | 131 | 18:30 | 122 | 10:00
| Chandpur | 140 | 13:00 | 131 | 6:00 | Saidpur | 129 | 18:30 | 121 | 19:30
| Feni | 138 | 13:00 | 128 | 6:00 | Purbasadipur | 128 | 19:00 | 119 | 10:00
| Chowmuhani | 135 | 14:00 | 128 | 0:00 | Thakurgaon | 129 | 19:00 | 117 | 1:00
| Ashuganj | 140 | 18:00 | 130 | 4:00 | Palashbari | 131 | 8:30 | 125 | 21:00
| Daudkandi | 132 | 19:00 | 126 | 23:00 | Barapukuria | 135 | 19:00 | 129 | 10:00
| B.Baria | 136 | 18:00 | 129 | 4:00 | Panchagar | 129 | 21:00 | 117 | 10:00
| Ramganj | 138 | 13:00 | 128 | 23:00 | Joldhaka | 129 | 0.77083 | 119 | 0.125
| Chaddagram | 137 | 12:00 | 131 | 0:00 | Kurigram | 129 | 0.77083 | 121 | 0.625
| PHP | 137 | 12:00 | 129 | 0:00 | Mithapukur | 132 | 19:00 | 124 | 10:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-06-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 150 | 6843 | 3256 | 10099 |  |  |  | QF-LDC-11
0:30 | 97 | 7064.5 | 3438 | 10502.5 | Date: | 2021-06-06
1:00 | 44 | 7286 | 3620 | 10906
1:30 | 49 | 7120 | 3543.5 | 10663.5
2:00 | 54 | 6954 | 3467 | 10421
2:30 | 58 | 6892.5 | 3380.5 | 10273 | [5 empty] | Gen. at Eve. Peak | 10227 | 10227 MW (21:00 )
3:00 | 62 | 6831 | 3294 | 10125 | [6 empty] | 21:00
3:30 | 57 | 6546.5 | 3265.5 | 9812 | [5 empty] | Gen. at Day Peak | 10141 | 10141 MW (12:00 )
4:00 | 52 | 6262 | 3237 | 9499 | [6 empty] | 12:00
4:30 | 50.5 | 6205 | 3205.5 | 9410.5 | [5 empty] | Highest Generation | 10906
5:00 | 49 | 6148 | 3174 | 9322 | [6 empty] | 1:00
5:30 | 69 | 5982 | 3092.5 | 9074.5
6:00 | 89 | 5816 | 3011 | 8827
6:30 | 75 | 5756 | 2986.5 | 8742.5
7:00 | 61 | 5696 | 2962 | 8658
7:30 | 75.5 | 5862.5 | 2971 | 8833.5
8:00 | 90 | 6029 | 2980 | 9009
8:30 | 86 | 6166.5 | 2978.5 | 9145
9:00 | 82 | 6304 | 2977 | 9281
9:30 | 86 | 6446 | 3013 | 9459
10:00 | 90 | 6588 | 3049 | 9637
10:30 | 155 | 6420.5 | 3127.5 | 9548
11:00 | 220 | 6253 | 3206 | 9459
11:30 | 200 | 6521.5 | 3278.5 | 9800
12:00 | 180 | 6790 | 3351 | 10141
12:30 | 110.5 | 7063.5 | 3409.5 | 10473
13:00 | 41 | 7337 | 3468 | 10805
13:30 | 23 | 7209 | 3406.5 | 10615.5
14:00 | 5 | 7081 | 3345 | 10426
14:30 | 44.5 | 6895 | 3208 | 10103
15:00 | 84 | 6709 | 3071 | 9780
15:30 | 238 | 6488.5 | 2920 | 9408.5
16:00 | 392 | 6268 | 2769 | 9037
16:30 | 317 | 6214 | 2578.5 | 8792.5
17:00 | 242 | 6160 | 2388 | 8548
17:30 | 231 | 6137 | 2383 | 8520
18:00 | 220 | 6114 | 2378 | 8492
18:30 | 250 | 6321.5 | 2613 | 8934.5
19:00 | 280 | 6529 | 2848 | 9377
19:30 | 254 | 6971 | 3061 | 10032
20:00 | 166 | 6951 | 3001 | 9952 |  |  |  | Executive Engineer
20:30 | 203 | 6984.5 | 3105 | 10089.5 |  |  |  | Network Operation Division
21:00 | 240 | 7018 | 3209 | 10227
21:30 | 246 | 6943 | 3272.5 | 10215.5
22:00 | 252 | 6868 | 3336 | 10204 |  |  |  |  | Page 6 of 7
22:30 | 251 | 6846 | 3308 | 10154
23:00 | 250 | 6824 | 3280 | 10104
23:30 | 200 | 6833.5 | 3268 | 10101.5
24:00 | 150 | 6843 | 3256 | 10099
10227 MW (21:00 )
10141 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-06 |  | Energy | 247104922
[11 empty] | 2021-06-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4807 | 914 | 1942 | 1488 | 550 | 20 | 271 | 0 | 112 | 0
0:30 | 4771.5 | 916 | 1986.5 | 1845.5 | 575 | 20 | 274.5 | 0 | 116 | 0 | Date: | 2021-06-06
1:00 | 4736 | 918 | 2031 | 2203 | 600 | 20 | 278 | 0 | 120 | 0
1:30 | 4739 | 918 | 2028 | 2015 | 600 | 20 | 225.5 | 0 | 118 | 0 | [7 empty] | Total Energy | 247.1049 | Total Energy Gen 247.105 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 247.105 MKWHr
2:00 | 4742 | 918 | 2025 | 1827 | 600 | 20 | 173 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4742.5 | 918 | 1994.5 | 1724 | 585 | 20 | 173 | 0 | 116 | 0 | [7 empty] | Energy Requirement | 247.1049
3:00 | 4743 | 918 | 1964 | 1621 | 570 | 20 | 173 | 0 | 116 | 0
3:30 | 4645.5 | 918 | 1971 | 1414 | 570 | 20 | 160.5 | 0 | 113 | 0 | [6 empty] | Shortage
4:00 | 4548 | 918 | 1978 | 1207 | 570 | 20 | 148 | 0 | 110 | 0
4:30 | 4564.5 | 917.5 | 1923.5 | 1199.5 | 549.5 | 20 | 131 | 0 | 105 | 0
5:00 | 4581 | 917 | 1869 | 1192 | 529 | 20 | 114 | 0 | 100 | 0
5:30 | 4533 | 917.5 | 1820 | 1076 | 514.5 | 20 | 97 | 0 | 94 | 2.5
6:00 | 4485 | 918 | 1771 | 960 | 500 | 20 | 80 | 0 | 88 | 5
6:30 | 4456 | 918 | 1727.5 | 964 | 500 | 20 | 75.5 | 0 | 71 | 10.5 |  |  |  |  | Coal
7:00 | 4427 | 918 | 1684 | 968 | 500 | 20 | 71 | 0 | 54 | 16
7:30 | 4445 | 917.5 | 1734 | 1070.5 | 515 | 20 | 50 | 0 | 57 | 24.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4463 | 917 | 1784 | 1173 | 530 | 20 | 29 | 0 | 60 | 33
8:30 | 4484.5 | 917 | 1757.5 | 1283.5 | 540 | 20 | 24.5 | 0 | 68 | 50
9:00 | 4506 | 917 | 1731 | 1394 | 550 | 20 | 20 | 0 | 76 | 67
9:30 | 4521 | 917.5 | 1806 | 1468.5 | 555 | 20 | 28 | 0 | 81 | 62
10:00 | 4536 | 918 | 1881 | 1543 | 560 | 20 | 36 | 0 | 86 | 57
10:30 | 4387.5 | 918 | 1839.5 | 1586.5 | 580 | 20 | 61 | 0 | 93 | 62.5
11:00 | 4239 | 918 | 1798 | 1630 | 600 | 20 | 86 | 0 | 100 | 68
11:30 | 4238 | 917.5 | 1774 | 1958 | 600 | 20 | 120 | 0 | 102 | 70.5
12:00 | 4237 | 917 | 1750 | 2286 | 600 | 20 | 154 | 0 | 104 | 73
12:30 | 4327 | 917 | 1745.5 | 2504 | 595 | 20 | 201.5 | 0 | 97 | 66
13:00 | 4417 | 917 | 1741 | 2722 | 590 | 20 | 249 | 0 | 90 | 59
13:30 | 4417 | 917 | 1741 | 2722 | 590 | 20 | 249 | 0 | 90 | 59
14:00 | 4417 | 917 | 1741 | 2722 | 590 | 20 | 249 | 0 | 90 | 59
14:30 | 4449.5 | 917 | 1685.5 | 2311.5 | 545 | 20 | 224 | 0 | 92 | 48
15:00 | 4482 | 917 | 1630 | 1901 | 500 | 20 | 199 | 0 | 94 | 37
15:30 | 4476.5 | 917 | 1618 | 1570 | 495 | 20 | 182 | 0 | 96 | 34
16:00 | 4471 | 917 | 1606 | 1239 | 490 | 20 | 165 | 0 | 98 | 31
16:30 | 4386.5 | 917 | 1562 | 1199 | 460 | 20 | 135.5 | 0 | 95 | 17.5
17:00 | 4302 | 917 | 1518 | 1159 | 430 | 20 | 106 | 0 | 92 | 4
17:30 | 4259 | 915.5 | 1525 | 1163 | 430 | 20 | 108 | 0 | 97 | 2.5
18:00 | 4216 | 914 | 1532 | 1167 | 430 | 20 | 110 | 0 | 102 | 1
18:30 | 4202.5 | 914.5 | 1574.5 | 1420.5 | 430 | 20 | 265 | 0 | 107 | 0.5
19:00 | 4189 | 915 | 1617 | 1674 | 430 | 20 | 420 | 0 | 112 | 0
19:30 | 4427 | 914 | 1598 | 1991 | 491 | 20 | 477 | 0 | 114 | 0
20:00 | 4461 | 913 | 1661 | 1887 | 480 | 20 | 420 | 0 | 110 | 0
20:30 | 4556 | 913.5 | 1744.5 | 1875.5 | 480 | 20 | 390 | 0 | 110 | 0
21:00 | 4651 | 914 | 1828 | 1864 | 480 | 20 | 360 | 0 | 110 | 0
21:30 | 4727.5 | 914.5 | 1842.5 | 1785 | 485 | 20 | 332 | 0 | 109 | 0
22:00 | 4804 | 915 | 1857 | 1706 | 490 | 20 | 304 | 0 | 108 | 0
22:30 | 4827 | 914.5 | 1878.5 | 1597 | 519.5 | 20 | 287.5 | 0 | 110 | 0
23:00 | 4850 | 914 | 1900 | 1488 | 549 | 20 | 271 | 0 | 112 | 0
23:30 | 4828.5 | 914 | 1921 | 1488 | 549.5 | 20 | 271 | 0 | 112 | 0 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 4807 | 914 | 1942 | 1488 | 550 | 20 | 271 | 0 | 112 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 247.105 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 247.105 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 488000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 3 | 17 |  | 7 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 363749
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 6 | 8 | 19 | 5 |  | 1 |  |  |  |  | 1 | 0 | [8 empty] | 34020
6 | Sikalbaha 225MW CCPP (Gas) | 197 | 198 | 198 | 196 | 197 | 196 | 209 | 198 | 198 | 196 | 0 | 71 | 82 | 84 | 80 | 83 | 81 | 140 |  | 195 | 195 | 196 | 196 | 197 | 212 | 199 | 3789174
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 115 | 115 | 115 | 0 |  |  | 70 | 120 | 120 | 120 | 120 |  | 90 | 90 | 120 | 120 | 120 | 110 | 110 | 2328371
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 85 | 85 | 51 | 51 | 51 | 6 | [11 empty] | 85 | 85 | 85 | 68 | 68 | 68 | 68 | 913076
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 68 | 68 | 68 | 68 | 80 |  | 55 | 105 | 105 | 105 | 17 | 17 | 17 |  | 46 | 105 | 105 | 105 | 105 | 105 | 105 | 2054945
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 25 |  |  |  |  | 57344
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 334 | 335 | 333 | 332 | 335 | 335 | 332 | 336 | 336 | 334 | 270 | 272 | 270 | 270 | 270 | 270 | 270 | 270 |  | 250 | 250 | 250 | 270 | 270 | 270 | 270 | 7163667
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 3 | 38 | 110 | 145 | 95 | 45 | 45 | 52 |  | 102 | 45 | 45 | 15 |  |  |  | 878181
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 24 | [7 empty] | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 167272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 170 | 170 | 170 | 170 | 170 | 170 | 160 |  | 170 | 185 | 185 | 185 | 185 | 185 | 185 | 4252500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 125 | 125 | 135 | 135 | 135 | 135 | 135 | 115 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2651860
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 |  | 16 | 0 | 16 | 0 | 20 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 501624
33 | Ashuganj 225 MW CCPP | 183 | 183 | 184 | [5 empty] | 30 | 38 | 56 | 98 | 194 | 184 | 186 | 202 | 184 | 184 |  | 186 | 221 | 221 | 221 | 219 | 217 | 218 | 3218000
34 | Ashuganj 450 MW CCPP(South) | 300 | 300 | 300 | 300 | 300 | 300 | 320 | 300 | 300 | 290 | 340 | 300 | 300 | 295 | 280 | 320 | 280 | 270 |  | 265 | 265 | 265 | 295 | 290 | 330 | 320 | 7252000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 280 | 260 | 260 | 270 | 335 | 270 | 270 | 270 | 270 | 270 | 270 | 260 |  | 260 | 260 | 260 | 275 | 280 | 320 | 300 | 6860000
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 56 | 0 | 0 | 20 | 12 | 30 | 30 | 40 | 45 | 49 | 48 | 49 | 49 | 51 | 52 | 54 |  | 54 | 54 | 54 | 53 | 54 | 54 | 55 | 1052640
36 | Chandpur 150 MW CCPP | 90 | 89 | 91 | 90 | 87 | 87 | 90 | 85 | 90 | 86 | 89 | 90 | 84 | 90 | 91 | 91 | 91 | 90 |  | 85 | 85 | 90 | 91 | 89 | 92 | 92 | 2111980
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 310 | 310 | 310 | 310 | 309 | 309 | 309 | 310 | 309 | 311 | 314 | 314 | 313 | 312 | 311 | 312 | 312 | 312 |  | 278 | 274 | 273 | 296 | 312 | 312 | 312 | 7535646
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6641000
41 | Haripur 360MW CCPP(HPL) | 243 | 244 | 263 | 263 | 283 | 293 | 274 | 253 | 250 | 205 | 195 | 181 | 171 | 168 | 168 | 169 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 172 | 191 | 5012000
42 | RPCL 210MW CCPP | 157 | 156 | 155 | 156 | 194 | 168 | 168 | 155 | 139 | 124 | 134 | 134 | 133 | 133 | 132 | 133 | 152 | 146 |  | 146 | 135 | 134 | 135 | 134 | 147 | 148 | 3406520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 4 | 9 | 20 | 18 | 31 | 33 | 22 | 19 | 14 | 17 | 2 | 1 | [8 empty] | 231820
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1007000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1003800
46 | Shajibazar 330 MW CCPP | 111 | 110 | 110 | 112 | 112 | 111 | 111 | 109 | 112 | 111 | 111 | 111 | 110 | 112 | 111 | 109 | 111 | 110 |  | 110 | 112 | 111 | 110 | 109 | 110 | 110 | 2473000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 63 | 63 | 63 | 62 | 63 | 62 | 62 | 61 | 62 | 62 | 62 | 61 | 61 | 62 | 40 |  | 63 | 62 | 62 | 62 | 62 | 62 | 62 | 1422928
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 83 | 83 | 20 | 20 | 20 | 40 | 40 | 80 | 80 | 80 | 83 | 83 | 83 | 83 | 83 | 83 |  | 83 | 80 | 80 | 83 | 83 | 83 | 83 | 1705920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 225 | 225 | 225 | 225 | 225 | 225 | 165 | 204 | 191 | 191 | 191 | 191 | 191 | 191 | 190 | 190 | 191 | 177 |  | 171 | 191 | 191 | 191 | 191 | 191 | 191 | 4740620
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 404000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 5 | 7 | 7 | 7 | 7 | 7 | 7 | 5 | 5 | 7 | 7 | 7 | 7 | 7 | 7 |  |  |  |  | 7 | 7 | 7 | 7 | 141300
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 8 |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 149376
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 11 | 11 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 1166400
56 | Shahjahanulla 25 MW PP | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 15 | 15 | 15 | 15 | 8 | 14 | 14 | 14 | 14 |  |  |  |  | 16 | 14 | 7 | 14 | 213576
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 295 | 295 | 295 | 280 | 280 | 280 | 280 | 270 | 300 | 280 | 300 | 280 | 275 | 285 | 270 | 290 | 290 |  | 270 | 270 | 280 | 290 | 275 | 290 | 310 | 7052000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 398 | 400 | 400 | 400 | 394 | 400 | 400 | 400 | 400 | 394 | 399 | 367 |  | 363 | 400 | 400 | 399 | 399 | 400 | 400 | 9457000
58 | Nababganj 55 MW PP (Southern power ) | [7 empty] | 17 | 55 | 55 | 55 | 50 | 54 |  |  |  | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 449918
59 | Tangail Palli Power Gen 22 MW | 24 | 22 | 24 | 24 | 24 | 24 | 25 | 22 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  |  | 12 | 24 | 24 | 24 | 24 | 24 | 24 | 550560
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 503712
61 | Narshingdi 22 MW PP (Doreen) | [9 empty] | 16 | 16 |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 235584
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 19 | 19 | 19 | [5 empty] | 19 |  |  |  | 20 | 332928
63 | Impoprt (Tripura) | 120 | 116 | 116 | 110 | 100 | 88 | 54 | 60 | 76 | 86 | 100 | 104 | 90 | 104 | 94 | 98 | 92 | 102 |  | 112 | 114 | 110 | 110 | 108 | 112 | 112 | 2402880
64 | Malancha, Ctg. EPZ (United) | 21 | 29 | 29 | 29 | 36 | 40 | 35 | 10 | 4 | 4 | 2 | 2 | 12 | 3 | 3 | 3 | 3 | 3 |  | 5 | 7 | 7 | 28 | 28 | 28 | 29 | 367680
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | [5 empty] | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 358020
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 8 | 8 | 8 |  | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 162180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 15 |  |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 708700
68 | Cumilla 25 MW PP (Summit) | 19 | 19 | 20 | 20 | 20 | 0 |  |  | 3 | 3 | 5 | 5 | 6 | 6 | 5 | 5 | 6 | 6 |  | 6 | 6 | 6 | 20 | 20 | 20 | 19 | 261580
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 26 | 26 | 26 | 28 | 28 | 28 | 28 | 28 | 30 | 29 | 18 |  | 18 | 18 | 20 | 27 | 29 | 29 | 29 | 635580
71 | Maona 33 MW PP(Summit) | 33 | 33 | 24 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 28 |  | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 672600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 835800
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 23 | 23 | 90 | 94 | 95 | 95 | 95 | 98 | 98 | 98 | 98 | 98 | 101 |  | 101 | 101 | 101 | 101 | 101 | 101 | 102 | 2152590
| Feni Lanka Power | 114 | 114 | 114 | 34 | 17 | 17 | 17 | 52 | 52 | 80 | 114 | 104 | 70 | 52 | 52 | 17 | 17 | 17 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1452360
| Chowmuhani 113 MW | 114 | 111 | 111 | 111 | 65 | 36 | 36 | 70 | 110 | 112 | 116 | 115 | 75 | 55 | 17 | 17 | 17 | 17 |  | 39 | 55 | 55 | 55 | 55 | 55 | 55 | 1796760
| Manikgonj 162MW PP(MPGL) | [10 empty] | 52 | 115 | 126 | 126 | 72 | 17 | 17 | 17 |  | 20 | 54 | 54 | 54 | 17 |  |  | 848160
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 24 |  |  |  | 4 | 45 | 50 | 70 | 100 | 100 | 100 | 100 | 70 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 1233600
78 | Gazipur 52 MW PP | 42 | 16 | 16 |  |  |  | 13 | 25 | 25 | 37 | 41 | 41 | 41 | 41 | 41 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 789600
79 | Kodda 150MW PP | 16 | [5 empty] | 16 | 16 | 16 | 32 | 82 | 150 | 150 | 98 | 98 | 64 | 64 | 64 |  | 64 | 98 | 98 | 82 | 64 | 32 | 32 | 1292640
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 245760
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 20 | 34 | 43 | 43 | 43 | 43 | 43 | 34 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1003550
| Gazipur 100 MW PP | 84 | 84 | 84 |  | 56 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 72 | 68 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1897200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | [9 empty] | 4561
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 10 | 36 | 49 | 54 | 35 | 35 | 35 |  | 45 | 54 | 54 | 54 | 54 | 54 | 54 | 1164091
| Karnaphuli Power Ltd. | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 51 |  | 7 | 70 | 100 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 863123
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 8 | [6 empty] | 13257
86 | Meghnaghat CCPP ( Summit) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 250 | 275 | 230 | 260 | 245 | 265 | 285 | 260 | 270 |  | 265 | 270 | 250 | 260 | 270 | 295 | 290 | 6045236
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 17 | 53 | 40 | 17 |  |  | 1 |  | 15 | 17 | 17 |  |  |  |  | 192960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 60 | 60 | 92 | 92 | 80 |  | 60 | 80 | 92 | 92 | 60 | 60 | 60 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1954440
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 22 | 51 | 43 | [9 empty] | 1 | 7 | 18 | 43 | 45 | 51 | 51 | 607810
94 | Gagnagar 102 MW PP (Digital Power) | [7 empty] | 2 | 16 | 16 | 16 | 24 | 92 | 102 | 64 | 32 | 32 | 32 |  | 48 | 64 | 32 | 16 | 16 |  |  | 633024
95 | Patenga 50MW PP (Baraka) | 19 | [10 empty] | 11 | 46 | 47 | 50 | 24 | 25 | 25 |  | 26 | 25 | 25 | 25 |  |  |  | 377760
96 | Chattogram 108 MW PP (ECPV) | [13 empty] | 5 | 5 | 3 | 2 | 6 |  | 6 | 6 | [5 empty] | 32640
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | [9 empty] | 10 | 40 | 30 | 15 | 15 | 15 | 15 |  | 42 | 55 | 55 | 40 | 30 | 15 | 15 | 420700
100 | Manikganj 55 MW PP (Northern) | [7 empty] | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 35 |  | 35 | 35 | 17 |  |  |  |  | 563370
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 100 | 130 | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 |  | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 3532173
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13400
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 54 | 35 | 35 | 17 | 17 | 40 | 53 | 35 | 35 | 54 | 54 | 54 | 54 | 35 | 35 | 35 |  | 53 | 53 | 53 | 53 | 54 | 54 | 54 | 1061640
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 100 | 80 | 35 | 35 | 35 | 8 | 8 | 26 | 40 | 40 | 40 | 58 | 70 | 70 | 30 | 8 | 8 | 8 |  | 8 | 100 | 86 | 120 | 120 | 100 | 100 | 1440000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 95 | 72 | 61 | 42 | 66 | 23 | 17 | 18 | 19 | 53 | 104 | 117 | 131 | 112 | 100 | 100 | 100 | 100 |  | 113 | 149 | 140 | 116 | 92 | 81 | 81 | 1994690
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 60 |  | 40 | 40 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 446400
116 | Chandpur 200MW (Desh energy) | 170 | 80 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 111 | 177 | 145 | 51 | 17 | 17 | 17 | 17 |  | 26 | 51 | 51 | 51 | 51 |  |  | 1413120
117 | Ashuganj 150MW PP (Midland) | 132 | 10 | [18 empty] | 26 | 21 | 50 | 20 |  |  | 607810
118 | Bibiyana-III 400 MW CCPP | 366 | 366 | 364 | 367 | 366 | 367 | 313 | 400 | 376 | 376 | 377 | 377 | 376 | 376 | 377 | 377 | 376 | 377 |  | 372 | 376 | 376 | 376 | 377 | 377 | 377 | 8948000
| Jamalpur 115 MW PP (United) | 107 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 65 | 65 | 65 |  | 90 | 115 | 115 | 115 | 115 | 115 | 115 | 2613600
| Anwara 300 MW PP (United) | [26 empty] | 0
| Juldah unit-2 (Acorn) | 10 | 10 | [9 empty] | 40 | 40 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237120
| Anlima Energy Ltd. | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 25 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 421527
| Bhairob 54.5 MW | 35 | 35 | 35 | 25 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 740880
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 4 | 11 | 24 | 29 | 30 | 33 | 32 | 29 | 21 | 10 | 0 | [9 empty] | 217369
120 | Eastern Zone Total | 7286 | 6954 | 6831 | 6262 | 6148 | 5816 | 5696 | 6029 | 6304 | 6588 | 6253 | 6790 | 7337 | 7081 | 6709 | 6268 | 6160 | 6114 |  | 6529 | 6971 | 6951 | 7018 | 6868 | 6824 | 6843 | 160652952
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 7 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | [9 empty] | 61440
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 70 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 70 | 80 | 88 | 90 | 90 | 35 | 17 | [6 empty] | 15 | 35 | 35 | 1182240
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 225 | 225 | 226 | 225 | 216 | 211 | 223 | 221 | 130 | 148 | 149 | 148 | 147 | 150 | 110 | 95 | 90 | 90 |  | 90 | 90 | 90 | 133 | 133 | 133 | 133 | 3801273
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 13 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 10 | 10 | 12 | 11 | 11 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 294116
| Bhola 225 MW CCPP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 63 | 63 | 64 | 63 | 64 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1401000
140 | Bhola 33 MW PP (Venture) | 30 | 29 | 28 | 26 | 27 | 24 | 21 | 20 | 19 | 22 | 20 | 13 | 16 | 12 | 1 | 5 | 9 | 9 |  | 21 | 22 | 24 | 23 | 23 | 24 | 23 | 454451
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 80 | 40 | 40 | [8 empty] | 68 | 30 | [11 empty] | 579840
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 918 | 918 | 918 | 917 | 918 | 918 | 917 | 917 | 918 | 918 | 917 | 917 | 918 | 917 | 917 | 917 | 914 |  | 915 | 914 | 913 | 914 | 915 | 914 | 914 | 22134545
147 | Bheramara 410 MW CCPP | 305 | 305 | 310 | 315 | 315 | 320 | 320 | 320 | 320 | 315 | 310 | 305 | 300 | 295 | 290 | 290 | 230 | 230 |  | 230 | 365 | 340 | 340 | 355 | 340 | 320 | 7549920
148 | Payra 1320 MW | 450 | 450 | 420 | 420 | 380 | 350 | 350 | 380 | 400 | 410 | 450 | 450 | 440 | 440 | 350 | 340 | 280 | 280 |  | 280 | 340 | 330 | 330 | 340 | 400 | 400 | 10276200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 151 | 150 | 150 | 150 | 149 | 150 | 3666900
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | [11 empty] | 50 | 50 | 50 | 50 | 8 | 8 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 546816
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 1 | 1 | 2 | 3 | 3 | 1 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 18540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 120 | 119 | 120 | 120 | 120 | 100 | 100 | 119 | 125 | 121 | 80 | 106 | 115 | 109 | 108 | 105 | 60 | 60 |  | 60 | 60 | 60 | 108 | 144 | 144 | 144 | 2727600
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 175 | 183 | 188 | 189 | 187 | 187 | 187 | 183 | 181 | 175 | 168 | 157 | 157 | 156 | 151 | 146 | 134 | 130 |  | 130 | 130 | 130 | 138 | 186 | 160 | 160 | 4210355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 190 | 140 | 140 | 140 |  | 140 | 140 | 140 | 168 | 210 | 206 | 201 | 4718573
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 390 | 400 | 319 | 394 | 383 | 380 | 347 | 310 | 352 | 384 | 402 | 354 | 355 | 296 | 334 | 333 | 236 | 237 |  | 334 | 292 | 299 | 359 | 400 | 420 | 421 | 8495364
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 7 |  | 31 | 34 | [5 empty] | 36916
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 21 | 21 | 17 | 17 | 18 | 19 | 18 | 18 | 5 | 5 |  | 5 | 22 | 22 | 22 | 22 | 21 | 21 | 432000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  |  |  |  | 5 | 11 | 11 | 11 | 11 | 8 | 8 | 179154
165 | Amnura 50 MW PP(Sinha) | [10 empty] | 25 | 34 | 34 | 34 | 12 |  |  |  |  | 12 | 12 | 12 |  |  |  |  | 161320
166 | Katakhali 50 MW PP (Northern) | [17 empty] | 8 |  | 8 | [6 empty] | 9656
167 | Katakhali 50 MW Peaking PP | [19 empty] | 31 | 38 | 40 | 38 |  |  |  | 89724
168 | Santahar 50 MW Peaking PP | 34 | 34 | 34 | 34 | 34 | [14 empty] | 21 | 34 | 34 | 34 | 34 | 33 | 33 | 362084
169 | Natore 52 MW PP (Rajlanka) | 52 | 43 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 |  | 2 |  | 8 | 8 | 8 | 43 | 43 | 43 | 43 | 604320
170 | Chapainawabganj 100 MW Peaking PP | 88 | 49 | 49 | 24 | 24 | 24 | [6 empty] | 45 | 47 | 48 | 48 | 31 | 31 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1008560
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 35 | 35 | 35 | 35 |  |  | 13 | 35 | 38 | 71 | 101 | 113 | 70 | 35 |  |  |  |  | 32 | 35 | 35 | 35 | 35 | 35 | 35 | 986688
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [9 empty] | 35 | 100 | 113 | 70 | 35 |  |  |  |  | 25 | 35 | 35 | 35 | 35 |  |  | 607680
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 35 | 35 | [6 empty] | 6 | 34 | 111 | 113 | 70 | 45 |  |  |  |  | 105 | 113 | 113 | 113 | 70 |  |  | 9834720
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 2 | 2 | 1 | 2 | 3 |  | 2 | 1 | 0 | [8 empty] | 19975
178
178