## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-09 | Wednesday
|  |  | Date (day): | 2021-06-09 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14465.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15482 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-08 | 2021-06-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 95 | 97 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint.
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 222 | 201 | 260 | 260 | 100 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 260 | 280 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 51 | 87 | 87 |  | 13 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 21 | 20 | 21
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 90 | 182 | 150 | 200 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 332 | 335 | 300 | 320
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 40 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 53 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 98 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 35 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 50 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 55 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 42 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 228 | 245 | 245 |  | 55 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 80 | 132 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 86 | 85 | 85 | 85 |  | 20 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 91 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 78 | 126 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2287 | 2941 | 3445 | 3756 | 1031 | 1078
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 20 | 20 | 20 | 20 | 210 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 199 | 196 | 220 | 220 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 13 | 85 | 85 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 30 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 6 | 18 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 6 | 6 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 82 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 0 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 838 | 1005 | 1660 | 1650 | 572 | 123
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 100 | 135 | 110 | 135
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Machine problem.
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 187 | 219 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 265 | 280 | 320 | 340 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 275 | 320 | 350 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 56 | 56 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 26 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 28 | 50 | 143 | 143 |  | 7 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 88 | 127 | 135 | 140 |  | 23
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 162 | 179 | 185 | 185 |  | 15 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 124 | 152 | 180
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 34 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 11 | 20 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 99 | 100 | 100 | 100
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 111 | 120 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 10 | 17 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1659 | 1952 | 2220 | 2479 | 438 | 96
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 148 | 148 | 154 | 154 | 48 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 20 | 20 | 20 |  | 2
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 182 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 26 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 14 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 329 | 497 | 570.6 | 519 | 48 | 89
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 42 | 42 | 42 |  | 28 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 163 | 162 | 162 | 162 |  | 168 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 62 | 61 | 61
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 83 | 80 | 83
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 226 | 225 | 226
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 15 | 15 |  | 10 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 295 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 376 | 376 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 7 | 8 | 8 | 8 |  | 3
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1898 | 1954 | 2019 | 2023 | 0 | 357
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 814 | 905 | 927 | 927
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 80 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 300 | 340 | 360 | 50 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 5 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1149 | 1510 | 1602 | 1892 | 50 | 83
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 28 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 64 | 65 | 65 |  | 129 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 32 | 31 | 12 | 12 | 83 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 510 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 55 | 201 | 228 | 233 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 519 | 834 | 1070 | 1185 | 83 | 129
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 43 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 46 | 51 | 51 |  | 20 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 100 | 106 | 100 | 100 | 110 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 159 | 132 | 155 | 155 | 65 |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 190 | 186 | 185 | 185 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 365 | 400 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 34 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 24 | 85 | 50 | 90
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 59 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1050 | 1455 | 1608 | 1695 | 346 | 67
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 187 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 9916 | 12411 | 14465.6 | 15482 | 2692 | 2212
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9399.8662 | 11765 | 13712.6568 | 14676.1526
| A. |  | 2021-06-08 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12411 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8374 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12411 | MW
| 3 | Day peak Generation : |  |  | 9916 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11765 | MW
| 4 | Evening peak Generation : |  |  | 12411 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 248.5442 | MKWHr | By Solar | 0.52443 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 153.4277 | MKWHr |  | By Oil: | 57.75 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.2838 | MKWHr |  | By Hydro: | 0.484 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2692 | MW | Dhaka | 4082 | 4082 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2212 | MW | Chittagong | 1248 | 1248 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4904 | MW | Khulna | 1531 | 1531 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1238.47 | MMCFD |  |  | Rajshahi | 1339 | 1339 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 164382086.42 | ii) Oil : | Taka | 445899428.91 | Comilla | 1050 | 1050 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 66483407 | Total | Taka | 676764922.33 | Mymensingh | 987 | 987 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.5565 | MKWHr. | Sylhet | 480 | 480 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -98 | MW (E to W) at | 21:00 | hrs | Barisal | 316 | 316 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -102 | MW at | 5:00 | hrs | Rangpur | 732 | 732 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.1° C |  |  | Total | 11765 | 11765 |  | 0
| B. |  | 2021-06-09 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 31.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15482 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2482 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 260.3396 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9143 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.344 | MKWHr. | ii) HVDC Flow at Peak Time |  | 905 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7302 | MKWHr. | iii) Maximum HVDC Flow : |  | 918 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.11 |  | (b) Today: | 73.42 |  | (c) Rule Curve: |  | 78.08
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 332 | 233 |  | 0 | 290 | 250 | 0 | 0 | 0 | 270 | 0 | 0 | 90 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 20 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 120 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 0 | 30 | 0 | 100 | 0 | 275 | 260 | 219 | 8 | 87 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 128 | 156 | 8 | 17 | 0 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 83 | 0 | 218 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 74 | 0 | 20 | 144 | 120 | 376 | 115 | 86 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 0 | 400 | 0 | 0 | 10 | 17 | 0 | 35 | 0 |  | 918 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 164 | 0 | 12 | 0 | 189 | 0 | 397 | 17 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 440 | 153 | 0 | 0 | 0 |  | 7214 | 3198 | 10412 | 4718 | 918 | 1924 | 1967 | 590 | 20 | 147 | 128 | 0 | 0 | 73.01
2:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 332 | 266 |  | 0 | 290 | 260 | 0 | 0 | 0 | 270 | 0 | 0 | 100 | 7 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 21 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 208 | 0 | 120 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 0 | 22 | 0 | 100 | 0 | 290 | 280 | 217 | 8 | 88 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 128 | 155 | 8 | 17 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 62 | 83 | 0 | 218 | 18 | 0 | 7 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 35 | 0 | 0 | 120 | 80 | 376 | 115 | 86 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 727 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 107 | 0 | 161 | 0 | 12 | 0 | 189 | 0 | 417 | 0 | 0 | 35 | 0 | 50 | 0 | 0 | 0 | 440 | 153 | 0 | 0 | 0 |  | 7157 | 2947 | 10104 | 4757 | 727 | 2003 | 1748 | 590 | 20 | 131 | 128 | 0 | 0 | 73.03
3:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 332 | 293 |  | 0 | 290 | 260 | 0 | 0 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 120 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 0 | 22 | 0 | 100 | 0 | 300 | 290 | 217 | 8 | 88 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 122 | 156 | 8 | 17 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 62 | 83 | 0 | 218 | 18 | 0 | 7 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 30 | 0 | 0 | 50 | 10 | 376 | 115 | 86 | 105 | 0 | 0 | 54 | 110 | 100 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 726 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 107 | 0 | 160 | 0 | 12 | 0 | 189 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 154 | 0 | 0 | 0 |  | 7006 | 2814 | 9820 | 4771 | 726 | 2033 | 1492 | 580 | 20 | 76 | 122 | 0 | 0 | 73.05
4:00 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 332 | 302 |  | 0 | 290 | 290 | 0 | 0 | 0 | 270 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 21 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 211 | 0 | 120 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 0 | 22 | 0 | 100 | 0 | 270 | 260 | 216 | 8 | 87 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 124 | 156 | 8 | 17 | 0 | 42 | 42 | 47 | 0 | 163 | 161 | 62 | 83 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 0 | 0 | 17 | 0 | 375 | 115 | 86 | 105 | 0 | 0 | 54 | 85 | 70 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 35 | 0 |  | 726 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 160 | 0 | 12 | 0 | 193 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 154 | 0 | 0 | 0 |  | 6882 | 2716 | 9598 | 4719 | 726 | 1974 | 1409 | 550 | 20 | 76 | 124 | 0 | 0 | 73.07
5:00 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 300 |  | 0 | 290 | 265 | 0 | 0 | 0 | 270 | 0 | 0 | 100 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 10 | 21 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 0 | 24 | 0 | 135 | 0 | 285 | 270 | 184 | 8 | 87 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 112 | 158 | 8 | 17 | 0 | 42 | 42 | 47 | 0 | 130 | 160 | 62 | 83 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 41 | 0 | 28 | 0 | 0 | 42 | 8 | 376 | 115 | 86 | 105 | 0 | 0 | 54 | 102 | 100 | 110 | 0 | 370 | 17 | 0 | 0 | 0 | 0 | 35 | 0 |  | 624 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 107 | 0 | 160 | 0 | 12 | 0 | 194 | 0 | 324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 390 | 154 | 0 | 0 | 0 |  | 6638 | 2585 | 9223 | 4380 | 624 | 1915 | 1540 | 540 | 20 | 92 | 112 | 0 | 0 | 73.09
6:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 309 |  | 0 | 290 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 21 | 25 | 21 | 33 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 120 | 0 |  | 24 | 0 | 34 | 100 | 0 | 0 | 0 | 24 | 0 | 100 | 0 | 275 | 265 | 184 | 8 | 86 | 26 | 55 | 0 | 10 | 0 | 0 | 34 | 14 | 11 | 33 | 21 | 108 | 156 | 8 | 17 | 0 | 42 | 42 | 11 | 0 | 110 | 160 | 40 | 20 | 0 | 218 | 18 | 0 | 7 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 50 | 1 | 0 | 68 | 50 | 375 | 85 | 70 | 85 | 0 | 0 | 54 | 85 | 52 | 65 | 0 | 350 | 35 | 4 | 0 | 0 | 0 | 35 | 0 |  | 624 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 157 | 0 | 12 | 0 | 150 | 0 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 122 | 0 | 0 | 0 |  | 6141 | 2399 | 8540 | 4196 | 624 | 1686 | 1316 | 510 | 20 | 75 | 108 | 5 | 0 | 73.11
7:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 281 |  | 0 | 290 | 260 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 21 | 25 | 21 | 0 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 198 | 0 | 120 | 0 |  | 5 | 0 | 34 | 100 | 0 | 0 | 0 | 20 | 0 | 100 | 0 | 260 | 265 | 183 | 8 | 88 | 26 | 56 | 0 | 10 | 0 | 0 | 34 | 14 | 11 | 33 | 16 | 94 | 156 | 0 | 17 | 0 | 42 | 42 | 11 | 0 | 110 | 164 | 40 | 20 | 0 | 218 | 18 | 0 | 7 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 33 | 5 | 0 | 68 | 50 | 376 | 85 | 70 | 85 | 1 | 0 | 54 | 85 | 52 | 65 | 0 | 350 | 17 | 6 | 0 | 0 | 0 | 35 | 1 |  | 624 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 12 | 0 | 150 | 0 | 302 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 360 | 121 | 0 | 0 | 0 |  | 5985 | 2389 | 8374 | 4149 | 624 | 1659 | 1229 | 510 | 20 | 75 | 94 | 14 | 0 | 73.13
8:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 260 |  | 0 | 290 | 280 | 0 | 0 | 0 | 250 | 0 | 0 | 30 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 21 | 25 | 21 | 33 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 208 | 0 | 120 | 0 |  | 4 | 0 | 0 | 100 | 0 | 0 | 0 | 7 | 0 | 100 | 0 | 280 | 290 | 196 | 8 | 88 | 23 | 55 | 0 | 10 | 0 | 0 | 34 | 14 | 8 | 33 | 16 | 104 | 154 | 8 | 0 | 1 | 42 | 42 | 11 | 0 | 110 | 163 | 40 | 20 | 0 | 218 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 9 | 0 | 68 | 20 | 375 | 85 | 70 | 85 | 0 | 0 | 54 | 51 | 52 | 65 | 0 | 350 | 17 | 4 | 0 | 0 | 0 | 35 | 12 |  | 624 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 130 | 0 | 12 | 0 | 150 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 110 | 0 | 0 | 0 |  | 5982 | 2411 | 8393 | 4227 | 624 | 1666 | 1184 | 500 | 20 | 41 | 104 | 27 | 0 | 73.14
9:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 248 |  | 0 | 290 | 280 | 0 | 0 | 0 | 331 | 0 | 0 | 42 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 21 | 25 | 21 | 0 | 33 | 16 | 0 | 0 | 20 | 100 | 0 | 17 | 203 | 0 | 120 | 0 |  | 5 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 0 | 100 | 0 | 300 | 305 | 205 | 8 | 89 | 23 | 55 | 0 | 10 | 0 | 0 | 34 | 0 | 8 | 18 | 16 | 96 | 154 | 8 | 17 | 1 | 42 | 42 | 11 | 0 | 110 | 163 | 61 | 20 | 0 | 218 | 18 | 0 | 7 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 12 | 0 | 68 | 20 | 375 | 85 | 70 | 85 | 2 | 0 | 54 | 51 | 52 | 65 | 0 | 394 | 17 | 22 | 0 | 0 | 0 | 35 | 10 |  | 813 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 148 | 0 | 0 | 70 | 0 | 148 | 0 | 12 | 0 | 173 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 350 | 110 | 0 | 0 | 0 |  | 6131 | 2650 | 8781 | 4414 | 813 | 1662 | 1189 | 498 | 20 | 41 | 96 | 48 | 0 | 73.15
10:00 | 0 | 0 | 0 | 185 | 0 | 92 | 0 | 0 | 226 |  | 0 | 290 | 230 | 0 | 0 | 0 | 336 | 0 | 0 | 100 | 0 | 64 | 0 | 0 | 0 | 0 | 53 | 0 | 37 | 0 | 25 | 22 | 33 | 33 | 24 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 7 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 0 | 100 | 0 | 260 | 270 | 184 | 8 | 84 | 23 | 54 | 0 | 23 | 0 | 0 | 25 | 0 | 8 | 33 | 12 | 96 | 157 | 8 | 17 | 2 | 42 | 42 | 44 | 0 | 163 | 163 | 62 | 74 | 0 | 218 | 18 | 0 | 7 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 6 | 30 | 87 | 20 | 376 | 96 | 80 | 89 | 2 | 0 | 54 | 51 | 99 | 104 | 0 | 400 | 17 | 9 | 9 | 0 | 0 | 32 | 12 |  | 813 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 105 | 0 | 160 | 0 | 26 | 0 | 190 | 0 | 376 | 0 | 0 | 13 | 0 | 0 | 0 | 1 | 15 | 370 | 112 | 0 | 0 | 1 |  | 6411 | 2850 | 9261 | 4409 | 813 | 1817 | 1465 | 520 | 20 | 88 | 96 | 33 | 0 | 73.16
11:00 | 0 | 0 | 0 | 185 | 0 | 94 | 0 | 0 | 227 |  | 0 | 290 | 265 | 0 | 0 | 0 | 333 | 0 | 0 | 100 | 16 | 64 | 0 | 0 | 0 | 0 | 53 | 0 | 55 | 0 | 25 | 22 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 3 | 0 | 100 | 0 | 260 | 270 | 187 | 8 | 88 | 23 | 54 | 0 | 51 | 0 | 0 | 34 | 16 | 8 | 33 | 11 | 102 | 150 | 8 | 17 | 1 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 77 | 0 | 218 | 18 | 0 | 7 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 10 | 30 | 160 | 20 | 375 | 115 | 86 | 105 | 2 | 0 | 54 | 51 | 99 | 112 | 0 | 400 | 17 | 32 | 54 | 0 | 0 | 35 | 20 |  | 813 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 25 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 127 | 0 | 160 | 0 | 31 | 0 | 190 | 0 | 365 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 380 | 110 | 0 | 0 | 1 |  | 6729 | 2941 | 9670 | 4442 | 813 | 1805 | 1778 | 530 | 20 | 113 | 102 | 67 | 0 | 73.17
12:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 222 |  | 0 | 300 | 280 | 0 | 0 | 0 | 332 | 0 | 90 | 100 | 24 | 98 | 0 | 0 | 0 | 0 | 53 | 0 | 55 | 15 | 25 | 22 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 199 | 0 | 120 | 0 |  | 14 | 0 | 13 | 80 | 0 | 0 | 0 | 6 | 0 | 100 | 0 | 265 | 270 | 187 | 8 | 88 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 16 | 5 | 33 | 11 | 102 | 148 | 8 | 17 | 1 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 77 | 0 | 218 | 18 | 0 | 7 | 300 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 30 | 162 | 28 | 376 | 115 | 86 | 105 | 2 | 0 | 54 | 82 | 99 | 111 | 0 | 400 | 17 | 26 | 78 | 0 | 0 | 10 | 22 |  | 814 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 43 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 159 | 0 | 32 | 0 | 190 | 0 | 365 | 5 | 0 | 59 | 0 | 34 | 0 | 3 | 35 | 350 | 55 | 0 | 0 | 3 |  | 7011 | 2905 | 9916 | 4503 | 814 | 1792 | 1940 | 500 | 20 | 178 | 102 | 67 | 0 | 73.18
13:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 206 |  | 0 | 300 | 230 | 0 | 0 | 25 | 334 | 0 | 88 | 100 | 64 | 133 | 0 | 0 | 0 | 0 | 53 | 17 | 55 | 19 | 25 | 22 | 33 | 33 | 33 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 51 | 80 | 0 | 2 | 0 | 10 | 0 | 135 | 0 | 260 | 265 | 182 | 26 | 85 | 23 | 56 | 0 | 43 | 0 | 0 | 34 | 19 | 5 | 33 | 15 | 108 | 136 | 8 | 17 | 1 | 42 | 42 | 47 | 0 | 163 | 163 | 62 | 77 | 0 | 218 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 23 | 0 | 0 | 24 | 0 | 80 | 8 | 30 | 160 | 50 | 375 | 115 | 86 | 105 | 1 | 0 | 54 | 110 | 100 | 115 | 0 | 183 | 24 | 13 | 122 | 0 | 0 | 17 | 28 |  | 813 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 108 | 0 | 143 | 0 | 32 | 0 | 190 | 0 | 364 | 53 | 0 | 106 | 0 | 92 | 0 | 3 | 100 | 370 | 83 | 0 | 0 | 4 |  | 7098 | 3153 | 10251 | 4284 | 813 | 1839 | 2351 | 520 | 20 | 258 | 108 | 58 | 0 | 73.19
14:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 207 |  | 0 | 300 | 245 | 0 | 0 | 30 | 300 | 0 | 90 | 100 | 93 | 133 | 0 | 0 | 0 | 0 | 53 | 17 | 55 | 19 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 199 | 0 | 120 | 0 |  | 24 | 0 | 51 | 92 | 0 | 17 | 0 | 7 | 0 | 135 | 0 | 260 | 270 | 184 | 26 | 85 | 23 | 56 | 0 | 43 | 0 | 0 | 34 | 18 | 5 | 33 | 15 | 110 | 136 | 8 | 20 | 2 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 83 | 0 | 204 | 18 | 0 | 7 | 260 | 16 | 5 | 0 | 95 | 0 | 101 | 24 | 0 | 30 | 7 | 30 | 120 | 50 | 376 | 115 | 86 | 105 | 2 | 0 | 54 | 110 | 100 | 116 | 0 | 200 | 70 | 27 | 126 | 0 | 0 | 17 | 30 |  | 813 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 113 | 0 | 133 | 0 | 32 | 0 | 190 | 0 | 284 | 70 | 0 | 70 | 0 | 54 | 0 | 3 | 50 | 360 | 96 | 0 | 0 | 3 |  | 7258 | 2964 | 10222 | 4260 | 813 | 1715 | 2463 | 509 | 20 | 258 | 110 | 74 | 0 | 73.2
15:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 207 |  | 0 | 300 | 280 | 0 | 0 | 30 | 300 | 0 | 155 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 19 | 25 | 20 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 199 | 0 | 120 | 0 |  | 24 | 0 | 51 | 92 | 0 | 18 | 0 | 4 | 0 | 135 | 0 | 290 | 280 | 193 | 26 | 88 | 23 | 52 | 0 | 43 | 0 | 0 | 34 | 18 | 5 | 33 | 15 | 114 | 134 | 8 | 20 | 1 | 42 | 42 | 50 | 0 | 163 | 163 | 62 | 83 | 0 | 225 | 18 | 0 | 7 | 310 | 16 | 5 | 0 | 95 | 0 | 102 | 24 | 0 | 33 | 9 | 30 | 120 | 50 | 376 | 115 | 72 | 105 | 3 | 0 | 54 | 110 | 100 | 121 | 0 | 200 | 70 | 18 | 126 | 0 | 0 | 17 | 23 |  | 813 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 113 | 0 | 132 | 0 | 32 | 0 | 190 | 0 | 338 | 70 | 0 | 83 | 0 | 56 | 0 | 3 | 90 | 360 | 142 | 0 | 0 | 2 |  | 7361 | 3112 | 10473 | 4390 | 813 | 1890 | 2402 | 510 | 20 | 275 | 114 | 59 | 0 | 73.21
16:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 206 |  | 0 | 300 | 270 | 0 | 0 | 30 | 300 | 0 | 155 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 21 | 33 | 25 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 18 | 0 | 6 | 0 | 135 | 0 | 280 | 265 | 184 | 26 | 88 | 23 | 52 | 0 | 43 | 0 | 0 | 34 | 19 | 5 | 33 | 15 | 110 | 148 | 8 | 20 | 1 | 42 | 42 | 50 | 0 | 163 | 164 | 61 | 83 | 0 | 225 | 18 | 0 | 7 | 300 | 16 | 5 | 0 | 95 | 0 | 102 | 24 | 0 | 77 | 3 | 30 | 120 | 50 | 376 | 115 | 85 | 105 | 3 | 0 | 54 | 110 | 100 | 120 | 0 | 230 | 70 | 5 | 126 | 0 | 0 | 17 | 15 |  | 812 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 111 | 0 | 132 | 0 | 32 | 0 | 186 | 0 | 300 | 70 | 0 | 113 | 0 | 56 | 0 | 3 | 113 | 360 | 144 | 0 | 0 | 1 |  | 7339 | 3124 | 10463 | 4366 | 812 | 1844 | 2491 | 510 | 20 | 279 | 110 | 31 | 0 | 73.22
17:00 | 0 | 0 | 0 | 185 | 0 | 64 | 0 | 0 | 207 |  | 0 | 300 | 250 | 0 | 0 | 15 | 300 | 0 | 120 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 21 | 33 | 25 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 44 | 92 | 0 | 18 | 0 | 8 | 0 | 135 | 0 | 280 | 265 | 184 | 26 | 88 | 26 | 52 | 0 | 43 | 0 | 0 | 34 | 19 | 8 | 33 | 15 | 106 | 152 | 8 | 20 | 0 | 42 | 42 | 11 | 0 | 130 | 162 | 61 | 83 | 0 | 226 | 18 | 0 | 7 | 290 | 16 | 5 | 0 | 95 | 0 | 103 | 24 | 0 | 80 | 3 | 30 | 85 | 50 | 375 | 115 | 85 | 105 | 1 | 0 | 54 | 110 | 52 | 120 | 0 | 310 | 23 | 6 | 115 | 0 | 0 | 17 | 7 |  | 813 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 66 | 16 | 0 | 0 | 0 | 0 | 50 | 0 | 24 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 111 | 0 | 132 | 0 | 32 | 0 | 186 | 0 | 318 | 70 | 0 | 50 | 0 | 35 | 0 | 2 | 50 | 360 | 144 | 0 | 0 | 1 |  | 7069 | 2973 | 10042 | 4415 | 813 | 1752 | 2134 | 510 | 20 | 272 | 106 | 20 | 0 | 73.23
18:00 | 0 | 0 | 0 | 185 | 0 | 64 | 0 | 0 | 217 |  | 0 | 300 | 250 | 0 | 0 | 15 | 250 | 0 | 82 | 50 | 0 | 150 | 1 | 0 | 0 | 0 | 54 | 17 | 0 | 21 | 25 | 21 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 51 | 60 | 0 | 18 | 0 | 2 | 0 | 135 | 0 | 280 | 265 | 184 | 26 | 87 | 26 | 55 | 0 | 43 | 0 | 0 | 34 | 19 | 8 | 33 | 15 | 104 | 153 | 8 | 20 | 0 | 42 | 42 | 11 | 0 | 110 | 163 | 62 | 30 | 0 | 165 | 18 | 0 | 7 | 280 | 16 | 5 | 0 | 95 | 0 | 102 | 24 | 0 | 80 | 1 | 10 | 85 | 50 | 316 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 52 | 120 | 0 | 310 | 17 | 3 | 126 | 0 | 0 | 17 | 2 |  | 808 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 57 | 20 | 0 | 0 | 0 | 0 | 50 | 13 | 24 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 111 | 0 | 132 | 0 | 32 | 0 | 186 | 0 | 292 | 70 | 0 | 50 | 0 | 35 | 0 | 1 | 50 | 360 | 144 | 0 | 0 | 0 |  | 6743 | 2949 | 9692 | 4229 | 808 | 1654 | 2067 | 510 | 20 | 293 | 104 | 7 | 0 | 73.24
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 91 | 0 | 0 | 206 |  | 0 | 300 | 300 | 0 | 0 | 18 | 259 | 0 | 150 | 60 | 0 | 150 | 24 | 0 | 0 | 0 | 54 | 35 | 0 | 21 | 25 | 18 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 20 | 0 | 9 | 0 | 135 | 0 | 320 | 315 | 207 | 26 | 87 | 26 | 56 | 0 | 51 | 0 | 50 | 34 | 19 | 8 | 33 | 20 | 128 | 150 | 8 | 20 | 0 | 42 | 42 | 33 | 0 | 110 | 163 | 61 | 80 | 0 | 178 | 18 | 0 | 8 | 290 | 16 | 5 | 0 | 154 | 0 | 103 | 43 | 0 | 89 | 0 | 10 | 89 | 50 | 360 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 121 | 0 | 326 | 40 | 0 | 126 | 0 | 0 | 17 | 0 |  | 904 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 50 | 13 | 85 | 12 | 34 | 35 | 34 | 5 | 21 | 0 | 8 | 0 | 0 | 150 | 15 | 0 | 111 | 0 | 132 | 0 | 32 | 10 | 186 | 0 | 373 | 75 | 0 | 67 | 0 | 110 | 0 | 0 | 90 | 370 | 166 | 0 | 0 | 0 |  | 7555 | 3507 | 11062 | 4522 | 904 | 1879 | 2579 | 520 | 20 | 510 | 128 | 0 | 0 | 73.27
19:30 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 206 |  | 0 | 300 | 250 | 0 | 0 | 55 | 333 | 0 | 185 | 80 | 0 | 150 | 51 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 18 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 6 | 0 | 135 | 0 | 280 | 275 | 210 | 26 | 88 | 26 | 56 | 0 | 51 | 0 | 50 | 34 | 19 | 8 | 33 | 20 | 130 | 146 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 61 | 80 | 0 | 211 | 18 | 0 | 7 | 300 | 16 | 11 | 25 | 154 | 0 | 103 | 170 | 27 | 130 | 0 | 30 | 125 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 121 | 0 | 396 | 90 | 0 | 126 | 0 | 0 | 17 | 0 |  | 905 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 64 | 28 | 0 | 0 | 0 | 0 | 50 | 26 | 85 | 42 | 42 | 38 | 43 | 13 | 22 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 111 | 0 | 132 | 0 | 32 | 96 | 186 | 0 | 404 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 202 | 0 | 0 | 0 |  | 8135 | 3918 | 12053 | 4632 | 905 | 2028 | 3204 | 600 | 20 | 534 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 201 |  | 0 | 300 | 250 | 0 | 0 | 55 | 335 | 0 | 182 | 100 | 0 | 150 | 50 | 0 | 0 | 0 | 54 | 35 | 0 | 0 | 25 | 26 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 48 | 0 | 15 | 0 | 135 | 0 | 280 | 275 | 218 | 26 | 124 | 26 | 56 | 0 | 51 | 0 | 50 | 34 | 19 | 11 | 33 | 20 | 128 | 148 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 164 | 62 | 80 | 0 | 226 | 18 | 0 | 8 | 290 | 16 | 11 | 25 | 228 | 0 | 103 | 144 | 28 | 129 | 0 | 30 | 132 | 50 | 375 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 0 | 400 | 90 | 0 | 126 | 0 | 0 | 17 | 0 |  | 905 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 63 | 28 | 0 | 0 | 0 | 0 | 50 | 50 | 85 | 35 | 42 | 40 | 34 | 26 | 22 | 0 | 11 | 0 | 0 | 150 | 15 | 0 | 110 | 0 | 132 | 0 | 32 | 95 | 186 | 0 | 358 | 105 | 0 | 105 | 0 | 113 | 0 | 0 | 113 | 470 | 202 | 0 | 0 | 0 |  | 8278 | 3903 | 12181 | 4707 | 905 | 1979 | 3250 | 620 | 20 | 572 | 128 | 0 | 0 | 73.26
21:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 201 |  | 0 | 300 | 260 | 0 | 0 | 55 | 335 | 0 | 182 | 100 | 40 | 150 | 51 | 0 | 0 | 0 | 54 | 35 | 50 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 18 | 0 | 135 | 0 | 280 | 275 | 219 | 26 | 127 | 26 | 56 | 0 | 51 | 0 | 50 | 34 | 19 | 11 | 33 | 20 | 124 | 148 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 62 | 83 | 0 | 226 | 18 | 0 | 8 | 295 | 16 | 11 | 0 | 228 | 0 | 0 | 182 | 0 | 132 | 0 | 30 | 179 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 0 | 400 | 91 | 0 | 126 | 0 | 0 | 17 | 0 |  | 905 | 0 | 300 | 0 | 0 | 80 | 0 | 0 | 20 | 0 | 0 | 64 | 28 | 0 | 0 | 0 | 0 | 50 | 46 | 85 | 35 | 43 | 38 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 132 | 0 | 31 | 100 | 186 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 201 | 0 | 0 | 0 |  | 8349 | 4062 | 12411 | 4727 | 905 | 2030 | 3309 | 660 | 20 | 636 | 124 | 0 | 0 | 73.27
22:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 221 |  | 0 | 300 | 280 | 0 | 0 | 30 | 332 | 0 | 175 | 100 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 201 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 24 | 0 | 135 | 0 | 285 | 285 | 217 | 26 | 127 | 26 | 56 | 0 | 51 | 0 | 8 | 34 | 19 | 11 | 33 | 20 | 122 | 147 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 83 | 0 | 225 | 18 | 0 | 8 | 300 | 16 | 11 | 0 | 180 | 0 | 0 | 182 | 0 | 104 | 0 | 30 | 180 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 119 | 0 | 400 | 53 | 0 | 126 | 0 | 0 | 17 | 0 |  | 905 | 0 | 295 | 0 | 0 | 80 | 0 | 0 | 20 | 0 | 0 | 64 | 27 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 35 | 8 | 37 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 103 | 0 | 130 | 0 | 31 | 100 | 186 | 0 | 417 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 201 | 0 | 0 | 0 |  | 8171 | 3987 | 12158 | 4725 | 905 | 2045 | 3133 | 660 | 20 | 548 | 122 | 0 | 0 | 73.28
23:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 260 |  | 0 | 300 | 270 | 0 | 0 | 30 | 335 | 0 | 148 | 80 | 82 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 26 | 0 | 135 | 0 | 280 | 275 | 211 | 26 | 121 | 26 | 56 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 33 | 20 | 122 | 155 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 130 | 161 | 62 | 83 | 0 | 225 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 180 | 0 | 0 | 194 | 0 | 98 | 0 | 30 | 180 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 115 | 0 | 400 | 36 | 0 | 126 | 0 | 0 | 17 | 0 |  | 909 | 0 | 290 | 0 | 0 | 70 | 0 | 0 | 20 | 0 | 0 | 63 | 30 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 35 | 8 | 37 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 97 | 0 | 130 | 0 | 12 | 100 | 186 | 0 | 390 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 201 | 0 | 0 | 0 |  | 8091 | 3927 | 12018 | 4664 | 909 | 2024 | 3088 | 660 | 20 | 531 | 122 | 0 | 0 | 73.29
24:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 280 |  | 0 | 300 | 260 | 0 | 0 | 15 | 335 | 0 | 145 | 60 | 32 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 197 | 0 | 120 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 25 | 0 | 135 | 0 | 280 | 275 | 197 | 26 | 120 | 26 | 56 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 33 | 20 | 124 | 155 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 164 | 62 | 83 | 0 | 225 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 125 | 0 | 0 | 194 | 0 | 65 | 0 | 30 | 180 | 50 | 376 | 106 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 0 | 400 | 0 | 0 | 72 | 0 | 0 | 17 | 0 |  | 909 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 52 | 29 | 0 | 0 | 0 | 0 | 50 | 0 | 85 | 35 | 0 | 15 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 96 | 0 | 130 | 0 | 12 | 100 | 186 | 0 | 380 | 105 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 510 | 201 | 0 | 0 | 0 |  | 7833 | 3707 | 11540 | 4631 | 909 | 2064 | 2743 | 660 | 20 | 389 | 124 | 0 | 0 | 73.3
KWH | 0 | 0 | 0 | 4441500 | 0 | 2203818 | 0 | 1393660 | 5740000 |  | 0 | 6991000 | 6451375 | 0 | 0 | 398368 | 7208412 | 0 | 1833000 | 2019840 | 452016 | 2058720 | 141393 | 0 | 0 | 0 | 1208160 | 245766 | 611648 | 387792 | 600000 | 521280 | 751800 | 784900 | 893280 | 0 | 0 | 484000 | 2400000 | 0 | 414745 | 4776997 | 0 | 2871568 | 0 |  | 500640 | 0 | 1135682 | 2207280 | 0 | 389760 | 0 | 346560 | 0 | 2622175 | 0 | 7093300 | 6740000 | 4865000 | 418181 | 2245050 | 564336 | 1322880 | 0 | 1010489 | 0 | 140608 | 835258 | 361944 | 213840 | 757300 | 410350 | 2730240 | 3528560 | 179520 | 378504 | 9850 | 991000 | 988560 | 966600 | 0 | 3406091 | 3581000 | 1416864 | 1666560 | 0 | 5235680 | 401000 | 0 | 169020 | 7104000 | 355856 | 192000 | 22464 | 1688618 | 0 | 708830 | 1298400 | 26030 | 1545840 | 84780 | 450240 | 2810400 | 1164218 | 8912000 | 2624400 | 1988400 | 2531672 | 18480 | 0 | 1300727 | 2423771 | 2123820 | 2623320 | 0 | 8397000 | 773760 | 192660 | 1676160 | 21327 | 0 | 635400 | 172256 |  | 19344000 | 0 | 7585344 | 0 | 0 | 249203 | 0 | 0 | 99360 | 0 | 0 | 1549000 | 488705 | 0 | 0 | 0 | 0 | 645632 | 104056 | 1013192 | 163650 | 115061 | 192125 | 842880 | 139836 | 493200 | 0 | 198810 | 0 | 0 | 3667500 | 32000 | 0 | 2577800 | 0 | 3684355 | 0 | 540884 | 514560 | 4695018 | 0 | 8641727 | 1129440 | 0 | 1445280 | 0 | 1133443 | 0 | 25462 | 1208448 | 10616300 | 3405464 | 0 | 0 | 20940 |  | 171981549 | 76562675 | 248544224 | 108512555 | 19344000 | 44915179 | 51939608 | 14283800 | 484000 | 5810414 | 2730240 | 524428 | 0
Fuel Cost | 0 | 0 | 0 | 6529005 | 0 | 2909039.76 | 0 | 1407596.6 | 5912200 |  | 0 | 7620190 | 7161026.25 | 0 | 0 | 3370193.28 | 7496748.48 | 0 | 3171090 | 15209395.2 | 4122385.92 | 20257804.8 | 1303643.46 | 0 | 0 | 0 | 8819568 | 1899771.18 | 6030849.28 | 290844 | 450000 | 0 | 0 | 0 | 8638017.6 | 0 | 0 | 130680 | 4344000 | 0 | 3852981.05 | 5206926.73 | 0 | 4881665.6 | 0 |  | 0 | 0 | 11016115.4 | 21079524 | 0 | 3086899.2 | 0 | 1029283.2 | 0 | 3880819 | 0 | 5249042 | 6740000 | 4475800 | 539453.49 | 2581807.5 | 637699.68 | 1852032 | 0 | 1727936.19 | 0 | 1420140.8 | 7976713.9 | 459668.88 | 160380 | 1325275 | 307762.5 | 20476800 | 3740273.6 | 1630041.6 | 480700.08 | 157009 | 1625240 | 1581696 | 1720548 | 0 | 3882943.74 | 3724240 | 2791222.08 | 3183129.6 | 0 | 9057726.4 | 878190 | 0 | 344800.8 | 7175040 | 266892 | 145920 | 382112.64 | 12765952.08 | 0 | 11851637.6 | 6751680 | 435221.6 | 15211065.6 | 991078.2 | 3669456 | 30492840 | 8207736.9 | 8288160 | 23934528 | 18790380 | 22050863.12 | 0 | 0 | 11329332.17 | 21304947.09 | 21195723.6 | 22481852.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 111421440 | 0 | 7964611.2 | 0 | 0 | 3453953.58 | 0 | 0 | 1042286.4 | 0 | 0 | 1750370 | 757492.75 | 0 | 0 | 0 | 0 | 6353018.88 | 1057208.96 | 8966749.2 | 1260105 | 1555624.72 | 1861691.25 | 8167507.2 | 1356409.2 | 946944 | 0 | 150499.17 | 0 | 0 | 19877850 | 1108800 | 0 | 3016026 | 0 | 4863348.6 | 0 | 811326 | 8752665.6 | 5493171.06 | 0 | 8555309.73 | 11791353.6 | 0 | 13715707.2 | 0 | 8795517.68 | 0 | 281355.1 | 8930430.72 | 46605557 | 0 | 0 | 0 | 0 |  | 509558954.83 | 300664329.8 | 810223284.63 | 115414417.16 | 111421440 | 48967669.26 | 388005250.44 | 66483407 | 130680 | 57894178.47 | 20476800 | 1429442.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 222 |  | 0 | 300 | 280 | 0 | 0 | 0 | 332 | 0 | 90 | 100 | 24 | 98 | 0 | 0 | 0 | 0 | 53 | 0 | 55 | 15 | 25 | 22 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 199 | 0 | 120 | 0 |  | 14 | 0 | 13 | 80 | 0 | 0 | 0 | 6 | 0 | 100 | 0 | 265 | 270 | 187 | 8 | 88 | 23 | 56 | 0 | 51 | 0 | 0 | 34 | 16 | 5 | 33 | 11 | 102 | 148 | 8 | 17 | 1 | 42 | 42 | 50 | 0 | 130 | 163 | 62 | 77 | 0 | 218 | 18 | 0 | 7 | 300 | 8 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 10 | 30 | 162 | 28 | 376 | 115 | 86 | 105 | 2 | 0 | 54 | 82 | 99 | 111 | 0 | 400 | 17 | 26 | 78 | 0 | 0 | 10 | 22 |  | 814 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 0 | 0 | 43 | 0 | 24 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 159 | 0 | 32 | 0 | 190 | 0 | 365 | 5 | 0 | 59 | 0 | 34 | 0 | 3 | 35 | 350 | 55 | 0 | 0 | 3 |  | 9916 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 0 | 201 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 335 | 0 | 182 | 100 | 40 | 150 | 51 | 0 | 0 | 0 | 54 | 35 | 50 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 196 | 0 | 120 | 0 | 0 | 24 | 0 | 85 | 100 | 0 | 50 | 0 | 18 | 0 | 135 | 0 | 280 | 275 | 219 | 26 | 127 | 26 | 56 | 0 | 51 | 0 | 50 | 34 | 19 | 11 | 33 | 20 | 124 | 148 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 62 | 83 | 0 | 226 | 18 | 0 | 8 | 295 | 16 | 11 | 0 | 228 | 0 | 0 | 182 | 0 | 132 | 0 | 30 | 179 | 50 | 376 | 115 | 85 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 0 | 400 | 91 | 0 | 126 | 0 | 0 | 17 | 0 |  | 905 | 0 | 300 | 0 | 0 | 80 | 0 | 0 | 20 | 0 | 0 | 64 | 28 | 0 | 0 | 0 | 0 | 50 | 46 | 85 | 35 | 43 | 38 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 106 | 0 | 132 | 0 | 31 | 100 | 186 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 510 | 201 | 0 | 0 | 0 |  | 12411 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 260 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 320 | 0 | 200 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 25 | 0 | 135 | 0 | 340 | 350 | 220 | 26 | 140 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 180 | 154 | 8 | 20 | 0 | 42 | 42 | 51 | 0 | 163 | 162 | 61 | 83 | 0 | 226 | 18 | 0 | 8 | 341 | 15 | 11 | 200 | 245 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 35 |  |  | 927 | 0 | 360 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 90 | 35 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 100 | 0 | 155 | 0 | 12 | 100 | 185 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 233 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 260 | 0 | 0 | 300 | 280 | 0 | 0 | 55 | 300 | 0 | 150 | 100 | 102 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 20 | 100 | 0 | 17 | 220 | 0 | 120 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 10 | 0 | 110 | 0 | 320 | 320 | 220 | 26 | 135 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 152 | 154 | 8 | 20 | 1.6 | 42 | 42 | 51 | 0 | 163 | 162 | 61 | 80 | 0 | 225 | 18 | 0 | 8 | 341 | 15 | 11 | 100 | 245 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 35 | 30 |  | 927 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 50 | 35 | 43 | 40 | 34 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 155 | 0 | 12 | 50 | 185 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 228 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 0 | 236 | 0 | 0 | 300 | 285 | 0 | 0 | 30 | 270 | 0 | 123 | 7 | 50 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 19 | 25 | 29 | 25 |  | 8 | 0 | 0 | 20 | 100 | 0 | 17 | 202 | 0 | 110 | 0 | 0 | 24 | 0 | 85 | 70 | 0 | 0 | 0 | 10 | 0 | 110 | 0 | 290 | 290 | 216 | 26 | 134 | 23 | 40 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 25 | 16 | 100 | 154 | 8 | 20 | 0 | 42 | 42 | 50 | 0 | 163 | 162 | 40 | 80 | 0 | 225 | 18 | 0 | 8 | 270 | 16 | 5 | 0 | 0 | 0 | 0 | 8 | 0 | 65 | 10 | 10 | 17 | 10 | 352 | 85 | 68 | 68 | 3 | 0 | 54 | 17 | 17 | 17 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 0 | 919 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 64 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 101 | 0 | 153 | 0 | 12 | 0 | 186 | 0 | 388 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 360 | 175 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8374 | 7:00
| Highest Generation |  | 12411 | 21:00
| Day Peak Generation |  | 9916 | 12:00
| Evening Peak Generation |  | 12411 | 21:00
| HVDC Max Flow |  | 918 | 1:00
| HVDC EvPeak Flow |  | 905 | 21:00
| Load factor L.F |  | 83.44%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-09
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9916 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9143 | MW
Evening Peak Generation : |  | 12411 | MW Hour : | 21:00 | Available Max Generation : |  | 15482 | MW
E.P. Demand (at gen end) : |  | 12411 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12411 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2482 | MW
Total Gen. (MKWH) : |  | 248.5442 | System Load Factor : | 83.44% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -102 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-09
Actual : | 73.42 | Ft.(MSL) , | Rule curve : | 78.08 | Ft.( MSL )
Gas Consumed : | Total = | 1238.47 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 164382086.42
: |  | Coal : | 66483407 | Oil : | 445899428.91 | Total : | 676764922.33
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4580.5268 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1562.2189 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1400.5135 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1265.7723 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1143.7001 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 922.9371 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 510.1592 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.4753 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 711.8431 |  |  | 0 | 0%
Total | 0 |  | 12335.1462 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-3
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Naogaon 132/33 kV T1 transformer was under shut down from 08:22 to 09:27 due to red hot maintenance |  |  |  |  | About 20 MW power interruption occurred under Naogaon S/S area
at 33 kV PBS feeder. |  |  |  |  | from 08:22 to 09:27.
b) Mymensingh-Netrokona 132 kV Ckt-2 was under shut down from 09:05 to 16:17 for C/M.
c) Tangail 132/33 kV T2 transformer was under shut down from 09:58 to 10:52 for C/M.
d) Aminbazar-Manikganj PP 132 kV Ckt-2 was under shut down from 10:26 to 16:04 for C/M.
e) Chapainawabganj 132/33 kV T1 transformer was under shut down since 10:20 for C/M.
f) Saidpur 132/33 kV T2 transformer tripped at 09:40 due to 33 kV Y phase CT burst.
g) Ishurdi 230/132kV T3 transformer tripped at 10:53 L/O,OLTC and was switched on at 13:19.
h) Mymensingh 132/33 kV T1 transformer was under shut down from 13:36 to 14:35 for D/W.
i) Basundhara-Banani 132 kV Ckt charge from Bashundhara end.
j) Khulna 225 MW GT was synchronized at 20:25.
k) Madanganj 132/33 kV T2 transformer was switched on at 14:50.
l) Agargaon-Cantonment 132 kV Ckt-1 tripped at 22:54 showing differential relay .
m) Barisal(S) 132/33 kV T1 transformer with 33 kV bus was under shut down from 07:12 to |  |  |  |  | About 20 MW power interruption occurred under Barisal(S) S/S area
08:18(09-06-2021) for C/M. |  |  |  |  | from 07:12 to 08:18.
n) Chuadanga 132/33 kV T2 transformer was under shut down from 06:20 to 09:26(09-06-2021) for D/W.
o) Hasnabad-Brammangaon 132 kV Ckt was under shut down since 06:42(09-06-2021) for C/M.
p) Hasnabad-Sitalakhya 132 kV Ckt was under shut down since 07:14(09-06-2021) for C/M.
q) Rajshahi(O) 132/33 kV T3 transformer was under shut down from 22:28 to 00:12(09-06-2021) for red |  |  |  |  | About 35 MW power interruption occurred under Rajshahi(O) S/S area
hot maintenance. |  |  |  |  | from 22:28 to 00:12.
r) Srinagar 132 kV bus-1 tripped at 06:45 showing bus bar protection and was switched on at 08:44(09-06-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4441500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 97 | 2203818
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 1393660 | Under maint.
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 201 | 5740000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 6991000 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6451375 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 398368
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 51 | 141393 | Low demand
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 387792
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 182 | 1833000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2019840
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7208412
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 40 | 452016 | Line O/L
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1208160
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2058720
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 245766 | Engine problem
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 50 | 611648
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1121280 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 751800
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 784900
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 893280 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 228 | 1688618 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 708830 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 26030 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 1545840 | Engine problem
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 85 | 1988400 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 91 | 773760 | Engine problem
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1676160 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 172256
| Dhaka area Total |  |  |  | 5919 | 2941 | 55917622
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 414745 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 84780
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 389760
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 20 | 484000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 196 | 4776997 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2871568 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2531672
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1135682 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2207280
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 30 | 450240 | Line O/L
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 18 | 346560
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 18480
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300727
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2423771
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 0 | 0 | Line O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 21327 | Transformer O/L
| Chattogram area Total |  |  |  | 2382 | 1005 | 21857589
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 135 | 2622175
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 219 | 4865000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7093300 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6740000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 564336 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1322880
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 418181 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1010489
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 1164218 | Line O/L
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 140608
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 127 | 2245050 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 179 | 2810400 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 361944 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 213840
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2730240
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 757300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 835258 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 410350 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 22464 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 2123820
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 120 | 2623320
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 635400 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1952 | 41710573
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 148 | 3528560 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 378504 | Engine problem
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 179520 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9850
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 1298400 | Engine problem
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2624400
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 192660
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 500640
| Mymensingh Area Total |  |  |  | 709 | 497 | 8712534
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 42 | 991000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 988560 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3406091
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 3581000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 966600
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 192000
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1416864
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1666560
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 226 | 5235680
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 401000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 355856 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7104000 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 376 | 8912000
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 169020 | Engine problem
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8397000
| Sylhet Area Total |  |  |  | 2377 | 1954 | 43783231
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 905 | 19344000
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 99360 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 80 | 249203 | Low demand
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 300 | 7585344 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 514560
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1129440
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1510 | 28921907
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 28 | 488705
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 64 | 1549000 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 31 | 540884 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 510 | 10616300
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 201 | 3405464 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 834 | 16600353
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 645632
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 46 | 104056 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 163650 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 115061 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 192125 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 106 | 2577800 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 132 | 3684355 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 186 | 4695018 | FGMO and Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 400 | 8641727 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 139836
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 493200
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 198810
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 842880 | Engine problem
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 1013192
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1445280
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1208448
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20940
| Rajshahi Area Total |  |  |  | 2179 | 1455 | 26182010
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3667500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 32000 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1133443
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 25462
| Rangpur Area Total |  |  |  | 605 | 263 | 4858405
| Total |  |  |  | 21315 | 12411 | 248544224
| Eastern Grid Total |  |  |  | 14421 | 8349 | 171981549
| Western Grid Total |  |  |  | 6894 | 4062 | 76562675
| National Grid Total |  |  |  | 21315 | 12411 | 248544224
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-08
(a) ENTIRE EASTERN GRID : |  | 7847 | MW | (b) ENTIRE WESTERN GRID : |  | 3918 | MW
i) Dhaka area |  | 4082 | MW | i) Khulna area |  | 1531 | MW
ii) Chittagong area |  | 1248 | MW | ii) Rajshahi area |  | 1339 | MW
iii) Comilla area |  | 1050 | MW | iii) Barisal area |  | 316 | MW
iv) Mymensingh area |  | 987 | MW | iv) Rangpur area |  | 732 | MW
v) Sylhet area |  | 480 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11765 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 114 | 15:00 | Kishoreganj | 130 | 23:00 | Jessore | 115 | 21:00
Munsiganj | 92 | 23:00 | Netrokona | 118 | 21:00 | Benapol | 62 | 21:00
Sonargaon | 72 | 1:00 | Jamalpur | 136 | 19:30 | Jhenida | 109 | 21:00
Shyampur | 180 | 2:00 | Sherpur | 120 | 21::00 | Bottail | 140 | 21:00
Bhulta | 195 | 12:00 | Srimongal | 49 | 21:00 | G.K Project | 62 | 21:00
Madanganj | 51 | 20:00 | Shahjibazar | 111 | 21:00 | Faridpur | 188 | 21:00
Shitalakhya | 94 | 12:00 | Fenchuganj | 42 | 20:00 | Madaripur | 90 | 21:00
Rahim steel | 26 | 11:00 | Kulawara | 47 | 19:30 | Sariatpur | 54 | 20:00
Matuail | 54 | 11:00 | Sylhet | 114 | 19:00 | Gopalganj | 88 | 20:00
Ghorasal | 80 | 22:00 | Chatak | 25 | 20:00 | Bagerhat | 93 | 21:00
Narsingdi | 172 | 22:00 | Sunamganj | 45 | 21:00 | Mongla | 38 | 12:00
Haripur (SBU) | 113 | 13:00 | Biani Bazar | 56 | 19:30 | Satkhira | 102 | 21:00
Sreenagar | 36 | 22:00 | Comilla (S) | 130 | 19:30 | Gallamari | 33 | 13:00
Ullon | 61 | 20:00 | Comilla(N) | 127 | 20:00 | Magura | 54 | 21:00
Hasnabad | 78 | 23:00 | Chandpur | 64 | 21:00 | Norail | 47 | 20:00
Magbazar | 83 | 13:00 | Feni | 108 | 19:30 | Chuadanga | 92 | 21:00
Maniknagar | 64 | 13:00 | Chowmuhani | 154 | 19:30 | Borguna | 16 | 22:00
Bangabhaban | 11 | 12:00 | Ashuganj | 40 | 21:00 | Barisal(N) | 39 | 21:00
Motijheel | 19 | 12:00 | Daudkandi | 132 | 21:00 | Barisal (S) | 90 | 21:00
Narinda | 52 | 12:00 | B.Baria | 145 | 21:00 | Patuakhali | 96 | 21:00
Kazla | 73 | 16:00 | Ramganj | 80 | 19:00 | Bhandaria | 46 | 21:00
Dhanmondi | 168 | 13:00 | Chaddagram | 39 | 20:00 | Borhan Uddin | 40 | 22:00
Lalbag | 84 | 13:00 | PHP | 9 | 17:00 | Ishurdi | 70 | 21:00
Madartek | 66 | 23:00 | Kochua | 54 | 19:00 | Ruppur Paromanobik | 4 | 9:00
Dhaka University | 40 | 12:00 | Madunaghat | 58 | 19:00 | Natore | 140 | 23:00
Aftabnagar | 9 | 19:30 | Hathazari | 86 | 19:00 | Bogra | 159 | 23:00
Fatullah | 58 | 10:00 | Khulshi | 205 | 14:00 | Noagaon | 127 | 21:00
Nawabganj | 46 | 19:30 | Halishahar | 101 | 15:00 | Rajshahi | 164 | 21:00
Keraniganj | 64 | 19:30 | Baraulia | 139 | 9:00 | Rajshahi New | 27 | 20:00
Mirpur | 107 | 19:00 | Sikalbaha | 30 | 10:00 | C.Nawabganj | 61 | 23:00
Kalyanpur | 102 | 19:00 | Dohazari | 92 | 19:00 | Amnura | 51 | 21:00
Gulshan | 126 | 13:00 | Cox'sbazar | 83 | 21:00 | Pabna | 110 | 19:30
Uttara | 72 | 19:00 | Chandraghona | 28 | 19:30 | Shahjadpur | 89 | 20:00
Uttara New | 27 | 12:00 | Kaptai | 5.6 | 19:00 | Serajganj | 96 | 19:30
Kamrangirchar | 84 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 70 | 21:00
Savar | 156 | 19:00 | Bakulia | 100 | 19:00 | Joypurhat | 60 | 21:00
Bhasantec | 144 | 13:00 | Julda | 22 | 11:00 | Sherpur(Bogura) | 56 | 21:00
Agargaon | 72 | 13:00 | TK chemical | 25 | 19:00 | Mohastangor | 66 | 1:00
Satmosjid | 83 | 13:00 | Modern Steel |  |  | Bhangura | 32 | 20:00
Tongi | 111 | 0:00 | Shahmirpur | 25.2 | 0:00 | Rangpur | 116 | 19:30
Kabirpur | 250 | 16:00 | Khagrachhari | 22 | 7:00 | Lalmonirhat | 37 | 21:00
Basundhara | 150 | 15:00 | Matarbari | 29 | 19:00 | Saidpur | 96 | 22:00
Manikganj | 74 | 21:00 | Baroiar Hat | 36 | 19:30 | Purbasadipur | 106 | 1:00
Joydevpur | 169 | 15:00 | Rangamati | 12 | 19:00 | Thakurgaon | 87 | 21:00
New Tongi | 103 | 11:00 | Abul Khair 230 | 147 | 9:00 | Palashbari | 118 | 20:00
Kodda | 262 | 15:00 | BSRM | 154 | 21:00 | Barapukuria | 48 | 20:00
Dhamrai | 116 | 0:00 | GPH Ispat | 92 | 20:00 | Panchagar | 50 | 20:00
Rajendrapur | 100 | 20:00 | Agrabad | 24 | 11:00 | Joldhaka | 54 | 19:30
Valuka | 100 | 19:00 | Goalpara | 27 | 23:00 | Kurigram | 60 | 20:00
Tangail | 215 | 21:00 | Central S/S | 96 | 21:00 | Mithapukur | 43 | 20:00
Mymensing | 203 | 19:30 | Noapara | 55 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 5:00 | 395 | 2:00 | Kaliakoir | 389 | 0.25 | 376 | 0.45833
| Bheramara | 406 | 7:00 | 386 | 23:00 | Bhulta | 382 | 0.79167 | 369 | 0.41667
| Ashuganj(N) | 389 | 18:30 | 377 | 11:00 | Gopalganj | 405 | 0.625 | 382 | 0.875
| Payra | 408 | 19:30 | 393 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 221 | 14:00 | 213 | 9:00
| Ishurdi | 235 | 5:00 | 224 | 11:00 | Megnaghat | 230 | 13:00 | 224 | 11:00
| Ashuganj | 237 | 13:00 | 232 | 10:00 | Fenchuganj | 237 | 19:00 | 235 | 1:00
| Serajganj | 230 | 23:00 | 225 | 1:00 | Siddhirganj | 228 | 5:00 | 221 | 10:00
| Baghabari | 233 | 18:00 | 226 | 11:00 | Maniknagar | 226 | 5:00 | 220 | 11:00
| Barapukuria | 234 | 4:00 | 229 | 20:00 | Agargaon | 224 | 7:00 | 215 | 11:00
| Bogra | 226 | 19:00 | 218 | 1:00 | Barisal | 243 | 24:00 | 230 | 21:00
| Rajshahi | 233 | 24:00 | 223 | 11:00 | Bhola 225 MW | 246 | 9:00 | 236 | 23:00
| Khulna South | 227 | 18:00 | 209 | 12:00 | AKSML | 221 | 24:00 | 213 | 9:00
| Rampura | 227 | 19:00 | 221 | 10:00 | BSRM | 224 | 18:00 | 216 | 9:00
| Haripur | 226 | 19:00 | 219 | 11:00 | Bibiyana | 239 | 5:00 | 234 | 11:00
| Hasnabad | 225 | 14:00 | 219 | 2:00 | Bhulta | 230 | 20:00 | 221 | 10:00
| Shyampur | 224 | 19:30 | 220 | 11:00 | Ashuganj (S) | 234 | 5:00 | 229 | 10:00
| Aminbazar | 225 | 1:00 | 218 | 2:00 | Kaliakoir | 224 | 22:00 | 212 | 11:00
| Tongi | 224 | 21:00 | 213 | 9:00 | GPH | 222 | 14:00 | 214 | 9:00
| Comilla (N) | 228 | 18:30 | 222 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 132 | 19:00 | 126 | 11:00 | Kochua | 138 | 0.8125 | 134 | 0.083333
| Munsiganj | 133 | 19:00 | 126 | 11:00 | Madanhat | 132 | 0.125 | 128 | 0.375
| Sonargaon | 133 | 19:00 | 126 | 10:00 | Hathazari | 131 | 0.16667 | 127 | 0.375
| Shyampur | 134 | 19:00 | 128 | 11:00 | Khulshi | 128 | 0.125 | 123 | 0.5
| Bhulta | 124 | 18:30 | 118 | 10:00 | Halishahar | 128 | 0.20833 | 123 | 0.41667
| Madanganj | 131 | 7:00 | 125 | 11:00 | Baraulia | 128 | 0.083333 | 123 | 0.41667
| Shitalakhya | 138 | 14:00 | 127 | 16:00 | Sikalbaha | 132 | 0.20833 | 127 | 0.375
| Rahim steal | 132 | 19:00 | 126 | 11:00 | Dohazari | 128 | 0.20833 | 124 | 0.79167
| Matuail | 132 | 19:00 | 126 | 11:00 | Cox'sbazar | 115 | 0.29167 | 100 | 0.79167
| Ghorasal | 139 | 20:00 | 135 | 8:00 | Chandraghona | 130 | 0.125 | 127 | 0.45833
| Narsinghdi | 134 | 9:00 | 124 | 23:00 | Kaptai | 132 | 0.75 | 127 | 0.29167
| Haripur (SBU) | 132 | 19:00 | 103 | 23:00 | A. Khaer Stl. | 128 | 0.041667 | 125 | 0.375
| Sreenagar | 128 | 19:00 | 123 | 11:00 | Bakulia | 130 | 0 | 126 | 0.41667
| Ullon | 135 | 4:00 | 130 | 11:00 | Julda | 131 | 0.083333 | 129 | 0.375
| Hasnabad | 135 | 14:00 | 128 | 11:00 | TK Chemical | 131 | 0.16667 | 127 | 0.375
| Magbazar | 135 | 4:00 | 128 | 11:00 | Modern Steel
| Maniknagar | 135 | 3:00 | 131 | 11:00 | Shahmirpur | 132 | 0.125 | 128 | 0.375
| Bangabhaban | 135 | 3:00 | 131 | 11:00 | Khagrachhari | 130 | 0.29167 | 125 | 0.79167
| Motijheel | 135 | 3:00 | 131 | 11:00 | Matarbari | 116 | 0.29167 | 98 | 0.79167
| Narinda | 135 | 3:00 | 131 | 11:00 | Baroiar Hat | 135 | 0.83333 | 130 | 0.041667
| Kazla | 135 | 3:00 | 131 | 11:00 | Rangamati | 130 | 6:00 | 126 | 9:00
| Dhanmondi | 132 | 19:00 | 126 | 11:00 | Agrabad | 128 | 1:00 | 124 | 8:00
| Lalbag | 136 | 14:00 | 127 | 11:00 | Goalpara S/S | 139 | 18:00 | 126 | 0.45833
| Madartek | 135 | 4:00 | 130 | 11:00 | Khulna Central S/S | 137 | 18:00 | 125 | 0.45833
| Dhaka University | 136 | 5:00 | 129 | 12:00 | Noapara | 135 | 18:00 | 123 | 0.5
| Aftabnagar | 136 | 5:00 | 130 | 11:00 | Jessore | 132 | 18:00 | 116 | 0.83333
| Fatullah | 135 | 20:00 | 128 | 11:00 | Benapol | 133 | 0.20833 | 116 | 0.83333
| Nawabganj | 129 | 20:00 | 123 | 11:00 | Jhenida | 129 | 6:00 | 110 | 0.83333
| Keraniganj | 129 | 20:00 | 123 | 11:00 | Bottail | 133 | 0.25 | 121 | 0.83333
| Mirpur | 134 | 6:00 | 128 | 11:00 | G.K Project | 140 | 0.75 | 132 | 0.125
| Kalyanpur | 136 | 18:30 | 130 | 11:00 | Faridpur | 135 | 0.29167 | 125 | 0.875
| Gulshan | 135 | 5:00 | 129 | 11:00 | Madaripur | 140 | 0.45833 | 130 | 0.875
| Uttara | 135 | 21:00 | 128 | 11:00 | Shariyatpur S/S | 141 | 7:00 | 128 | 0.875
| Uttara New | 135 | 21:00 | 127 | 9:00 | Gopalganj | 144 | 0.20833 | 130 | 0.83333
| Kamrangirchar | 134 | 14:00 | 126 | 12:00 | Bagerhat | 136 | 18:00 | 121 | 0.45833
| Savar | 137 | 14:00 | 128 | 9:00 | Mongla | 135 | 18:00 | 121 | 0.45833
| Bhasantec | 134 | 5:00 | 128 | 11:00 | Satkhira | 137 | 18:00 | 124 | 12:00
| Agargaon | 135 | 5:00 | 129 | 11:00 | Gallamari | 140 | 0.75 | 127 | 11:00
| Satmosjid | 135 | 7:00 | 129 | 11:00 | Magura | 129 | 18:00 | 108 | 0.8125
| Tongi | 137 | 19:30 | 129 | 9:00 | Narail | 128 | 0.75 | 107 | 0.8125
| Kabirpur | 134 | 6:00 | 128 | 11:00 | Chuadanga | 126 | 7:00 | 99 | 0.83333
| Basundhara | 134 | 18:30 | 127 | 10:00 | Borguna | 140 | 6:00 | 127 | 0.875
| Manikganj | 138 | 6:00 | 131 | 10:00 | Barisal(N) | 142 | 7:00 | 131 | 21:00
| Joydevpur | 139 | 13:00 | 131 | 9:00 | Barisal (S) | 140 | 0.29167 | 129 | 0.91667
| New Tongi | 136 | 5:00 | 132 | 1:00 | Patuakhali(S) | 138 | 0.25 | 123 | 0.91667
| Kodda | 133 | 19:30 | 121 | 14:00 | Bhandaria | 139 | 0.45833 | 124 | 0.91667
| Dhamrai | 134 | 6:00 | 126 | 20:00 | Ishurdi | 136 | 5:00 | 131 | 11:00
| Rajendrapur | 132 | 6:00 | 121 | 15:00 | Ruppur Paromanobik | 136 | 18:00 | 130 | 19:30
| Valuka | 125 | 6:00 | 110 | 19:30 | Natore | 134 | 18:00 | 128 | 1:00
| Tangail | 134 | 6:00 | 121 | 19:30 | Bogra | 133 | 17:00 | 128 | 1:00
| Mymensing | 129 | 7:00 | 114 | 19:30 | Noagaon | 130 | 18:30 | 121 | 1:00
| Kishorganj | 130 | 6:00 | 119 | 19:30 | Rajshahi | 131 | 5:00 | 126 | 1:00
| Netrokona | 126 | 5:00 | 110 | 19:30 | Rajshahi New | 132 | 18:00 | 126 | 8:00
| Jamalpur | 132 | 5:00 | 123 | 19:30 | C.Nawabganj | 131 | 19:00 | 123 | 11:00
| Sherpur | 135 | 5:00 | 121 | 19:30 | Amnura | 130 | 7:00 | 123 | 11:00
| Srimongal | 137 | 10:00 | 133 | 1:00 | Pabna | 135 | 5:00 | 128 | 20:00
| Shahjibazar | 135 | 10:00 | 129 | 22:00 | Shahjadpur | 140 | 18:00 | 134 | 8:00
| Fenchuganj | 138 | 13:00 | 133 | 1:00 | Serajganj | 135 | 19:00 | 127 | 11:00
| Khulawara | 136 | 14:00 | 134 | 1:00 | Niyamatpur | 129 | 18:30 | 115 | 20:00
| Sylhet | 133 | 6:00 | 131 | 22:00 | Joypurhat | 130 | 18:30 | 119 | 19:30
| Chatak | 134 | 10:00 | 129 | 23:00 | Sherpur(Bogura) | 133 | 13:00 | 127 | 3:00
| Sunamganj | 132 | 7:00 | 127 | 22:00 | Mohastangor | 133 | 13:00 | 126 | 9:00
| Biani Bazar | 134 | 11:00 | 129 | 21:00 | Bangura | 136 | 5:00 | 132 | 1:00
| Comilla(s) | 131 | 18:00 | 127 | 1:00 | Rangpur | 128 | 13:00 | 121 | 9:00
| Comilla(n) | 138 | 13:00 | 135 | 1:00 | Lalmonirhat | 128 | 18:30 | 122 | 8:00
| Chandpur | 141 | 9:00 | 138 | 1:00 | Saidpur | 130 | 5:00 | 121 | 9:00
| Feni | 136 | 13:00 | 132 | 9:00 | Purbasadipur | 125 | 6:00 | 118 | 20:00
| Chowmuhani | 136 | 3:00 | 133 | 19:00 | Thakurgaon | 126 | 6:00 | 116 | 20:00
| Ashuganj | 139 | 8:00 | 134 | 21:00 | Palashbari | 129 | 13:00 | 123 | 20:00
| Daudkandi | 134 | 20:00 | 128 | 1:00 | Barapukuria | 134 | 4:00 | 129 | 20:00
| B.Baria | 135 | 8:00 | 127 | 21:00 | Panchagar | 126 | 6:00 | 113 | 20:00
| Ramganj | 138 | 12:00 | 131 | 4:00 | Joldhaka | 126 | 0.25 | 118 | 0.83333
| Chaddagram | 138 | 13:00 | 134 | 3:00 | Kurigram | 126 | 0.54167 | 118 | 0.83333
| PHP | 135 | 13:00 | 130 | 9:00 | Mithapukur | 130 | 13:00 | 123 | 8:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-06-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 34 | 7833 | 3707 | 11540 |  |  |  | QF-LDC-11
0:30 | 49 | 7523.5 | 3452.5 | 10976 | Date: | 2021-06-08
1:00 | 64 | 7214 | 3198 | 10412
1:30 | 53 | 7185.5 | 3072.5 | 10258
2:00 | 42 | 7157 | 2947 | 10104
2:30 | 46 | 7081.5 | 2880.5 | 9962 | [5 empty] | Gen. at Eve. Peak | 12411 | 12411 MW (21:00 )
3:00 | 50 | 7006 | 2814 | 9820 | [6 empty] | 21:00
3:30 | 61 | 6944 | 2765 | 9709 | [5 empty] | Gen. at Day Peak | 9916 | 9916 MW (12:00 )
4:00 | 72 | 6882 | 2716 | 9598 | [6 empty] | 12:00
4:30 | 87 | 6760 | 2650.5 | 9410.5 | [5 empty] | Highest Generation | 12411
5:00 | 102 | 6638 | 2585 | 9223 | [6 empty] | 21:00
5:30 | 87 | 6389.5 | 2492 | 8881.5
6:00 | 72 | 6141 | 2399 | 8540
6:30 | 73 | 6063 | 2394 | 8457
7:00 | 74 | 5985 | 2389 | 8374
7:30 | 75 | 5983.5 | 2400 | 8383.5
8:00 | 76 | 5982 | 2411 | 8393
8:30 | 90.5 | 6056.5 | 2530.5 | 8587
9:00 | 105 | 6131 | 2650 | 8781
9:30 | 136 | 6271 | 2750 | 9021
10:00 | 167 | 6411 | 2850 | 9261
10:30 | 142 | 6570 | 2895.5 | 9465.5
11:00 | 117 | 6729 | 2941 | 9670
11:30 | 78.5 | 6870 | 2923 | 9793
12:00 | 40 | 7011 | 2905 | 9916
12:30 | 26 | 7054.5 | 3029 | 10083.5
13:00 | 12 | 7098 | 3153 | 10251
13:30 | 28.5 | 7178 | 3058.5 | 10236.5
14:00 | 45 | 7258 | 2964 | 10222
14:30 | 51.5 | 7309.5 | 3038 | 10347.5
15:00 | 58 | 7361 | 3112 | 10473
15:30 | 77.5 | 7350 | 3118 | 10468
16:00 | 97 | 7339 | 3124 | 10463
16:30 | 81.5 | 7204 | 3048.5 | 10252.5
17:00 | 66 | 7069 | 2973 | 10042
17:30 | 91 | 6906 | 2961 | 9867
18:00 | 116 | 6743 | 2949 | 9692
18:30 | 81.5 | 7149 | 3228 | 10377
19:00 | 47 | 7555 | 3507 | 11062
19:30 | 55 | 8135 | 3918 | 12053
20:00 | 94 | 8278 | 3903 | 12181 |  |  |  | Executive Engineer
20:30 | 96 | 8313.5 | 3982.5 | 12296 |  |  |  | Network Operation Division
21:00 | 98 | 8349 | 4062 | 12411
21:30 | 83.5 | 8260 | 4024.5 | 12284.5
22:00 | 69 | 8171 | 3987 | 12158 |  |  |  |  | Page 6 of 7
22:30 | 48 | 8131 | 3957 | 12088
23:00 | 27 | 8091 | 3927 | 12018
23:30 | 30.5 | 7962 | 3817 | 11779
24:00 | 34 | 7833 | 3707 | 11540
12411 MW (21:00 )
9916 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-08 |  | Energy | 248544224
[11 empty] | 2021-06-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4631 | 909 | 2064 | 3088 | 660 | 20 | 389 | 0 | 124 | 0
0:30 | 4674.5 | 913.5 | 1994 | 2527.5 | 625 | 20 | 268 | 0 | 126 | 0 | Date: | 2021-06-08
1:00 | 4718 | 918 | 1924 | 1967 | 590 | 20 | 147 | 0 | 128 | 0
1:30 | 4737.5 | 822.5 | 1963.5 | 1857.5 | 590 | 20 | 139 | 0 | 128 | 0 | [7 empty] | Total Energy | 248.5442 | Total Energy Gen 248.544 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 248.544 MKWHr
2:00 | 4757 | 727 | 2003 | 1748 | 590 | 20 | 131 | 0 | 128 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4764 | 726.5 | 2018 | 1620 | 585 | 20 | 103.5 | 0 | 125 | 0 | [7 empty] | Energy Requirement | 248.5442
3:00 | 4771 | 726 | 2033 | 1492 | 580 | 20 | 76 | 0 | 122 | 0
3:30 | 4745 | 726 | 2003.5 | 1450.5 | 565 | 20 | 76 | 0 | 123 | 0 | [6 empty] | Shortage
4:00 | 4719 | 726 | 1974 | 1409 | 550 | 20 | 76 | 0 | 124 | 0
4:30 | 4549.5 | 675 | 1944.5 | 1474.5 | 545 | 20 | 84 | 0 | 118 | 0
5:00 | 4380 | 624 | 1915 | 1540 | 540 | 20 | 92 | 0 | 112 | 0
5:30 | 4288 | 624 | 1800.5 | 1428 | 525 | 20 | 83.5 | 0 | 110 | 2.5
6:00 | 4196 | 624 | 1686 | 1316 | 510 | 20 | 75 | 0 | 108 | 5
6:30 | 4172.5 | 624 | 1672.5 | 1272.5 | 510 | 20 | 75 | 0 | 101 | 9.5 |  |  |  |  | Coal
7:00 | 4149 | 624 | 1659 | 1229 | 510 | 20 | 75 | 0 | 94 | 14
7:30 | 4188 | 624 | 1662.5 | 1206.5 | 505 | 20 | 58 | 0 | 99 | 20.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4227 | 624 | 1666 | 1184 | 500 | 20 | 41 | 0 | 104 | 27
8:30 | 4320.5 | 718.5 | 1664 | 1186.5 | 499 | 20 | 41 | 0 | 100 | 37.5
9:00 | 4414 | 813 | 1662 | 1189 | 498 | 20 | 41 | 0 | 96 | 48
9:30 | 4411.5 | 813 | 1739.5 | 1327 | 509 | 20 | 64.5 | 0 | 96 | 40.5
10:00 | 4409 | 813 | 1817 | 1465 | 520 | 20 | 88 | 0 | 96 | 33
10:30 | 4425.5 | 813 | 1811 | 1621.5 | 525 | 20 | 100.5 | 0 | 99 | 50
11:00 | 4442 | 813 | 1805 | 1778 | 530 | 20 | 113 | 0 | 102 | 67
11:30 | 4472.5 | 813.5 | 1798.5 | 1859 | 515 | 20 | 145.5 | 0 | 102 | 67
12:00 | 4503 | 814 | 1792 | 1940 | 500 | 20 | 178 | 0 | 102 | 67
12:30 | 4393.5 | 813.5 | 1815.5 | 2145.5 | 510 | 20 | 218 | 0 | 105 | 62.5
13:00 | 4284 | 813 | 1839 | 2351 | 520 | 20 | 258 | 0 | 108 | 58
13:30 | 4284 | 813 | 1839 | 2351 | 520 | 20 | 258 | 0 | 108 | 58
14:00 | 4284 | 813 | 1839 | 2351 | 520 | 20 | 258 | 0 | 108 | 58
14:30 | 4337 | 813 | 1864.5 | 2376.5 | 515 | 20 | 266.5 | 0 | 111 | 58.5
15:00 | 4390 | 813 | 1890 | 2402 | 510 | 20 | 275 | 0 | 114 | 59
15:30 | 4378 | 812.5 | 1867 | 2446.5 | 510 | 20 | 277 | 0 | 112 | 45
16:00 | 4366 | 812 | 1844 | 2491 | 510 | 20 | 279 | 0 | 110 | 31
16:30 | 4390.5 | 812.5 | 1798 | 2312.5 | 510 | 20 | 275.5 | 0 | 108 | 25.5
17:00 | 4415 | 813 | 1752 | 2134 | 510 | 20 | 272 | 0 | 106 | 20
17:30 | 4322 | 810.5 | 1703 | 2100.5 | 510 | 20 | 282.5 | 0 | 105 | 13.5
18:00 | 4229 | 808 | 1654 | 2067 | 510 | 20 | 293 | 0 | 104 | 7
18:30 | 4375.5 | 856 | 1766.5 | 2323 | 515 | 20 | 401.5 | 0 | 116 | 3.5
19:00 | 4522 | 904 | 1879 | 2579 | 520 | 20 | 510 | 0 | 128 | 0
19:30 | 4632 | 905 | 2028 | 3204 | 600 | 20 | 534 | 0 | 130 | 0
20:00 | 4707 | 905 | 1979 | 3250 | 620 | 20 | 572 | 0 | 128 | 0
20:30 | 4717 | 905 | 2004.5 | 3279.5 | 640 | 20 | 604 | 0 | 126 | 0
21:00 | 4727 | 905 | 2030 | 3309 | 660 | 20 | 636 | 0 | 124 | 0
21:30 | 4726 | 905 | 2037.5 | 3221 | 660 | 20 | 592 | 0 | 123 | 0
22:00 | 4725 | 905 | 2045 | 3133 | 660 | 20 | 548 | 0 | 122 | 0
22:30 | 4694.5 | 907 | 2034.5 | 3110.5 | 660 | 20 | 539.5 | 0 | 122 | 0
23:00 | 4664 | 909 | 2024 | 3088 | 660 | 20 | 531 | 0 | 122 | 0
23:30 | 4647.5 | 909 | 2044 | 3088 | 660 | 20 | 460 | 0 | 123 | 0 | Max Temp. in Dhaka |  | 31.1° C
24:00 | 4631 | 909 | 2064 | 3088 | 660 | 20 | 389 | 0 | 124 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 248.544 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 248.544 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 484000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 414745
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 9 | 12 | 6 | 10 | 10 | 8 | 7 | 9 | 3 | 3 | 1 | [8 empty] | 84780
6 | Sikalbaha 225MW CCPP (Gas) | 198 | 208 | 202 | 211 | 197 | 198 | 198 | 208 | 203 | 197 | 197 | 199 | 197 | 199 | 199 | 196 | 196 | 196 |  | 220 | 196 | 196 | 196 | 201 | 197 | 197 | 4776997
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2871568
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | 34 | 34 |  |  |  |  | 13 | 51 | 51 | 51 | 51 | 44 | 51 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1135682
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 85 | 85 | 85 | 85 | 89 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2531672
| Daudkandi 200 MW PP (B.Trac) | [20 empty] | 25 | 25 |  |  |  |  | 22464
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 8 | 0 | 0 | 140608
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [11 empty] | 90 | 88 | 90 | 155 | 155 | 120 | 82 |  | 150 | 185 | 182 | 182 | 175 | 148 | 145 | 1833000
17 | Siddhirganj 335 MW CCPP | 270 | 270 | 270 | 270 | 270 | 250 | 250 | 250 | 331 | 336 | 333 | 332 | 334 | 300 | 300 | 300 | 300 | 250 |  | 259 | 333 | 335 | 335 | 332 | 335 | 335 | 7208412
18 | Kodda 300 MW PP Unit-2 (Summit) | [12 empty] | 23 | 95 | 95 | 95 | 95 | 95 |  | 154 | 154 | 228 | 228 | 180 | 180 | 125 | 1688618
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 418181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4441500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4 | 100 | 100 | 100 | 100 | 135 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 135 | 135 | 135 | 135 | 135 | 135 |  | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 2622175
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 564336
33 | Ashuganj 225 MW CCPP | 219 | 217 | 217 | 216 | 184 | 184 | 183 | 196 | 205 | 184 | 187 | 187 | 182 | 184 | 193 | 184 | 184 | 184 |  | 207 | 210 | 218 | 219 | 217 | 211 | 197 | 4865000
34 | Ashuganj 450 MW CCPP(South) | 260 | 280 | 290 | 260 | 270 | 265 | 265 | 290 | 305 | 270 | 270 | 270 | 265 | 270 | 280 | 265 | 265 | 265 |  | 315 | 275 | 275 | 275 | 285 | 275 | 275 | 6740000
| Ashuganj 450 MW CCPP(North) | 275 | 290 | 300 | 270 | 285 | 275 | 260 | 280 | 300 | 260 | 260 | 265 | 260 | 260 | 290 | 280 | 280 | 280 |  | 320 | 280 | 280 | 280 | 285 | 280 | 280 | 7093300
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 55 | 55 | 55 | 56 | 55 | 55 | 54 | 54 | 56 | 56 | 56 | 52 | 52 | 52 | 55 |  | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 1322880
36 | Chandpur 150 MW CCPP | 87 | 88 | 88 | 87 | 87 | 86 | 88 | 88 | 89 | 84 | 88 | 88 | 85 | 85 | 88 | 88 | 88 | 87 |  | 87 | 88 | 124 | 127 | 127 | 121 | 120 | 2245050
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 332 | 332 | 332 | 332 | [22 empty] | 1393660
40 | Meghnaghat 450 MW CCPP(MPL) | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 290 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6991000
41 | Haripur 360MW CCPP(HPL) | 233 | 266 | 293 | 302 | 300 | 309 | 281 | 260 | 248 | 226 | 227 | 222 | 206 | 207 | 207 | 206 | 207 | 217 |  | 206 | 206 | 201 | 201 | 221 | 260 | 280 | 5740000
42 | RPCL 210MW CCPP | 156 | 155 | 156 | 156 | 158 | 156 | 156 | 154 | 154 | 157 | 150 | 148 | 136 | 136 | 134 | 148 | 152 | 153 |  | 150 | 146 | 148 | 148 | 147 | 155 | 155 | 3528560
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 4 | 6 | 4 | 22 | 9 | 32 | 26 | 13 | 27 | 18 | 5 | 6 | 3 | [8 empty] | 192660
44 | Fenchugonj CCPP Phase-1 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 991000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 988560
46 | Shajibazar 330 MW CCPP | 163 | 162 | 162 | 161 | 160 | 160 | 164 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 164 | 162 | 163 |  | 163 | 162 | 164 | 162 | 163 | 161 | 164 | 3581000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 40 | 40 | 40 | 61 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 62 |  | 61 | 61 | 62 | 62 | 62 | 62 | 62 | 1416864
48 | Shahjibazar 86MW PP (Shahjibazar) | 83 | 83 | 83 | 83 | 83 | 20 | 20 | 20 | 20 | 74 | 77 | 77 | 77 | 83 | 83 | 83 | 83 | 30 |  | 80 | 80 | 80 | 83 | 83 | 83 | 83 | 1666560
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 204 | 225 | 225 | 226 | 165 |  | 178 | 211 | 226 | 226 | 225 | 225 | 225 | 5235680
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 401000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 8 | 7 | 8 | 8 | 8 | 8 | 8 | 169020
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 192000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 47 | 47 | 11 | 11 | 11 | 11 | 44 | 50 | 50 | 47 | 50 | 50 | 50 | 11 | 11 |  | 33 | 50 | 50 | 50 | 50 | 50 | 50 | 966600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 355856
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 285 | 290 | 290 | 265 | 280 | 300 | 305 | 280 | 270 | 300 | 290 | 260 | 310 | 300 | 290 | 280 |  | 290 | 300 | 290 | 295 | 300 | 280 | 280 | 7104000
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 370 | 350 | 350 | 350 | 394 | 400 | 400 | 400 | 183 | 200 | 200 | 230 | 310 | 310 |  | 326 | 396 | 400 | 400 | 400 | 400 | 400 | 8397000
58 | Nababganj 55 MW PP (Southern power ) | 17 |  |  |  | 10 | 17 | 17 | 17 | 17 | 37 | 55 | 55 | 55 | 55 | [8 empty] | 50 | 55 | 55 | 55 | 611648
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 5 | 4 | 5 | 7 |  | 14 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 500640
60 | Barabkunda 22 MW PP (Regent) | [21 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 15 | 19 | 19 | 19 |  |  | 21 |  | 21 |  |  | 21 | 22 | 22 | 19 | 387792
62 | Tangail 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 378504
63 | Impoprt (Tripura) | 128 | 128 | 122 | 124 | 112 | 108 | 94 | 104 | 96 | 96 | 102 | 102 | 108 | 110 | 114 | 110 | 106 | 104 |  | 128 | 130 | 128 | 124 | 122 | 122 | 124 | 2730240
64 | Malancha, Ctg. EPZ (United) | 30 | 22 | 22 | 22 | 24 | 24 | 20 | 7 | 4 | 4 | 3 | 6 | 10 | 7 | 4 | 6 | 8 | 2 |  | 9 | 6 | 15 | 18 | 24 | 26 | 25 | 346560
65 | Feni 22MW PP (Doreen) | 14 | 14 | 14 | 14 | 14 | 14 | 14 | 14 |  |  | 16 | 16 | 19 | 18 | 18 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 361944
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 213840
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 18 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 757300
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 16 | 16 | 16 | 12 | 11 | 11 | 15 | 15 | 15 | 15 | 15 | 15 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 410350
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 20 | 20 | 21 | 21 | 21 |  | 18 | 18 | 26 | 30 | 30 | 30 | 30 | 521280
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 0 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 751800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 784900
73 | Ghorashal 108MW PP (Regent) | 95 | 95 | 95 | 96 | 96 | 95 | 95 | 95 | 95 | 92 | 94 | 95 | 98 | 95 | 95 | 95 | 64 | 64 |  | 91 | 95 | 97 | 97 | 98 | 99 | 99 | 2203818
| Feni Lanka Power | 100 | 100 | 100 | 70 | 100 | 52 | 52 | 52 | 52 | 99 | 99 | 99 | 100 | 100 | 100 | 100 | 52 | 52 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2123820
| Chowmuhani 113 MW | 110 | 110 | 110 | 110 | 110 | 65 | 65 | 65 | 65 | 104 | 112 | 111 | 115 | 116 | 121 | 120 | 120 | 120 |  | 121 | 121 | 120 | 120 | 119 | 115 | 120 | 2623320
| Manikgonj 162MW PP(MPGL) | 10 | [8 empty] | 9 | 54 | 78 | 122 | 126 | 126 | 126 | 115 | 126 |  | 126 | 126 | 126 | 126 | 126 | 126 | 72 | 1676160
77 | Siddhirganj 100 PP(Dutch Bangla) | 90 | 100 | 100 | 100 | 100 | 50 | 30 | 30 | 42 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 50 |  | 60 | 80 | 100 | 100 | 100 | 80 | 60 | 2019840
78 | Gazipur 52 MW PP | 42 | 42 | 42 | 42 | 42 | 16 | 16 | 16 | 16 | 24 | 42 | 42 | 33 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 893280
79 | Kodda 150MW PP | 32 | 16 |  |  | 16 | 16 | 16 | 16 | 16 | 64 | 64 | 98 | 133 | 133 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2058720
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 179520
81 | Jangalia 52 MW PP (Lakdanavi) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 25 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 835258
| Gazipur 100 MW PP | 86 | 86 | 86 | 86 | 86 | 70 | 70 | 70 | 70 | 80 | 86 | 86 | 86 | 86 | 72 | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1988400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 0 | 2 | 2 | 2 | 2 | 1 | 2 | 3 | 3 | 1 | 0 | [8 empty] | 18480
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300727
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 85 | 102 | 85 | 85 | 51 | 51 | 51 | 51 | 82 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2423771
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 1 |  | 24 | 51 | 50 | 51 |  |  |  | 141393
86 | Meghnaghat CCPP ( Summit) | 250 | 260 | 260 | 290 | 265 | 265 | 260 | 280 | 280 | 230 | 265 | 280 | 230 | 245 | 280 | 270 | 250 | 250 |  | 300 | 250 | 250 | 260 | 280 | 270 | 260 | 6451375
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) |  |  |  |  | 17 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 24 | 70 | 70 | 70 | 23 | 17 |  | 40 | 90 | 90 | 91 | 53 | 36 |  | 773760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 80 | 80 | 80 | 92 | 92 | 82 | 92 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2207280
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 10 | 10 | 10 | 10 | 23 | 51 | 51 | 43 | 43 | 43 | 43 | 43 | 43 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1010489
94 | Gagnagar 102 MW PP (Digital Power) | 7 | 7 | [8 empty] | 16 | 24 | 64 | 93 | [8 empty] | 40 | 82 | 82 | 32 | 452016
95 | Patenga 50MW PP (Baraka) | [12 empty] | 2 | 17 | 18 | 18 | 18 | 18 |  | 20 | 50 | 48 | 50 | 50 | 50 | 50 | 389760
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [12 empty] | 25 | 30 | 30 | 30 | 15 | 15 |  | 18 | 55 | 55 | 55 | 30 | 30 | 15 | 398368
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 | 0 | 245766
101 | Kushiara 163 MW CCPP (KP) | 130 | 163 | 163 | 163 | 130 | 110 | 110 | 110 | 110 | 163 | 130 | 130 | 163 | 130 | 163 | 163 | 130 | 110 |  | 110 | 163 | 163 | 163 | 130 | 130 | 163 | 3406091
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 1 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 9850
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 35 | 35 | 54 | 35 | 35 | 35 | 35 | 53 | 53 | 53 | 53 | 53 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1208160
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko) | [13 empty] | 101 | 102 | 102 | 103 | 102 |  | 103 | 103 | 103 |  |  |  | 0 | 708830
106 | Mymensingh 200 MW PP (United) | 24 | 24 | 24 | 24 | 41 | 8 | 8 | [5 empty] | 24 | 24 | 24 | 24 | 24 | 24 |  | 43 | 170 | 144 | 182 | 182 | 194 | 194 | 1298400
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 27 | 28 |  |  |  | 0 | 26030
114 | Kodda 149 MW PP Unit-1 (Summit) | 74 | 35 | 30 | 15 | 28 | 50 | 33 | 33 | 33 | 33 | 57 | 80 | 80 | 30 | 33 | 77 | 80 | 80 |  | 89 | 130 | 129 | 132 | 104 | 98 | 65 | 1545840
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | [8 empty] | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 10 |  | 10 | 30 | 30 | 30 | 30 | 30 | 30 | 450240
116 | Chandpur 200MW (Desh energy) | 144 | 120 | 50 | 17 | 42 | 68 | 68 | 68 | 68 | 87 | 160 | 162 | 160 | 120 | 120 | 120 | 85 | 85 |  | 89 | 125 | 132 | 179 | 180 | 180 | 180 | 2810400
117 | Ashuganj 150MW PP (Midland) | 120 | 80 | 10 |  | 8 | 50 | 50 | 20 | 20 | 20 | 20 | 28 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1164218
118 | Bibiyana-III 400 MW CCPP | 376 | 376 | 376 | 375 | 376 | 375 | 376 | 375 | 375 | 376 | 375 | 376 | 375 | 376 | 376 | 376 | 375 | 316 |  | 360 | 376 | 375 | 376 | 376 | 376 | 376 | 8912000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 85 | 85 | 96 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 106 | 2624400
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | [25 empty] | 0 | 0
| Anlima Energy Ltd. | 17 | [24 empty] | 0 | 21327
| Bhairob 54.5 MW | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 32 | 35 | 10 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 635400
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 1 | 12 | 10 | 12 | 20 | 22 | 28 | 30 | 23 | 15 | 7 | 2 | [8 empty] | 172256
120 | Eastern Zone Total | 7214 | 7157 | 7006 | 6882 | 6638 | 6141 | 5985 | 5982 | 6131 | 6411 | 6729 | 7011 | 7098 | 7258 | 7361 | 7339 | 7069 | 6743 |  | 7555 | 8135 | 8278 | 8349 | 8171 | 8091 | 7833 | 171981549
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 4 | 5 |  | 22 | 22 | 21 | 20 | 20 | 20 | 4 | 99360
| Khulna 225 MW CCPP | [22 empty] | 80 | 80 | 70 |  | 249203
129 | Rupsha 105 MW PP (Orion rupsha) | 17 | [10 empty] | 5 | 53 | 70 | 70 | 70 | 70 | 70 |  | 75 | 105 | 105 | 105 | 105 | 105 | 105 | 1129440
130
131
132 | United Payra Power Ltd.
133 | Bhola Nutan Biddut BD LTD (GAS) | 153 | 153 | 154 | 154 | 154 | 122 | 121 | 110 | 110 | 112 | 110 | 55 | 83 | 96 | 142 | 144 | 144 | 144 |  | 166 | 202 | 202 | 201 | 201 | 201 | 201 | 3405464
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 26 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 |  | 32 | 32 | 32 | 31 | 31 | 12 | 12 | 540884
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 66 | 57 |  | 65 | 64 | 63 | 64 | 64 | 63 | 52 | 1549000
140 | Bhola 33 MW PP (Venture) | 28 | 24 | 23 | 22 | 22 | 18 | 14 | 14 | 15 | 16 | 16 | 17 | 17 | 18 | 17 | 16 | 16 | 20 |  | 27 | 28 | 28 | 28 | 27 | 30 | 29 | 488705
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 10 | 96 | 95 | 100 | 100 | 100 | 100 | 514560
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 918 | 727 | 726 | 726 | 624 | 624 | 624 | 624 | 813 | 813 | 813 | 814 | 813 | 813 | 813 | 812 | 813 | 808 |  | 904 | 905 | 905 | 905 | 905 | 909 | 909 | 19344000
147 | Bheramara 410 MW CCPP | 280 | 280 | 280 | 280 | 285 | 300 | 330 | 340 | 345 | 340 | 340 | 330 | 315 | 315 | 310 | 310 | 305 | 305 |  | 305 | 305 | 305 | 300 | 295 | 290 | 290 | 7585344
148 | Payra 1320 MW | 440 | 440 | 430 | 400 | 390 | 360 | 360 | 350 | 350 | 370 | 380 | 350 | 370 | 360 | 360 | 360 | 360 | 360 |  | 370 | 450 | 470 | 510 | 510 | 510 | 510 | 10616300
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 148 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3667500
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [10 empty] | 25 | 43 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 645632
| Sirajgonj 6.55 MW Solar | [9 empty] | 1 | 1 | 3 | 4 | 3 | 2 | 1 | 1 | 0 | [8 empty] | 20940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 108 | 107 | 107 | 106 | 107 | 70 | 70 | 70 | 70 | 105 | 127 | 100 | 108 | 113 | 113 | 111 | 111 | 111 |  | 111 | 111 | 110 | 106 | 103 | 97 | 96 | 2577800
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 164 | 161 | 160 | 160 | 160 | 157 | 130 | 130 | 148 | 160 | 160 | 159 | 143 | 133 | 132 | 132 | 132 | 132 |  | 132 | 132 | 132 | 132 | 130 | 130 | 130 | 3684355
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 189 | 189 | 193 | 194 | 150 | 150 | 150 | 173 | 190 | 190 | 190 | 190 | 190 | 190 | 186 | 186 | 186 |  | 186 | 186 | 186 | 186 | 186 | 186 | 186 | 4695018
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 397 | 417 | 420 | 350 | 324 | 308 | 302 | 335 | 340 | 376 | 365 | 365 | 364 | 284 | 338 | 300 | 318 | 292 |  | 373 | 404 | 358 | 400 | 417 | 390 | 380 | 8641727
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 13 |  | 13 | 26 | 50 | 46 |  |  |  | 104056
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 21 | 21 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 21 | 493200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 8 | 198810
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 12 | 42 | 35 | 35 | 35 | 35 | 35 | 163650
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 34 | 42 | 42 | 43 | 8 | 8 | 0 | 115061
167 | Katakhali 50 MW Peaking PP | [19 empty] | 35 | 38 | 40 | 38 | 37 | 37 | 15 | 192125
168 | Santahar 50 MW Peaking PP | [19 empty] | 5 | 13 | 26 | 32 | 33 | 34 |  | 139836
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 8 | 8 | 8 | 8 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 25 |  | 34 | 43 | 34 | 43 | 43 | 43 | 43 | 842880
170 | Chapainawabganj 100 MW Peaking PP | 64 | 64 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1013192
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | 35 | [7 empty] | 13 | 35 | 59 | 106 | 70 | 83 | 113 | 50 | 50 |  | 67 | 113 | 105 | 113 | 113 | 113 | 113 | 1445280
172 | Confidence Power Bogura Unit-1 113 MW | [9 empty] | 15 | 35 | 35 | 100 | 50 | 90 | 113 | 50 | 50 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1208448
173 | Rangpur 20 MW GTPP | [19 empty] | 15 | 15 | 15 |  |  |  | 0 | 32000
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | 70 | 50 | [9 empty] | 34 | 92 | 54 | 56 | 56 | 35 | 35 |  | 110 | 113 | 113 | 113 | 113 | 113 | 70 | 1133443
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | [8 empty] | 25462
178
178