## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-13 | Sunday
|  |  | Date (day): | 2021-06-13 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14265.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15227 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-12 | 2021-06-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 101 | 104 | 104
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 0 | 0 | 0 | 0 | 412 |  | Under maint.
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 172 | 127 | 150 | 150 | 210 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 260 | 260 | 260 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 15 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 62 | 85 | 85 |  | 13 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 20 | 21 | 21 | 21
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 182 | 90 | 150 | 180
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 50 | 96 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 328 | 332 | 335 | 335
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 102 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 54 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 42 | 42 | 42 |  | 10 | Engine problem
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 97 | 225 | 250 | 250 |  | 50 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 130 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 100 | 50 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 107 | 129 | 133 | 133
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 88 | 85 | 85 |  | 20 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 20 | 104 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 126 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 20 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2548 | 3159 | 3338 | 3588 | 931 | 1073
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 25 | 25 | 25 | 25 | 205 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 212 | 203 | 220 | 220 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 100 | 100 | 100
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 92 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 0 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 28 | 20 | 35
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 6 | 6 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 35 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 30 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 0 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 938 | 1177 | 1655 | 1645 | 567 | 123
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 |  |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Machine problem.
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 206 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 260 | 260 | 320 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 270 | 300 | 300 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 51 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 147 | 143 | 143 |  | 7 | Engine problem
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 133 | 133 | 135 | 140 |  | 23
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 180 | 180 | 185 | 185 |  | 15 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 18 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 92 | 152 | 151 | 179
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 41 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 80 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 100 | 100
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 119 | 117 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1754 | 2029 | 2109 | 2353 | 358 | 96
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 126 | 118 | 180 | 180 | 22 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 0 | 20 | 20 |  | 2
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 156 | 200 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 30 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 5 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 327 | 402 | 596.6 | 545 | 22 | 89
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 0 | 0 | 42 | 42 |  | 28 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 161 | 164 | 162 | 162 |  | 168 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 56 | 62 | 62
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 80 | 83
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 220 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 15 | 15 |  | 10 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 404 | 404 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 385 | 398 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1907 | 1919 | 2017 | 2025 | 0 | 354
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 426 | 899 | 916 | 916
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 2 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 80 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 305 | 295 | 350 | 400 | 10
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 91 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 731 | 1467 | 1601 | 1921 | 10 | 83
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 15 | 33 | 33 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 84 | 85 | 85 |  | 109 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 12 | 22 | 22 | 73 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 530 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 167 | 221 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 630 | 896 | 1092 | 1202 | 73 | 109
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 71 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 10 | 51 | 51 |  | 20 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 12 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 184 | 187 | 200 | 200 | 20 |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 194 | 190 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 397 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 88 | 50 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 50 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1034 | 1356 | 1586 | 1665 | 401 | 67
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 45 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 4 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 199 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 10068 | 12668 | 14265.6 | 15227 | 2486 | 2184
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9572.0707 | 12044 | 13562.9055 | 14476.9488
| A. |  | 2021-06-12 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 12668 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8472 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12668 | MW
| 3 | Day peak Generation : |  |  | 10068 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12044 | MW
| 4 | Evening peak Generation : |  |  | 12668 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 253.1879 | MKWHr | By Solar | 0.56798 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 154.5987 | MKWHr |  | By Oil: | 62.8956 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.4189 | MKWHr |  | By Hydro: | 0.604 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2486 | MW | Dhaka | 4337 | 4337 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2184 | MW | Chittagong | 1239 | 1239 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4670 | MW | Khulna | 1504 | 1504 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1177.54 | MMCFD |  |  | Rajshahi | 1194 | 1194 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163174053.694 | ii) Oil : | Taka | 481791751.17 | Comilla | 1180 | 1180 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 67097920 | Total | Taka | 712063724.864 | Mymensingh | 915 | 915 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.741 | MKWHr. | Sylhet | 526 | 526 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -90 | MW (E to W) at | 21:00 | hrs | Barisal | 349 | 349 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -126 | MW at | 11:00 | hrs | Rangpur | 800 | 800 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 12044 | 12044 |  | 0
| B. |  | 2021-06-13 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15227 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 1727 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 269.8166 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9302 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.5251 | MKWHr. | ii) HVDC Flow at Peak Time |  | 899 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5776 | MKWHr. | iii) Maximum HVDC Flow : |  | 900 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 73.97 |  | (b) Today: | 74.48 |  | (c) Rule Curve: |  | 79.19
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 331 |  | 0 | 300 | 275 | 0 | 0 | 0 | 338 | 0 | 120 | 50 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 21 | 25 | 30 | 28 | 33 | 25 | 0 | 0 | 25 | 100 | 0 | 17 | 202 | 0 | 100 | 0 |  | 24 | 0 | 68 | 100 | 0 | 0 | 0 | 33 | 100 | 0 | 0 | 260 | 265 | 170 | 26 | 131 | 26 | 56 | 0 | 51 | 0 | 0 | 22 | 19 | 11 | 33 | 21 | 108 | 188 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 130 | 162 | 62 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 175 | 0 | 32 | 0 | 100 | 120 | 50 | 402 | 115 | 86 | 105 | 0 | 0 | 54 | 110 | 36 | 110 | 70 | 400 | 0 | 0 | 17 | 0 | 0 | 17 | 0 |  | 900 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 20 | 0 | 0 | 0 | 0 | 50 | 0 | 89 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 100 | 186 | 0 | 322 | 91 | 0 | 70 | 0 | 113 | 0 | 0 | 35 | 520 | 223 | 0 | 0 | 0 |  | 7271 | 3581 | 10852 | 4570 | 900 | 2052 | 2288 | 670 | 25 | 239 | 108 | 0 | 0 | 73.92
2:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 337 |  | 0 | 300 | 280 | 0 | 0 | 0 | 336 | 0 | 95 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 21 | 25 | 30 | 28 | 33 | 25 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 39 | 100 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 260 | 265 | 167 | 26 | 133 | 26 | 56 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 104 | 199 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 162 | 62 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 175 | 0 | 32 | 0 | 100 | 120 | 50 | 402 | 115 | 86 | 105 | 0 | 0 | 54 | 110 | 36 | 110 | 70 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 900 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 27 | 0 | 0 | 0 | 0 | 50 | 0 | 88 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 70 | 180 | 0 | 338 | 35 | 0 | 0 | 0 | 95 | 0 | 0 | 0 | 460 | 223 | 0 | 0 | 0 |  | 7118 | 3328 | 10446 | 4529 | 900 | 2061 | 2024 | 610 | 25 | 193 | 104 | 0 | 0 | 73.93
3:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 346 |  | 0 | 300 | 295 | 0 | 0 | 0 | 335 | 0 | 95 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 17 | 25 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 280 | 285 | 152 | 26 | 133 | 26 | 56 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 104 | 202 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 162 | 62 | 81 | 0 | 219 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 176 | 0 | 20 | 0 | 100 | 85 | 0 | 402 | 115 | 70 | 105 | 0 | 0 | 54 | 110 | 36 | 110 | 0 | 401 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 900 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 50 | 182 | 0 | 341 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 440 | 223 | 0 | 0 | 0 |  | 6892 | 3093 | 9985 | 4549 | 900 | 2074 | 1645 | 590 | 25 | 98 | 104 | 0 | 0 | 73.94
4:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 349 |  | 0 | 300 | 285 | 0 | 0 | 0 | 334 | 0 | 95 | 50 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 0 | 25 | 100 | 0 | 17 | 205 | 0 | 100 | 0 |  | 0 | 0 | 17 | 92 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 270 | 270 | 201 | 8 | 132 | 23 | 10 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 100 | 201 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 163 | 62 | 81 | 0 | 218 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 15 | 0 | 70 | 34 | 0 | 376 | 115 | 70 | 105 | 0 | 0 | 54 | 110 | 36 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 899 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 186 | 0 | 339 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 223 | 0 | 0 | 0 |  | 6669 | 2957 | 9626 | 4568 | 899 | 2012 | 1440 | 549 | 25 | 33 | 100 | 0 | 0 | 73.95
5:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 349 |  | 0 | 300 | 285 | 0 | 0 | 0 | 334 | 0 | 96 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 0 | 25 | 100 | 0 | 17 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 265 | 270 | 207 | 8 | 132 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 90 | 204 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 164 | 62 | 81 | 0 | 191 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 0 | 50 | 17 | 0 | 377 | 115 | 70 | 105 | 0 | 0 | 50 | 110 | 17 | 26 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 17 | 0 |  | 899 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 2 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 191 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 223 | 0 | 0 | 0 |  | 6346 | 2909 | 9255 | 4565 | 899 | 2005 | 1121 | 550 | 25 | 0 | 90 | 0 | 0 | 73.96
6:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 349 |  | 0 | 300 | 300 | 0 | 0 | 0 | 270 | 0 | 96 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 0 | 25 | 100 | 0 | 17 | 216 | 0 | 100 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 33 | 80 | 0 | 0 | 285 | 290 | 209 | 8 | 133 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 18 | 80 | 202 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 162 | 61 | 81 | 0 | 191 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 1 | 50 | 17 | 0 | 359 | 115 | 70 | 105 | 0 | 0 | 43 | 110 | 17 | 26 | 0 | 400 | 0 | 2 | 0 | 0 | 0 | 17 | 2 |  | 441 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 12 | 0 | 189 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 360 | 223 | 0 | 0 | 0 |  | 6261 | 2405 | 8666 | 4523 | 441 | 2015 | 1067 | 510 | 25 | 0 | 80 | 5 | 0 | 73.97
7:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 321 |  | 0 | 300 | 300 | 0 | 0 | 0 | 270 | 0 | 75 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 0 | 25 | 100 | 0 | 17 | 210 | 0 | 100 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 30 | 80 | 0 | 0 | 280 | 280 | 208 | 8 | 134 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 82 | 185 | 8 | 19 | 1 | 0 | 42 | 47 | 0 | 110 | 161 | 61 | 81 | 0 | 191 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 15 | 1 | 50 | 17 | 0 | 359 | 115 | 70 | 105 | 2 | 0 | 35 | 110 | 17 | 26 | 0 | 320 | 0 | 9 | 0 | 0 | 0 | 17 | 5 |  | 425 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 193 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 222 | 0 | 0 | 0 |  | 6092 | 2380 | 8472 | 4405 | 425 | 1978 | 1058 | 480 | 25 | 0 | 82 | 19 | 0 | 73.98
8:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 280 |  | 0 | 300 | 270 | 0 | 0 | 0 | 290 | 0 | 145 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 5 | 20 | 25 | 30 | 28 | 33 | 4 | 0 | 0 | 25 | 100 | 0 | 17 | 205 | 0 | 100 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 10 | 80 | 0 | 0 | 275 | 260 | 197 | 8 | 132 | 23 | 10 | 0 | 51 | 0 | 0 | 0 | 19 | 11 | 33 | 17 | 92 | 183 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 110 | 163 | 61 | 81 | 0 | 191 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 17 | 4 | 50 | 19 | 0 | 358 | 115 | 70 | 105 | 3 | 0 | 35 | 110 | 17 | 34 | 0 | 320 | 0 | 22 | 0 | 0 | 0 | 17 | 6 |  | 426 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 196 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 320 | 222 | 0 | 0 | 2 |  | 6095 | 2435 | 8530 | 4438 | 426 | 1991 | 1051 | 470 | 25 | 0 | 92 | 37 | 0 | 73.99
9:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 242 |  | 0 | 300 | 285 | 0 | 0 | 0 | 331 | 0 | 150 | 50 | 0 | 10 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 20 | 25 | 30 | 28 | 33 | 25 | 0 | 0 | 25 | 100 | 0 | 17 | 217 | 0 | 100 | 0 |  | 16 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 310 | 300 | 199 | 8 | 133 | 20 | 10 | 0 | 43 | 0 | 0 | 4 | 19 | 11 | 33 | 18 | 94 | 166 | 8 | 19 | 1 | 0 | 42 | 47 | 0 | 163 | 162 | 61 | 78 | 0 | 191 | 18 | 0 | 9 | 305 | 16 | 8 | 0 | 0 | 0 | 0 | 40 | 0 | 24 | 9 | 50 | 50 | 6 | 402 | 115 | 70 | 105 | 4 | 0 | 35 | 110 | 17 | 110 | 10 | 320 | 0 | 13 | 0 | 0 | 0 | 17 | 9 |  | 425 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 12 | 0 | 198 | 0 | 414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 202 | 0 | 0 | 1 |  | 6583 | 2444 | 9027 | 4591 | 425 | 1972 | 1383 | 490 | 25 | 10 | 94 | 37 | 0 | 74
10:00 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 214 |  | 0 | 300 | 270 | 0 | 0 | 0 | 331 | 0 | 151 | 50 | 16 | 60 | 0 | 0 | 0 | 0 | 54 | 35 | 25 | 20 | 25 | 30 | 33 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 205 | 0 | 100 | 0 |  | 17 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 275 | 265 | 190 | 8 | 135 | 23 | 10 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 18 | 92 | 142 | 8 | 19 | 1 | 0 | 42 | 44 | 0 | 163 | 162 | 61 | 78 | 0 | 224 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 90 | 7 | 70 | 72 | 31 | 402 | 115 | 70 | 105 | 5 | 0 | 35 | 110 | 17 | 120 | 10 | 401 | 0 | 15 | 23 | 0 | 0 | 17 | 21 |  | 426 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 12 | 0 | 200 | 0 | 414 | 0 | 0 | 17 | 0 | 0 | 0 | 1 | 25 | 340 | 168 | 0 | 0 | 1 |  | 6791 | 2433 | 9224 | 4550 | 426 | 1911 | 1619 | 490 | 25 | 60 | 92 | 51 | 0 | 74.02
11:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 0 | 181 |  | 0 | 300 | 285 | 0 | 0 | 0 | 331 | 0 | 150 | 50 | 32 | 140 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 20 | 25 | 30 | 28 | 33 | 25 | 0 | 0 | 25 | 100 | 0 | 13 | 205 | 0 | 100 | 0 |  | 17 | 0 | 0 | 92 | 0 | 0 | 0 | 3 | 80 | 0 | 0 | 280 | 270 | 198 | 8 | 134 | 23 | 10 | 0 | 51 | 0 | 0 | 16 | 19 | 11 | 33 | 20 | 98 | 124 | 8 | 19 | 3 | 0 | 42 | 44 | 0 | 163 | 162 | 60 | 78 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 35 | 0 | 0 | 8 | 0 | 108 | 6 | 70 | 173 | 105 | 403 | 115 | 70 | 105 | 3 | 0 | 35 | 110 | 17 | 119 | 30 | 388 | 1 | 21 | 86 | 0 | 0 | 17 | 18 |  | 426 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 45 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 195 | 0 | 12 | 0 | 192 | 0 | 414 | 0 | 0 | 35 | 0 | 35 | 0 | 2 | 35 | 340 | 168 | 0 | 0 | 4 |  | 7176 | 2495 | 9671 | 4512 | 426 | 1875 | 2048 | 490 | 25 | 140 | 98 | 57 | 0 | 74.04
12:00 | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 172 |  | 0 | 300 | 290 | 0 | 0 | 15 | 328 | 0 | 182 | 50 | 48 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 20 | 25 | 30 | 33 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 212 | 0 | 100 | 0 |  | 18 | 0 | 0 | 92 | 0 | 0 | 0 | 3 | 80 | 0 | 0 | 295 | 290 | 205 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 20 | 92 | 126 | 8 | 19 | 3 | 0 | 42 | 47 | 0 | 163 | 161 | 60 | 78 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 97 | 0 | 0 | 8 | 0 | 107 | 8 | 100 | 180 | 135 | 404 | 115 | 70 | 105 | 6 | 0 | 35 | 110 | 17 | 119 | 30 | 385 | 20 | 30 | 108 | 0 | 0 | 17 | 20 |  | 426 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 12 | 0 | 194 | 0 | 414 | 0 | 0 | 50 | 0 | 45 | 0 | 4 | 95 | 350 | 167 | 0 | 0 | 3 |  | 7474 | 2594 | 10068 | 4584 | 426 | 1867 | 2350 | 500 | 25 | 150 | 92 | 74 | 0 | 74.06
13:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 158 |  | 0 | 300 | 245 | 0 | 0 | 40 | 327 | 0 | 179 | 50 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 205 | 0 | 100 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 0 | 3 | 80 | 0 | 0 | 275 | 265 | 202 | 8 | 128 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 20 | 94 | 121 | 8 | 19 | 3 | 0 | 42 | 47 | 0 | 130 | 162 | 61 | 80 | 0 | 219 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 175 | 0 | 0 | 8 | 0 | 125 | 10 | 100 | 179 | 140 | 404 | 103 | 70 | 105 | 6 | 0 | 39 | 110 | 17 | 118 | 50 | 390 | 66 | 42 | 108 | 0 | 0 | 17 | 12 |  | 426 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 35 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 0 | 192 | 0 | 414 | 0 | 0 | 93 | 0 | 100 | 0 | 4 | 113 | 360 | 161 | 0 | 0 | 3 |  | 7563 | 2844 | 10407 | 4580 | 426 | 1824 | 2668 | 510 | 25 | 200 | 94 | 80 | 0 | 74.08
14:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 152 |  | 0 | 300 | 285 | 0 | 0 | 55 | 270 | 0 | 150 | 50 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 205 | 0 | 100 | 0 |  | 10 | 0 | 0 | 92 | 0 | 0 | 0 | 5 | 80 | 0 | 0 | 270 | 275 | 210 | 8 | 132 | 23 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 21 | 98 | 119 | 8 | 19 | 2 | 0 | 42 | 47 | 0 | 130 | 162 | 62 | 81 | 0 | 219 | 18 | 0 | 8 | 295 | 16 | 0 | 0 | 208 | 0 | 0 | 8 | 0 | 132 | 3 | 100 | 181 | 140 | 379 | 115 | 70 | 105 | 6 | 0 | 54 | 110 | 34 | 117 | 50 | 350 | 101 | 43 | 108 | 0 | 0 | 17 | 32 |  | 423 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 35 | 0 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 12 | 0 | 175 | 0 | 414 | 30 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 360 | 167 | 0 | 0 | 5 |  | 7624 | 2883 | 10507 | 4407 | 423 | 1813 | 2911 | 510 | 25 | 225 | 98 | 95 | 0 | 74.1
15:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 156 |  | 0 | 300 | 295 | 0 | 0 | 55 | 270 | 0 | 90 | 50 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 10 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 208 | 0 | 100 | 0 |  | 6 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 285 | 290 | 204 | 8 | 133 | 23 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 21 | 120 | 120 | 8 | 19 | 2 | 0 | 42 | 47 | 0 | 130 | 163 | 40 | 81 | 0 | 206 | 18 | 0 | 8 | 300 | 16 | 0 | 0 | 208 | 0 | 0 | 8 | 0 | 132 | 5 | 100 | 180 | 137 | 379 | 115 | 70 | 105 | 4 | 0 | 54 | 110 | 34 | 116 | 50 | 350 | 104 | 40 | 108 | 0 | 0 | 17 | 11 |  | 900 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 35 | 0 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 12 | 0 | 184 | 0 | 400 | 53 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 360 | 169 | 0 | 0 | 1 |  | 7546 | 3395 | 10941 | 4326 | 900 | 1818 | 2938 | 510 | 25 | 237 | 120 | 67 | 0 | 74.12
16:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 161 |  | 0 | 300 | 280 | 0 | 0 | 55 | 270 | 0 | 90 | 50 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 203 | 0 | 100 | 0 |  | 6 | 0 | 0 | 92 | 0 | 0 | 0 | 4 | 80 | 0 | 0 | 260 | 270 | 213 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 20 | 114 | 131 | 8 | 19 | 1 | 0 | 42 | 47 | 0 | 163 | 162 | 40 | 81 | 0 | 206 | 18 | 0 | 8 | 300 | 16 | 5 | 0 | 208 | 0 | 0 | 8 | 0 | 132 | 3 | 100 | 180 | 138 | 378 | 115 | 70 | 105 | 3 | 0 | 54 | 110 | 34 | 116 | 50 | 350 | 104 | 32 | 54 | 0 | 0 | 17 | 3 |  | 899 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 35 | 0 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 13 | 0 | 157 | 0 | 360 | 53 | 0 | 100 | 0 | 70 | 0 | 3 | 70 | 360 | 168 | 0 | 0 | 1 |  | 7441 | 3235 | 10676 | 4280 | 899 | 1813 | 2752 | 510 | 25 | 237 | 114 | 46 | 0 | 74.14
17:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 0 | 163 |  | 0 | 300 | 260 | 0 | 0 | 30 | 270 | 0 | 90 | 50 | 40 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 0 | 203 | 0 | 100 | 0 |  | 6 | 0 | 0 | 92 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 260 | 265 | 211 | 8 | 132 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 104 | 139 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 163 | 162 | 50 | 81 | 0 | 206 | 17 | 0 | 8 | 310 | 16 | 5 | 0 | 208 | 0 | 0 | 8 | 0 | 132 | 1 | 100 | 180 | 138 | 378 | 115 | 70 | 105 | 1 | 0 | 54 | 110 | 36 | 118 | 50 | 351 | 63 | 10 | 54 | 0 | 0 | 17 | 3 |  | 899 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 16 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 13 | 0 | 179 | 0 | 362 | 53 | 0 | 35 | 0 | 34 | 0 | 2 | 35 | 360 | 132 | 0 | 0 | 1 |  | 7252 | 3032 | 10284 | 4312 | 899 | 1793 | 2421 | 510 | 25 | 202 | 104 | 18 | 0 | 74.16
18:00 | 0 | 0 | 0 | 185 | 0 | 64 | 0 | 0 | 168 |  | 0 | 300 | 270 | 0 | 0 | 30 | 250 | 0 | 37 | 50 | 40 | 80 | 0 | 0 | 0 | 0 | 35 | 17 | 35 | 21 | 25 | 28 | 25 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 0 | 203 | 0 | 100 | 0 |  | 6 | 0 | 0 | 100 | 0 | 0 | 0 | 2 | 80 | 0 | 0 | 265 | 270 | 215 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 18 | 11 | 33 | 20 | 106 | 140 | 8 | 19 | 0 | 0 | 42 | 25 | 0 | 163 | 162 | 61 | 40 | 0 | 179 | 17 | 0 | 8 | 285 | 16 | 5 | 0 | 220 | 0 | 0 | 8 | 0 | 132 | 0 | 50 | 180 | 143 | 378 | 115 | 70 | 105 | 0 | 0 | 54 | 110 | 17 | 65 | 10 | 350 | 53 | 5 | 54 | 0 | 0 | 17 | 1 |  | 900 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 155 | 0 | 12 | 0 | 154 | 0 | 360 | 35 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 360 | 130 | 0 | 0 | 0 |  | 6818 | 2972 | 9790 | 4200 | 900 | 1667 | 2208 | 510 | 25 | 167 | 106 | 7 | 0 | 74.18
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 157 |  | 0 | 300 | 290 | 0 | 0 | 34 | 318 | 0 | 60 | 60 | 84 | 133 | 17 | 0 | 0 | 0 | 54 | 35 | 55 | 21 | 25 | 18 | 25 | 33 | 25 | 0 | 0 | 25 | 100 | 0 | 4 | 218 | 0 | 100 | 0 |  | 6 | 0 | 85 | 100 | 0 | 1 | 0 | 7 | 80 | 0 | 0 | 320 | 325 | 197 | 8 | 132 | 26 | 10 | 0 | 51 | 0 | 0 | 32 | 18 | 11 | 33 | 20 | 126 | 131 | 8 | 19 | 0 | 0 | 42 | 40 | 0 | 163 | 160 | 60 | 81 | 0 | 220 | 17 | 0 | 9 | 310 | 16 | 8 | 0 | 225 | 0 | 0 | 41 | 0 | 130 | 0 | 100 | 179 | 147 | 404 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 17 | 90 | 65 | 383 | 69 | 0 | 69 | 0 | 0 | 20 | 0 |  | 899 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 30 | 5 | 0 | 0 | 0 | 10 | 0 | 88 | 35 | 0 | 8 | 16 | 12 | 21 | 0 | 0 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 175 | 0 | 12 | 7 | 172 | 0 | 380 | 53 | 0 | 45 | 0 | 102 | 0 | 0 | 100 | 400 | 142 | 0 | 0 | 0 |  | 7760 | 3306 | 11066 | 4517 | 899 | 1822 | 2792 | 549 | 25 | 336 | 126 | 0 | 0 | 74.24
19:30 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 137 |  | 0 | 300 | 280 | 0 | 0 | 55 | 327 | 0 | 90 | 80 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 18 | 25 | 33 | 33 | 0 | 0 | 25 | 100 | 0 | 17 | 216 | 0 | 100 | 0 |  | 6 | 0 | 85 | 100 | 0 | 13 | 0 | 11 | 80 | 0 | 0 | 290 | 295 | 195 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 38 | 34 | 18 | 11 | 33 | 21 | 122 | 130 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 163 | 162 | 56 | 81 | 0 | 220 | 17 | 0 | 10 | 315 | 16 | 11 | 0 | 225 | 109 | 50 | 157 | 53 | 130 | 0 | 100 | 180 | 147 | 399 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 17 | 113 | 100 | 385 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 31 | 16 | 0 | 0 | 0 | 43 | 0 | 88 | 35 | 0 | 26 | 36 | 25 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 12 | 100 | 195 | 0 | 400 | 90 | 0 | 90 | 0 | 113 | 0 | 0 | 113 | 540 | 221 | 0 | 0 | 0 |  | 8425 | 3806 | 12231 | 4456 | 899 | 1919 | 3665 | 690 | 25 | 455 | 122 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 133 |  | 0 | 300 | 260 | 0 | 0 | 55 | 329 | 0 | 91 | 91 | 102 | 150 | 68 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 40 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 5 | 0 | 85 | 100 | 0 | 38 | 0 | 16 | 80 | 0 | 0 | 265 | 270 | 194 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 50 | 34 | 18 | 11 | 33 | 21 | 124 | 128 | 8 | 0 | 0 | 0 | 42 | 47 | 0 | 163 | 164 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 305 | 16 | 11 | 80 | 225 | 138 | 50 | 156 | 100 | 129 | 0 | 100 | 180 | 148 | 404 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 17 | 117 | 100 | 395 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 285 | 0 | 0 | 60 | 0 | 0 | 2 | 0 | 0 | 83 | 31 | 16 | 0 | 0 | 0 | 50 | 10 | 88 | 35 | 16 | 31 | 52 | 36 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 12 | 97 | 199 | 0 | 415 | 91 | 0 | 110 | 0 | 113 | 0 | 0 | 113 | 530 | 220 | 0 | 0 | 0 |  | 8568 | 3957 | 12525 | 4408 | 899 | 1925 | 3902 | 680 | 25 | 562 | 124 | 0 | 0 | 74.22
21:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 127 |  | 0 | 300 | 260 | 0 | 0 | 55 | 332 | 0 | 90 | 96 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 5 | 0 | 85 | 100 | 0 | 50 | 0 | 28 | 80 | 0 | 0 | 260 | 270 | 206 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 50 | 41 | 18 | 11 | 33 | 21 | 152 | 118 | 8 | 0 | 0 | 0 | 42 | 47 | 0 | 163 | 164 | 56 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 80 | 225 | 130 | 50 | 156 | 100 | 129 | 0 | 100 | 180 | 147 | 404 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 100 | 117 | 100 | 398 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 295 | 0 | 0 | 80 | 0 | 0 | 2 | 0 | 0 | 84 | 33 | 16 | 0 | 0 | 0 | 50 | 10 | 88 | 35 | 34 | 30 | 52 | 35 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 12 | 100 | 190 | 0 | 397 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 221 | 0 | 0 | 0 |  | 8686 | 3982 | 12668 | 4411 | 899 | 1901 | 4020 | 680 | 25 | 580 | 152 | 0 | 0 | 74.24
22:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 155 |  | 0 | 300 | 245 | 0 | 0 | 55 | 336 | 0 | 90 | 100 | 102 | 150 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 5 | 0 | 85 | 100 | 0 | 50 | 0 | 30 | 80 | 0 | 0 | 260 | 270 | 212 | 8 | 127 | 26 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 154 | 119 | 8 | 16 | 0 | 0 | 42 | 47 | 0 | 163 | 161 | 62 | 82 | 0 | 219 | 18 | 0 | 10 | 295 | 16 | 11 | 20 | 225 | 27 | 25 | 170 | 53 | 132 | 0 | 100 | 179 | 148 | 402 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 100 | 111 | 88 | 400 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 320 | 0 | 0 | 60 | 0 | 0 | 3 | 0 | 0 | 84 | 33 | 16 | 0 | 0 | 0 | 50 | 37 | 88 | 35 | 25 | 30 | 52 | 35 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 12 | 100 | 185 | 0 | 380 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 221 | 0 | 0 | 0 |  | 8503 | 3980 | 12483 | 4451 | 899 | 1919 | 3767 | 680 | 25 | 588 | 154 | 0 | 0 | 74.26
23:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 185 |  | 0 | 300 | 275 | 0 | 0 | 55 | 333 | 0 | 92 | 100 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 207 | 0 | 100 | 0 |  | 6 | 0 | 85 | 92 | 0 | 50 | 0 | 31 | 80 | 0 | 0 | 275 | 280 | 210 | 8 | 132 | 26 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 154 | 121 | 8 | 19 | 0 | 0 | 42 | 47 | 0 | 163 | 163 | 62 | 82 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 225 | 0 | 0 | 163 | 0 | 132 | 0 | 100 | 173 | 148 | 403 | 107 | 88 | 105 | 0 | 0 | 54 | 110 | 100 | 113 | 90 | 394 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 34 | 16 | 0 | 0 | 0 | 50 | 44 | 88 | 35 | 25 | 30 | 52 | 35 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 100 | 182 | 0 | 357 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 222 | 0 | 0 | 0 |  | 8438 | 3892 | 12330 | 4484 | 899 | 1919 | 3647 | 670 | 25 | 532 | 154 | 0 | 0 | 74.28
24:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 0 | 212 |  | 0 | 300 | 260 | 0 | 0 | 55 | 334 | 0 | 92 | 100 | 60 | 150 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 6 | 0 | 85 | 92 | 0 | 50 | 0 | 31 | 80 | 0 | 0 | 260 | 265 | 217 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 50 | 43 | 18 | 11 | 33 | 21 | 152 | 136 | 8 | 19 | 0 | 0 | 40 | 47 | 0 | 163 | 162 | 62 | 82 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 225 | 0 | 0 | 165 | 0 | 132 | 0 | 100 | 180 | 148 | 402 | 107 | 88 | 105 | 0 | 0 | 38 | 110 | 100 | 111 | 100 | 401 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 34 | 16 | 0 | 0 | 0 | 50 | 44 | 88 | 35 | 25 | 30 | 52 | 35 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 161 | 0 | 12 | 100 | 176 | 0 | 362 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 221 | 0 | 0 | 0 |  | 8415 | 3881 | 12296 | 4471 | 899 | 1975 | 3592 | 650 | 25 | 532 | 152 | 0 | 0 | 74.3
KWH | 0 | 0 | 0 | 4410000 | 0 | 2295818 | 0 | 0 | 5462000 |  | 0 | 7126250 | 6750458 | 0 | 0 | 601909 | 7474794 | 0 | 2863000 | 1412160 | 1025568 | 2034720 | 348847 | 0 | 0 | 0 | 1031400 | 704021 | 922682 | 471240 | 600000 | 679320 | 739100 | 816100 | 572640 | 0 | 0 | 604000 | 2400000 | 0 | 370035 | 4839828 | 0 | 2351387 | 0 |  | 225840 | 0 | 639233 | 2220000 | 0 | 242880 | 0 | 439200 | 2105718 | 0 | 0 | 6916200 | 6724000 | 4832000 | 284363 | 3152710 | 556416 | 416640 | 0 | 1248825 | 0 | 232328 | 493776 | 425952 | 255780 | 816900 | 505560 | 2577600 | 3585920 | 188160 | 402192 | 12700 | 0 | 990000 | 1102800 | 0 | 3449372 | 3613000 | 1401120 | 1884480 | 0 | 5038160 | 392000 | 0 | 210060 | 7302003 | 367248 | 177408 | 155712 | 2752472 | 297623 | 138215 | 1936800 | 239781 | 2088000 | 63045 | 2019840 | 3126720 | 2149454 | 9424000 | 2617200 | 1808400 | 2599406 | 38400 | 0 | 1145771 | 2724024 | 882360 | 2452800 | 1054080 | 8974500 | 1141440 | 289080 | 1539360 | 0 | 0 | 537480 | 114985 |  | 17525090 | 0 | 8575776 | 0 | 0 | 149363 | 0 | 0 | 5760 | 0 | 0 | 2057072 | 502266 | 78912 | 0 | 0 | 0 | 336112 | 119653 | 1204384 | 388030 | 108165 | 137832 | 922560 | 179010 | 504720 | 0 | 120942 | 0 | 0 | 3688300 | 0 | 0 | 0 | 0 | 4576382 | 0 | 294107 | 777600 | 4676045 | 0 | 9039000 | 968640 | 0 | 1333056 | 0 | 1435363 | 0 | 24927 | 1327584 | 10730600 | 4729000 | 0 | 0 | 24840 |  | 176646769 | 76541091 | 253187860 | 108307770 | 17525090 | 46290904 | 57857224 | 14418900 | 604000 | 5038395 | 2577600 | 567977 | 0
Fuel Cost | 0 | 0 | 0 | 6482700 | 0 | 3030479.76 | 0 | 0 | 5625860 |  | 0 | 7767612.5 | 7493008.38 | 0 | 0 | 5092150.14 | 7773785.76 | 0 | 4952990 | 10633564.8 | 9353180.16 | 20021644.8 | 3216369.34 | 0 | 0 | 0 | 7529220 | 5442082.33 | 9097644.52 | 353430 | 450000 | 0 | 0 | 0 | 5537428.8 | 0 | 0 | 163080 | 4344000 | 0 | 3437625.15 | 5275412.52 | 0 | 3997357.9 | 0 |  | 0 | 0 | 6200560.1 | 21201000 | 0 | 1923609.6 | 0 | 1304424 | 3116462.64 | 0 | 0 | 5117988 | 6724000 | 4445440 | 366828.27 | 3625616.5 | 628750.08 | 583296 | 0 | 2135490.75 | 0 | 2346512.8 | 4715560.8 | 540959.04 | 191835 | 1429575 | 379170 | 19332000 | 3801075.2 | 1708492.8 | 510783.84 | 202438 | 0 | 1584000 | 1962984 | 0 | 3932284.08 | 3757520 | 2760206.4 | 3599356.8 | 0 | 8716016.8 | 858480 | 0 | 428522.4 | 7375023.03 | 275436 | 134830.08 | 2648661.12 | 20808688.32 | 5053638.54 | 2310954.8 | 10071360 | 4009138.32 | 20545920 | 736996.05 | 16461696 | 33924912 | 15153650.7 | 8764320 | 23868864 | 17089380 | 22640826.26 | 0 | 0 | 9979665.41 | 23944170.96 | 8805952.8 | 21020496 | 7020172.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100944518.4 | 0 | 9004564.8 | 0 | 0 | 2070171.18 | 0 | 0 | 60422.4 | 0 | 0 | 2324491.36 | 778512.3 | 770181.12 | 0 | 0 | 0 | 3307342.08 | 1215674.48 | 10658798.4 | 2987831 | 1462390.8 | 1335592.08 | 8939606.4 | 1736397 | 969062.4 | 0 | 91553.094 | 0 | 0 | 19990586 | 0 | 0 | 0 | 0 | 6040824.24 | 0 | 441160.5 | 13226976 | 5470972.65 | 0 | 8948610 | 10112601.6 | 0 | 12650701.44 | 0 | 11138416.88 | 0 | 275443.35 | 9810845.76 | 47107334 | 0 | 0 | 0 | 0 |  | 539846618.95 | 293871581.714 | 833718200.664 | 113924546.904 | 100944518.4 | 49249506.79 | 432838635.85 | 67097920 | 163080 | 48953115.32 | 19332000 | 1214877.4 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 96 | 0 | 0 | 172 |  | 0 | 300 | 290 | 0 | 0 | 15 | 328 | 0 | 182 | 50 | 48 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 20 | 25 | 30 | 33 | 33 | 25 | 0 | 0 | 25 | 95 | 0 | 17 | 212 | 0 | 100 | 0 |  | 18 | 0 | 0 | 92 | 0 | 0 | 0 | 3 | 80 | 0 | 0 | 295 | 290 | 205 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 20 | 92 | 126 | 8 | 19 | 3 | 0 | 42 | 47 | 0 | 163 | 161 | 60 | 78 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 97 | 0 | 0 | 8 | 0 | 107 | 8 | 100 | 180 | 135 | 404 | 115 | 70 | 105 | 6 | 0 | 35 | 110 | 17 | 119 | 30 | 385 | 20 | 30 | 108 | 0 | 0 | 17 | 20 |  | 426 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 12 | 0 | 194 | 0 | 414 | 0 | 0 | 50 | 0 | 45 | 0 | 4 | 95 | 350 | 167 | 0 | 0 | 3 |  | 10068 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 0 | 127 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 332 | 0 | 90 | 96 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 | 0 | 5 | 0 | 85 | 100 | 0 | 50 | 0 | 28 | 80 | 0 | 0 | 260 | 270 | 206 | 8 | 133 | 26 | 10 | 0 | 51 | 0 | 50 | 41 | 18 | 11 | 33 | 21 | 152 | 118 | 8 | 0 | 0 | 0 | 42 | 47 | 0 | 163 | 164 | 56 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 80 | 225 | 130 | 50 | 156 | 100 | 129 | 0 | 100 | 180 | 147 | 404 | 115 | 88 | 105 | 0 | 0 | 54 | 110 | 100 | 117 | 100 | 398 | 104 | 0 | 126 | 0 | 0 | 35 | 0 |  | 899 | 0 | 295 | 0 | 0 | 80 | 0 | 0 | 2 | 0 | 0 | 84 | 33 | 16 | 0 | 0 | 0 | 50 | 10 | 88 | 35 | 34 | 30 | 52 | 35 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 12 | 100 | 190 | 0 | 397 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 221 | 0 | 0 | 0 |  | 12668 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 150 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 335 | 0 | 180 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 220 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 35 | 80 | 0 | 0 | 320 | 300 | 220 | 26 | 140 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 179 | 180 | 8 | 20 | 0 | 42 | 42 | 51 | 0 | 163 | 162 | 62 | 83 | 0 | 225 | 18 | 0 | 10 | 341 | 15 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 133 | 0 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 35 |  |  | 916 | 0 | 400 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 100 | 35 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 22 | 100 | 200 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 0 | 104 | 0 | 0 | 150 | 0 | 0 | 300 | 260 | 0 | 0 | 55 | 335 | 0 | 150 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 30 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 220 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 6 | 50 | 22 | 20 | 80 | 0 | 0 | 260 | 300 | 220 | 26 | 135 | 26 | 55 | 0 | 51 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 151 | 180 | 8 | 20 | 1.6 | 42 | 42 | 51 | 0 | 163 | 162 | 62 | 80 | 0 | 220 | 18 | 0 | 10 | 341 | 15 | 11 | 100 | 250 | 100 | 100 | 200 | 50 | 133 | 20 | 100 | 185 | 143 | 400 | 115 | 85 | 105 | 5 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 35 | 30 |  | 916 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 85 | 33 | 110 | 0 | 0 | 0 | 50 | 51 | 50 | 35 | 43 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 0 | 102 | 0 | 0 | 117 | 0 | 0 | 300 | 260 | 0 | 0 | 0 | 334 | 0 | 37 | 32 | 5 | 48 | 0 | 0 | 0 | 0 | 54 | 17 | 20 | 21 | 25 | 29 | 33 |  | 2 | 0 | 0 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 | 0 | 6 | 0 | 51 | 92 | 0 | 0 | 0 | 6 | 80 | 0 | 0 | 260 | 265 | 218 | 8 | 129 | 16 | 10 | 0 | 51 | 0 | 0 | 16 | 16 | 11 | 33 | 19 | 110 | 129 | 8 | 19 | 1 | 0 | 40 | 39 | 0 | 163 | 162 | 61 | 78 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 30 | 3 | 65 | 70 | 40 | 402 | 115 | 88 | 105 | 3 | 0 | 54 | 75 | 65 | 85 | 10 | 396 | 0 | 26 | 54 | 1 | 0 | 35 | 11 | 0 | 899 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 0 | 170 | 0 | 332 | 17 | 0 | 0 | 0 | 10 | 0 | 1 | 0 | 380 | 170 | 0 | 0 | 3 | 0
199
| Minimum Generation |  | 8472 | 7:00
| Highest Generation |  | 12668 | 21:00
| Day Peak Generation |  | 10068 | 12:00
| Evening Peak Generation |  | 12668 | 21:00
| HVDC Max Flow |  | 900 | 1:00
| HVDC EvPeak Flow |  | 899 | 21:00
| Load factor L.F |  | 83.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-13
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10068 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9302 | MW
Evening Peak Generation : |  | 12668 | MW Hour : | 21:00 | Available Max Generation : |  | 15227 | MW
E.P. Demand (at gen end) : |  | 12668 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 12668 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1727 | MW
Total Gen. (MKWH) : |  | 253.1879 | System Load Factor : | 83.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -126 | MW at | 11:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-13
Actual : | 74.48 | Ft.(MSL) , | Rule curve : | 79.19 | Ft.( MSL )
Gas Consumed : | Total = | 1177.54 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163174053.694
: |  | Coal : | 67097920 | Oil : | 481791751.17 | Total : | 712063724.864
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4768.2597 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1627.4195 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1459.1737 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1318.8628 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1191.6297 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 961.618 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 530.0362 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 247.3882 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 741.6842 |  |  | 0 | 0%
Total | 0 |  | 12846.0721 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Haripur 412 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 230/132 kV T3 transformer was under shut down from 09:57 to 13:05 for C/M.
b) Aminbazar-Mirpur 132 kV Ckt-2 was under shut down from 09:15 to 17:45 for C/M.
c) Chandpur-Ramganj 132 kV Ckt-1 tripped at 09:29 from both end showing E/F,O/C relays and was
switched on at 11:30.
e) Gopalganj 132/33 kV T1 transformer was under shut down from 08:03 to 09:15 for C/M.
f) Kachua 132/33 kV T1 transformer was under shut down from 09:52 to 11:22 due to red hot maintenance
at 33 kV end.
g) Kodda 132/33 kV T1 & T2 transformers were under shut down from 08:03 to 18:36 for C/M. |  |  |  |  | About 50 MW power interruption has been running under Kodda S/S area
from 08:53 to 18:36.
h) Saidpur 132/33 kV T2 transformer was under shut down from 10:15 to 11:95 for C/M.
i) Saver 132/33 kV T-3 transformer was under shut down from 09:07 to 16:37 for D/W.
j) Ashuganj-Ghorashal 132 kV Ckt-2 was switched on at 16:41.
k) Khulna 225 MW GT was synchronized at 19:46 and was shut down at 22:24.
l) Dohazari-Cox's Bazar 132 kV Ckt-2 is shut down since 06:15(13/06/2021) for D/W.
m) Fenchuganj-Srimongal 132 kV Ckt-1 tripped at 06:15(13-06-2021) showing Dist.AB-phase at Srimongal
end and was switched on at 06:38(13-06-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4410000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 101 | 2295818 | Engine problem
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 0 | 0 | Under maint.
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 127 | 5462000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7126250 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6750458 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 601909
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 62 | 348847 | Low demand
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 471240
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 90 | 2863000 | FGMO
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 96 | 1412160 | Engine problem
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7474794
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1025568
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1031400
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2034720
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 704021
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 922682
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1279320 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 739100
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 816100
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 572640 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 225 | 2752472 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 130 | 297623 | Low demand
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 138215 | Low demand
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 239781
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 129 | 2088000 | Engine problem
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 88 | 1808400 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1141440
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 1539360 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 114985
| Dhaka area Total |  |  |  | 5919 | 3159 | 58462303
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 370035 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 63045
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 242880
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 25 | 604000 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4839828 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2351387 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2599406
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 639233 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2220000
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2019840
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 0 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 439200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 38400
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1145771
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2724024
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1054080
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 0 | Transformer O/L
| Chattogram area Total |  |  |  | 2382 | 1177 | 23751129
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2105718 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4832000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6916200 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 6724000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 556416 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 416640 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 284363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 1248825
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 147 | 2149454
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 232328
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 133 | 3152710 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 180 | 3126720 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 18 | 425952 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255780
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 152 | 2577600
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 816900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 41 | 493776 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 505560 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 80 | 155712 | Low demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 882360 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 117 | 2452800
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 537480 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2029 | 40849294
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 118 | 3585920 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 402192
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 188160 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12700
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 156 | 1936800 | Engine problem
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2617200
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 289080
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 5 | 225840 | Engine problem
| Mymensingh Area Total |  |  |  | 709 | 402 | 9257892
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 0 | 0 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 990000 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3449372
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 164 | 3613000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1102800
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 177408
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1401120
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1884480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5038160
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 392000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 367248 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7302003 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9424000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 210060
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 398 | 8974500
| Sylhet Area Total |  |  |  | 2377 | 1919 | 44326151
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 899 | 17525090
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 2 | 5760 | Low demand
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 80 | 149363 | Low demand
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 295 | 8575776 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 777600
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 91 | 968640 | Engine problem
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1467 | 28002229
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 78912 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 502266
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 84 | 2057072 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 294107 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 10730600
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 221 | 4729000 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Reserve.
| Barisal Area Total |  |  |  | 1826 | 896 | 18391957
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 336112
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 10 | 119653 | Low demand
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 388030 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 108165 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 137832 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 187 | 4576382 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4676045 | FGMO and Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 397 | 9039000 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 179010 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 504720
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 0 | 120942 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 922560
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 88 | 1204384 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1333056
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1327584
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 24840
| Rajshahi Area Total |  |  |  | 2179 | 1356 | 24998315
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3688300 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser problem
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Condenser problem
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1435363
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 24927
| Rangpur Area Total |  |  |  | 605 | 263 | 5148590
| Total |  |  |  | 21315 | 12668 | 253187860
| Eastern Grid Total |  |  |  | 14421 | 8686 | 176646769
| Western Grid Total |  |  |  | 6894 | 3982 | 76541091
| National Grid Total |  |  |  | 21315 | 12668 | 253187860
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-12
(a) ENTIRE EASTERN GRID : |  | 8197 | MW | (b) ENTIRE WESTERN GRID : |  | 3847 | MW
i) Dhaka area |  | 4337 | MW | i) Khulna area |  | 1504 | MW
ii) Chittagong area |  | 1239 | MW | ii) Rajshahi area |  | 1194 | MW
iii) Comilla area |  | 1180 | MW | iii) Barisal area |  | 349 | MW
iv) Mymensingh area |  | 915 | MW | iv) Rangpur area |  | 800 | MW
v) Sylhet area |  | 526 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12044 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 120 | 16:00 | Kishoreganj | 126 | 22:00 | Jessore | 114 | 22:00
Munsiganj | 98 | 21:00 | Netrokona | 122 | 19:30 | Benapol | 60 | 20:00
Sonargaon | 79 | 0:00 | Jamalpur | 146 | 23:00 | Jhenida | 106 | 19:30
Shyampur | 190 | 12:00 | Sherpur | 122 | 22:00 | Bottail | 136 | 21:00
Bhulta | 214 | 21:00 | Srimongal | 61 | 21:00 | G.K Project | 56 | 21:00
Madanganj | 63 | 11:00 | Shahjibazar | 116 | 21:00 | Faridpur | 184 | 21:00
Shitalakhya | 124 | 12:00 | Fenchuganj | 49 | 22:00 | Madaripur | 88 | 21:00
Rahim steel | 27 | 17:00 | Kulawara | 45 | 20:00 | Sariatpur | 62 | 20:00
Matuail | 54 | 17:00 | Sylhet | 129 | 15:00 | Gopalganj | 93 | 20:00
Ghorasal | 69 | 13:00 | Chatak | 31 | 21:00 | Bagerhat | 100 | 21:00
Narsingdi | 175 | 13:00 | Sunamganj | 52 | 19:30 | Mongla | 32 | 11:00
Haripur (SBU) | 117 | 9:00 | Biani Bazar | 65 | 24:00 | Satkhira | 104 | 22:00
Sreenagar | 41 | 22:00 | Comilla (S) | 154 | 22:00 | Gallamari | 41 | 12:00
Ullon | 66 | 19:30 | Comilla(N) | 163 | 20:00 | Magura | 54 | 21:00
Hasnabad | 84 | 22:00 | Chandpur | 78 | 20:00 | Norail | 46 | 20:00
Magbazar | 89 | 14:00 | Feni | 134 | 21:00 | Chuadanga | 93 | 21:00
Maniknagar | 60 | 13:00 | Chowmuhani | 175 | 20:00 | Borguna | 18 | 20:00
Bangabhaban | 6 | 11:00 | Ashuganj | 41 | 1:00 | Barisal(N) | 40 | 22:00
Motijheel | 15 | 12:00 | Daudkandi | 159 | 21:00 | Barisal (S) | 104 | 21:00
Narinda | 50 | 13:00 | B.Baria | 158 | 19:30 | Patuakhali | 107 | 22:00
Kazla | 61 | 12:00 | Ramganj | 88 | 19:30 | Bhandaria | 52 | 22:00
Dhanmondi | 178 | 13:00 | Chaddagram | 46 | 21:00 | Borhan Uddin | 43 | 21:00
Lalbag | 81 | 13:00 | PHP | 12 | 14:00 | Ishurdi | 63 | 19:30
Madartek | 74 | 23:00 | Kochua | 66 | 21:00 | Ruppur Paromanobik | 3 | 9:00
Dhaka University | 39 | 13:00 | Madunaghat | 72 | 14:00 | Natore | 116 | 21:00
Aftabnagar | 10 | 13:00 | Hathazari | 99 | 21:00 | Bogra | 155 | 21:00
Fatullah | 61 | 24:00 | Khulshi | 226 | 16:00 | Noagaon | 123 | 20:00
Nawabganj | 50 | 21:00 | Halishahar | 91 | 13:00 | Rajshahi | 144 | 21:00
Keraniganj | 68 | 19:30 | Baraulia | 144 | 0:00 | Rajshahi New | 20 | 20:00
Mirpur | 122 | 19:30 | Sikalbaha | 38 | 15:00 | C.Nawabganj | 55 | 21:00
Kalyanpur | 87 | 1:00 | Dohazari | 98 | 19:30 | Amnura | 46 | 20:00
Gulshan | 114 | 13:00 | Cox'sbazar | 88 | 19:30 | Pabna | 94 | 20:00
Uttara | 86 | 19:00 | Chandraghona | 30 | 21:00 | Shahjadpur | 93 | 22:00
Uttara New | 27 | 13:00 | Kaptai | 8 | 10:00 | Serajganj | 86 | 20:00
Kamrangirchar | 86 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 69 | 21:00
Savar | 181 | 16:00 | Bakulia | 110 | 16:00 | Joypurhat | 58 | 21:00
Bhasantec | 122 | 13:00 | Julda | 18 | 7:00 | Sherpur(Bogura) | 52 | 21:00
Agargaon | 68 | 13:00 | TK chemical | 28.5 | 19:30 | Mohastangor | 62 | 21:00
Satmosjid | 90 | 13:00 | Modern Steel | 0 | #N/A | Bhangura | 30 | 20:00
Tongi | 116 | 24:00 | Shahmirpur | 26 | 0:00 | Rangpur | 110 | 21:00
Kabirpur | 260 | 15:00 | Khagrachhari | 28 | 7:00 | Lalmonirhat | 43 | 19:30
Basundhara | 171 | 14:00 | Matarbari | 36.5 | 23:00 | Saidpur | 102 | 19:30
Manikganj | 80 | 21:00 | Baroiar Hat | 46 | 15:00 | Purbasadipur | 109 | 21:00
Joydevpur | 163 | 19:00 | Rangamati | 12 | 19:00 | Thakurgaon | 76 | 22:00
New Tongi | 107 | 11:00 | Abul Khair 230 | 138 | 23:00 | Palashbari | 118 | 21:00
Kodda | 260 | 21:00 | BSRM | 161 | 20:00 | Barapukuria | 54 | 21:00
Dhamrai | 110 | 20:00 | GPH Ispat | 90 | 16:00 | Panchagar | 50 | 21:00
Rajendrapur | 102 | 15:00 | Agrabad | 45 | 1:00 | Joldhaka | 58 | 20:00
Valuka | 116 | 21:00 | Goalpara | 26 | 1:00 | Kurigram | 57 | 21:00
Tangail | 164 | 19:30 | Central S/S | 99 | 20:00 | Mithapukur | 41 | 22:00
Mymensing | 189 | 22:00 | Noapara | 51 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 21:00 | 394 | 20:00 | Kaliakoir | 386 | 0.25 | 371 | 0.33333
| Bheramara | 410 | 13:00 | 386 | 22:00 | Bhulta | 380 | 0.91667 | 369 | 0.66667
| Ashuganj(N) | 387 | 6:00 | 378 | 17:00 | Gopalganj | 407 | 0.625 | 389 | 0.041667
| Payra | 411 | 24:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 10:00 | 215 | 17:00
| Ishurdi | 234 | 14:00 | 226 | 19:30 | Megnaghat | 230 | 7:00 | 223 | 13:00
| Ashuganj | 237 | 24:00 | 233 | 16:00 | Fenchuganj | 237 | 24:00 | 234 | 19:00
| Serajganj | 235 | 12:00 | 225 | 19:30 | Siddhirganj | 228 | 22:00 | 221 | 17:00
| Baghabari | 234 | 9:00 | 226 | 20:00 | Maniknagar | 226 | 22:00 | 220 | 17:00
| Barapukuria | 238 | 6:00 | 228 | 19:30 | Agargaon | 225 | 6:00 | 217 | 17:00
| Bogra | 228 | 13:00 | 217 | 19:30 | Barisal | 241 | 21:00 | 233 | 19:00
| Rajshahi | 234 | 14:00 | 225 | 19:30 | Bhola 225 MW | 245 | 6:00 | 238 | 20:00
| Khulna South | 223 | 18:00 | 208 | 13:00 | AKSML | 223 | 21:00 | 215 | 5:00
| Rampura | 226 | 21:00 | 221 | 10:00 | BSRM | 224 | 13:00 | 218 | 5:00
| Haripur | 226 | 22:00 | 219 | 17:00 | Bibiyana | 238 | 22:00 | 233 | 12:00
| Hasnabad | 225 | 18:00 | 218 | 16:00 | Bhulta | 229 | 22:00 | 221 | 16:00
| Shyampur | 233 | 24:00 | 220 | 17:00 | Ashuganj (S) | 233 | 13:00 | 230 | 3:00
| Aminbazar | 226 | 1:00 | 218 | 2:00 | Kaliakoir | 226 | 21:00 | 217 | 8:00
| Tongi | 224 | 23:00 | 215 | 8:00 | GPH | 222 | 13:00 | 215 | 5:00
| Comilla (N) | 244 | 12:00 | 222 | 4:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 20:00 | 127 | 9:00 | Kochua | 138 | 0.45833 | 129 | 0.25
| Munsiganj | 133 | 22:00 | 126 | 11:00 | Madanhat | 132 | 0.41667 | 128 | 0.75
| Sonargaon | 132 | 20:00 | 126 | 1:00 | Hathazari | 132 | 0.41667 | 128 | 0.70833
| Shyampur | 134 | 22:00 | 128 | 17:00 | Khulshi | 129 | 0.875 | 125 | 0.20833
| Bhulta | 124 | 5:00 | 118 | 11:00 | Halishahar | 131 | 0.875 | 126 | 0.70833
| Madanganj | 132 | 22:00 | 125 | 17:00 | Baraulia | 129 | 0.875 | 125 | 0.70833
| Shitalakhya | 139 | 21:00 | 128 | 10:00 | Sikalbaha | 132 | 0.875 | 129 | 0.20833
| Rahim steal | 131 | 20:00 | 126 | 17:00 | Dohazari | 129 | 0.41667 | 125 | 0.70833
| Matuail | 131 | 20:00 | 127 | 9:00 | Cox'sbazar | 122 | 0.79167 | 113 | 0.75
| Ghorasal | 140 | 22:00 | 135 | 16:00 | Chandraghona | 130 | 0.33333 | 127 | 0.66667
| Narsinghdi | 132 | 22:00 | 120 | 16:00 | Kaptai | 128 | 0.041667 | 128 | 0.041667
| Haripur (SBU) | 131 | 20:00 | 126 | 16:00 | A. Khaer Stl. | 130 | 0.875 | 126 | 0.75
| Sreenagar | 130 | 20:00 | 122 | 17:00 | Bakulia | 130 | 0.041667 | 126 | 0.75
| Ullon | 134 | 3:00 | 127 | 16:00 | Julda | 132 | 0.79167 | 128 | 0.75
| Hasnabad | 136 | 21:00 | 128 | 17:00 | TK Chemical | 131 | 0.041667 | 128 | 0.75
| Magbazar | 133 | 4:00 | 126 | 17:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Maniknagar | 136 | 23:00 | 131 | 16:00 | Shahmirpur | 133 | 0.875 | 128 | 0.75
| Bangabhaban | 136 | 23:00 | 131 | 16:00 | Khagrachhari | 129 | 0.29167 | 126 | 0.66667
| Motijheel | 136 | 23:00 | 131 | 16:00 | Matarbari | 124 | 0.77083 | 100 | 0.083333
| Narinda | 136 | 23:00 | 131 | 16:00 | Baroiar Hat | 132 | 0.375 | 127 | 0.20833
| Kazla | 136 | 23:00 | 131 | 16:00 | Rangamati | 129 | 10:00 | 126 | 15:00
| Dhanmondi | 131 | 21:00 | 125 | 16:00 | Agrabad | 130 | 21:00 | 126 | 14:00
| Lalbag | 136 | 21:00 | 127 | 12:00 | Goalpara S/S | 135 | 17:00 | 124 | 0.8125
| Madartek | 134 | 22:00 | 128 | 15:00 | Khulna Central S/S | 134 | 17:00 | 123 | 0.8125
| Dhaka University | 134 | 1:00 | 127 | 16:00 | Noapara | 132 | 18:00 | 121 | 0.8125
| Aftabnagar | 134 | 5:00 | 128 | 15:00 | Jessore | 128 | 18:00 | 114 | 0.8125
| Fatullah | 134 | 20:00 | 129 | 10:00 | Benapol | 128 | 0.20833 | 114 | 0.8125
| Nawabganj | 130 | 21:00 | 121 | 16:00 | Jhenida | 126 | 18:00 | 109 | 0.8125
| Keraniganj | 131 | 21:00 | 123 | 17:00 | Bottail | 130 | 0.20833 | 122 | 0.8125
| Mirpur | 135 | 20:00 | 129 | 18:30 | G.K Project | 138 | 0.41667 | 134 | 0.79167
| Kalyanpur | 135 | 13:00 | 131 | 9:00 | Faridpur | 136 | 0.45833 | 129 | 0.8125
| Gulshan | 133 | 3:00 | 127 | 15:00 | Madaripur | 141 | 0.25 | 133 | 0.041667
| Uttara | 135 | 21:00 | 128 | 10:00 | Shariyatpur S/S | 140 | 6:00 | 132 | 0.041667
| Uttara New | 134 | 14:00 | 129 | 8:00 | Gopalganj | 142 | 0.375 | 134 | 0.041667
| Kamrangirchar | 135 | 21:00 | 126 | 11:00 | Bagerhat | 133 | 17:00 | 120 | 0.16667
| Savar | 137 | 22:00 | 128 | 8:00 | Mongla | 130 | 17:00 | 119 | 0.20833
| Bhasantec | 134 | 22:00 | 129 | 12:00 | Satkhira | 135 | 17:00 | 120 | 19:30
| Agargaon | 135 | 8:00 | 129 | 17:00 | Gallamari | 135 | 0.70833 | 124 | 19:30
| Satmosjid | 133 | 2:00 | 130 | 17:00 | Magura | 125 | 8:00 | 110 | 0.95833
| Tongi | 136 | 13:00 | 130 | 8:00 | Narail | 125 | 0.41667 | 108 | 0.95833
| Kabirpur | 132 | 1:00 | 127 | 19:00 | Chuadanga | 120 | 8:00 | 99 | 0.8125
| Basundhara | 134 | 18:30 | 128 | 8:00 | Borguna | 139 | 6:00 | 128 | 0.79167
| Manikganj | 138 | 18:00 | 132 | 8:00 | Barisal(N) | 140 | 6:00 | 133 | 1:00
| Joydevpur | 138 | 13:00 | 132 | 7:00 | Barisal (S) | 139 | 0.25 | 131 | 0.79167
| New Tongi | 135 | 13:00 | 132 | 17:00 | Patuakhali(S) | 139 | 0.375 | 124 | 0.91667
| Kodda | 134 | 18:00 | 127 | 8:00 | Bhandaria | 137 | 0.375 | 126 | 0.79167
| Dhamrai | 131 | 5:00 | 126 | 15:00 | Ishurdi | 136 | 6:00 | 131 | 19:30
| Rajendrapur | 133 | 18:30 | 122 | 9:00 | Ruppur Paromanobik | 135 | 5:00 | 131 | 19:00
| Valuka | 125 | 8:00 | 110 | 16:00 | Natore | 136 | 14:00 | 130 | 5:00
| Tangail | 131 | 6:00 | 122 | 16:00 | Bogra | 138 | 14:00 | 129 | 1:00
| Mymensing | 129 | 7:00 | 120 | 15:00 | Noagaon | 131 | 13:00 | 129 | 1:00
| Kishorganj | 129 | 9:00 | 120 | 20:00 | Rajshahi | 132 | 7:00 | 127 | 3:00
| Netrokona | 128 | 7:00 | 111 | 19:30 | Rajshahi New | 133 | 14:00 | 128 | 1:00
| Jamalpur | 134 | 4:00 | 119 | 16:0 | C.Nawabganj | 133 | 14:00 | 127 | 1:00
| Sherpur | 133 | 07:0 | 118 | 15:00 | Amnura | 134 | 14:00 | 124 | 4:00
| Srimongal | 136 | 9:00 | 132 | 15:00 | Pabna | 135 | 14:00 | 129 | 19:30
| Shahjibazar | 133 | 6:00 | 129 | 20:00 | Shahjadpur | 138 | 4:00 | 134 | 22:00
| Fenchuganj | 135 | 5:00 | 133 | 1:00 | Serajganj | 134 | 14:00 | 130 | 1:00
| Khulawara | 135 | 8:00 | 132 | 20:00 | Niyamatpur | 131 | 6:00 | 118 | 19:30
| Sylhet | 132 | 7:00 | 130 | 19:30 | Joypurhat | 132 | 6:00 | 118 | 19:30
| Chatak | 132 | 10:00 | 127 | 19:30 | Sherpur(Bogura) | 137 | 14:00 | 128 | 3:00
| Sunamganj | 131 | 7:00 | 125 | 19:30 | Mohastangor | 137 | 14:00 | 127 | 1:00
| Biani Bazar | 133 | 8:30 | 127 | 24:00 | Bangura | 135 | 11:00 | 133 | 19:00
| Comilla(s) | 130 | 5:00 | 126 | 15:00 | Rangpur | 133 | 14:00 | 119 | 19:30
| Comilla(n) | 137 | 21:00 | 132 | 3:00 | Lalmonirhat | 133 | 14:00 | 120 | 19:30
| Chandpur | 140 | 21:00 | 134 | 5:00 | Saidpur | 135 | 5:00 | 118 | 20:00
| Feni | 134 | 10:00 | 126 | 5:00 | Purbasadipur | 132 | 6:00 | 114 | 19:30
| Chowmuhani | 135 | 8:00 | 128 | 6:00 | Thakurgaon | 132 | 6:00 | 114 | 19:30
| Ashuganj | 136 | 8:00 | 133 | 16:00 | Palashbari | 134 | 14:00 | 123 | 19:30
| Daudkandi | 134 | 21:00 | 127 | 1:00 | Barapukuria | 138 | 6:00 | 128 | 19:30
| B.Baria | 132 | 9:00 | 127 | 20:00 | Panchagar | 132 | 6:00 | 110 | 19:30
| Ramganj | 137 | 13:00 | 128 | 4:00 | Joldhaka | 132 | 0.25 | 116 | 0.8125
| Chaddagram | 134 | 8:00 | 130 | 5:00 | Kurigram | 133 | 0.58333 | 116 | 0.8125
| PHP | 133 | 9:00 | 126 | 19:00 | Mithapukur | 135 | 13:00 | 124 | 19:30
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-06-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 48 | 8415 | 3881 | 12296 |  |  |  | QF-LDC-11
0:30 | 42 | 7843 | 3731 | 11574 | Date: | 2021-06-12
1:00 | 36 | 7271 | 3581 | 10852
1:30 | 38 | 7194.5 | 3454.5 | 10649
2:00 | 40 | 7118 | 3328 | 10446
2:30 | 24 | 7005 | 3210.5 | 10215.5 | [5 empty] | Gen. at Eve. Peak | 12668 | 12668 MW (21:00 )
3:00 | 8 | 6892 | 3093 | 9985 | [6 empty] | 21:00
3:30 | 33 | 6780.5 | 3025 | 9805.5 | [5 empty] | Gen. at Day Peak | 10068 | 10068 MW (12:00 )
4:00 | 58 | 6669 | 2957 | 9626 | [6 empty] | 12:00
4:30 | 79 | 6507.5 | 2933 | 9440.5 | [5 empty] | Highest Generation | 12668
5:00 | 100 | 6346 | 2909 | 9255 | [6 empty] | 21:00
5:30 | 103 | 6303.5 | 2657 | 8960.5
6:00 | 106 | 6261 | 2405 | 8666
6:30 | 82 | 6176.5 | 2392.5 | 8569
7:00 | 58 | 6092 | 2380 | 8472
7:30 | 43 | 6093.5 | 2407.5 | 8501
8:00 | 28 | 6095 | 2435 | 8530
8:30 | 18 | 6339 | 2439.5 | 8778.5
9:00 | 8 | 6583 | 2444 | 9027
9:30 | 56 | 6687 | 2438.5 | 9125.5
10:00 | 104 | 6791 | 2433 | 9224
10:30 | 115 | 6983.5 | 2464 | 9447.5
11:00 | 126 | 7176 | 2495 | 9671
11:30 | 116 | 7325 | 2544.5 | 9869.5
12:00 | 106 | 7474 | 2594 | 10068
12:30 | 100 | 7518.5 | 2719 | 10237.5
13:00 | 94 | 7563 | 2844 | 10407
13:30 | 69 | 7593.5 | 2863.5 | 10457
14:00 | 44 | 7624 | 2883 | 10507
14:30 | 222 | 7585 | 3139 | 10724
15:00 | 400 | 7546 | 3395 | 10941
15:30 | 408 | 7493.5 | 3315 | 10808.5
16:00 | 416 | 7441 | 3235 | 10676
16:30 | 412 | 7346.5 | 3133.5 | 10480
17:00 | 408 | 7252 | 3032 | 10284
17:30 | 387 | 7035 | 3002 | 10037
18:00 | 366 | 6818 | 2972 | 9790
18:30 | 274 | 7289 | 3139 | 10428
19:00 | 182 | 7760 | 3306 | 11066
19:30 | 30 | 8425 | 3806 | 12231
20:00 | 56 | 8568 | 3957 | 12525 |  |  |  | Executive Engineer
20:30 | 73 | 8627 | 3969.5 | 12596.5 |  |  |  | Network Operation Division
21:00 | 90 | 8686 | 3982 | 12668
21:30 | 95 | 8594.5 | 3981 | 12575.5
22:00 | 100 | 8503 | 3980 | 12483 |  |  |  |  | Page 6 of 7
22:30 | 103 | 8470.5 | 3936 | 12406.5
23:00 | 106 | 8438 | 3892 | 12330
23:30 | 77 | 8426.5 | 3886.5 | 12313
24:00 | 48 | 8415 | 3881 | 12296
12668 MW (21:00 )
10068 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-12 |  | Energy | 253187860
[11 empty] | 2021-06-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4471 | 899 | 1975 | 3647 | 650 | 25 | 532 | 0 | 152 | 0
0:30 | 4520.5 | 899.5 | 2013.5 | 2967.5 | 660 | 25 | 385.5 | 0 | 130 | 0 | Date: | 2021-06-12
1:00 | 4570 | 900 | 2052 | 2288 | 670 | 25 | 239 | 0 | 108 | 0
1:30 | 4549.5 | 900 | 2056.5 | 2156 | 640 | 25 | 216 | 0 | 106 | 0 | [7 empty] | Total Energy | 253.1879 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4529 | 900 | 2061 | 2024 | 610 | 25 | 193 | 0 | 104 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4539 | 900 | 2067.5 | 1834.5 | 600 | 25 | 145.5 | 0 | 104 | 0 | [7 empty] | Energy Requirement | 253.1879
3:00 | 4549 | 900 | 2074 | 1645 | 590 | 25 | 98 | 0 | 104 | 0
3:30 | 4558.5 | 899.5 | 2043 | 1542.5 | 569.5 | 25 | 65.5 | 0 | 102 | 0 | [6 empty] | Shortage
4:00 | 4568 | 899 | 2012 | 1440 | 549 | 25 | 33 | 0 | 100 | 0
4:30 | 4566.5 | 899 | 2008.5 | 1280.5 | 549.5 | 25 | 16.5 | 0 | 95 | 0
5:00 | 4565 | 899 | 2005 | 1121 | 550 | 25 | 0 | 0 | 90 | 0
5:30 | 4544 | 670 | 2010 | 1094 | 530 | 25 | 0 | 0 | 85 | 2.5
6:00 | 4523 | 441 | 2015 | 1067 | 510 | 25 | 0 | 0 | 80 | 5
6:30 | 4464 | 433 | 1996.5 | 1062.5 | 495 | 25 | 0 | 0 | 81 | 12 |  |  |  |  | Coal
7:00 | 4405 | 425 | 1978 | 1058 | 480 | 25 | 0 | 0 | 82 | 19
7:30 | 4421.5 | 425.5 | 1984.5 | 1054.5 | 475 | 25 | 0 | 0 | 87 | 28 |  |  |  | Oil |  |  |  | ,
8:00 | 4438 | 426 | 1991 | 1051 | 470 | 25 | 0 | 0 | 92 | 37
8:30 | 4514.5 | 425.5 | 1981.5 | 1217 | 480 | 25 | 5 | 0 | 93 | 37
9:00 | 4591 | 425 | 1972 | 1383 | 490 | 25 | 10 | 0 | 94 | 37
9:30 | 4570.5 | 425.5 | 1941.5 | 1501 | 490 | 25 | 35 | 0 | 93 | 44
10:00 | 4550 | 426 | 1911 | 1619 | 490 | 25 | 60 | 0 | 92 | 51
10:30 | 4531 | 426 | 1893 | 1833.5 | 490 | 25 | 100 | 0 | 95 | 54
11:00 | 4512 | 426 | 1875 | 2048 | 490 | 25 | 140 | 0 | 98 | 57
11:30 | 4548 | 426 | 1871 | 2199 | 495 | 25 | 145 | 0 | 95 | 65.5
12:00 | 4584 | 426 | 1867 | 2350 | 500 | 25 | 150 | 0 | 92 | 74
12:30 | 4582 | 426 | 1845.5 | 2509 | 505 | 25 | 175 | 0 | 93 | 77
13:00 | 4580 | 426 | 1824 | 2668 | 510 | 25 | 200 | 0 | 94 | 80
13:30 | 4580 | 426 | 1824 | 2668 | 510 | 25 | 200 | 0 | 94 | 80
14:00 | 4580 | 426 | 1824 | 2668 | 510 | 25 | 200 | 0 | 94 | 80
14:30 | 4453 | 663 | 1821 | 2803 | 510 | 25 | 218.5 | 0 | 107 | 73.5
15:00 | 4326 | 900 | 1818 | 2938 | 510 | 25 | 237 | 0 | 120 | 67
15:30 | 4303 | 899.5 | 1815.5 | 2845 | 510 | 25 | 237 | 0 | 117 | 56.5
16:00 | 4280 | 899 | 1813 | 2752 | 510 | 25 | 237 | 0 | 114 | 46
16:30 | 4296 | 899 | 1803 | 2586.5 | 510 | 25 | 219.5 | 0 | 109 | 32
17:00 | 4312 | 899 | 1793 | 2421 | 510 | 25 | 202 | 0 | 104 | 18
17:30 | 4256 | 899.5 | 1730 | 2314.5 | 510 | 25 | 184.5 | 0 | 105 | 12.5
18:00 | 4200 | 900 | 1667 | 2208 | 510 | 25 | 167 | 0 | 106 | 7
18:30 | 4358.5 | 899.5 | 1744.5 | 2500 | 529.5 | 25 | 251.5 | 0 | 116 | 3.5
19:00 | 4517 | 899 | 1822 | 2792 | 549 | 25 | 336 | 0 | 126 | 0
19:30 | 4456 | 899 | 1919 | 3665 | 690 | 25 | 455 | 0 | 122 | 0
20:00 | 4408 | 899 | 1925 | 3902 | 680 | 25 | 562 | 0 | 124 | 0
20:30 | 4409.5 | 899 | 1913 | 3961 | 680 | 25 | 571 | 0 | 138 | 0
21:00 | 4411 | 899 | 1901 | 4020 | 680 | 25 | 580 | 0 | 152 | 0
21:30 | 4431 | 899 | 1910 | 3893.5 | 680 | 25 | 584 | 0 | 153 | 0
22:00 | 4451 | 899 | 1919 | 3767 | 680 | 25 | 588 | 0 | 154 | 0
22:30 | 4467.5 | 899 | 1919 | 3707 | 675 | 25 | 560 | 0 | 154 | 0
23:00 | 4484 | 899 | 1919 | 3647 | 670 | 25 | 532 | 0 | 154 | 0
23:30 | 4477.5 | 899 | 1947 | 3647 | 660 | 25 | 532 | 0 | 153 | 0 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 4471 | 899 | 1975 | 3647 | 650 | 25 | 532 | 0 | 152 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 100 | 95 | 95 | 95 | 95 | 95 | 95 | 95 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 13 | 17 | 17 | 17 | 17 | 17 |  |  |  | 4 | 17 | 17 | 17 | 17 | 17 | 17 | 370035
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 1 | 4 | 9 | 7 | 6 | 8 | 10 | 3 | 5 | 3 | 1 | 0 | [8 empty] | 63045
6 | Sikalbaha 225MW CCPP (Gas) | 202 | 203 | 203 | 205 | 205 | 216 | 210 | 205 | 217 | 205 | 205 | 212 | 205 | 205 | 208 | 203 | 203 | 203 |  | 218 | 216 | 203 | 203 | 203 | 207 | 203 | 4839828
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2351387
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 39 | 34 | 17 | [5 empty] | 0 | [9 empty] | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 639233
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2599406
| Daudkandi 200 MW PP (B.Trac) | [21 empty] | 80 | 80 | 20 |  |  | 155712
14 | Titas 50 MW Peaking PP | [20 empty] | 38 | 50 | 50 | 50 | 50 | 50 | 232328
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 120 | 95 | 95 | 95 | 96 | 96 | 75 | 145 | 150 | 151 | 150 | 182 | 179 | 150 | 90 | 90 | 90 | 37 |  | 60 | 90 | 91 | 90 | 90 | 92 | 92 | 2863000
17 | Siddhirganj 335 MW CCPP | 338 | 336 | 335 | 334 | 334 | 270 | 270 | 290 | 331 | 331 | 331 | 328 | 327 | 270 | 270 | 270 | 270 | 250 |  | 318 | 327 | 329 | 332 | 336 | 333 | 334 | 7474794
18 | Kodda 300 MW PP Unit-2 (Summit) | [10 empty] | 35 | 97 | 175 | 208 | 208 | 208 | 208 | 220 |  | 225 | 225 | 225 | 225 | 225 | 225 | 225 | 2752472
19 | Ashuganj 195MW PP (APSCL-United) | 26 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 284363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4410000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2105718
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 26 | 26 | 23 | 23 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 556416
33 | Ashuganj 225 MW CCPP | 170 | 167 | 152 | 201 | 207 | 209 | 208 | 197 | 199 | 190 | 198 | 205 | 202 | 210 | 204 | 213 | 211 | 215 |  | 197 | 195 | 194 | 206 | 212 | 210 | 217 | 4832000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 285 | 270 | 270 | 290 | 280 | 260 | 300 | 265 | 270 | 290 | 265 | 275 | 290 | 270 | 265 | 270 |  | 325 | 295 | 270 | 270 | 270 | 280 | 265 | 6724000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 280 | 270 | 265 | 285 | 280 | 275 | 310 | 275 | 280 | 295 | 275 | 270 | 285 | 260 | 260 | 265 |  | 320 | 290 | 265 | 260 | 260 | 275 | 260 | 6916200
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 416640
36 | Chandpur 150 MW CCPP | 131 | 133 | 133 | 132 | 132 | 133 | 134 | 132 | 133 | 135 | 134 | 133 | 128 | 132 | 133 | 133 | 132 | 133 |  | 132 | 133 | 133 | 133 | 127 | 132 | 133 | 3152710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7126250
41 | Haripur 360MW CCPP(HPL) | 331 | 337 | 346 | 349 | 349 | 349 | 321 | 280 | 242 | 214 | 181 | 172 | 158 | 152 | 156 | 161 | 163 | 168 |  | 157 | 137 | 133 | 127 | 155 | 185 | 212 | 5462000
42 | RPCL 210MW CCPP | 188 | 199 | 202 | 201 | 204 | 202 | 185 | 183 | 166 | 142 | 124 | 126 | 121 | 119 | 120 | 131 | 139 | 140 |  | 131 | 130 | 128 | 118 | 119 | 121 | 136 | 3585920
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 9 | 22 | 13 | 15 | 21 | 30 | 42 | 43 | 40 | 32 | 10 | 5 | [8 empty] | 289080
44 | Fenchugonj CCPP Phase-1
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 990000
46 | Shajibazar 330 MW CCPP | 162 | 162 | 162 | 163 | 164 | 162 | 161 | 163 | 162 | 162 | 162 | 161 | 162 | 162 | 163 | 162 | 162 | 162 |  | 160 | 162 | 164 | 164 | 161 | 163 | 162 | 3613000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 61 | 62 | 40 | 40 | 50 | 61 |  | 60 | 56 | 61 | 56 | 62 | 62 | 62 | 1401120
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 78 | 80 | 81 | 81 | 81 | 81 | 40 |  | 81 | 81 | 81 | 81 | 82 | 82 | 82 | 1884480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 218 | 191 | 191 | 191 | 191 | 191 | 224 | 219 | 219 | 219 | 219 | 206 | 206 | 206 | 179 |  | 220 | 220 | 219 | 219 | 219 | 219 | 219 | 5038160
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 |  | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 392000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 8 | 8 | 8 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 210060
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 0 | 177408
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 47 | 47 | 47 | 47 | 47 | 47 | 25 |  | 40 | 47 | 47 | 47 | 47 | 47 | 47 | 1102800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 367248
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 295 | 300 | 290 | 300 | 300 | 300 | 305 | 305 | 300 | 300 | 305 | 295 | 300 | 300 | 310 | 285 |  | 310 | 315 | 305 | 290 | 295 | 285 | 310 | 7302003
| Bibiyana South 400 MW | 400 | 401 | 401 | 400 | 400 | 400 | 320 | 320 | 320 | 401 | 388 | 385 | 390 | 350 | 350 | 350 | 351 | 350 |  | 383 | 385 | 395 | 398 | 400 | 394 | 401 | 8974500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | [5 empty] | 5 | 17 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 922682
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | [6 empty] | 16 | 17 | 17 | 18 | 24 | 10 | 6 | 6 | 6 | 6 |  | 6 | 6 | 5 | 5 | 5 | 6 | 6 | 225840
60 | Barabkunda 22 MW PP (Regent) | [9 empty] | 0
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 471240
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 |  |  | 16 | 19 | 19 | 402192
63 | Impoprt (Tripura) | 108 | 104 | 104 | 100 | 90 | 80 | 82 | 92 | 94 | 92 | 98 | 92 | 94 | 98 | 120 | 114 | 104 | 106 |  | 126 | 122 | 124 | 152 | 154 | 154 | 152 | 2577600
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 33 | 33 | 33 | 33 | 30 | 10 | 4 | 4 | 3 | 3 | 3 | 5 | 4 | 4 | 6 | 2 |  | 7 | 11 | 16 | 28 | 30 | 31 | 31 | 439200
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 425952
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255780
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 17 | 18 | 18 | 20 | 20 | 20 | 21 | 21 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 505560
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 29 | 29 | 28 |  | 18 | 18 | 29 | 29 | 29 | 30 | 30 | 679320
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 28 | 33 | 33 | 33 | 10 | 25 | 25 | 25 |  | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 739100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 816100
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 96 | 98 | 96 | 100 | 101 | 101 | 100 | 99 | 64 |  | 101 | 101 | 101 | 101 | 100 | 100 | 100 | 2295818
| Feni Lanka Power | 36 | 36 | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 36 | 17 |  | 17 | 17 | 17 | 100 | 100 | 100 | 100 | 882360
| Chowmuhani 113 MW | 110 | 110 | 110 | 110 | 26 | 26 | 26 | 34 | 110 | 120 | 119 | 119 | 118 | 117 | 116 | 116 | 118 | 65 |  | 90 | 113 | 117 | 117 | 111 | 113 | 111 | 2452800
| Manikgonj 162MW PP(MPGL) | 17 | [7 empty] | 0 | 23 | 86 | 108 | 108 | 108 | 108 | 54 | 54 | 54 |  | 69 | 126 | 126 | 126 | 126 | 126 | 126 | 1539360
77 | Siddhirganj 100 PP(Dutch Bangla) | 50 | 50 | 50 | 50 | 30 | 8 | 7 | 8 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 60 | 80 | 91 | 96 | 100 | 100 | 100 | 1412160
78 | Gazipur 52 MW PP | 25 | 25 | 25 |  |  |  |  | 4 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 33 | 40 | 42 | 42 | 42 | 42 | 572640
79 | Kodda 150MW PP | 32 | 16 | 16 | 16 |  |  |  |  | 10 | 60 | 140 | 150 | 150 | 150 | 150 | 150 | 115 | 80 |  | 133 | 150 | 150 | 150 | 150 | 150 | 150 | 2034720
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 188160
81 | Jangalia 52 MW PP (Lakdanavi) | 22 | 16 | 16 | 16 |  |  |  |  | 4 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 32 | 34 | 34 | 41 | 43 | 43 | 43 | 493776
| Gazipur 100 MW PP | 86 | 86 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1808400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 2 | 3 | 4 | 5 | 3 | 6 | 6 | 6 | 4 | 3 | 1 | 0 | [8 empty] | 38400
| Jodiac Power | 54 | 54 | 54 | 54 | 50 | 43 | 35 | 35 | 35 | 35 | 35 | 35 | 39 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 1145771
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2724024
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 17 | 62 | 68 | 62 | 63 | 62 | 63 | 348847
86 | Meghnaghat CCPP ( Summit) | 275 | 280 | 295 | 285 | 285 | 300 | 300 | 270 | 285 | 270 | 285 | 290 | 245 | 285 | 295 | 280 | 260 | 270 |  | 290 | 280 | 260 | 260 | 245 | 275 | 260 | 6750458
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [10 empty] | 1 | 20 | 66 | 101 | 104 | 104 | 63 | 53 |  | 69 | 104 | 104 | 104 | 104 | 104 | 104 | 1141440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 100 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 2220000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 43 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1248825
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 16 | 32 | 48 | 64 | 102 | 102 | 64 | 40 | 40 |  | 84 | 102 | 102 | 102 | 102 | 102 | 60 | 1025568
95 | Patenga 50MW PP (Baraka) | [19 empty] | 1 | 13 | 38 | 50 | 50 | 50 | 50 | 242880
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 0 | [14 empty] | 0 | 0
97 | katpotti 52 MW
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [11 empty] | 15 | 40 | 55 | 55 | 55 | 30 | 30 |  | 34 | 55 | 55 | 55 | 55 | 55 | 55 | 601909
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 704021
101 | Kushiara 163 MW CCPP (KP) | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3449372
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 0 | 1 | 1 | 3 | 3 | 3 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 12700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1031400
104 | Keranigonj 300 MW PP (APR) | [20 empty] | 109 | 138 | 130 | 27 |  | 0 | 297623
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 50 | 50 | 50 | 25 |  | 0 | 138215
106 | Mymensingh 200 MW PP (United) | 175 | 175 | 176 | 150 | 80 | 40 | 40 | 40 | 40 | 24 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 41 | 157 | 156 | 156 | 170 | 163 | 165 | 1936800
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 53 | 100 | 100 | 53 |  | 0 | 239781
114 | Kodda 149 MW PP Unit-1 (Summit) | 32 | 32 | 20 | 15 | 15 | 15 | 15 | 17 | 24 | 90 | 108 | 107 | 125 | 132 | 132 | 132 | 132 | 132 |  | 130 | 130 | 129 | 129 | 132 | 132 | 132 | 2088000
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 70 | 50 | 50 | 50 | 50 | 50 | 70 | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2019840
116 | Chandpur 200MW (Desh energy) | 120 | 120 | 85 | 34 | 17 | 17 | 17 | 19 | 50 | 72 | 173 | 180 | 179 | 181 | 180 | 180 | 180 | 180 |  | 179 | 180 | 180 | 180 | 179 | 173 | 180 | 3126720
117 | Ashuganj 150MW PP (Midland) | 50 | 50 | [6 empty] | 6 | 31 | 105 | 135 | 140 | 140 | 137 | 138 | 138 | 143 |  | 147 | 147 | 148 | 147 | 148 | 148 | 148 | 2149454
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 376 | 377 | 359 | 359 | 358 | 402 | 402 | 403 | 404 | 404 | 379 | 379 | 378 | 378 | 378 |  | 404 | 399 | 404 | 404 | 402 | 403 | 402 | 9424000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 103 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 107 | 107 | 2617200
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 70 | 70 | [6 empty] | 10 | 10 | 30 | 30 | 50 | 50 | 50 | 50 | 50 | 10 |  | 65 | 100 | 100 | 100 | 88 | 90 | 100 | 1054080
| Anlima Energy Ltd. | [25 empty] | 0 | 0
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 20 | 35 | 35 | 35 | 35 | 35 | 35 | 537480
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 6 | 9 | 21 | 18 | 20 | 12 | 32 | 11 | 3 | 3 | 1 | [8 empty] | 114985
120 | Eastern Zone Total | 7271 | 7118 | 6892 | 6669 | 6346 | 6261 | 6092 | 6095 | 6583 | 6791 | 7176 | 7474 | 7563 | 7624 | 7546 | 7441 | 7252 | 6818 |  | 7760 | 8425 | 8568 | 8686 | 8503 | 8438 | 8415 | 176646769
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [21 empty] | 2 | 2 | 3 |  |  | 5760
| Khulna 225 MW CCPP | [21 empty] | 60 | 80 | 60 |  | 0 | 149363
129 | Rupsha 105 MW PP (Orion rupsha) | 91 | 35 | 17 | 17 | [9 empty] | 30 | 53 | 53 | 53 | 35 |  | 53 | 90 | 91 | 91 | 91 | 91 | 91 | 968640
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 223 | 223 | 223 | 223 | 223 | 222 | 222 | 202 | 168 | 168 | 167 | 161 | 167 | 169 | 168 | 132 | 130 |  | 142 | 221 | 220 | 221 | 221 | 222 | 221 | 4729000
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 5 | 16 | 16 | 16 | 16 | 16 | 16 | 78912
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 294107
| Bhola 225 MW CCPP | 88 | 88 | 88 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 85 | 83 | 83 | 84 | 84 | 84 | 86 | 2057072
140 | Bhola 33 MW PP (Venture) | 20 | 27 | 23 | 19 | 20 | 18 | 16 | 15 | 13 | 13 | 14 | 15 | 14 | 12 | 21 | 19 | 20 | 20 |  | 30 | 31 | 31 | 33 | 33 | 34 | 34 | 502266
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 70 | 50 | [16 empty] | 7 | 100 | 97 | 100 | 100 | 100 | 100 | 777600
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 900 | 900 | 900 | 899 | 899 | 441 | 425 | 426 | 425 | 426 | 426 | 426 | 426 | 423 | 900 | 899 | 899 | 900 |  | 899 | 899 | 899 | 899 | 899 | 899 | 899 | 17525090
147 | Bheramara 410 MW CCPP | 350 | 355 | 360 | 365 | 375 | 370 | 385 | 370 | 370 | 315 | 300 | 305 | 360 | 360 | 360 | 355 | 360 | 355 |  | 360 | 280 | 285 | 295 | 320 | 320 | 345 | 8575776
148 | Payra 1320 MW | 520 | 460 | 440 | 400 | 400 | 360 | 330 | 320 | 340 | 340 | 340 | 350 | 360 | 360 | 360 | 360 | 360 | 360 |  | 400 | 540 | 530 | 530 | 530 | 520 | 500 | 10730600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 3688300
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | [17 empty] | 10 | 43 | 50 | 50 | 50 | 50 | 50 | 336112
| Sirajgonj 6.55 MW Solar |  |  |  |  | 0 | 0 | 0 | 2 | 1 | 1 | 4 | 3 | 3 | 5 | 1 | 1 | 1 | 0 | [8 empty] | 24840
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 184 | 184 | 186 | 189 | 189 | 187 | 194 | 194 | 182 | 192 | 195 | 184 | 189 | 175 | 173 | 169 | 162 | 155 |  | 175 | 191 | 191 | 187 | 183 | 177 | 161 | 4576382
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 180 | 182 | 186 | 191 | 189 | 193 | 196 | 198 | 200 | 192 | 194 | 192 | 175 | 184 | 157 | 179 | 154 |  | 172 | 195 | 199 | 190 | 185 | 182 | 176 | 4676045
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 322 | 338 | 341 | 339 | 341 | 342 | 339 | 414 | 414 | 414 | 414 | 414 | 414 | 414 | 400 | 360 | 362 | 360 |  | 380 | 400 | 415 | 397 | 380 | 357 | 362 | 9039000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [21 empty] | 10 | 10 | 37 | 44 | 44 | 119653
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 20 | 20 | 20 | 20 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 504720
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 5 | 0 | 0 | 0 | 2 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 0 | 8 | 0 | 0 | 0 | 8 | 8 | 120942
165 | Amnura 50 MW PP(Sinha) | [10 empty] | 12 | 12 | 35 | 35 | 35 | 35 | 18 | 18 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 388030
166 | Katakhali 50 MW PP (Northern) | [21 empty] | 16 | 34 | 25 | 25 | 25 | 108165
167 | Katakhali 50 MW Peaking PP | [19 empty] | 8 | 26 | 31 | 30 | 30 | 30 | 30 | 137832
168 | Santahar 50 MW Peaking PP | [19 empty] | 12 | 25 | 36 | 35 | 35 | 35 | 35 | 179010
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 |  |  |  | 1 | 21 | 43 | 45 | 52 | 52 | 52 | 52 | 52 | 16 | 16 |  | 16 | 36 | 52 | 52 | 52 | 52 | 52 | 922560
170 | Chapainawabganj 100 MW Peaking PP | 89 | 88 | 48 | [9 empty] | 50 | 75 | 87 | 87 | 87 | 87 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 1204384
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 70 | [8 empty] | 17 | 35 | 50 | 93 | 94 | 94 | 100 | 35 | 35 |  | 45 | 90 | 110 | 113 | 113 | 113 | 113 | 1333056
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [8 empty] | 25 | 35 | 95 | 113 | 113 | 113 | 70 | 35 | 35 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1327584
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | [15 empty] | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 95 | [8 empty] | 35 | 45 | 100 | 113 | 113 | 70 | 34 | 34 |  | 102 | 113 | 113 | 113 | 113 | 113 | 113 | 1435363
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 |  |  | 1 | 2 | 4 | 4 | 4 | 4 | 3 | 2 | 1 | [8 empty] | 24927
178
178