## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-06-23 | Wednesday
|  |  | Date (day): | 2021-06-23 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14654.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15715 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-06-22 | 2021-06-23 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 190 | 200 | 200 |  | 165 | ST under S/D
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 98 | 90 | 100 | 100
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 339 | 338 | 350 | 380 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 276 | 247 | 350 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 265 | 290 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 15 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 22 | 22 | 16 | 19
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 11 | 222 | 220 | 220 | 115 |  | ST under maint.
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 102 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 150 | 133 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 55 | 55 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 51 | 51 | 51
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 2 | 275 | 290 | 290
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 66 | 104 | 135 | 135 |  | 14 | Engine problem
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 90 | 105 | 90 | 105
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 17 | 126 | 126 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 22 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5919 | 2136 | 3117 | 3866 | 4203 | 634 | 794
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 17 | 17 | 17 | 17 |  | 8 | Engine problem
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 30 | 40 | 45 |  | 5 | Engine problem
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 51 | 49 | 51 | 51 | 179 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 220 | 220 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 100 | 100 | 100 | 50 |  | Gas shortage
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 85 | 85
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 85 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 5 | 28 | 10 | 20
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 102 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 300 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 10 | 50 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 0 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 987 | 1170 | 1655 | 1645 | 591 | 111
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 183 | 220 | 220 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 280 | 310 | 330 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 280 | 310 | 330 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 40 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 0 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 0 | 5 | 50 | 50 |  |  | Ash. 230 kV GIS Bus S/D
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 23 | 150 | 150 |  |  | Ash. 230 kV GIS Bus S/D
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST Under maint.
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 133 | 165 | 160 | 180 |  | 20 | Engine problem
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 124 | 151 | 180
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 16 | 34 | 34 | 43 |  | 9 | Fuel shortage
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 17 | 21 |  | 4 | Engine problem
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 100 | 34 | 100 |  | 14 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 120 | 120 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 36 | 35 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1561 | 1692 | 2009 | 2327 | 505 | 158
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 118 | 102 | 120 | 150 | 52 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 85 | 189 | 175 | 192 |  | 8 | Engine problem
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 430 | 459 | 512.6 | 508 | 52 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 44 | 44 |  | 26 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 164 | 162 | 164 |  | 166 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 2 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 51 | 62 | 62 | 62
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 81 | 83
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 192 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 15 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 270 | 341 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 368 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 310 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1796 | 1911 | 1992 | 2030 | 0 | 349
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 826 | 753 | 905 | 905
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 115 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 160 |  |  | ST not available
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 5 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 380 | 385 | 380 | 380 | 30 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 40 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 9 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 91 | 91 | 90 | 90 |  | 15 | Engine problem
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2284 | 1311 | 1329 | 1605 | 1815 | 30 | 98
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 31 | 25 | 25 |  | 8 | Engine problem
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 83 | 85 | 86 |  | 108 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 11 | 12 | 12 | 83 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 480 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 151 | 202 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 558 | 807 | 1074 | 1185 | 83 | 116
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 65 | 65 | 65 | 65 | 6 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 39 | 30 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 34 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 38 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 189 | 166 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 180 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 392 | 356 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 35 |  | 15 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 87 | 90 | 100
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 25 | 113 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 15 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 949 | 1358 | 1670 | 1719 | 316 | 78
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 156 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21315 | 9884 | 12106 | 14654.6 | 15715 | 2335 | 1981
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9489.6524 | 11623 | 14069.917 | 15088.0097
| A. |  | 2021-06-22 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12145 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8623 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12106 | MW
| 3 | Day peak Generation : |  |  | 9884 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11623 | MW
| 4 | Evening peak Generation : |  |  | 12106 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 249.666 | MKWHr | By Solar | 0.5768 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 159.3461 | MKWHr |  | By Oil: | 53.0003 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.3806 | MKWHr |  | By Hydro: | 1.0909 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2335 | MW | Dhaka | 4084 | 4084 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 1981 | MW | Chittagong | 1244 | 1244 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4316 | MW | Khulna | 1399 | 1399 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1264.97 | MMCFD |  |  | Rajshahi | 1308 | 1308 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 168126602.946 | ii) Oil : | Taka | 404508273.5 | Comilla | 1113 | 1113 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 62518874 | Total | Taka | 635153750.446 | Mymensingh | 896 | 896 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.0055 | MKWHr. | Sylhet | 462 | 462 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -224 | MW (E to W) at | 21:00 | hrs | Barisal | 329 | 329 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -224 | MW at | 21:00 | hrs | Rangpur | 788 | 788 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 29.9° C |  |  | Total | 11623 | 11623 |  | 0
| B. |  | 2021-06-23 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 32.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15715 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10600 | MW
| 4 | Reserve(Generation end) |  |  |  | 2715 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 267.2423 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8988 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.6822 | MKWHr. | ii) HVDC Flow at Peak Time |  | 753 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5891 | MKWHr. | iii) Maximum HVDC Flow : |  | 893 | MW at | 19:30 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 75.18 |  | (b) Today: | 75.22 |  | (c) Rule Curve: |  | 81.84
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-06-22
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 338 | 303 |  | 0 | 300 | 285 | 0 | 0 | 0 | 221 | 0 | 0 | 100 | 24 | 138 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 23 | 0 | 85 | 100 | 0 | 0 | 22 | 38 | 80 | 0 | 0 | 260 | 270 | 216 | 8 | 87 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 120 | 181 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 130 | 162 | 61 | 78 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 15 | 0 | 0 | 192 | 0 | 55 | 0 | 100 | 178 | 24 | 366 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 17 | 111 | 30 | 400 | 0 | 0 | 54 | 17 | 0 | 36 | 0 |  | 733 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 0 | 0 | 0 | 65 | 43 | 16 | 87 | 0 | 0 | 38 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 0 | 188 | 0 | 409 | 91 | 0 | 35 | 0 | 70 | 0 | 0 | 0 | 420 | 223 | 0 | 0 | 0 |  | 7731 | 3343 | 11074 | 4789 | 733 | 2098 | 2308 | 570 | 49 | 407 | 120 | 0 | 0 | 75.16
2:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 340 | 347 |  | 0 | 300 | 270 | 0 | 0 | 0 | 222 | 0 | 0 | 100 | 7 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 0 | 0 | 51 | 100 | 0 | 0 | 22 | 39 | 80 | 0 | 0 | 260 | 270 | 217 | 8 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 110 | 181 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 130 | 161 | 40 | 78 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 50 | 0 | 70 | 85 | 0 | 367 | 115 | 105 | 90 | 0 | 0 | 54 | 68 | 17 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 19 | 0 |  | 845 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 27 | 0 | 0 | 0 | 65 | 0 | 0 | 87 | 0 | 0 | 38 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 12 | 0 | 190 | 0 | 399 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 223 | 0 | 0 | 0 |  | 7220 | 3222 | 10442 | 4775 | 845 | 2142 | 1747 | 550 | 49 | 224 | 110 | 0 | 0 | 75.16
3:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 341 | 351 |  | 0 | 300 | 285 | 0 | 0 | 0 | 223 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 22 | 25 | 30 | 33 | 33 | 45 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 22 | 39 | 80 | 0 | 0 | 260 | 270 | 181 | 8 | 90 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 108 | 181 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 130 | 162 | 40 | 78 | 0 | 232 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 35 | 0 | 70 | 85 | 0 | 330 | 115 | 105 | 68 | 0 | 0 | 54 | 68 | 17 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | 844 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 65 | 0 | 0 | 40 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 12 | 0 | 191 | 0 | 416 | 53 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 400 | 223 | 0 | 0 | 0 |  | 7008 | 3203 | 10211 | 4721 | 844 | 2167 | 1698 | 550 | 49 | 74 | 108 | 0 | 0 | 75.17
4:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 338 | 349 |  | 0 | 300 | 285 | 0 | 0 | 0 | 221 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 24 | 0 | 25 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 0 | 0 | 34 | 100 | 0 | 0 | 22 | 39 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 91 | 26 | 53 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 104 | 193 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 130 | 162 | 40 | 78 | 0 | 232 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 25 | 0 | 30 | 50 | 0 | 330 | 115 | 105 | 68 | 0 | 0 | 54 | 68 | 17 | 110 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | 845 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 12 | 0 | 183 | 0 | 406 | 17 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 380 | 222 | 0 | 0 | 0 |  | 6822 | 3085 | 9907 | 4720 | 845 | 2135 | 1489 | 530 | 50 | 34 | 104 | 0 | 0 | 75.17
5:00 | 0 | 0 | 0 | 185 | 0 | 100 | 0 | 338 | 353 |  | 0 | 300 | 270 | 0 | 0 | 0 | 224 | 0 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 22 | 25 | 30 | 33 | 33 | 24 | 0 | 25 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 0 | 0 | 10 | 100 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 260 | 270 | 181 | 8 | 90 | 26 | 53 | 0 | 35 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 100 | 197 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 130 | 163 | 40 | 78 | 0 | 225 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 15 | 0 | 0 | 17 | 0 | 330 | 115 | 105 | 68 | 0 | 0 | 54 | 17 | 17 | 113 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 18 | 0 |  | 837 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 12 | 0 | 190 | 0 | 399 | 17 | 0 | 0 | 0 | 49 | 0 | 0 | 0 | 360 | 222 | 0 | 0 | 0 |  | 6638 | 3050 | 9688 | 4721 | 837 | 2132 | 1328 | 510 | 50 | 10 | 100 | 0 | 0 | 75.18
6:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 340 | 350 |  | 0 | 300 | 260 | 0 | 0 | 0 | 170 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 22 | 25 | 30 | 33 | 25 | 0 | 0 | 26 | 25 | 100 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 0 | 100 | 0 | 0 | 22 | 40 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 91 | 26 | 53 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 96 | 197 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 110 | 164 | 40 | 40 | 0 | 192 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 65 | 0 | 15 | 1 | 0 | 17 | 0 | 328 | 115 | 105 | 68 | 0 | 0 | 54 | 17 | 17 | 26 | 0 | 400 | 0 | 1 | 0 | 0 | 0 | 18 | 1 |  | 827 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 130 | 0 | 336 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 222 | 0 | 0 | 0 |  | 6187 | 2704 | 8891 | 4518 | 827 | 1969 | 977 | 450 | 51 | 0 | 96 | 3 | 0 | 75.18
7:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 359 | 348 |  | 0 | 300 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 26 | 25 | 65 | 0 | 8 | 216 | 0 | 100 | 0 |  | 0 | 0 | 0 | 100 | 0 | 0 | 22 | 34 | 80 | 0 | 0 | 300 | 315 | 214 | 0 | 91 | 26 | 53 | 0 | 0 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 90 | 105 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 110 | 162 | 40 | 40 | 0 | 192 | 18 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 67 | 0 | 15 | 6 | 0 | 17 | 0 | 375 | 115 | 105 | 68 | 0 | 0 | 54 | 17 | 17 | 26 | 0 | 400 | 0 | 5 | 0 | 0 | 0 | 18 | 3 |  | 827 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 130 | 0 | 12 | 0 | 137 | 0 | 352 | 30 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 222 | 0 | 0 | 0 |  | 6075 | 2678 | 8753 | 4399 | 827 | 1986 | 965 | 420 | 51 | 0 | 90 | 15 | 0 | 75.19
8:00 | 0 | 0 | 0 | 185 | 0 | 52 | 0 | 330 | 355 |  | 0 | 300 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 3 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 20 | 22 | 25 | 30 | 33 | 33 | 13 | 0 | 26 | 25 | 100 | 0 | 13 | 204 | 0 | 100 | 0 |  | 4 | 0 | 0 | 100 | 0 | 0 | 22 | 9 | 80 | 0 | 0 | 260 | 290 | 182 | 0 | 91 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 11 | 33 | 18 | 90 | 122 | 8 | 21 | 1 | 44 | 42 | 14 | 0 | 110 | 162 | 40 | 75 | 0 | 185 | 18 | 0 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 85 | 0 | 15 | 11 | 20 | 53 | 0 | 306 | 115 | 90 | 68 | 1 | 0 | 54 | 36 | 17 | 49 | 10 | 355 | 0 | 7 | 14 | 7 | 0 | 18 | 2 |  | 826 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 174 | 0 | 285 | 80 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 280 | 180 | 0 | 0 | 0 |  | 5975 | 2648 | 8623 | 4198 | 826 | 1747 | 1241 | 430 | 51 | 16 | 90 | 24 | 0 | 75.19
9:00 | 0 | 0 | 0 | 185 | 0 | 52 | 0 | 306 | 292 |  | 0 | 300 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 22 | 25 | 30 | 33 | 33 | 10 | 0 | 26 | 25 | 100 | 0 | 17 | 216 | 0 | 100 | 0 |  | 18 | 0 | 0 | 70 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 285 | 310 | 199 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 11 | 33 | 18 | 90 | 119 | 8 | 21 | 0 | 44 | 42 | 14 | 0 | 110 | 163 | 40 | 75 | 0 | 185 | 18 | 0 | 9 | 295 | 16 | 5 | 0 | 0 | 0 | 0 | 85 | 0 | 19 | 15 | 20 | 85 | 0 | 333 | 115 | 90 | 68 | 2 | 0 | 54 | 51 | 17 | 55 | 10 | 350 | 0 | 9 | 17 | 17 | 0 | 18 | 10 |  | 827 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 12 | 0 | 169 | 0 | 335 | 91 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 290 | 150 | 0 | 0 | 0 |  | 6127 | 2742 | 8869 | 4308 | 827 | 1728 | 1354 | 440 | 51 | 32 | 90 | 39 | 0 | 75.19
10:00 | 0 | 0 | 0 | 185 | 0 | 85 | 0 | 345 | 292 |  | 0 | 300 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 24 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 45 | 22 | 25 | 30 | 33 | 33 | 28 | 0 | 26 | 25 | 100 | 0 | 17 | 217 | 0 | 100 | 0 |  | 23 | 0 | 0 | 85 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 295 | 320 | 203 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 18 | 90 | 119 | 8 | 21 | 0 | 44 | 42 | 14 | 0 | 130 | 162 | 50 | 78 | 0 | 185 | 18 | 0 | 9 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 85 | 0 | 48 | 17 | 20 | 89 | 0 | 376 | 115 | 90 | 68 | 4 | 0 | 54 | 51 | 34 | 76 | 10 | 350 | 0 | 28 | 17 | 17 | 0 | 18 | 6 |  | 826 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 12 | 0 | 182 | 0 | 395 | 91 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 290 | 151 | 0 | 0 | 2 |  | 6473 | 2826 | 9299 | 4441 | 826 | 1850 | 1507 | 440 | 51 | 32 | 90 | 62 | 0 | 75.19
11:00 | 0 | 0 | 0 | 185 | 0 | 95 | 0 | 339 | 306 |  | 0 | 300 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 40 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 38 | 0 | 26 | 25 | 100 | 0 | 17 | 212 | 0 | 100 | 0 |  | 24 | 0 | 0 | 85 | 0 | 0 | 22 | 4 | 80 | 0 | 0 | 265 | 290 | 187 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 21 | 100 | 118 | 8 | 21 | 1 | 44 | 42 | 45 | 0 | 130 | 163 | 51 | 78 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 8 | 0 | 0 | 0 | 0 | 85 | 0 | 50 | 19 | 60 | 112 | 0 | 375 | 115 | 90 | 92 | 5 | 0 | 38 | 83 | 34 | 115 | 10 | 301 | 0 | 9 | 17 | 17 | 0 | 18 | 13 |  | 827 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 12 | 0 | 198 | 0 | 413 | 91 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 290 | 151 | 0 | 0 | 1 |  | 6654 | 2886 | 9540 | 4381 | 827 | 1919 | 1736 | 440 | 51 | 32 | 100 | 54 | 0 | 75.2
12:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 339 | 276 |  | 0 | 300 | 275 | 0 | 0 | 0 | 11 | 0 | 0 | 100 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 26 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 85 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 345 | 295 | 183 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 21 | 100 | 118 | 8 | 21 | 3 | 44 | 42 | 50 | 0 | 130 | 162 | 51 | 78 | 0 | 219 | 18 | 0 | 9 | 295 | 16 | 5 | 0 | 2 | 0 | 0 | 85 | 0 | 66 | 19 | 100 | 133 | 0 | 367 | 115 | 90 | 105 | 6 | 0 | 36 | 110 | 34 | 120 | 10 | 310 | 0 | 56 | 17 | 17 | 0 | 18 | 22 |  | 826 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 86 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 9 | 188 | 0 | 392 | 91 | 0 | 25 | 0 | 0 | 0 | 6 | 15 | 290 | 151 | 0 | 0 | 0 |  | 6910 | 2974 | 9884 | 4490 | 826 | 1873 | 1955 | 440 | 51 | 37 | 100 | 112 | 0 | 75.2
13:00 | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 339 | 256 |  | 0 | 300 | 279 | 0 | 0 | 0 | 150 | 0 | 0 | 100 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 33 | 33 | 42 | 0 | 0 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 85 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 310 | 290 | 183 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 21 | 102 | 117 | 8 | 21 | 1 | 44 | 42 | 51 | 0 | 130 | 165 | 51 | 75 | 0 | 219 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 15 | 0 | 0 | 85 | 0 | 95 | 17 | 100 | 160 | 0 | 367 | 115 | 105 | 105 | 5 | 0 | 30 | 110 | 34 | 118 | 10 | 340 | 0 | 54 | 17 | 17 | 0 | 18 | 6 |  | 827 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 86 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 60 | 187 | 0 | 367 | 91 | 0 | 35 | 0 | 0 | 0 | 6 | 35 | 290 | 151 | 0 | 0 | 1 |  | 7048 | 3034 | 10082 | 4614 | 827 | 1829 | 2116 | 440 | 25 | 39 | 102 | 90 | 0 | 0
14:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 338 | 252 |  | 0 | 300 | 285 | 0 | 0 | 0 | 150 | 0 | 0 | 100 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 26 | 33 | 33 | 42 | 0 | 22 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 90 | 0 | 0 | 22 | 10 | 80 | 0 | 0 | 315 | 270 | 186 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 21 | 104 | 116 | 8 | 21 | 2 | 44 | 42 | 50 | 0 | 130 | 163 | 61 | 78 | 0 | 219 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 14 | 0 | 0 | 85 | 0 | 95 | 17 | 100 | 160 | 0 | 374 | 115 | 105 | 105 | 3 | 0 | 38 | 110 | 34 | 116 | 10 | 340 | 0 | 34 | 17 | 17 | 0 | 18 | 9 |  | 826 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 86 | 20 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 12 | 60 | 185 | 0 | 374 | 91 | 0 | 35 | 0 | 0 | 0 | 6 | 35 | 310 | 151 | 0 | 0 | 4 |  | 7060 | 3021 | 10081 | 4571 | 826 | 1826 | 2132 | 460 | 47 | 40 | 104 | 75 | 0 | 0
15:00 | 0 | 0 | 0 | 185 | 0 | 99 | 0 | 351 | 252 |  | 0 | 300 | 280 | 0 | 0 | 0 | 180 | 0 | 0 | 100 | 48 | 40 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 22 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 92 | 0 | 0 | 22 | 4 | 80 | 0 | 0 | 325 | 285 | 216 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 112 | 117 | 8 | 21 | 1 | 44 | 42 | 50 | 0 | 163 | 160 | 60 | 78 | 0 | 219 | 18 | 0 | 9 | 305 | 16 | 0 | 0 | 14 | 0 | 0 | 85 | 0 | 95 | 13 | 100 | 160 | 0 | 368 | 115 | 105 | 105 | 1 | 0 | 54 | 110 | 34 | 113 | 10 | 340 | 0 | 44 | 17 | 17 | 0 | 18 | 5 |  | 826 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 60 | 196 | 0 | 376 | 91 | 0 | 35 | 0 | 0 | 0 | 5 | 35 | 320 | 151 | 0 | 0 | 1 |  | 7228 | 3037 | 10265 | 4679 | 826 | 1880 | 2133 | 470 | 47 | 48 | 112 | 70 | 0 | 0
16:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 343 | 265 |  | 0 | 300 | 280 | 0 | 0 | 0 | 180 | 0 | 0 | 100 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 22 | 25 | 100 | 0 | 15 | 203 | 0 | 100 | 0 |  | 24 | 0 | 0 | 97 | 0 | 0 | 22 | 4 | 80 | 0 | 0 | 315 | 275 | 215 | 0 | 90 | 26 | 53 | 0 | 0 | 0 | 0 | 16 | 19 | 11 | 33 | 21 | 106 | 118 | 8 | 21 | 1 | 43 | 42 | 50 | 0 | 163 | 162 | 60 | 80 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 0 | 0 | 15 | 0 | 0 | 85 | 0 | 77 | 9 | 100 | 160 | 0 | 372 | 115 | 105 | 105 | 1 | 0 | 37 | 110 | 34 | 110 | 10 | 340 | 0 | 19 | 17 | 17 | 0 | 18 | 7 |  | 827 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 85 | 20 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 188 | 0 | 12 | 0 | 190 | 0 | 377 | 91 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 320 | 150 | 0 | 0 | 2 |  | 7166 | 2974 | 10140 | 4643 | 827 | 1901 | 2048 | 470 | 47 | 56 | 106 | 42 | 0 | 0
17:00 | 0 | 0 | 0 | 185 | 0 | 97 | 0 | 342 | 280 |  | 0 | 300 | 260 | 0 | 0 | 0 | 180 | 0 | 0 | 50 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 22 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 0 | 100 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 310 | 265 | 214 | 0 | 90 | 26 | 53 | 0 | 0 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 108 | 116 | 8 | 21 | 1 | 43 | 42 | 50 | 0 | 163 | 165 | 61 | 80 | 0 | 219 | 18 | 0 | 9 | 295 | 16 | 8 | 0 | 15 | 0 | 0 | 85 | 0 | 64 | 5 | 50 | 90 | 0 | 367 | 115 | 105 | 105 | 1 | 0 | 37 | 110 | 34 | 114 | 10 | 340 | 0 | 13 | 17 | 17 | 0 | 18 | 5 |  | 827 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 86 | 19 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 186 | 0 | 12 | 0 | 188 | 0 | 354 | 35 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 320 | 151 | 0 | 0 | 1 |  | 6970 | 2892 | 9862 | 4628 | 827 | 1889 | 1807 | 470 | 47 | 58 | 108 | 28 | 0 | 0
18:00 | 0 | 0 | 0 | 185 | 0 | 55 | 0 | 340 | 282 |  | 0 | 300 | 260 | 0 | 0 | 4 | 180 | 0 | 0 | 50 | 48 | 48 | 1 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 22 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 17 | 70 | 0 | 5 | 22 | 11 | 80 | 0 | 0 | 310 | 265 | 215 | 0 | 90 | 26 | 51 | 0 | 0 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 104 | 114 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 130 | 163 | 61 | 50 | 0 | 219 | 18 | 0 | 9 | 280 | 16 | 8 | 0 | 34 | 0 | 0 | 85 | 0 | 51 | 1 | 30 | 85 | 0 | 331 | 115 | 105 | 68 | 0 | 0 | 54 | 51 | 34 | 45 | 10 | 340 | 0 | 3 | 17 | 17 | 0 | 18 | 2 |  | 827 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 18 | 0 | 0 | 0 | 65 | 0 | 6 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 12 | 0 | 177 | 0 | 359 | 35 | 0 | 35 | 0 | 0 | 0 | 0 | 35 | 320 | 131 | 0 | 0 | 0 |  | 6617 | 2805 | 9422 | 4567 | 827 | 1762 | 1568 | 470 | 47 | 71 | 104 | 6 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 110 | 80 | 0 | 340 | 280 |  | 0 | 300 | 272 | 0 | 0 | 15 | 150 | 0 | 0 | 55 | 60 | 70 | 10 | 0 | 0 | 0 | 38 | 17 | 55 | 22 | 25 | 18 | 33 | 33 | 30 | 0 | 24 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 102 | 100 | 0 | 6 | 22 | 5 | 80 | 0 | 0 | 315 | 270 | 214 | 0 | 90 | 26 | 51 | 0 | 0 | 0 | 33 | 34 | 19 | 11 | 33 | 21 | 120 | 114 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 130 | 163 | 61 | 50 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 102 | 0 | 0 | 93 | 0 | 51 | 0 | 75 | 90 | 0 | 372 | 115 | 105 | 77 | 0 | 0 | 54 | 60 | 100 | 57 | 40 | 365 | 17 | 0 | 24 | 17 | 0 | 19 | 0 |  | 892 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 27 | 0 | 0 | 0 | 65 | 50 | 10 | 70 | 6 | 8 | 24 | 8 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 12 | 0 | 175 | 0 | 376 | 53 | 0 | 40 | 0 | 42 | 0 | 0 | 50 | 320 | 160 | 0 | 0 | 0 |  | 7326 | 3172 | 10498 | 4719 | 892 | 1845 | 2044 | 470 | 49 | 359 | 120 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 185 | 170 | 96 | 0 | 337 | 275 |  | 0 | 300 | 230 | 0 | 0 | 55 | 221 | 0 | 0 | 100 | 86 | 150 | 10 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 18 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 102 | 100 | 0 | 20 | 22 | 6 | 80 | 0 | 0 | 300 | 265 | 217 | 8 | 85 | 26 | 51 | 0 | 0 | 0 | 50 | 34 | 19 | 11 | 33 | 21 | 128 | 102 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 163 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 275 | 16 | 11 | 0 | 240 | 0 | 0 | 184 | 0 | 60 | 0 | 100 | 160 | 0 | 367 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 116 | 50 | 400 | 72 | 0 | 126 | 17 | 0 | 36 | 0 |  | 893 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 23 | 0 | 0 | 0 | 65 | 50 | 16 | 86 | 35 | 16 | 40 | 16 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 65 | 183 | 0 | 323 | 91 | 0 | 55 | 0 | 80 | 0 | 0 | 80 | 380 | 202 | 0 | 0 | 0 |  | 8415 | 3508 | 11923 | 4864 | 893 | 1898 | 3067 | 530 | 49 | 494 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 190 | 90 | 0 | 341 | 257 |  | 0 | 300 | 255 | 0 | 0 | 15 | 190 | 0 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 25 | 0 | 102 | 100 | 0 | 22 | 22 | 15 | 80 | 0 | 0 | 260 | 265 | 182 | 8 | 86 | 26 | 54 | 0 | 0 | 0 | 50 | 34 | 19 | 11 | 33 | 21 | 124 | 105 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 163 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 260 | 16 | 2 | 0 | 240 | 0 | 0 | 184 | 0 | 64 | 0 | 100 | 155 | 1 | 368 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 116 | 50 | 400 | 53 | 0 | 125 | 0 | 0 | 36 | 0 |  | 893 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 30 | 0 | 0 | 0 | 65 | 50 | 42 | 86 | 35 | 43 | 40 | 32 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 75 | 179 | 0 | 340 | 92 | 0 | 93 | 0 | 108 | 0 | 0 | 100 | 390 | 202 | 0 | 0 | 0 |  | 8268 | 3702 | 11970 | 4784 | 893 | 1896 | 3164 | 540 | 49 | 520 | 124 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 185 | 190 | 90 | 0 | 338 | 247 |  | 0 | 300 | 265 | 0 | 0 | 15 | 222 | 0 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 102 | 100 | 0 | 30 | 22 | 28 | 80 | 0 | 0 | 280 | 280 | 183 | 8 | 90 | 26 | 54 | 0 | 5 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 124 | 102 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 164 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 275 | 0 | 0 | 189 | 0 | 104 | 0 | 100 | 165 | 23 | 368 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 50 | 400 | 0 | 0 | 126 | 0 | 0 | 36 | 0 |  | 753 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 31 | 0 | 0 | 0 | 65 | 50 | 39 | 87 | 35 | 34 | 38 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 100 | 180 | 0 | 356 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 202 | 0 | 0 | 0 |  | 8349 | 3757 | 12106 | 4870 | 753 | 1931 | 3283 | 630 | 49 | 466 | 124 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 185 | 190 | 99 | 0 | 338 | 247 |  | 0 | 300 | 245 | 0 | 0 | 15 | 223 | 0 | 0 | 100 | 64 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 102 | 100 | 0 | 30 | 22 | 35 | 80 | 0 | 0 | 280 | 280 | 181 | 8 | 87 | 26 | 55 | 0 | 25 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 124 | 102 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 164 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 245 | 0 | 0 | 190 | 0 | 100 | 0 | 100 | 178 | 70 | 367 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 50 | 400 | 0 | 0 | 110 | 0 | 0 | 36 | 0 |  | 753 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 32 | 0 | 0 | 0 | 65 | 50 | 28 | 87 | 35 | 43 | 38 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 100 | 189 | 0 | 327 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 202 | 0 | 0 | 0 |  | 8347 | 3798 | 12145 | 4892 | 753 | 1947 | 3245 | 680 | 49 | 455 | 124 | 0 | 0 | 75.22
23:00 | 0 | 0 | 0 | 185 | 190 | 99 | 0 | 337 | 252 |  | 0 | 300 | 280 | 0 | 0 | 0 | 220 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 23 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 85 | 100 | 0 | 0 | 22 | 37 | 80 | 0 | 0 | 280 | 280 | 183 | 8 | 90 | 26 | 56 | 0 | 51 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 122 | 155 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 164 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 45 | 0 | 0 | 190 | 0 | 93 | 0 | 100 | 180 | 70 | 368 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 113 | 50 | 400 | 0 | 0 | 54 | 0 | 0 | 36 | 0 |  | 753 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 32 | 0 | 0 | 0 | 65 | 50 | 0 | 87 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 100 | 187 | 0 | 374 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 202 | 0 | 0 | 0 |  | 8100 | 3710 | 11810 | 4958 | 753 | 2028 | 2849 | 680 | 48 | 372 | 122 | 0 | 0 | 75.22
24:00 | 0 | 0 | 0 | 185 | 190 | 98 | 0 | 341 | 292 |  | 0 | 300 | 265 | 0 | 0 | 0 | 224 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 23 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 |  | 24 | 0 | 68 | 100 | 0 | 0 | 22 | 38 | 80 | 0 | 0 | 280 | 280 | 182 | 8 | 89 | 26 | 56 | 0 | 43 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 118 | 155 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 163 | 164 | 61 | 81 | 0 | 218 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 45 | 0 | 0 | 190 | 0 | 86 | 0 | 100 | 180 | 70 | 366 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 17 | 110 | 50 | 400 | 0 | 0 | 54 | 0 | 0 | 36 | 0 |  | 753 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 31 | 0 | 0 | 0 | 65 | 50 | 0 | 87 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 50 | 189 | 0 | 354 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 202 | 0 | 0 | 0 |  | 8021 | 3635 | 11656 | 4967 | 753 | 2054 | 2691 | 670 | 48 | 355 | 118 | 0 | 0 | 75.22
KWH | 0 | 0 | 0 | 4473000 | 909000 | 2168272 | 0 | 8343854 | 7058000 |  | 0 | 7125750 | 6494865 | 0 | 0 | 113654 | 3692547 | 0 | 0 | 1920778 | 813888 | 1386240 | 22394 | 0 | 0 | 0 | 1002960 | 57906 | 1059103 | 476208 | 600000 | 679140 | 824800 | 817400 | 871200 | 0 | 486900 | 604000 | 2300000 | 0 | 382140 | 4799272 | 0 | 2441725 | 0 |  | 425280 | 0 | 804506 | 2229000 | 0 | 101280 | 526032 | 514080 | 1977200 | 0 | 0 | 7225000 | 6795000 | 4779000 | 100363 | 2125220 | 590976 | 1193760 | 0 | 411164 | 0 | 64360 | 604620 | 450684 | 244260 | 817900 | 507890 | 2589120 | 3174520 | 192960 | 485100 | 9200 | 1034000 | 996720 | 1134600 | 0 | 3413618 | 3659000 | 1267776 | 1780800 | 0 | 5173600 | 395000 | 0 | 232380 | 7149500 | 394554 | 195500 | 0 | 1332327 | 0 | 0 | 2911200 | 0 | 1428770 | 149445 | 1602240 | 2897760 | 289381 | 8544000 | 2762400 | 2500800 | 2211345 | 26881 | 0 | 1195969 | 2041554 | 1002060 | 2333520 | 432000 | 8779900 | 123840 | 229290 | 832320 | 249655 | 0 | 558720 | 101190 |  | 19682181 | 0 | 9066240 | 0 | 0 | 0 | 0 | 0 | 0 | 40323 | 0 | 2067345 | 552434 | 0 | 0 | 0 | 1485000 | 336528 | 131940 | 694488 | 142010 | 99224 | 215304 | 920160 | 0 | 499440 | 0 | 151128 | 0 | 0 | 3668000 | 0 | 0 | 0 | 0 | 4415436 | 0 | 288654 | 698880 | 4647473 | 0 | 8959500 | 1750560 | 0 | 951840 | 0 | 835785 | 0 | 46211 | 930240 | 9712600 | 4435400 | 0 | 0 | 14580 |  | 172227086 | 77438904 | 249665990 | 112328400 | 19682181 | 47017715 | 49326588 | 13380600 | 1090900 | 3673689 | 2589120 | 576797 | 0
Fuel Cost | 0 | 0 | 0 | 6575310 | 1008990 | 2862119.04 | 0 | 8427292.54 | 7269740 |  | 0 | 7767067.5 | 7209300.15 | 0 | 0 | 961512.84 | 3840248.88 | 0 | 0 | 14463458.34 | 7422658.56 | 13640601.6 | 206472.68 | 0 | 0 | 0 | 7321608 | 447613.38 | 10442755.58 | 357156 | 450000 | 0 | 0 | 0 | 8424504 | 0 | 131463 | 163080 | 4163000 | 0 | 3550080.6 | 5231206.48 | 0 | 4150932.5 | 0 |  | 0 | 0 | 7803708.2 | 21286950 | 0 | 802137.6 | 662800.32 | 1526817.6 | 2926256 | 0 | 0 | 5346500 | 6795000 | 4396680 | 129468.27 | 2444003 | 667802.88 | 1671264 | 0 | 703090.44 | 0 | 650036 | 5774121 | 572368.68 | 183195 | 1431325 | 380917.5 | 19418400 | 3364991.2 | 1752076.8 | 616077 | 146648 | 1695760 | 1594752 | 2019588 | 0 | 3891524.52 | 3805360 | 2497518.72 | 3401328 | 0 | 8950328 | 865050 | 0 | 474055.2 | 7220995 | 295915.5 | 148580 | 0 | 10072392.12 | 0 | 0 | 15138240 | 0 | 14059096.8 | 1747012.05 | 13058256 | 31440696 | 2040136.05 | 7945920 | 25193088 | 23632560 | 19260814.95 | 0 | 0 | 10416889.99 | 17945259.66 | 10000558.8 | 19998266.4 | 2877120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 113369362.56 | 0 | 9519552 | 0 | 0 | 0 | 0 | 0 | 0 | 422585.04 | 0 | 2336099.85 | 856272.7 | 0 | 0 | 0 | 3044250 | 3311435.52 | 1340510.4 | 6146218.8 | 1093477 | 1341508.48 | 2086295.76 | 8916350.4 | 0 | 958924.8 | 0 | 114403.896 | 0 | 0 | 19880560 | 0 | 0 | 0 | 0 | 5828375.52 | 0 | 432981 | 11887948.8 | 5437543.41 | 0 | 8869905 | 18275846.4 | 0 | 9032961.6 | 0 | 6485691.6 | 0 | 510631.55 | 6874473.6 | 42638314 | 0 | 0 | 0 | 0 |  | 479627867.92 | 291012479.686 | 770640347.606 | 118071461.876 | 113369362.56 | 50055141.07 | 369106882.18 | 62518874 | 294543 | 35401391.32 | 19418400 | 2404291.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 98 | 0 | 339 | 276 |  | 0 | 300 | 275 | 0 | 0 | 0 | 11 | 0 | 0 | 100 | 48 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 42 | 0 | 26 | 25 | 100 | 0 | 17 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 85 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 345 | 295 | 183 | 0 | 90 | 26 | 40 | 0 | 0 | 0 | 0 | 16 | 19 | 8 | 33 | 21 | 100 | 118 | 8 | 21 | 3 | 44 | 42 | 50 | 0 | 130 | 162 | 51 | 78 | 0 | 219 | 18 | 0 | 9 | 295 | 16 | 5 | 0 | 2 | 0 | 0 | 85 | 0 | 66 | 19 | 100 | 133 | 0 | 367 | 115 | 90 | 105 | 6 | 0 | 36 | 110 | 34 | 120 | 10 | 310 | 0 | 56 | 17 | 17 | 0 | 18 | 22 |  | 826 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 86 | 19 | 0 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 189 | 0 | 12 | 9 | 188 | 0 | 392 | 91 | 0 | 25 | 0 | 0 | 0 | 6 | 15 | 290 | 151 | 0 | 0 | 0 |  | 9884 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 190 | 90 | 0 | 338 | 247 | 0 | 0 | 300 | 265 | 0 | 0 | 15 | 222 | 0 | 0 | 100 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 24 | 25 | 100 | 0 | 17 | 203 | 0 | 100 | 0 | 0 | 24 | 0 | 102 | 100 | 0 | 30 | 22 | 28 | 80 | 0 | 0 | 280 | 280 | 183 | 8 | 90 | 26 | 54 | 0 | 5 | 0 | 0 | 34 | 19 | 11 | 33 | 21 | 124 | 102 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 164 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 270 | 16 | 2 | 0 | 275 | 0 | 0 | 189 | 0 | 104 | 0 | 100 | 165 | 23 | 368 | 115 | 105 | 105 | 0 | 0 | 54 | 110 | 100 | 120 | 50 | 400 | 0 | 0 | 126 | 0 | 0 | 36 | 0 |  | 753 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 31 | 0 | 0 | 0 | 65 | 50 | 39 | 87 | 35 | 34 | 38 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 100 | 180 | 0 | 356 | 91 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 480 | 202 | 0 | 0 | 0 |  | 12106 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 200 | 100 | 0 | 380 | 360 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 26 | 25 | 100 | 0 | 17 | 220 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 0 | 45 | 22 | 20 | 80 | 0 | 0 | 330 | 330 | 220 | 8 | 90 | 26 | 55 | 0 | 50 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 180 | 150 | 8 | 21 | 0 | 44 | 42 | 51 | 0 | 163 | 164 | 62 | 83 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 290 | 300 | 100 | 192 | 100 | 135 | 0 | 100 | 180 | 150 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 35 |  |  | 905 | 0 | 380 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 86 | 25 | 110 | 0 | 0 | 65 | 50 | 40 | 100 | 35 | 43 | 40 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 12 | 100 | 200 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 185 | 200 | 100 | 0 | 350 | 350 | 0 | 0 | 300 | 290 | 0 | 0 | 55 | 220 | 0 | 0 | 100 | 100 | 133 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 30 | 33 | 33 | 51 | 0 | 26 | 25 | 100 | 0 | 17 | 220 | 0 | 100 | 0 | 0 | 22 |  | 85 | 100 | 0 | 40 | 22 | 10 | 80 | 0 | 0 | 310 | 310 | 220 | 8 | 90 | 26 | 55 | 0 | 50 | 0 | 0 | 34 | 22 | 11 | 33 | 17 | 151 | 120 | 8 | 21 | 1.6 | 44 | 42 | 51 | 0 | 163 | 162 | 62 | 81 | 0 | 192 | 18 | 0 | 10 | 341 | 15 | 11 | 100 | 290 | 100 | 100 | 175 | 100 | 135 | 20 | 100 | 160 | 150 | 400 | 115 | 90 | 105 | 5 | 300 | 54 | 110 | 34 | 113 | 100 | 400 | 90 | 50 | 126 | 116 | 0 | 35 | 30 |  | 905 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 85 | 25 | 110 | 0 | 0 | 65 | 50 | 30 | 90 | 35 | 43 | 40 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 12 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 190 | 60 | 0 | 350 | 277 | 0 | 0 | 300 | 275 | 0 | 0 | 0 | 150 | 0 | 0 | 20 | 16 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 40 | 22 | 25 | 30 | 33 |  | 27 | 0 | 25 | 25 | 100 | 0 | 8 | 203 | 0 | 100 | 0 | 0 | 5 | 0 | 0 | 30 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 280 | 265 | 183 | 8 | 88 | 26 | 56 | 0 | 19 | 0 | 0 | 34 | 19 | 0 | 33 | 21 | 98 | 119 | 8 | 21 | 1 | 43 | 42 | 44 | 0 | 130 | 164 | 61 | 81 | 0 | 191 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 150 | 0 | 1 | 0 | 0 | 17 | 0 | 365 | 106 | 105 | 51 | 1 | 0 | 54 | 0 | 17 | 85 | 0 | 396 | 0 | 25 | 0 | 0 | 0 | 18 | 14 | 0 | 889 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 65 | 0 | 0 | 47 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 12 | 0 | 150 | 0 | 356 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 320 | 202 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 8623 | 8:00
| Highest Generation |  | 12145 | 22:00
| Day Peak Generation |  | 9884 | 12:00
| Evening Peak Generation |  | 12106 | 21:00
| HVDC Max Flow |  | 893 | 19:30
| HVDC EvPeak Flow |  | 753 | 21:00
| Load factor L.F |  | 85.65%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-06-23
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-06-22 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9884 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8988 | MW
Evening Peak Generation : |  | 12106 | MW Hour : | 21:00 | Available Max Generation : |  | 15715 | MW
E.P. Demand (at gen end) : |  | 12106 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12145 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2715 | MW
Total Gen. (MKWH) : |  | 249.666 | System Load Factor : | 85.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -224 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-06-23
Actual : | 75.22 | Ft.(MSL) , | Rule curve : | 81.84 | Ft.( MSL )
Gas Consumed : | Total = | 1264.97 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168126602.946
: |  | Coal : | 62518874 | Oil : | 404508273.5 | Total : | 635153750.446
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4637.4558 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1581.9906 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1418.3019 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1281.8717 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1158.2345 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 934.6669 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 516.1868 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 240.4813 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 720.8923 |  |  | 0 | 0%
Total | 0 |  | 12490.0818 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Chandpur-150 MW ST
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj 230 kV Bus-1 was under shut down from 09:00 to 18:00 for R/H maintenance.
b) Mahasthangar 132/33 kV T-1 transformer was under shut down from 08:18 to 09:58 for R/H maintenance.
c) Kurigram 132/33 kV T-1 transformer was under shut down from 11:48 to 16:00 for tan delta test.
d) Siddhirganj 335 MW CCPP GT was synchronized at 11:18.
e) Shahjadpur 132/33 kV T-2 transformer was under shut down from 10:08 to 13:15 for R/H maintenance
at 33 kV Y-phase Bushing.
f) Aminbazar 230 kV Bus-2 was under shut down from 11:31 to 13:41 for 400 kV project work.
g) Banani 132/33 kV T-1 transformer was charged at 16:26.
h) Aminbazar 400/230 kV ART-01 transformer was switched on at 16:26.
i) Faridpur-Bheramara 132 kV Ckt-1 was switched on at 17:50.
j) Kamrangirchar-Zigatala 132 kV Ckt-1 & 2 was charged at 16:15 & 16:20 respectively from Kamrangirchar.
k) Kurigram 132/33 kV T-2 transformer was under shut down from 11:48 to 16:00 for tan delta test.
l) Ghorashal unit-7 GT was synchronized at 18:07.
m) Payra Unit-2 was synchronized at 23:41.
n) Payra Unit-1 was shutdown at 05:04(23/06/2021).
o) Mymensingh-Mymensingh RPCL 132 kV Ckt-2 was shut down at 07:01(23/06/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-06-22 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4473000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 190 | 909000 | Machine problem
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 90 | 2168272 | Engine problem
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 338 | 8343854 | FGMO
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 247 | 7058000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7125750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 265 | 6494865 | Gas shortage
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 15 | 113654 | Low demand
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 22394 | Reserve.
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 22 | 476208
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 1920778
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 222 | 3692547 | Gas shortage
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 813888
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1002960
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1386240
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 57906 | Reserve.
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1059103
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1279140 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 824800
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817400
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 871200
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 1332327 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 104 | 1428770 | Low demand
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2500800
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 123840 | Reserve.
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 832320 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 101190
| Dhaka area Total |  |  |  | 5919 | 3117 | 57230206
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 17 | 382140 | Engine problem
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 149445
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 30 | 101280 | Low demand
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 49 | 1090900 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4799272 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2441725 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2211345
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 804506
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 2229000
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1602240
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 526032
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 28 | 514080
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26881
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1195969
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2041554
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 432000 | Transformer O/L
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 0 | 249655 | Transformer O/L
| Chattogram area Total |  |  |  | 2382 | 1170 | 23098024
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1977200 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 183 | 4779000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7225000 | Gas shortage
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6795000 | Gas shortage
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 590976 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1193760
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 100363 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 5 | 411164 | APSCL 230 kV Bus-1 S/D
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 23 | 289381 | APSCL 230 kV Bus-1 S/D
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 64360 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2125220 | ST under maint
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 165 | 2897760 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 450684
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244260
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 124 | 2589120
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817900
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 604620 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 507890
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1002060 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 120 | 2333520
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 558720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1692 | 37557958
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 3174520 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 485100
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 192960 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9200
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 189 | 2911200 | Engine problem
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2762400
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 229290
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 425280
| Mymensingh Area Total |  |  |  | 709 | 459 | 10189950
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1034000
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 996720 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3413618
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 164 | 3659000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1134600
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 2 | 195500
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1267776
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1780800
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5173600
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 395000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 394554 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7149500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 368 | 8544000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232380
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8779900
| Sylhet Area Total |  |  |  | 2377 | 1911 | 44150948
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 753 | 19682181
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 115 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 40323 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 385 | 9066240 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 40 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 698880
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 91 | 1750560 | Engine problem
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2284 | 1329 | 31238184
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 552434 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 83 | 2067345 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 288654 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 9712600 | Line O/L
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 202 | 4435400 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 807 | 17056433
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 65 | 1485000 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 336528
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 39 | 131940 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 142010 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 34 | 99224 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 38 | 215304 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 166 | 4415436 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 180 | 4647473 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 356 | 8959500 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Under maint.
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 499440
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 151128
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 920160
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 694488 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 951840
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 930240
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 14580
| Rajshahi Area Total |  |  |  | 2179 | 1358 | 24594291
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3668000 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 835785
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46211
| Rangpur Area Total |  |  |  | 605 | 263 | 4549996
| Total |  |  |  | 21315 | 12106 | 249665990
| Eastern Grid Total |  |  |  | 14421 | 8349 | 172227086
| Western Grid Total |  |  |  | 6894 | 3757 | 77438904
| National Grid Total |  |  |  | 21315 | 12106 | 249665990
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-06-22
(a) ENTIRE EASTERN GRID : |  | 7799 | MW | (b) ENTIRE WESTERN GRID : |  | 3824 | MW
i) Dhaka area |  | 4084 | MW | i) Khulna area |  | 1399 | MW
ii) Chittagong area |  | 1244 | MW | ii) Rajshahi area |  | 1308 | MW
iii) Comilla area |  | 1113 | MW | iii) Barisal area |  | 329 | MW
iv) Mymensingh area |  | 896 | MW | iv) Rangpur area |  | 788 | MW
v) Sylhet area |  | 462 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11623 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 102 | 15:00 | Kishoreganj | 130 | 19:30 | Jessore | 104 | 19:30
Munsiganj | 94 | 1:00 | Netrokona | 118 | 24:00 | Benapol | 54 | 20:00
Sonargaon | 70 | 1:00 | Jamalpur | 135 | 24:00 | Jhenida | 108 | 20:00
Shyampur | 180 | 0:00 | Sherpur | 122 | 1:00 | Bottail | 110 | 21:00
Bhulta | 199 | 1:00 | Srimongal | 53 | 19:30 | G.K Project | 53 | 21:00
Madanganj | 47 | 2:00 | Shahjibazar | 115 | 22:00 | Faridpur | 172 | 20:00
Shitalakhya | 106 | 12:00 | Fenchuganj | 47 | 19:30 | Madaripur | 97 | 22:00
Rahim steel | 21 | 12:00 | Kulawara | 51 | 19:30 | Sariatpur | 62 | 22:00
Matuail | 54 | 12:00 | Sylhet | 127 | 13:00 | Gopalganj | 88 | 20:00
Ghorasal | 74 | 0:00 | Chatak | 30 | 21:00 | Bagerhat | 94 | 19:30
Narsingdi | 168 | 0:00 | Sunamganj | 46 | 21:00 | Mongla | 40 | 12:00
Haripur (SBU) | 111 | 20:00 | Biani Bazar | 67 | 19:30 | Satkhira | 96 | 20:00
Sreenagar | 36 | 21:00 | Comilla (S) | 128 | 19:30 | Gallamari | 38 | 13:00
Ullon | 63 | 20:00 | Comilla(N) | 135 | 20:00 | Magura | 46 | 1:00
Hasnabad | 79 | 15:00 | Chandpur | 72 | 21:00 | Norail | 42 | 20:00
Magbazar | 71 | 15:00 | Feni | 109 | 20:00 | Chuadanga | 89 | 19:30
Maniknagar | 70 | 13:00 | Chowmuhani | 182 | 19:30 | Borguna | 16 | 20:00
Bangabhaban | 10 | 11:00 | Ashuganj | 35 | 5:00 | Barisal(N) | 42 | 21:00
Motijheel | 18 | 11:00 | Daudkandi | 138 | 21:00 | Barisal (S) | 96 | 19:30
Narinda | 56 | 14:00 | B.Baria | 156 | 21:00 | Patuakhali | 104 | 22:00
Kazla | 76 | 16:00 | Ramganj | 80 | 19:00 | Bhandaria | 48 | 22:00
Dhanmondi | 143 | 14:00 | Chaddagram | 42 | 23:00 | Borhan Uddin | 40 | 21:00
Lalbag | 93 | 13:00 | PHP | 4 | 19:30 | Ishurdi | 63 | 19:30
Madartek | 68 | 22:00 | Kochua | 64 | 20:00 | Ruppur Paromanobik | 3 | 12:00
Dhaka University | 30 | 13:00 | Madunaghat | 62 | 16:00 | Natore | 129 | 21:00
Aftabnagar | 9 | 13:00 | Hathazari | 89 | 19:00 | Bogra | 155 | 20:00
Fatullah | 52 | 1:00 | Khulshi | 187 | 15:00 | Noagaon | 123 | 21:00
Nawabganj | 48 | 22:00 | Halishahar | 83 | 16:00 | Rajshahi | 150 | 21:00
Keraniganj | 64 | 20:00 | Baraulia | 138 | 8:00 | Rajshahi New | 17 | 20:00
Mirpur | 124 | 19:00 | Sikalbaha | 30 | 17:00 | C.Nawabganj | 71 | 21:00
Kalyanpur | 99 | 19:30 | Dohazari | 80 | 20:00 | Amnura | 32 | 21:00
Gulshan | 104 | 14:00 | Cox'sbazar | 103 | 22:00 | Pabna | 98 | 21:00
Uttara | 91 | 19:00 | Chandraghona | 26 | 21:00 | Shahjadpur | 96 | 21:00
Uttara New | 14 | 14:00 | Kaptai | 5.5 | 19:00 | Serajganj | 97 | 21:00
Kamrangirchar | 88 | 19:30 | A. Khaer Stl. | 0 | 1:00 | Niyamatpur | 71 | 21:00
Savar | 160 | 20:00 | Bakulia | 105 | 19:00 | Joypurhat | 57 | 21:00
Bhasantec | 112 | 14:00 | Julda | 20 | 14:00 | Sherpur(Bogura) | 56 | 19:30
Agargaon | 67 | 15:00 | TK chemical | 23.8 | 1:00 | Mohastangor | 64 | 20:00
Satmosjid | 82 | 14:00 | Modern Steel | 0 | #N/A | Bhangura | 32 | 20:00
Tongi | 92 | 22:00 | Shahmirpur | 34 | 23:00 | Rangpur | 130 | 20:00
Kabirpur | 228 | 21:00 | Khagrachhari | 24 | 20:00 | Lalmonirhat | 42 | 20:00
Basundhara | 179 | 14:00 | Matarbari | 34 | 20:00 | Saidpur | 102 | 20:00
Manikganj | 70 | 21:00 | Baroiar Hat | 40 | 19:00 | Purbasadipur | 113 | 21:00
Joydevpur | 167 | 19:30 | Rangamati | 12 | 19:00 | Thakurgaon | 82 | 20:00
New Tongi | 101 | 12:00 | Abul Khair 230 | 6 | 18:00 | Palashbari | 115 | 21:00
Kodda | 266 | 14:00 | BSRM | 123 | 2:00 | Barapukuria | 55 | 21:00
Dhamrai | 110 | 0:00 | GPH Ispat | 90 | 6:00 | Panchagar | 49 | 20:00
Rajendrapur | 108 | 22:00 | Agrabad | 58 | 19:30 | Joldhaka | 58 | 19:30
Valuka | 114 | 1:00 | Goalpara | 29 | 20:00 | Kurigram | 60 | 19:30
Tangail | 194 | 21:00 | Central S/S | 78 | 19:30 | Mithapukur | 29 | 19:30
Mymensing | 188 | 1:00 | Noapara | 51 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-06-22 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 19:30 | 396 | 2:00 | Kaliakoir | 388 | 0.77083 | 379 | 0.375
| Bheramara | 400 | 19:30 | 394 | 20:00 | Bhulta | 381 | 0.91667 | 370 | 0.45833
| Ashuganj(N) | 385 | 21:00 | 375 | 11:00 | Gopalganj | 408 | 0.625 | 385 | 0.91667
| Payra | 412 | 8:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 19:30 | 218 | 7:00
| Ishurdi | 232 | 17:00 | 226 | 2:00 | Megnaghat | 228 | 5:00 | 222 | 1:00
| Ashuganj | 235 | 21:00 | 230 | 8:00 | Fenchuganj | 238 | 4:00 | 234 | 19:30
| Serajganj | 230 | 6:00 | 225 | 2:00 | Siddhirganj | 226 | 19:30 | 221 | 11:00
| Baghabari | 230 | 18:00 | 226 | 1:00 | Maniknagar | 225 | 19:30 | 219 | 11:00
| Barapukuria | 233 | 18:00 | 224 | 23:00 | Agargaon | 223 | 8:00 | 215 | 16:00
| Bogra | 222 | 18:00 | 213 | 10:00 | Barisal | 243 | 19:00 | 230 | 21:00
| Rajshahi | 233 | 18:30 | 223 | 3:00 | Bhola 225 MW | 246 | 8:00 | 236 | 21:00
| Khulna South | 229 | 8:00 | 217 | 3:00 | AKSML | 223 | 19:00 | 215 | 7:00
| Rampura | 226 | 19:30 | 221 | 11:00 | BSRM | 225 | 13:00 | 218 | 7:00
| Haripur | 224 | 20:00 | 219 | 11:00 | Bibiyana | 238 | 4:00 | 232 | 12:00
| Hasnabad | 224 | 1:00 | 218 | 10:00 | Bhulta | 228 | 20:00 | 221 | 16:00
| Shyampur | 222 | 8:00 | 220 | 10:00 | Ashuganj (S) | 232 | 20:00 | 227 | 11:00
| Aminbazar | 224 | 1:00 | 217 | 2:00 | Kaliakoir | 226 | 19:00 | 218 | 10:00
| Tongi | 224 | 1:00 | 128 | 24:00 | GPH | 226 | 8:00 | 217 | 7:00
| Comilla (N) | 227 | 19:30 | 223 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 19:00 | 128 | 9:00 | Kochua | 137 | 0.54167 | 131 | 0.16667
| Munsiganj | 133 | 19:30 | 127 | 16:00 | Madanhat | 132 | 0.041667 | 128 | 0.41667
| Sonargaon | 132 | 19:30 | 126 | 1:00 | Hathazari | 132 | 0.041667 | 129 | 0.29167
| Shyampur | 133 | 8:00 | 129 | 10:00 | Khulshi | 130 | 0.8125 | 126 | 0.41667
| Bhulta | 124 | 18:30 | 119 | 11:00 | Halishahar | 132 | 0.8125 | 127 | 0.41667
| Madanganj | 131 | 19:00 | 126 | 13:00 | Baraulia | 132 | 0.83333 | 128 | 0.29167
| Shitalakhya | 135 | 20:00 | 126 | 11:00 | Sikalbaha | 133 | 0.8125 | 128 | 0.29167
| Rahim steal | 132 | 19:00 | 128 | 11:00 | Dohazari | 130 | 0.77083 | 125 | 0.25
| Matuail | 131 | 19:00 | 128 | 9:00 | Cox'sbazar | 122 | 0.8125 | 116 | 0.54167
| Ghorasal | 138 | 0:00 | 136 | 15:00 | Chandraghona | 132 | 0.33333 | 129 | 0.29167
| Narsinghdi | 132 | 18:00 | 124 | 0:00 | Kaptai | 131 | 0.29167 | 130 | 0.041667
| Haripur (SBU) | 132 | 19:30 | 128 | 12:00 | A. Khaer Stl. | 130 | 0.041667 | 127 | 0.54167
| Sreenagar | 127 | 19:00 | 122 | 7:00 | Bakulia | 132 | 0.8125 | 127 | 0.29167
| Ullon | 135 | 7:00 | 129 | 11:00 | Julda | 134 | 0.79167 | 128 | 0.20833
| Hasnabad | 133 | 21:00 | 126 | 10:00 | TK Chemical | 131 | 0.041667 | 130 | 0.083333
| Magbazar | 134 | 8:00 | 129 | 12:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Maniknagar | 135 | 8:00 | 131 | 11:00 | Shahmirpur | 133 | 0.8125 | 128 | 0.25
| Bangabhaban | 135 | 8:00 | 131 | 11:00 | Khagrachhari | 131 | 0.83333 | 128 | 0.29167
| Motijheel | 135 | 8:00 | 131 | 11:00 | Matarbari | 126 | 0.95833 | 0 | #N/A
| Narinda | 135 | 8:00 | 131 | 11:00 | Baroiar Hat | 134 | 0.8125 | 130 | 0.041667
| Kazla | 135 | 8:00 | 131 | 11:00 | Rangamati | 131 | 19:30 | 128 | 10:00
| Dhanmondi | 131 | 5:00 | 127 | 11:00 | Agrabad | 131 | 21:00 | 127 | 9:00
| Lalbag | 131 | 8:00 | 123 | 16:00 | Goalpara S/S | 137 | 7:00 | 130 | 0.083333
| Madartek | 135 | 8:00 | 129 | 15:00 | Khulna Central S/S | 137 | 7:00 | 128 | 0.20833
| Dhaka University | 135 | 7:00 | 129 | 11:00 | Noapara | 135 | 15:00 | 126 | 0.041667
| Aftabnagar | 135 | 7:00 | 130 | 11:00 | Jessore | 132 | 9:00 | 120 | 0.083333
| Fatullah | 134 | 19:30 | 129 | 11:00 | Benapol | 132 | 0.77083 | 123 | 0.875
| Nawabganj | 127 | 20:00 | 122 | 15:00 | Jhenida | 129 | 17:00 | 117 | 0.8125
| Keraniganj | 127 | 8:00 | 123 | 10:00 | Bottail | 133 | 0.77083 | 126 | 0.041667
| Mirpur | 134 | 3:00 | 127 | 15:00 | G.K Project | 140 | 0.77083 | 134 | 0.125
| Kalyanpur | 135 | 20:00 | 129 | 11:00 | Faridpur | 136 | 0.77083 | 127 | 0.875
| Gulshan | 134 | 6:00 | 129 | 11:00 | Madaripur | 140 | 0.33333 | 130 | 0.875
| Uttara | 134 | 19:30 | 127 | 12:00 | Shariyatpur S/S | 140 | 17:00 | 128 | 0.91667
| Uttara New | 134 | 11:00 | 127 | 11:00 | Gopalganj | 143 | 0.29167 | 131 | 0.875
| Kamrangirchar | 132 | 19:30 | 124 | 12:00 | Bagerhat | 135 | 15:00 | 128 | 0.041667
| Savar | 127 | 20:00 | 127 | 11:00 | Mongla | 134 | 5:00 | 128 | 0.041667
| Bhasantec | 134 | 7:00 | 128 | 12:00 | Satkhira | 138 | 18:30 | 128 | 19:30
| Agargaon | 135 | 8:00 | 129 | 12:00 | Gallamari | 139 | 0.77083 | 130 | 4:00
| Satmosjid | 134 | 8:00 | 129 | 11:00 | Magura | 129 | 8:00 | 115 | 0.041667
| Tongi | 137 | 1:00 | 132 | 12:00 | Narail | 126 | 0.375 | 113 | 0.041667
| Kabirpur | 133 | 5:00 | 128 | 23:00 | Chuadanga | 124 | 9:00 | 109 | 0.95833
| Basundhara | 135 | 18:30 | 128 | 11:00 | Borguna | 138 | 8:00 | 125 | 0.91667
| Manikganj | 138 | 19:00 | 126 | 11:00 | Barisal(N) | 140 | 7:00 | 130 | 21:00
| Joydevpur | 140 | 19:00 | 128 | 9:00 | Barisal (S) | 139 | 0.29167 | 129 | 0.875
| New Tongi | 136 | 5:00 | 132 | 10:00 | Patuakhali(S) | 138 | 0.33333 | 125 | 0.91667
| Kodda | 132 | 13:00 | 125 | 11:00 | Bhandaria | 137 | 0.29167 | 124 | 0.91667
| Dhamrai | 132 | 8:00 | 126 | 21:00 | Ishurdi | 136 | 18:30 | 131 | 3:00
| Rajendrapur | 131 | 1:00 | 122 | 12:00 | Ruppur Paromanobik | 135 | 18:30 | 133 | 19:00
| Valuka | 124 | 12:00 | 107 | 19:00 | Natore | 133 | 18:30 | 128 | 1:00
| Tangail | 130 | 18:00 | 124 | 23:00 | Bogra | 133 | 18:30 | 128 | 2:00
| Mymensing | 128 | 6:00 | 112 | 19:00 | Noagaon | 128 | 18:00 | 116 | 10:00
| Kishorganj | 130 | 12:00 | 117 | 22:00 | Rajshahi | 131 | 18:30 | 127 | 1:00
| Netrokona | 125 | 12:00 | 109 | 22:00 | Rajshahi New | 134 | 18:30 | 125 | 5:00
| Jamalpur | 135 | 5:00 | 125 | 22:00 | C.Nawabganj | 130 | 20:00 | 124 | 12:00
| Sherpur | 134 | 6:00 | 129 | 18:00 | Amnura | 133 | 20:00 | 123 | 3:00
| Srimongal | 136 | 11:00 | 132 | 23:00 | Pabna | 134 | 18:00 | 130 | 2:00
| Shahjibazar | 134 | 7:00 | 129 | 23:00 | Shahjadpur | 135 | 6:00 | 133 | 1:00
| Fenchuganj | 138 | 8:00 | 134 | 1:00 | Serajganj | 130 | 4:00 | 127 | 21:00
| Khulawara | 136 | 4:00 | 134 | 16:00 | Niyamatpur | 128 | 18:00 | 116 | 21:00
| Sylhet | 134 | 4:00 | 132 | 19:00 | Joypurhat | 128 | 18:30 | 115 | 1:00
| Chatak | 134 | 7:00 | 129 | 22:00 | Sherpur(Bogura) | 132 | 18:00 | 125 | 10:00
| Sunamganj | 133 | 8:00 | 127 | 21:00 | Mohastangor | 131 | 18:00 | 123 | 10:00
| Biani Bazar | 134 | 7:00 | 128 | 22:00 | Bangura | 134 | 5:00 | 132 | 1:00
| Comilla(s) | 130 | 3:00 | 125 | 19:30 | Rangpur | 125 | 18:30 | 115 | 20:00
| Comilla(n) | 137 | 19:00 | 133 | 24:00 | Lalmonirhat | 126 | 18:30 | 117 | 15:00
| Chandpur | 137 | 11:00 | 130 | 6:00 | Saidpur | 126 | 5:00 | 114 | 20:00
| Feni | 135 | 20:00 | 130 | 24:00 | Purbasadipur | 125 | 18:00 | 108 | 20:00
| Chowmuhani | 135 | 21:00 | 129 | 6:00 | Thakurgaon | 125 | 18:00 | 108 | 20:00
| Ashuganj | 138 | 8:00 | 133 | 24:00 | Palashbari | 125 | 18:00 | 120 | 2:00
| Daudkandi | 133 | 19:00 | 126 | 24:00 | Barapukuria | 133 | 18:00 | 125 | 20:00
| B.Baria | 134 | 7:00 | 126 | 22:00 | Panchagar | 125 | 18:00 | 106 | 20:00
| Ramganj | 137 | 11:00 | 130 | 24:00 | Joldhaka | 124 | 0.77083 | 109 | 0.83333
| Chaddagram | 136 | 13:00 | 131 | 24:00 | Kurigram | 123 | 0.77083 | 111 | 0.041667
| PHP | 134 | 20:00 | 129 | 24:00 | Mithapukur | 128 | 18:30 | 118 | 0.041667
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-06-22
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 136 | 8021 | 3635 | 11656 |  |  |  | QF-LDC-11
0:30 | 155 | 7876 | 3489 | 11365 | Date: | 2021-06-22
1:00 | 174 | 7731 | 3343 | 11074
1:30 | 116 | 7475.5 | 3282.5 | 10758
2:00 | 58 | 7220 | 3222 | 10442
2:30 | 39 | 7114 | 3212.5 | 10326.5 | [5 empty] | Gen. at Eve. Peak | 12106 | 12106 MW (21:00 )
3:00 | 20 | 7008 | 3203 | 10211 | [6 empty] | 21:00
3:30 | 19 | 6915 | 3144 | 10059 | [5 empty] | Gen. at Day Peak | 9884 | 9884 MW (12:00 )
4:00 | 18 | 6822 | 3085 | 9907 | [6 empty] | 12:00
4:30 | 32 | 6730 | 3067.5 | 9797.5 | [5 empty] | Highest Generation | 12145
5:00 | 46 | 6638 | 3050 | 9688 | [6 empty] | 22:00
5:30 | 25 | 6412.5 | 2877 | 9289.5
6:00 | 4 | 6187 | 2704 | 8891
6:30 | 5 | 6131 | 2691 | 8822
7:00 | 6 | 6075 | 2678 | 8753
7:30 | 19.5 | 6025 | 2663 | 8688
8:00 | 33 | 5975 | 2648 | 8623
8:30 | 74.5 | 6051 | 2695 | 8746
9:00 | 116 | 6127 | 2742 | 8869
9:30 | 115 | 6300 | 2784 | 9084
10:00 | 114 | 6473 | 2826 | 9299
10:30 | 102.5 | 6563.5 | 2856 | 9419.5
11:00 | 91 | 6654 | 2886 | 9540
11:30 | 77.5 | 6782 | 2930 | 9712
12:00 | 64 | 6910 | 2974 | 9884
12:30 | 62.5 | 6979 | 3004 | 9983
13:00 | 61 | 7048 | 3034 | 10082
13:30 | 38.5 | 7054 | 3027.5 | 10081.5
14:00 | 16 | 7060 | 3021 | 10081
14:30 | 25 | 7144 | 3029 | 10173
15:00 | 34 | 7228 | 3037 | 10265
15:30 | 67 | 7197 | 3005.5 | 10202.5
16:00 | 100 | 7166 | 2974 | 10140
16:30 | 122.5 | 7068 | 2933 | 10001
17:00 | 145 | 6970 | 2892 | 9862
17:30 | 169.5 | 6793.5 | 2848.5 | 9642
18:00 | 194 | 6617 | 2805 | 9422
18:30 | 102 | 6971.5 | 2988.5 | 9960
19:00 | 10 | 7326 | 3172 | 10498
19:30 | 200 | 8415 | 3508 | 11923
20:00 | 188 | 8268 | 3702 | 11970 |  |  |  | Executive Engineer
20:30 | 206 | 8308.5 | 3729.5 | 12038 |  |  |  | Network Operation Division
21:00 | 224 | 8349 | 3757 | 12106
21:30 | 213 | 8348 | 3777.5 | 12125.5
22:00 | 202 | 8347 | 3798 | 12145 |  |  |  |  | Page 6 of 7
22:30 | 161 | 8223.5 | 3754 | 11977.5
23:00 | 120 | 8100 | 3710 | 11810
23:30 | 128 | 8060.5 | 3672.5 | 11733
24:00 | 136 | 8021 | 3635 | 11656
12106 MW (21:00 )
9884 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-06-22 |  | Energy | 249665990
[11 empty] | 2021-06-22 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4967 | 753 | 2054 | 2849 | 670 | 48 | 355 | 0 | 118 | 0
0:30 | 4878 | 743 | 2076 | 2578.5 | 620 | 48.5 | 381 | 0 | 119 | 0 | Date: | 2021-06-22
1:00 | 4789 | 733 | 2098 | 2308 | 570 | 49 | 407 | 0 | 120 | 0
1:30 | 4782 | 789 | 2120 | 2027.5 | 560 | 49 | 315.5 | 0 | 115 | 0 | [7 empty] | Total Energy | 249.666 | Total Energy Gen 249.666 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.666 MKWHr
2:00 | 4775 | 845 | 2142 | 1747 | 550 | 49 | 224 | 0 | 110 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4748 | 844.5 | 2154.5 | 1722.5 | 550 | 49 | 149 | 0 | 109 | 0 | [7 empty] | Energy Requirement | 249.666
3:00 | 4721 | 844 | 2167 | 1698 | 550 | 49 | 74 | 0 | 108 | 0
3:30 | 4720.5 | 844.5 | 2151 | 1593.5 | 540 | 49.5 | 54 | 0 | 106 | 0 | [6 empty] | Shortage
4:00 | 4720 | 845 | 2135 | 1489 | 530 | 50 | 34 | 0 | 104 | 0
4:30 | 4720.5 | 841 | 2133.5 | 1408.5 | 520 | 50 | 22 | 0 | 102 | 0
5:00 | 4721 | 837 | 2132 | 1328 | 510 | 50 | 10 | 0 | 100 | 0
5:30 | 4619.5 | 832 | 2050.5 | 1152.5 | 480 | 50.5 | 5 | 0 | 98 | 1.5
6:00 | 4518 | 827 | 1969 | 977 | 450 | 51 | 0 | 0 | 96 | 3
6:30 | 4458.5 | 827 | 1977.5 | 971 | 435 | 51 | 0 | 0 | 93 | 9 |  |  |  |  | Coal
7:00 | 4399 | 827 | 1986 | 965 | 420 | 51 | 0 | 0 | 90 | 15
7:30 | 4298.5 | 826.5 | 1866.5 | 1103 | 425 | 51 | 8 | 0 | 90 | 19.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4198 | 826 | 1747 | 1241 | 430 | 51 | 16 | 0 | 90 | 24
8:30 | 4253 | 826.5 | 1737.5 | 1297.5 | 435 | 51 | 24 | 0 | 90 | 31.5
9:00 | 4308 | 827 | 1728 | 1354 | 440 | 51 | 32 | 0 | 90 | 39
9:30 | 4374.5 | 826.5 | 1789 | 1430.5 | 440 | 51 | 32 | 0 | 90 | 50.5
10:00 | 4441 | 826 | 1850 | 1507 | 440 | 51 | 32 | 0 | 90 | 62
10:30 | 4411 | 826.5 | 1884.5 | 1621.5 | 440 | 51 | 32 | 0 | 95 | 58
11:00 | 4381 | 827 | 1919 | 1736 | 440 | 51 | 32 | 0 | 100 | 54
11:30 | 4435.5 | 826.5 | 1896 | 1845.5 | 440 | 51 | 34.5 | 0 | 100 | 83
12:00 | 4490 | 826 | 1873 | 1955 | 440 | 51 | 37 | 0 | 100 | 112
12:30 | 4552 | 826.5 | 1851 | 2035.5 | 440 | 38 | 38 | 0 | 101 | 101
13:00 | 4614 | 827 | 1829 | 2116 | 440 | 25 | 39 | 0 | 102 | 90
13:30 | 4614 | 827 | 1829 | 2116 | 440 | 25 | 39 | 0 | 102 | 90
14:00 | 4614 | 827 | 1829 | 2116 | 440 | 25 | 39 | 0 | 102 | 90
14:30 | 4646.5 | 826.5 | 1854.5 | 2124.5 | 455 | 36 | 43.5 | 0 | 107 | 80
15:00 | 4679 | 826 | 1880 | 2133 | 470 | 47 | 48 | 0 | 112 | 70
15:30 | 4661 | 826.5 | 1890.5 | 2090.5 | 470 | 47 | 52 | 0 | 109 | 56
16:00 | 4643 | 827 | 1901 | 2048 | 470 | 47 | 56 | 0 | 106 | 42
16:30 | 4635.5 | 827 | 1895 | 1927.5 | 470 | 47 | 57 | 0 | 107 | 35
17:00 | 4628 | 827 | 1889 | 1807 | 470 | 47 | 58 | 0 | 108 | 28
17:30 | 4597.5 | 827 | 1825.5 | 1687.5 | 470 | 47 | 64.5 | 0 | 106 | 17
18:00 | 4567 | 827 | 1762 | 1568 | 470 | 47 | 71 | 0 | 104 | 6
18:30 | 4643 | 859.5 | 1803.5 | 1806 | 470 | 48 | 215 | 0 | 112 | 3
19:00 | 4719 | 892 | 1845 | 2044 | 470 | 49 | 359 | 0 | 120 | 0
19:30 | 4864 | 893 | 1898 | 3067 | 530 | 49 | 494 | 0 | 128 | 0
20:00 | 4784 | 893 | 1896 | 3164 | 540 | 49 | 520 | 0 | 124 | 0
20:30 | 4827 | 823 | 1913.5 | 3223.5 | 585 | 49 | 493 | 0 | 124 | 0
21:00 | 4870 | 753 | 1931 | 3283 | 630 | 49 | 466 | 0 | 124 | 0
21:30 | 4881 | 753 | 1939 | 3264 | 655 | 49 | 460.5 | 0 | 124 | 0
22:00 | 4892 | 753 | 1947 | 3245 | 680 | 49 | 455 | 0 | 124 | 0
22:30 | 4925 | 753 | 1987.5 | 3047 | 680 | 48.5 | 413.5 | 0 | 123 | 0
23:00 | 4958 | 753 | 2028 | 2849 | 680 | 48 | 372 | 0 | 122 | 0
23:30 | 4962.5 | 753 | 2041 | 2849 | 675 | 48 | 363.5 | 0 | 120 | 0 | Max Temp. in Dhaka |  | 29.9° C
24:00 | 4967 | 753 | 2054 | 2849 | 670 | 48 | 355 | 0 | 118 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 249.666 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 249.666 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-06-22
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 24 | 24 | 24 | 25 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 0 | 22 | 22 | 22 | 22 | 22 |  | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 486900
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 604000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 65 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 17 | 17 | 17 | 17 | 17 | 8 | 8 | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 15 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 382140
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 6 | 11 | 15 | 17 | 19 | 19 | 17 | 17 | 13 | 9 | 5 | 1 | [8 empty] | 149445
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 203 | 203 | 203 | 216 | 204 | 216 | 217 | 212 | 204 | 204 | 204 | 204 | 203 | 203 | 203 |  | 204 | 203 | 203 | 203 | 203 | 203 | 203 | 4799272
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2441725
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 51 | 34 | 34 | 10 | 0 |  |  |  | 0 | [7 empty] | 17 |  | 102 | 102 | 102 | 102 | 102 | 85 | 68 | 804506
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 90 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 68 | 92 | 105 | 105 | 105 | 105 | 105 | 105 | 68 |  | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 2211345
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 33 | 50 | 50 |  |  |  | 0 | 64360
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 221 | 222 | 223 | 221 | 224 | 170 | [5 empty] | 11 | 150 | 150 | 180 | 180 | 180 | 180 |  | 150 | 221 | 190 | 222 | 223 | 220 | 224 | 3692547
18 | Kodda 300 MW PP Unit-2 (Summit) | 15 | 0 | [9 empty] | 2 | 15 | 14 | 14 | 15 | 15 | 34 |  | 102 | 240 | 240 | 275 | 245 | 45 | 45 | 1332327
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 0 | [13 empty] | 8 | 8 | 8 | 8 | 8 | 8 | 100363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4473000
24
25 | Ghorasal 365 MW CCPP Unit-7 | [19 empty] | 110 | 170 | 190 | 190 | 190 | 190 | 190 | 909000
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1977200
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 590976
33 | Ashuganj 225 MW CCPP | 216 | 217 | 181 | 183 | 181 | 183 | 214 | 182 | 199 | 203 | 187 | 183 | 183 | 186 | 216 | 215 | 214 | 215 |  | 214 | 217 | 182 | 183 | 181 | 183 | 182 | 4779000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 315 | 290 | 310 | 320 | 290 | 295 | 290 | 270 | 285 | 275 | 265 | 265 |  | 270 | 265 | 265 | 280 | 280 | 280 | 280 | 6795000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 300 | 260 | 285 | 295 | 265 | 345 | 310 | 315 | 325 | 315 | 310 | 310 |  | 315 | 300 | 260 | 280 | 280 | 280 | 280 | 7225000
35 | Ashuganj 55 MW PP (Precision) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 53 | 53 | 51 |  | 51 | 51 | 54 | 54 | 55 | 56 | 56 | 1193760
36 | Chandpur 150 MW CCPP | 87 | 90 | 90 | 91 | 90 | 91 | 91 | 91 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 85 | 86 | 90 | 87 | 90 | 89 | 2125220
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 338 | 340 | 341 | 338 | 338 | 340 | 359 | 330 | 306 | 345 | 339 | 339 | 339 | 338 | 351 | 343 | 342 | 340 |  | 340 | 337 | 341 | 338 | 338 | 337 | 341 | 8343854
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7125750
41 | Haripur 360MW CCPP(HPL) | 303 | 347 | 351 | 349 | 353 | 350 | 348 | 355 | 292 | 292 | 306 | 276 | 256 | 252 | 252 | 265 | 280 | 282 |  | 280 | 275 | 257 | 247 | 247 | 252 | 292 | 7058000
42 | RPCL 210MW CCPP | 181 | 181 | 181 | 193 | 197 | 197 | 105 | 122 | 119 | 119 | 118 | 118 | 117 | 116 | 117 | 118 | 116 | 114 |  | 114 | 102 | 105 | 102 | 102 | 155 | 155 | 3174520
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 5 | 7 | 9 | 28 | 9 | 56 | 54 | 34 | 44 | 19 | 13 | 3 | [8 empty] | 229290
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1034000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 996720
46 | Shajibazar 330 MW CCPP | 162 | 161 | 162 | 162 | 163 | 164 | 162 | 162 | 163 | 162 | 163 | 162 | 165 | 163 | 160 | 162 | 165 | 163 |  | 163 | 163 | 163 | 164 | 164 | 164 | 164 | 3659000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 50 | 51 | 51 | 51 | 61 | 60 | 60 | 61 | 61 |  | 61 | 61 | 62 | 62 | 62 | 61 | 61 | 1267776
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 40 | 40 | 75 | 75 | 78 | 78 | 78 | 75 | 78 | 78 | 80 | 80 | 50 |  | 50 | 81 | 81 | 81 | 81 | 81 | 81 | 1780800
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 232 | 232 | 225 | 192 | 192 | 185 | 185 | 185 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 |  | 219 | 219 | 219 | 219 | 219 | 219 | 218 | 5173600
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 395000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 232380
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 8 | 5 | 5 | 5 |  |  | 8 | 8 |  | 11 | 11 | 2 | 2 | 8 | 11 | 11 | 195500
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 14 | 14 | 14 | 45 | 50 | 51 | 50 | 50 | 50 | 50 | 53 |  | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 1134600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 394554
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 295 | 285 | 295 | 290 | 310 | 265 | 295 | 300 | 300 | 295 | 290 | 280 | 305 | 300 | 295 | 280 |  | 290 | 275 | 260 | 270 | 280 | 280 | 295 | 7149500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 355 | 350 | 350 | 301 | 310 | 340 | 340 | 340 | 340 | 340 | 340 |  | 365 | 400 | 400 | 400 | 400 | 400 | 400 | 8779900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 35 | 35 | 17 | 17 | 0 |  | 20 | 35 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1059103
59 | Tangail Palli Power Gen 22 MW | 23 | 0 | [5 empty] | 4 | 18 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 25 | 24 | 24 | 24 | 24 | 425280
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 526032
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 476208
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 485100
63 | Impoprt (Tripura) | 120 | 110 | 108 | 104 | 100 | 96 | 90 | 90 | 90 | 90 | 100 | 100 | 102 | 104 | 112 | 106 | 108 | 104 |  | 120 | 128 | 124 | 124 | 124 | 122 | 118 | 2589120
64 | Malancha, Ctg. EPZ (United) | 38 | 39 | 39 | 39 | 40 | 40 | 34 | 9 | 5 | 5 | 4 | 5 | 10 | 10 | 4 | 4 | 5 | 11 |  | 5 | 6 | 15 | 28 | 35 | 37 | 38 | 514080
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 450684
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244260
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817900
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 507890
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 26 | 26 | 30 | 30 | 30 | 30 |  | 18 | 18 | 30 | 30 | 30 | 30 | 30 | 679140
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 824800
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817400
73 | Ghorashal 108MW PP (Regent) | 100 | 100 | 100 | 100 | 100 | 101 | 101 | 52 | 52 | 85 | 95 | 98 | 98 | 99 | 99 | 97 | 97 | 55 |  | 80 | 96 | 90 | 90 | 99 | 99 | 98 | 2168272
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 100 | 100 | 100 | 100 | 100 | 100 | 17 | 1002060
| Chowmuhani 113 MW | 111 | 110 | 110 | 110 | 113 | 26 | 26 | 49 | 55 | 76 | 115 | 120 | 118 | 116 | 113 | 110 | 114 | 45 |  | 57 | 116 | 116 | 120 | 120 | 113 | 110 | 2333520
| Manikgonj 162MW PP(MPGL) | 54 | 0 | [5 empty] | 14 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 126 | 125 | 126 | 110 | 54 | 54 | 832320
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 75 | 7 | 7 | 22 | 40 | 42 | 87 | 100 | 100 | 100 | 100 | 100 | 50 | 50 |  | 55 | 100 | 100 | 100 | 100 | 100 | 100 | 1920778
78 | Gazipur 52 MW PP | 51 | 51 | 45 | 24 | 24 | 0 |  | 13 | 10 | 28 | 38 | 42 | 42 | 42 | 42 | 42 | 42 | 25 |  | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 871200
79 | Kodda 150MW PP | 138 | 48 | 0 |  |  |  |  | 16 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 48 | 48 | 48 |  | 70 | 150 | 150 | 150 | 150 | 150 | 150 | 1386240
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 192960
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 25 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 604620
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2500800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 4 | 5 | 6 | 5 | 3 | 1 | 1 | 1 | 0 | [8 empty] | 26881
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 38 | 36 | 30 | 38 | 54 | 37 | 37 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1195969
| Karnaphuli Power Ltd. | 110 | 68 | 68 | 68 | 17 | 17 | 17 | 36 | 51 | 51 | 83 | 110 | 110 | 110 | 110 | 110 | 110 | 51 |  | 60 | 110 | 110 | 110 | 110 | 110 | 110 | 2041554
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [17 empty] | 1 |  | 10 | 10 |  |  |  |  | 0 | 22394
86 | Meghnaghat CCPP ( Summit) | 285 | 270 | 285 | 285 | 270 | 260 | 260 | 265 | 270 | 285 | 280 | 275 | 279 | 285 | 280 | 280 | 260 | 260 |  | 272 | 230 | 255 | 265 | 245 | 280 | 265 | 6494865
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 17 | 72 | 53 |  |  |  | 0 | 123840
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 85 | 85 | 85 | 85 | 90 | 92 | 97 | 100 | 70 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2229000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 51 | 43 | 35 | 0 | [16 empty] | 5 | 25 | 51 | 43 | 411164
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 7 | 0 |  |  |  |  | 3 | 7 | 24 | 40 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 60 | 86 | 102 | 102 | 64 | 24 | 24 | 813888
95 | Patenga 50MW PP (Baraka) | [17 empty] | 5 |  | 6 | 20 | 22 | 30 | 30 |  | 0 | 101280
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 4 |  | 15 | 55 | 15 | 15 | 15 |  | 0 | 113654
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 35 | 35 |  |  |  | 0 | 57906
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 163 | 130 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3413618
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | [8 empty] | 9200
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 35 | 35 | 35 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 38 | 54 | 54 | 54 | 54 | 54 | 54 | 1002960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 192 | 192 | 130 | 100 | 100 | 65 | 67 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 93 | 184 | 184 | 189 | 190 | 190 | 190 | 2911200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 55 | 50 | 35 | 25 | 15 | 15 | 15 | 15 | 19 | 48 | 50 | 66 | 95 | 95 | 95 | 77 | 64 | 51 |  | 51 | 60 | 64 | 104 | 100 | 93 | 86 | 1428770
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 70 | 70 | 30 | 0 |  |  | 20 | 20 | 20 | 60 | 100 | 100 | 100 | 100 | 100 | 50 | 30 |  | 75 | 100 | 100 | 100 | 100 | 100 | 100 | 1602240
116 | Chandpur 200MW (Desh energy) | 178 | 85 | 85 | 50 | 17 | 17 | 17 | 53 | 85 | 89 | 112 | 133 | 160 | 160 | 160 | 160 | 90 | 85 |  | 90 | 160 | 155 | 165 | 178 | 180 | 180 | 2897760
117 | Ashuganj 150MW PP (Midland) | 24 | 0 | [19 empty] | 1 | 23 | 70 | 70 | 70 | 289381
118 | Bibiyana-III 400 MW CCPP | 366 | 367 | 330 | 330 | 330 | 328 | 375 | 306 | 333 | 376 | 375 | 367 | 367 | 374 | 368 | 372 | 367 | 331 |  | 372 | 367 | 368 | 368 | 367 | 368 | 366 | 8544000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2762400
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 30 | 0 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 432000
| Anlima Energy Ltd. | 17 | 0 | [5 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 |  |  |  |  | 0 | 249655
| Bhairob 54.5 MW | 36 | 19 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 19 | 36 | 36 | 36 | 36 | 36 | 36 | 558720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 2 | 10 | 6 | 13 | 22 | 6 | 9 | 5 | 7 | 5 | 2 | [8 empty] | 101190
120 | Eastern Zone Total | 7731 | 7220 | 7008 | 6822 | 6638 | 6187 | 6075 | 5975 | 6127 | 6473 | 6654 | 6910 | 7048 | 7060 | 7228 | 7166 | 6970 | 6617 |  | 7326 | 8415 | 8268 | 8349 | 8347 | 8100 | 8021 | 172227086
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 91 | 53 | 53 | 17 | 17 | 17 | 30 | 80 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 35 | 35 |  | 53 | 91 | 92 | 91 | 91 | 91 | 91 | 1750560
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 223 | 223 | 222 | 222 | 222 | 222 | 180 | 150 | 151 | 151 | 151 | 151 | 151 | 151 | 150 | 151 | 131 |  | 160 | 202 | 202 | 202 | 202 | 202 | 202 | 4435400
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | 12 | 12 |  | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 288654
| Bhola 225 MW CCPP | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 85 | 86 | 82 |  | 85 | 82 | 83 | 83 | 83 | 84 | 84 | 2067345
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 26 | 25 | 22 | 22 | 19 | 18 | 17 | 18 | 18 | 19 | 20 | 20 | 20 | 20 | 19 | 18 |  | 27 | 23 | 30 | 31 | 32 | 32 | 31 | 552434
141 | Noapara 100 MW PP (Bangla Trac) | [11 empty] | 9 | 60 | 60 | 60 | [5 empty] | 65 | 75 | 100 | 100 | 100 | 50 | 698880
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [11 empty] | 5 | 7 | 8 | 8 | 8 | 10 | [9 empty] | 40323
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 733 | 845 | 844 | 845 | 837 | 827 | 827 | 826 | 827 | 826 | 827 | 826 | 827 | 826 | 826 | 827 | 827 | 827 |  | 892 | 893 | 893 | 753 | 753 | 753 | 753 | 19682181
147 | Bheramara 410 MW CCPP | 390 | 390 | 390 | 390 | 385 | 350 | 350 | 300 | 350 | 350 | 380 | 380 | 380 | 340 | 340 | 340 | 340 | 340 |  | 360 | 370 | 370 | 385 | 380 | 390 | 390 | 9066240
148 | Payra 1320 MW | 420 | 400 | 400 | 380 | 360 | 300 | 270 | 280 | 290 | 290 | 290 | 290 | 290 | 310 | 320 | 320 | 320 | 320 |  | 320 | 380 | 390 | 480 | 530 | 530 | 520 | 9712600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3668000
153 | Baghabari 71 MW GTPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 50 | 50 | 50 | 65 | 65 | 65 | 60 | 60 | 60 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1485000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 0 | [17 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 336528
| Sirajgonj 6.55 MW Solar | [9 empty] | 2 | 1 | 0 | 1 | 4 | 1 | 2 | 1 | 0 | [8 empty] | 14580
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 177 | 178 | 179 | 176 | 177 | 160 | 130 | 153 | 169 | 176 | 166 | 189 | 184 | 182 | 194 | 188 | 186 | 176 |  | 160 | 167 | 163 | 166 | 183 | 183 | 187 | 4415436
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 188 | 190 | 191 | 183 | 190 | 130 | 137 | 174 | 169 | 182 | 198 | 188 | 187 | 185 | 196 | 190 | 188 | 177 |  | 175 | 183 | 179 | 180 | 189 | 187 | 189 | 4647473
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 409 | 399 | 416 | 406 | 399 | 336 | 352 | 285 | 335 | 395 | 413 | 392 | 367 | 374 | 376 | 377 | 354 | 359 |  | 376 | 323 | 340 | 356 | 327 | 374 | 354 | 8959500
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 16 | 0 | [15 empty] | 6 |  | 10 | 16 | 42 | 39 | 28 |  |  | 131940
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 499440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 151128
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 6 | 35 | 35 | 35 | 35 |  | 0 | 142010
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 8 | 16 | 43 | 34 | 43 |  |  | 99224
167 | Katakhali 50 MW Peaking PP | 38 | 38 | 0 | [16 empty] | 24 | 40 | 40 | 38 | 38 |  |  | 215304
168 | Santahar 50 MW Peaking PP
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 |  |  | 11 | 16 | 16 | 24 | 52 | 52 | 52 | 43 | 52 | 52 | 8 |  | 8 | 16 | 32 | 52 | 52 | 52 | 52 | 920160
170 | Chapainawabganj 100 MW Peaking PP | 87 | 87 | 40 | 0 | [15 empty] | 70 | 86 | 86 | 87 | 87 | 87 | 87 | 694488
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 35 | 0 | [9 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 |  | 40 | 55 | 93 | 113 | 113 | 113 | 113 | 951840
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 15 | 35 | 35 | 35 | 35 | 35 | 35 |  | 50 | 80 | 100 | 113 | 113 | 113 | 113 | 930240
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 70 | 0 | 49 | 49 | 49 | 0 | [13 empty] | 42 | 80 | 108 | 113 | 113 | 113 | 113 | 835785
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 5 | 6 | 6 | 6 | 6 | 5 | 3 | 2 | 0 | [8 empty] | 46211
178
178