## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-04 | Sunday
|  |  | Date (day): | 2021-07-04 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14133.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15507 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-03 | 2021-07-04 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 89 | 98 | 100 | 100
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 360 | 340 | 350 | 360 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 343 | 341 | 350 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 310 | 310 | 300 | 310 | 140 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 270 | 300 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 19 | 19 | 19 |  | 3 | Engine problem
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 95 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 103 | 222 | 220 | 220 |  | 115 | Machine problem
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 0 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 35 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 55 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 37 | 42 | 51 | 51
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 250 | 290
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 30 | 80 | 130 | 132 |  | 17 | Engine problem
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 85 | 86 | 84 | 86 |  | 19 | Engine problem
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 4 | 0 | 90 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 14 | 108 | 126 | 126 |  | 36 | Engine problem
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 21 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5819 | 2217 | 2687 | 3760 | 4050 | 509 | 1060
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 7 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 27 | 28 | 29 | 29 | 201 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 210 | 215
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 115 | 100 | 110 | 115 |  | 50 | Machine problem
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 76 | 105 | 85 | 105 |  | 0 | Engine problem
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 68 | 68 |  | 34 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 0 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 4 | 24 | 5 | 15
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 97 | 95 | 97 |  | 11 | Engine problem
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 7 | 17 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 18 | 85 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 10 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 111 | 112 | 112 | 112 |  | 24
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 878 | 1090 | 1594 | 1711 | 461 | 217
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 214 | 182 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 315 | 350 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 300 | 330 | 350 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 54 | 57 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 26 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 51 | 51 | 51
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 3 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 24 | 34 | 170 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 46 | 128 | 148 | 172
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 25 | 34 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 114 | 100 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 116 | 116 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 18 | 18 |  | 36 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1372 | 1726 | 2048 | 2305 | 353 | 361
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 201 | 167 | 200 | 200
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 90 | 175 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 48 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 10 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 303 | 411 | 592.6 | 566 | 0 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 42 | 42 |  | 48 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 110 | 110 | 110 | 110 |  | 220 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 62 | 63
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 84 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 218 | 225 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 14 | 15 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 285 | 300 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 401 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 401 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1719 | 1735 | 1771 | 1814 | 0 | 567
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 804 | 816 | 816
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 20 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 0 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 60 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 400 | 400 | 350 | 380 | 30 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 25 | 90 | 90 | 90 |  | 15 | Engine problem
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2129 | 1135 | 1394 | 1486 | 1786 | 30 | 98
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 19 | 29 | 25 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 86 | 85 | 86 |  | 108 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 10 | 11 | 11 | 84 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 500 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 221 | 223 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 657 | 848 | 1073 | 1192 | 84 | 108
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 70 | 60 | 60
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 80 | 80 | 80 | 20 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 43 |  | 28 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 12 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 50 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 181 | 200 | 200 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 183 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 394 | 415 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 42 | 0 | 40 |  | 10 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 18 | 18
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 0 | 95
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 35 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 50 | 90 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 955 | 1361 | 1538 | 1800 | 230 | 63
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 186 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21060 | 9422 | 11515 | 14133.6 | 15507 | 1791 | 2751
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9000.6079 | 11000 | 13501.485 | 14813.4607
| A. |  | 2021-07-03 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 11515 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7594 | MW at | 6:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11515 | MW
| 3 | Day peak Generation : |  |  | 9422 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11000 | MW
| 4 | Evening peak Generation : |  |  | 11515 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 226.5232 | MKWHr | By Solar | 0.51257 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 157.8895 | MKWHr |  | By Oil: | 35.0633 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6334 | MKWHr |  | By Hydro: | 0.5766 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1791 | MW | Dhaka | 3842 | 3842 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2751 | MW | Chittagong | 1150 | 1150 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4542 | MW | Khulna | 1377 | 1377 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1253.34 | MMCFD |  |  | Rajshahi | 1185 | 1185 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 165881768.162 | ii) Oil : | Taka | 233740812.39 | Comilla | 1039 | 1039 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 63643292 | Total | Taka | 463265872.552 | Mymensingh | 897 | 897 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.7 | MKWHr. | Sylhet | 445 | 445 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 14 | MW (E to W) at | 21:00 | hrs | Barisal | 322 | 322 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -128 | MW at | 19:30 | hrs | Rangpur | 743 | 743 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 11000 | 11000 |  | 0
| B. |  | 2021-07-04 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15507 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9800 | MW
| 4 | Reserve(Generation end) |  |  |  | 3507 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 236.0641 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8335 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.3076 | MKWHr. | ii) HVDC Flow at Peak Time |  | 804 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5402 | MKWHr. | iii) Maximum HVDC Flow : |  | 805 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 78.38 |  | (b) Today: | 79.16 |  | (c) Rule Curve: |  | 84.48
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-03
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 317 | 296 |  | 0 | 310 | 270 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 25 | 28 | 28 | 33 | 0 | 0 | 27 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 34 | 40 | 97 | 0 | 16 | 42 | 100 | 0 | 0 | 260 | 265 | 183 | 8 | 0 | 23 | 57 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 11 | 102 | 203 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 110 | 62 | 84 | 0 | 218 | 18 | 0 | 0 | 280 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 55 | 50 | 0 | 0 | 0 | 0 | 0 | 114 | 94 | 0 | 350 | 0 | 0 | 0 | 110 | 0 | 18 | 0 |  | 613 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 80 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 148 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 170 | 0 | 0 | 0 |  | 6058 | 2700 | 8758 | 4663 | 613 | 1841 | 898 | 580 | 27 | 34 | 102 | 0 | 0 | 78.18
2:00 | 0 | 0 | 0 | 0 | 300 | 97 | 0 | 317 | 323 |  | 0 | 310 | 275 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 27 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 17 | 0 | 97 | 0 | 16 | 42 | 100 | 0 | 0 | 260 | 270 | 185 | 8 | 0 | 23 | 57 | 0 | 51 | 0 | 0 | 0 | 13 | 11 | 33 | 12 | 100 | 204 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 110 | 62 | 50 | 0 | 218 | 18 | 0 | 0 | 290 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 55 | 34 | 0 | 0 | 0 | 0 | 0 | 114 | 45 | 0 | 380 | 0 | 0 | 0 | 110 | 0 | 18 | 0 |  | 567 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 60 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 148 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 170 | 0 | 0 | 0 |  | 5917 | 2595 | 8512 | 4651 | 567 | 1807 | 773 | 570 | 27 | 17 | 100 | 0 | 0 | 78.22
3:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 325 | 350 |  | 0 | 310 | 275 | 0 | 0 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 27 | 0 | 100 | 0 | 0 | 211 | 0 | 110 | 0 |  | 0 | 0 | 17 | 0 | 90 | 0 | 16 | 42 | 100 | 0 | 0 | 275 | 280 | 193 | 8 | 0 | 23 | 57 | 0 | 10 | 0 | 0 | 0 | 13 | 11 | 33 | 12 | 98 | 204 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 111 | 40 | 10 | 0 | 218 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 114 | 36 | 0 | 401 | 0 | 0 | 0 | 35 | 0 | 18 | 0 |  | 567 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 155 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 170 | 0 | 0 | 0 |  | 5715 | 2552 | 8267 | 4685 | 567 | 1661 | 662 | 550 | 27 | 17 | 98 | 0 | 0 | 78.26
4:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 324 | 351 |  | 0 | 310 | 275 | 0 | 0 | 0 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 28 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 17 | 0 | 55 | 0 | 16 | 42 | 80 | 0 | 0 | 260 | 265 | 185 | 8 | 0 | 23 | 57 | 0 | 10 | 0 | 0 | 0 | 13 | 11 | 33 | 17 | 100 | 204 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 110 | 40 | 10 | 0 | 218 | 18 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 376 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 114 | 36 | 0 | 401 | 0 | 0 | 0 | 17 | 0 | 18 | 0 |  | 566 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 162 | 0 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 170 | 0 | 0 | 0 |  | 5604 | 2558 | 8162 | 4629 | 566 | 1663 | 609 | 550 | 28 | 17 | 100 | 0 | 0 | 78.3
5:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 318 | 354 |  | 0 | 310 | 250 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 28 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 17 | 0 | 51 | 0 | 16 | 42 | 80 | 0 | 0 | 260 | 265 | 182 | 8 | 0 | 23 | 57 | 0 | 10 | 0 | 0 | 0 | 13 | 11 | 33 | 17 | 96 | 203 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 109 | 40 | 10 | 0 | 218 | 18 | 0 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 353 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 114 | 36 | 0 | 380 | 0 | 0 | 0 | 17 | 0 | 18 | 0 |  | 567 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 180 | 0 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 170 | 0 | 0 | 0 |  | 5515 | 2522 | 8037 | 4589 | 567 | 1630 | 580 | 530 | 28 | 17 | 96 | 0 | 0 | 78.34
6:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 316 | 282 |  | 0 | 310 | 260 | 0 | 0 | 0 | 222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 28 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 17 | 0 | 52 | 0 | 16 | 42 | 80 | 0 | 0 | 260 | 265 | 182 | 8 | 0 | 23 | 57 | 0 | 10 | 0 | 0 | 0 | 13 | 11 | 33 | 17 | 84 | 204 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 109 | 40 | 10 | 0 | 178 | 18 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 322 | 35 | 34 | 0 | 0 | 0 | 0 | 0 | 17 | 78 | 0 | 320 | 0 | 0 | 0 | 17 | 0 | 18 | 0 |  | 579 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 15 | 0 | 0 | 60 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 149 | 0 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 340 | 132 | 0 | 0 | 0 |  | 5236 | 2358 | 7594 | 4364 | 579 | 1495 | 536 | 490 | 28 | 17 | 84 | 1 | 0 | 78.38
7:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 317 | 283 |  | 0 | 310 | 260 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 28 | 0 | 100 | 0 | 0 | 203 | 0 | 110 | 0 |  | 0 | 0 | 17 | 50 | 53 | 0 | 16 | 35 | 80 | 0 | 0 | 260 | 265 | 189 | 8 | 0 | 23 | 56 | 0 | 10 | 0 | 0 | 0 | 13 | 11 | 33 | 17 | 86 | 204 | 8 | 21 | 0 | 44 | 30 | 14 | 0 | 0 | 110 | 40 | 10 | 0 | 178 | 18 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 324 | 35 | 37 | 3 | 1 | 0 | 0 | 0 | 17 | 118 | 0 | 320 | 0 | 2 | 0 | 30 | 0 | 18 | 4 |  | 675 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 14 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 11 | 0 | 147 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 130 | 0 | 0 | 0 |  | 5335 | 2426 | 7761 | 4328 | 675 | 1491 | 646 | 480 | 28 | 17 | 86 | 10 | 0 | 78.42
8:00 | 0 | 0 | 0 | 0 | 300 | 13 | 0 | 339 | 282 |  | 0 | 310 | 280 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 28 | 28 | 33 | 0 | 0 | 27 | 0 | 100 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 17 | 50 | 95 | 0 | 16 | 17 | 80 | 0 | 0 | 265 | 280 | 200 | 8 | 0 | 20 | 57 | 0 | 10 | 0 | 0 | 7 | 13 | 11 | 33 | 17 | 88 | 204 | 8 | 21 | 0 | 44 | 30 | 30 | 0 | 0 | 111 | 63 | 60 | 0 | 178 | 18 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 324 | 8 | 61 | 17 | 2 | 0 | 0 | 0 | 17 | 121 | 0 | 320 | 0 | 4 | 0 | 90 | 0 | 18 | 10 |  | 567 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 14 | 0 | 0 | 80 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 11 | 0 | 145 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 130 | 0 | 0 | 0 |  | 5613 | 2369 | 7982 | 4407 | 567 | 1586 | 789 | 480 | 27 | 17 | 88 | 21 | 0 | 78.46
9:00 | 0 | 0 | 0 | 0 | 300 | 13 | 0 | 377 | 281 |  | 0 | 310 | 300 | 0 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 17 | 17 | 25 | 28 | 33 | 33 | 13 | 0 | 27 | 0 | 100 | 0 | 0 | 217 | 0 | 110 | 0 |  | 0 | 0 | 17 | 50 | 96 | 0 | 16 | 3 | 80 | 0 | 0 | 300 | 315 | 203 | 8 | 0 | 23 | 56 | 0 | 10 | 0 | 0 | 25 | 13 | 11 | 33 | 18 | 82 | 203 | 8 | 21 | 0 | 43 | 30 | 45 | 0 | 0 | 110 | 60 | 81 | 0 | 178 | 18 | 0 | 0 | 320 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 9 | 0 | 0 | 0 | 323 | 8 | 76 | 17 | 3 | 0 | 0 | 0 | 17 | 120 | 0 | 320 | 0 | 6 | 0 | 90 | 0 | 18 | 15 |  | 659 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 14 | 0 | 0 | 80 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 163 | 0 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 131 | 0 | 0 | 0 |  | 5922 | 2525 | 8447 | 4630 | 659 | 1639 | 879 | 480 | 27 | 17 | 82 | 34 | 0 | 78.5
10:00 | 0 | 0 | 0 | 0 | 300 | 13 | 0 | 375 | 344 |  | 0 | 310 | 285 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 45 | 15 | 25 | 28 | 33 | 33 | 41 | 0 | 26 | 0 | 100 | 0 | 0 | 215 | 0 | 110 | 0 |  | 0 | 0 | 17 | 50 | 96 | 0 | 16 | 5 | 80 | 0 | 0 | 280 | 300 | 213 | 8 | 0 | 23 | 55 | 0 | 10 | 0 | 0 | 25 | 0 | 11 | 33 | 18 | 92 | 203 | 8 | 21 | 0 | 43 | 30 | 45 | 0 | 0 | 110 | 61 | 81 | 0 | 178 | 18 | 0 | 0 | 310 | 8 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 11 | 0 | 0 | 0 | 322 | 8 | 85 | 17 | 4 | 0 | 0 | 0 | 17 | 120 | 0 | 320 | 0 | 22 | 0 | 90 | 0 | 35 | 21 |  | 709 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 15 | 0 | 0 | 80 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 195 | 0 | 11 | 0 | 191 | 0 | 411 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 131 | 0 | 0 | 3 |  | 6094 | 2703 | 8797 | 4676 | 709 | 1767 | 969 | 479 | 26 | 17 | 92 | 62 | 0 | 78.54
11:00 | 0 | 0 | 0 | 0 | 300 | 79 | 0 | 367 | 345 |  | 0 | 310 | 285 | 0 | 0 | 0 | 214 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 55 | 15 | 25 | 28 | 33 | 33 | 42 | 0 | 26 | 0 | 100 | 0 | 0 | 215 | 0 | 115 | 0 |  | 0 | 0 | 0 | 100 | 85 | 0 | 16 | 3 | 80 | 0 | 0 | 330 | 300 | 215 | 8 | 0 | 23 | 55 | 0 | 22 | 0 | 0 | 25 | 0 | 11 | 33 | 18 | 88 | 201 | 8 | 21 | 1 | 43 | 30 | 47 | 0 | 0 | 110 | 61 | 81 | 0 | 218 | 18 | 0 | 0 | 310 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 7 | 0 | 0 | 0 | 389 | 8 | 85 | 23 | 6 | 0 | 0 | 0 | 17 | 119 | 0 | 394 | 0 | 34 | 0 | 101 | 0 | 36 | 21 |  | 566 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 60 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 196 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 330 | 171 | 0 | 0 | 3 |  | 6446 | 2605 | 9051 | 4891 | 566 | 1888 | 1039 | 480 | 26 | 0 | 88 | 73 | 0 | 78.58
12:00 | 0 | 0 | 0 | 0 | 300 | 89 | 0 | 360 | 343 |  | 0 | 310 | 265 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 15 | 25 | 28 | 33 | 33 | 37 | 0 | 27 | 0 | 100 | 0 | 7 | 204 | 0 | 115 | 0 |  | 0 | 0 | 0 | 100 | 85 | 0 | 16 | 4 | 80 | 0 | 0 | 310 | 275 | 214 | 26 | 0 | 20 | 54 | 0 | 43 | 0 | 0 | 25 | 21 | 11 | 33 | 18 | 46 | 201 | 8 | 21 | 1 | 43 | 30 | 47 | 0 | 0 | 110 | 61 | 81 | 0 | 218 | 18 | 0 | 0 | 300 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 8 | 0 | 24 | 3 | 402 | 48 | 85 | 76 | 0 | 0 | 7 | 18 | 17 | 116 | 0 | 401 | 4 | 24 | 14 | 111 | 0 | 36 | 21 |  | 710 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 188 | 0 | 394 | 25 | 0 | 0 | 0 | 34 | 0 | 2 | 50 | 320 | 221 | 0 | 0 | 3 |  | 6489 | 2933 | 9422 | 4803 | 710 | 1960 | 1331 | 470 | 27 | 16 | 46 | 59 | 0 | 78.62
13:00 | 0 | 0 | 0 | 0 | 300 | 92 | 0 | 340 | 343 |  | 0 | 310 | 265 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 15 | 25 | 28 | 33 | 33 | 42 | 0 | 27 | 0 | 100 | 0 | 18 | 204 | 0 | 115 | 0 |  | 0 | 0 | 0 | 100 | 90 | 0 | 16 | 2 | 80 | 0 | 0 | 310 | 275 | 215 | 26 | 0 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 18 | 112 | 162 | 8 | 21 | 2 | 43 | 30 | 49 | 0 | 0 | 112 | 61 | 84 | 0 | 218 | 18 | 0 | 0 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 18 | 0 | 34 | 23 | 403 | 115 | 68 | 105 | 0 | 0 | 17 | 51 | 17 | 117 | 0 | 397 | 34 | 35 | 35 | 112 | 0 | 36 | 18 |  | 710 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 60 | 60 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 181 | 0 | 323 | 53 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 310 | 221 | 0 | 0 | 3 |  | 6887 | 2902 | 9789 | 4844 | 710 | 1883 | 1589 | 460 | 27 | 86 | 112 | 78 | 0 | 78.65
14:00 | 0 | 0 | 0 | 0 | 300 | 89 | 0 | 340 | 321 |  | 0 | 310 | 270 | 0 | 0 | 0 | 212 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 15 | 25 | 28 | 33 | 33 | 42 | 0 | 27 | 0 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 0 | 0 | 12 | 100 | 89 | 0 | 16 | 3 | 80 | 0 | 0 | 260 | 265 | 214 | 26 | 0 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 20 | 116 | 161 | 8 | 21 | 2 | 43 | 30 | 50 | 0 | 0 | 110 | 60 | 84 | 0 | 218 | 18 | 0 | 9 | 280 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 18 | 0 | 34 | 30 | 404 | 115 | 86 | 105 | 2 | 0 | 17 | 51 | 17 | 118 | 0 | 394 | 17 | 40 | 35 | 111 | 0 | 36 | 17 |  | 709 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 65 | 60 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 172 | 0 | 340 | 53 | 0 | 0 | 0 | 34 | 0 | 2 | 35 | 320 | 220 | 0 | 0 | 2 |  | 6847 | 2874 | 9721 | 4708 | 709 | 1886 | 1624 | 470 | 27 | 98 | 116 | 83 | 0 | 78.68
15:00 | 0 | 0 | 0 | 0 | 300 | 88 | 0 | 366 | 316 |  | 0 | 310 | 275 | 0 | 0 | 0 | 215 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 17 | 25 | 28 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 102 | 0 |  | 0 | 0 | 12 | 100 | 90 | 0 | 16 | 3 | 80 | 0 | 0 | 275 | 275 | 213 | 26 | 0 | 23 | 53 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 20 | 118 | 162 | 8 | 21 | 1 | 44 | 30 | 50 | 0 | 0 | 110 | 61 | 83 | 0 | 218 | 18 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 9 | 0 | 34 | 36 | 404 | 115 | 86 | 105 | 2 | 0 | 17 | 51 | 17 | 119 | 0 | 392 | 17 | 38 | 35 | 112 | 0 | 36 | 8 |  | 710 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 70 | 65 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 189 | 0 | 399 | 53 | 0 | 0 | 0 | 34 | 0 | 5 | 35 | 330 | 220 | 0 | 0 | 0 |  | 6903 | 3028 | 9931 | 4841 | 710 | 1955 | 1638 | 480 | 28 | 98 | 118 | 63 | 0 | 78.71
16:00 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 339 | 316 |  | 0 | 310 | 265 | 0 | 0 | 0 | 218 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 17 | 25 | 28 | 33 | 33 | 25 | 0 | 28 | 0 | 100 | 0 | 8 | 202 | 0 | 100 | 0 |  | 0 | 0 | 12 | 100 | 94 | 0 | 15 | 8 | 80 | 0 | 0 | 275 | 275 | 214 | 26 | 0 | 26 | 52 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 20 | 108 | 177 | 8 | 21 | 1 | 44 | 30 | 50 | 0 | 0 | 110 | 60 | 30 | 0 | 218 | 18 | 0 | 0 | 290 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 10 | 0 | 17 | 36 | 403 | 105 | 86 | 51 | 1 | 0 | 17 | 17 | 17 | 55 | 0 | 396 | 17 | 22 | 35 | 112 | 0 | 36 | 0 |  | 710 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 75 | 70 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 0 | 181 | 0 | 366 | 53 | 0 | 0 | 0 | 34 | 0 | 4 | 35 | 320 | 180 | 0 | 0 | 1 |  | 6604 | 2952 | 9556 | 4852 | 710 | 1813 | 1438 | 470 | 28 | 98 | 108 | 39 | 0 | 78.74
17:00 | 0 | 0 | 0 | 0 | 300 | 47 | 0 | 339 | 336 |  | 0 | 310 | 255 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 17 | 25 | 28 | 33 | 33 | 30 | 0 | 28 | 0 | 100 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 17 | 20 | 97 | 0 | 15 | 8 | 80 | 0 | 0 | 275 | 275 | 215 | 26 | 0 | 26 | 52 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 20 | 104 | 177 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 111 | 60 | 30 | 0 | 191 | 18 | 0 | 0 | 280 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 17 | 10 | 353 | 85 | 86 | 17 | 1 | 0 | 17 | 17 | 17 | 55 | 0 | 350 | 17 | 1 | 35 | 72 | 0 | 36 | 0 |  | 710 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 75 | 65 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 184 | 0 | 312 | 17 | 0 | 0 | 0 | 35 | 0 | 3 | 35 | 320 | 151 | 0 | 0 | 0 |  | 6140 | 2835 | 8975 | 4691 | 710 | 1663 | 1201 | 470 | 28 | 103 | 104 | 5 | 0 | 78.77
18:00 | 0 | 0 | 0 | 0 | 300 | 47 | 0 | 339 | 346 |  | 0 | 310 | 265 | 0 | 0 | 0 | 175 | 0 | 0 | 0 | 16 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 19 | 25 | 28 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 8 | 203 | 0 | 100 | 0 |  | 0 | 0 | 17 | 20 | 97 | 0 | 15 | 6 | 80 | 0 | 0 | 275 | 275 | 183 | 26 | 0 | 26 | 53 | 0 | 51 | 0 | 0 | 25 | 21 | 11 | 33 | 20 | 96 | 183 | 8 | 21 | 0 | 43 | 30 | 14 | 0 | 0 | 111 | 61 | 30 | 0 | 184 | 18 | 0 | 0 | 290 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 0 | 0 | 17 | 10 | 304 | 55 | 86 | 17 | 0 | 0 | 17 | 17 | 17 | 55 | 0 | 350 | 17 | 0 | 35 | 53 | 0 | 36 | 1 |  | 709 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 80 | 65 | 0 | 10 | 56 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 162 | 0 | 11 | 0 | 185 | 0 | 329 | 17 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 320 | 152 | 0 | 0 | 0 |  | 6024 | 2775 | 8799 | 4526 | 709 | 1700 | 1154 | 470 | 28 | 115 | 96 | 1 | 0 | 78.8
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 47 | 0 | 340 | 350 |  | 0 | 310 | 290 | 0 | 0 | 0 | 175 | 0 | 0 | 7 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 16 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 10 | 206 | 0 | 100 | 0 |  | 4 | 0 | 63 | 100 | 97 | 0 | 16 | 6 | 80 | 0 | 0 | 285 | 285 | 191 | 26 | 0 | 26 | 54 | 0 | 51 | 0 | 42 | 25 | 21 | 11 | 33 | 0 | 130 | 170 | 8 | 21 | 0 | 44 | 30 | 14 | 0 | 0 | 110 | 61 | 30 | 0 | 184 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 6 | 0 | 0 | 15 | 0 | 59 | 0 | 0 | 28 | 36 | 324 | 73 | 86 | 30 | 0 | 0 | 17 | 21 | 114 | 72 | 10 | 350 | 17 | 0 | 48 | 71 | 0 | 36 | 0 |  | 709 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 0 | 0 | 80 | 65 | 50 | 10 | 95 | 12 | 0 | 30 | 7 | 27 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 185 | 0 | 344 | 20 | 0 | 18 | 0 | 95 | 0 | 0 | 50 | 340 | 152 | 0 | 0 | 0 |  | 6682 | 3084 | 9766 | 4556 | 709 | 1737 | 1649 | 490 | 28 | 467 | 130 | 0 | 0 | 78.89
19:30 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 339 | 351 |  | 0 | 310 | 275 | 0 | 0 | 0 | 220 | 0 | 0 | 40 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 16 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 10 | 0 | 68 | 100 | 97 | 0 | 16 | 10 | 80 | 0 | 0 | 275 | 275 | 182 | 26 | 0 | 26 | 55 | 0 | 51 | 0 | 50 | 25 | 22 | 11 | 33 | 0 | 128 | 170 | 8 | 21 | 0 | 44 | 30 | 49 | 0 | 0 | 110 | 61 | 30 | 0 | 218 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 15 | 0 | 0 | 80 | 0 | 80 | 0 | 0 | 68 | 148 | 400 | 115 | 86 | 105 | 0 | 0 | 17 | 85 | 114 | 120 | 10 | 395 | 0 | 0 | 100 | 112 | 0 | 36 | 0 |  | 804 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 80 | 65 | 50 | 13 | 96 | 12 | 0 | 30 | 23 | 37 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 65 | 180 | 0 | 327 | 90 | 0 | 35 | 0 | 111 | 0 | 0 | 70 | 430 | 220 | 0 | 0 | 0 |  | 7542 | 3548 | 11090 | 4733 | 804 | 1879 | 2444 | 580 | 28 | 494 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 91 | 0 | 349 | 355 |  | 0 | 310 | 240 | 0 | 0 | 0 | 225 | 0 | 0 | 65 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 29 | 33 | 12 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 0 | 0 | 68 | 100 | 97 | 0 | 16 | 14 | 80 | 0 | 0 | 275 | 300 | 182 | 26 | 0 | 26 | 55 | 0 | 51 | 0 | 42 | 25 | 22 | 11 | 33 | 12 | 130 | 169 | 8 | 21 | 0 | 43 | 30 | 49 | 0 | 0 | 111 | 62 | 84 | 0 | 218 | 18 | 0 | 10 | 300 | 14 | 11 | 0 | 15 | 0 | 0 | 70 | 0 | 76 | 0 | 0 | 68 | 128 | 400 | 115 | 86 | 105 | 0 | 0 | 17 | 75 | 114 | 117 | 10 | 401 | 0 | 0 | 106 | 112 | 0 | 36 | 0 |  | 805 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 28 | 0 | 0 | 80 | 65 | 43 | 32 | 95 | 12 | 0 | 33 | 48 | 43 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 70 | 186 | 0 | 376 | 85 | 0 | 35 | 0 | 113 | 0 | 0 | 90 | 450 | 220 | 0 | 0 | 0 |  | 7590 | 3753 | 11343 | 4846 | 805 | 1998 | 2430 | 600 | 28 | 506 | 130 | 0 | 0 | 78.86
21:00 | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 340 | 341 |  | 0 | 310 | 270 | 0 | 0 | 0 | 222 | 0 | 0 | 95 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 10 | 0 | 68 | 100 | 97 | 0 | 16 | 24 | 80 | 0 | 0 | 315 | 300 | 182 | 26 | 0 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 128 | 167 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 110 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 285 | 14 | 11 | 0 | 15 | 0 | 0 | 90 | 0 | 80 | 0 | 0 | 34 | 150 | 401 | 115 | 86 | 105 | 0 | 0 | 17 | 85 | 114 | 116 | 10 | 400 | 0 | 0 | 108 | 112 | 0 | 36 | 0 |  | 804 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 80 | 70 | 50 | 0 | 95 | 12 | 0 | 30 | 52 | 42 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 10 | 100 | 183 | 0 | 415 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 90 | 500 | 223 | 0 | 0 | 0 |  | 7649 | 3866 | 11515 | 4912 | 804 | 2031 | 2527 | 650 | 28 | 435 | 128 | 0 | 0 | 78.89
22:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 321 | 332 |  | 0 | 310 | 270 | 0 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 11 | 0 | 68 | 100 | 97 | 0 | 16 | 29 | 80 | 0 | 0 | 320 | 300 | 182 | 26 | 0 | 26 | 56 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 114 | 169 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 109 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 14 | 11 | 0 | 15 | 0 | 0 | 90 | 0 | 80 | 0 | 0 | 34 | 150 | 401 | 115 | 86 | 105 | 0 | 0 | 17 | 85 | 114 | 115 | 10 | 392 | 0 | 0 | 35 | 112 | 0 | 36 | 0 |  | 804 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 30 | 0 | 0 | 80 | 70 | 50 | 0 | 96 | 12 | 0 | 30 | 52 | 36 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 11 | 100 | 186 | 0 | 398 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 90 | 520 | 223 | 0 | 0 | 0 |  | 7545 | 3879 | 11424 | 4902 | 804 | 2017 | 2459 | 670 | 28 | 430 | 114 | 0 | 0 | 78.92
23:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 318 | 350 |  | 0 | 310 | 270 | 0 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 34 | 100 | 97 | 0 | 16 | 33 | 80 | 0 | 0 | 310 | 300 | 187 | 26 | 0 | 26 | 56 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 130 | 183 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 110 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 285 | 14 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 67 | 0 | 0 | 17 | 148 | 402 | 115 | 86 | 105 | 0 | 0 | 0 | 85 | 114 | 117 | 10 | 400 | 0 | 0 | 0 | 111 | 0 | 36 | 0 |  | 804 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 80 | 65 | 50 | 0 | 96 | 0 | 0 | 30 | 52 | 36 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 11 | 100 | 189 | 0 | 411 | 90 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 500 | 221 | 0 | 0 | 0 |  | 7284 | 3724 | 11008 | 4914 | 804 | 2045 | 2077 | 649 | 28 | 361 | 130 | 0 | 0 | 78.95
24:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 324 | 353 |  | 0 | 310 | 250 | 0 | 0 | 0 | 220 | 0 | 0 | 100 | 0 | 115 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 30 | 33 | 33 | 13 | 0 | 26 | 0 | 100 | 0 | 0 | 203 | 0 | 100 | 0 |  | 0 | 0 | 17 | 100 | 91 | 0 | 16 | 32 | 80 | 0 | 0 | 310 | 300 | 183 | 26 | 0 | 26 | 57 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 124 | 186 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 110 | 62 | 84 | 0 | 218 | 18 | 0 | 10 | 295 | 14 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 55 | 0 | 0 | 17 | 150 | 402 | 115 | 86 | 105 | 0 | 0 | 0 | 68 | 114 | 116 | 10 | 401 | 0 | 0 | 0 | 112 | 0 | 36 | 0 |  | 804 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 0 | 0 | 80 | 65 | 50 | 0 | 96 | 0 | 0 | 30 | 52 | 29 | 18 | 0 | 8 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 196 | 0 | 11 | 100 | 196 | 0 | 392 | 91 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 470 | 223 | 0 | 0 | 0 |  | 7201 | 3613 | 10814 | 4940 | 804 | 2039 | 1925 | 619 | 26 | 337 | 124 | 0 | 0 | 78.98
KWH | 0 | 0 | 0 | 0 | 7101055 | 1453181 | 0 | 8224770 | 7866000 |  | 0 | 7365750 | 6503564 | 0 | 0 | 0 | 5034493 | 0 | 0 | 488640 | 160128 | 953760 | 0 | 0 | 0 | 0 | 758880 | 0 | 746 | 273672 | 600000 | 639360 | 803600 | 815300 | 601440 | 0 | 576600 | 0 | 2400000 | 0 | 223122 | 4883660 | 0 | 2534616 | 0 |  | 46560 | 0 | 573601 | 1455240 | 2085120 | 0 | 366960 | 523200 | 2056288 | 0 | 0 | 7187000 | 6901000 | 4753000 | 451636 | 0 | 547200 | 1323360 | 0 | 952629 | 0 | 80936 | 389659 | 385740 | 252180 | 817500 | 432450 | 2540160 | 4419120 | 184320 | 479412 | 8900 | 1038000 | 707400 | 841200 | 0 | 0 | 2444000 | 1351488 | 1428480 | 0 | 5046600 | 402000 | 0 | 62100 | 7208000 | 212496 | 138048 | 0 | 57709 | 0 | 0 | 376800 | 0 | 909940 | 105570 | 0 | 408960 | 955127 | 8890000 | 1724400 | 1677600 | 1206872 | 17879 | 0 | 202513 | 704215 | 1521900 | 2341920 | 65280 | 8865000 | 158400 | 217020 | 635040 | 2126455 | 0 | 720720 | 139846 |  | 16307636 | 0 | 8951904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2109108 | 493663 | 0 | 0 | 1729000 | 1485000 | 257872 | 45359 | 862160 | 53230 | 0 | 148081 | 308160 | 257705 | 338400 | 0 | 170226 | 0 | 0 | 3682200 | 0 | 0 | 0 | 0 | 4388264 | 0 | 277012 | 476160 | 4440818 | 0 | 8668909 | 792480 | 0 | 151968 | 0 | 780912 | 0 | 23351 | 629664 | 9951200 | 4358291 | 0 | 0 | 0 |  | 154384486 | 72138733 | 226523219 | 114277728 | 16307636 | 43611811 | 31883844 | 13633400 | 576600 | 3179474 | 2540160 | 512566 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7882171.05 | 1918198.92 | 0 | 8307017.7 | 8101980 |  | 0 | 8028667.5 | 7218956.04 | 0 | 0 | 0 | 5235872.72 | 0 | 0 | 3679459.2 | 1460367.36 | 9384998.4 | 0 | 0 | 0 | 0 | 5539824 | 0 | 7355.56 | 205254 | 450000 | 0 | 0 | 0 | 5815924.8 | 0 | 155682 | 0 | 4344000 | 0 | 2072803.38 | 5323189.4 | 0 | 4308847.2 | 0 |  | 0 | 0 | 5563929.7 | 13897542 | 18140544 | 0 | 462369.6 | 1553904 | 3043306.24 | 0 | 0 | 5318380 | 6901000 | 4372760 | 582610.44 | 0 | 618336 | 1852704 | 0 | 1628995.59 | 0 | 817453.6 | 3721243.45 | 489889.8 | 189135 | 1430625 | 324337.5 | 19051200 | 4684267.2 | 1673625.6 | 608853.24 | 141866 | 1702320 | 1131840 | 1497336 | 0 | 0 | 2541760 | 2662431.36 | 2728396.8 | 0 | 8730618 | 880380 | 0 | 126684 | 7280080 | 159372 | 104916.48 | 0 | 436280.04 | 0 | 0 | 1959360 | 0 | 8953809.6 | 1234113.3 | 0 | 4437216 | 6733645.35 | 8267700 | 15726528 | 15853320 | 10511855.12 | 0 | 0 | 1763888.23 | 6190049.85 | 15188562 | 20070254.4 | 434764.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 93931983.36 | 0 | 9399499.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2383292.04 | 765177.65 | 0 | 0 | 3544450 | 3044250 | 2537460.48 | 460847.44 | 7630116 | 409871 | 0 | 1434904.89 | 2986070.4 | 2499738.5 | 649728 | 0 | 128861.082 | 0 | 0 | 19957524 | 0 | 0 | 0 | 0 | 5792508.48 | 0 | 415518 | 8099481.6 | 5195757.06 | 0 | 8582219.91 | 8273491.2 | 0 | 1442176.32 | 0 | 6059877.12 | 0 | 258028.55 | 4653216.96 | 43685768 | 0 | 0 | 0 | 0 |  | 333816928.52 | 244221817.242 | 578038745.762 | 120169567.352 | 93931983.36 | 45712200.81 | 203411363.38 | 63643292 | 155682 | 30329449.01 | 19051200 | 1634007.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 89 | 0 | 360 | 343 |  | 0 | 310 | 265 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 15 | 25 | 28 | 33 | 33 | 37 | 0 | 27 | 0 | 100 | 0 | 7 | 204 | 0 | 115 | 0 |  | 0 | 0 | 0 | 100 | 85 | 0 | 16 | 4 | 80 | 0 | 0 | 310 | 275 | 214 | 26 | 0 | 20 | 54 | 0 | 43 | 0 | 0 | 25 | 21 | 11 | 33 | 18 | 46 | 201 | 8 | 21 | 1 | 43 | 30 | 47 | 0 | 0 | 110 | 61 | 81 | 0 | 218 | 18 | 0 | 0 | 300 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 8 | 0 | 24 | 3 | 402 | 48 | 85 | 76 | 0 | 0 | 7 | 18 | 17 | 116 | 0 | 401 | 4 | 24 | 14 | 111 | 0 | 36 | 21 |  | 710 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 60 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 188 | 0 | 394 | 25 | 0 | 0 | 0 | 34 | 0 | 2 | 50 | 320 | 221 | 0 | 0 | 3 |  | 9422 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 98 | 0 | 340 | 341 | 0 | 0 | 310 | 270 | 0 | 0 | 0 | 222 | 0 | 0 | 95 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 42 | 0 | 28 | 0 | 100 | 0 | 25 | 203 | 0 | 100 | 0 | 0 | 10 | 0 | 68 | 100 | 97 | 0 | 16 | 24 | 80 | 0 | 0 | 315 | 300 | 182 | 26 | 0 | 26 | 57 | 0 | 51 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 128 | 167 | 8 | 21 | 0 | 43 | 30 | 50 | 0 | 0 | 110 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 285 | 14 | 11 | 0 | 15 | 0 | 0 | 90 | 0 | 80 | 0 | 0 | 34 | 150 | 401 | 115 | 86 | 105 | 0 | 0 | 17 | 85 | 114 | 116 | 10 | 400 | 0 | 0 | 108 | 112 | 0 | 36 | 0 |  | 804 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 80 | 70 | 50 | 0 | 95 | 12 | 0 | 30 | 52 | 42 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 10 | 100 | 183 | 0 | 415 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 90 | 500 | 223 | 0 | 0 | 0 |  | 11515 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 360 | 360 | 0 | 0 | 310 | 300 | 0 | 0 | 55 | 220 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 29 | 0 | 100 | 0 | 25 | 215 | 0 | 115 | 0 | 0 | 22 |  | 68 | 100 | 97 | 50 | 16 | 15 | 80 | 0 | 0 | 360 | 350 | 210 | 26 | 0 | 26 | 55 | 0 | 51 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 200 | 8 | 21 | 0 | 43 | 42 | 51 | 0 | 0 | 110 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 290 | 300 | 100 | 200 | 100 | 132 | 0 | 100 | 200 | 150 | 400 | 115 | 86 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 126 | 112 | 0 | 18 |  |  | 816 | 0 | 380 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 86 | 33 | 110 | 0 | 80 | 60 | 50 | 43 | 95 | 35 | 50 | 40 | 52 | 40 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 11 | 100 | 200 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 350 | 350 | 0 | 0 | 300 | 300 | 0 | 0 | 55 | 220 | 0 | 0 | 100 | 100 | 150 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 29 | 0 | 100 | 0 | 25 | 210 | 0 | 110 | 0 | 0 | 22 |  | 68 | 100 | 95 | 50 | 16 | 5 | 80 | 0 | 0 | 350 | 330 | 210 | 26 | 0 | 26 | 55 | 0 | 51 | 0 | 0 | 34 | 22 | 11 | 33 | 21 | 148 | 200 | 8 | 21 | 1.6 | 43 | 42 | 51 | 0 | 0 | 110 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 15 | 11 | 100 | 250 | 100 | 100 | 175 | 100 | 130 | 20 | 100 | 170 | 150 | 400 | 115 | 84 | 85 | 5 | 200 | 54 | 110 | 100 | 113 | 100 | 400 | 90 | 50 | 126 | 112 | 0 | 18 | 30 |  | 816 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 20 | 60 | 0 | 85 | 25 | 110 | 0 | 80 | 60 | 0 | 0 | 0 | 35 | 50 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 42 | 0 | 327 | 351 | 0 | 0 | 310 | 290 | 0 | 0 | 0 | 150 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 30 | 33 |  | 0 | 0 | 29 | 0 | 100 | 0 | 0 | 213 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 10 | 88 | 0 | 16 | 2 | 80 | 0 | 0 | 345 | 340 | 203 | 26 | 0 | 23 | 57 | 0 | 51 | 0 | 0 | 0 | 22 | 11 | 0 | 21 | 92 | 200 | 8 | 21 | 1 | 43 | 30 | 11 | 0 | 0 | 110 | 40 | 50 | 0 | 165 | 18 | 0 | 5 | 300 | 14 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 16 | 0 | 0 | 0 | 0 | 346 | 21 | 27 | 17 | 1 | 0 | 0 | 7 | 17 | 75 | 0 | 360 | 0 | 10 | 0 | 72 | 0 | 18 | 2 | 0 | 705 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 80 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 11 | 0 | 151 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 320 | 180 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 7594 | 6:00
| Highest Generation |  | 11515 | 21:00
| Day Peak Generation |  | 9422 | 12:00
| Evening Peak Generation |  | 11515 | 21:00
| HVDC Max Flow |  | 805 | 20:00
| HVDC EvPeak Flow |  | 804 | 21:00
| Load factor L.F |  | 81.97%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-04
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-03 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9422 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8335 | MW
Evening Peak Generation : |  | 11515 | MW Hour : | 21:00 | Available Max Generation : |  | 15507 | MW
E.P. Demand (at gen end) : |  | 11515 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11515 | MW Hour : | 21:00 | Reserve(Generation end) |  | 3507 | MW
Total Gen. (MKWH) : |  | 226.5232 | System Load Factor : | 81.97% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -128 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-04
Actual : | 79.16 | Ft.(MSL) , | Rule curve : | 84.48 | Ft.( MSL )
Gas Consumed : | Total = | 1253.34 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165881768.162
: |  | Coal : | 63643292 | Oil : | 233740812.39 | Total : | 463265872.552
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4263.8776 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1452.2449 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1301.5714 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1176.2245 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1062.8571 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 857.6939 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 476.6327 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 220.7551 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 661.5102 |  |  | 0 | 0%
Total | 0 |  | 11473.3673 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Chandpur-150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Kallyanpur-Lalbagh 132 kV Ckt-1 & 2 were under shutdown from 08:28 to 18:25 for D/W.
b) Gallamari 132/33 kV GT-1 transformer was under shut down from 11:49 to 14:09 for C/M.
c) Natore 132/33 kV T1 & T2 transformer tripped at 16:29 showing O/C,E/F & lock out relay due to LA |  |  |  |  | About 42 MW power interruption occurred under Natore S/S area
burst of NESCO feeder and was switched on at 16:44. |  |  |  |  | from 16:29 to 16:44.
d) Hasnabad-Keraniganj 230 kV Ckt-1 was under shutdown since 22:49 due to red hot maintenance at
B-phase at tower #01.
e) Dohazari-Cox's Bazar 132 kV Ckt-2 was under shutdown since 07:01 for D/W.
f) Kabirpur-Tongi 132 kV Ckt-2 tripped at 06:45(04-07-21) showing O/C relay and was switched on at 06:55.
g) Manikganj 132/33 kV T-2 transformer with Kabirpur 132 kV Ckt-2 was under shut down from 06:46 to
10:18(04-07-21) due to oil leakage from bushing of T2 transformer.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-03 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7101055 | Machine problem
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 98 | 1453181
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 340 | 8224770 | FGMO
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 341 | 7866000
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 310 | 7365750 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6503564 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve.
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 273672 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 95 | 488640
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 222 | 5034493 | Machine problem
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 160128 | Reserve.
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 758880 | Low demand
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 953760
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 0 | Reserve.
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 746
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 55 | 1239360 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 803600
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 815300
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 601440 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 57709 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 80 | 909940 | Low demand
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 86 | 1677600 | Engine problem
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 158400 | Reserve.
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 108 | 635040 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 139846
| Dhaka area Total |  |  |  | 5819 | 2687 | 53222874
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 223122
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 105570
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve.
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 28 | 576600 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4883660 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 100 | 2534616 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1206872
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 573601 | Engine problem
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1455240
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 0 | 0 | Reserve.
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 366960 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 523200
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 2085120 | Engine problem
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17879
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 17 | 202513 | Low demand
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 85 | 704215 | Engine problem
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 10 | 65280 | Low demand
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 112 | 2126455
| Chattogram area Total |  |  |  | 2382 | 1090 | 20050903
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2056288 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 182 | 4753000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7187000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6901000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 547200 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 57 | 1323360
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 451636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 51 | 952629
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 955127
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 80936 | Reserve.
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 34 | 408960 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 385740 | Engine problem
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 252180
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2540160
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 817500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 25 | 389659 | Low demand
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 432450 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1521900
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 116 | 2341920
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 720720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1726 | 35019365
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 167 | 4419120 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 479412
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 184320 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8900
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 90 | 376800 | Low demand
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1724400
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 217020
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 10 | 46560 | Low demand
| Mymensingh Area Total |  |  |  | 709 | 411 | 7456532
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1038000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 707400 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 110 | 2444000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 841200
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 138048
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1351488
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1428480
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 5046600
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 402000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 14 | 212496 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 285 | 7208000 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 8890000
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 62100
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8865000
| Sylhet Area Total |  |  |  | 2377 | 1735 | 38634812
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 804 | 16307636
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 8951904 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 476160
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 792480 | Engine problem
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1394 | 26528180
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 493663 | Engine problem
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2109108 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 277012 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 9951200
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 223 | 4358291 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 848 | 17189274
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 70 | 1485000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 80 | 1729000 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 257872
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 45359 | Reserve.
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 12 | 53230 | Low demand
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Reserve.
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 148081 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 181 | 4388264 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4440818 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 415 | 8668909 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 42 | 257705 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 338400 | Engine problem
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 8 | 170226 | Engine problem
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 308160
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 862160 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 35 | 151968 | Low demand
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 90 | 629664 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 0
| Rajshahi Area Total |  |  |  | 2179 | 1361 | 23934816
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3682200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 780912
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 23351
| Rangpur Area Total |  |  |  | 605 | 263 | 4486463
| Total |  |  |  | 21060 | 11515 | 226523219
| Eastern Grid Total |  |  |  | 14321 | 7649 | 154384486
| Western Grid Total |  |  |  | 6739 | 3866 | 72138733
| National Grid Total |  |  |  | 21060 | 11515 | 226523219
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-03
(a) ENTIRE EASTERN GRID : |  | 7373 | MW | (b) ENTIRE WESTERN GRID : |  | 3627 | MW
i) Dhaka area |  | 3842 | MW | i) Khulna area |  | 1377 | MW
ii) Chittagong area |  | 1150 | MW | ii) Rajshahi area |  | 1185 | MW
iii) Comilla area |  | 1039 | MW | iii) Barisal area |  | 322 | MW
iv) Mymensingh area |  | 897 | MW | iv) Rangpur area |  | 743 | MW
v) Sylhet area |  | 445 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11000 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 116 | 15:00 | Kishoreganj | 138 | 22:00 | Jessore | 102 | 20:00
Munsiganj | 92 | 21:00 | Netrokona | 100 | 20:00 | Benapol | 56 | 21:00
Sonargaon | 64 | 21:00 | Jamalpur | 114 | 21:00 | Jhenida | 107 | 20:00
Shyampur | 184 | 13:00 | Sherpur | 84 | 20:00 | Bottail | 124 | 20:00
Bhulta | 197 | 0:00 | Srimongal | 50 | 21:00 | G.K Project | 50 | 20:00
Madanganj | 38 | 12:00 | Shahjibazar | 107 | 23:00 | Faridpur | 115 | 20:00
Shitalakhya | 101 | 17:00 | Fenchuganj | 42 | 20:00 | Rajbari | 39 | 19:00
Rahim steel | 22 | 12:00 | Kulawara | 47 | 20:00 | Madaripur | 88 | 21:00
Matuail | 58 | 12:00 | Sylhet | 92 | 20:00 | Sariatpur | 60 | 21:00
Ghorasal | 74 | 22:00 | Chatak | 21 | 19:00 | Gopalganj | 87 | 20:00
Narsingdi | 157 | 22:00 | Sunamganj | 40 | 21:00 | Bagerhat | 92 | 21:00
Haripur (SBU) | 108 | 13:00 | Biani Bazar | 55 | 20:00 | Mongla | 34 | 10:00
Sreenagar | 34 | 21:00 | Comilla (S) | 130 | 19:00 | Satkhira | 98 | 20:00
Ullon | 58 | 14:00 | Comilla(N) | 111 | 19:00 | Gallamari | 27 | 23:00
Hasnabad | 88 | 19:00 | Chandpur | 72 | 23:00 | Magura | 48 | 20:00
Magbazar | 63 | 13:00 | Feni | 107 | 22:00 | Norail | 41 | 20:00
Maniknagar | 58 | 17:00 | Chowmuhani | 184 | 20:00 | Chuadanga | 87 | 20:00
Bangabhaban | 4 | 11:00 | Ashuganj | 35 | 1:00 | Borguna | 16 | 21:00
Motijheel | 13 | 12:00 | Daudkandi | 140 | 20:00 | Barisal(N) | 39 | 20:00
Narinda | 40 | 13:00 | B.Baria | 155 | 22:00 | Barisal (S) | 92 | 20:00
Kazla | 69 | 13:00 | Ramganj | 84 | 19:30 | Patuakhali | 96 | 22:00
Dhanmondi | 94 | 14:00 | Chaddagram | 39 | 22:00 | Bhandaria | 46 | 19:30
Lalbag | 74 | 12:00 | PHP | 3 | 20:00 | Borhan Uddin | 43 | 22:00
Madartek | 68 | 20:00 | Kochua | 54 | 20:00 | Ishurdi | 59 | 21:00
Dhaka University | 16 | 12:00 | Madunaghat | 53 | 11:00 | Ruppur Paromanobik | 2 | 18:00
Aftabnagar | 9 | 21:00 | Hathazari | 83 | 19:00 | Natore | 120 | 20:00
Fatullah | 51 | 10:00 | Khulshi | 176 | 0:00 | Bogra | 142 | 22:00
Nawabganj | 47 | 21:00 | Halishahar | 92 | 7:00 | Noagaon | 112 | 21:00
Keraniganj | 58 | 19:30 | Baraulia | 120 | 14:00 | Rajshahi | 135 | 21:00
Mirpur | 112 | 19:30 | Sikalbaha | 26 | 0:00 | Rajshahi New | 15 | 22:00
Kalyanpur | 99 | 21:00 | Dohazari | 90 | 23:00 | C.Nawabganj | 56 | 20:00
Gulshan | 60 | 13:00 | Cox'sbazar | 80 | 19:30 | Amnura | 46 | 21:00
Uttara | 71 | 19:00 | Chandraghona | 24 | 20:00 | Pabna | 92 | 20:00
Uttara New | 12 | 15:00 | Kaptai | 4 | 19:00 | Shahjadpur | 88 | 20:00
Kamrangirchar | 78 | 12:00 | A. Khaer Stl. | 7 | 2:00 | Serajganj | 91 | 21:00
Savar | 162 | 15:00 | Bakulia | 88 | 15:00 | Niyamatpur | 65 | 21:00
Bhasantec | 100 | 20:00 | Julda | 21 | 7:00 | Joypurhat | 50 | 21:00
Agargaon | 58 | 13:00 | TK chemical | 26 | 21:00 | Sherpur(Bogura) | 54 | 22:00
Satmosjid | 77 | 13:00 | Modern Steel | 0 | #N/A | Mohastangor | 54 | 20:00
Tongi | 104 | 0:00 | Shahmirpur | 30 | 22:00 | Bhangura | 29 | 20:00
Kabirpur | 222 | 16:00 | Khagrachhari | 24 | 19:30 | Rangpur | 112 | 20:00
Basundhara | 176 | 14:00 | Matarbari | 30 | 21:00 | Lalmonirhat | 35 | 20:00
Manikganj | 58 | 19:30 | Baroiar Hat | 36 | 19:00 | Saidpur | 96 | 20:00
Joydevpur | 153 | 13:00 | Rangamati | 10 | 12:00 | Purbasadipur | 105 | 22:00
New Tongi | 108 | 12:00 | Abul Khair 230 | 11 | 16:00 | Thakurgaon | 82 | 20:00
Kodda | 286 | 11:00 | BSRM | 156 | 12:00 | Palashbari | 100 | 20:00
Dhamrai | 92 | 21:00 | GPH Ispat | 95 | 7:00 | Barapukuria | 53 | 21:00
Rajendrapur | 98 | 22:00 | Agrabad | 48 | 19:00 | Panchagar | 50 | 20:00
Valuka | 112 | 20:00 | Goalpara | 25 | 13:00 | Joldhaka | 49 | 21:00
Tangail | 182 | 20:00 | Central S/S | 90 | 20:00 | Kurigram | 49 | 20:00
Mymensing | 187 | 21:00 | Noapara | 58 | 21:00 | Mithapukur | 41 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-03 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 401 | 7:00 | 394 | 15:00 | Kaliakoir | 391 | 0.75 | 378 | 0.45833
| Bheramara | 407 | 2:00 | 396 | 15:00 | Bhulta | 381 | 0.25 | 337 | 0.375
| Ashuganj(N) | 386 | 7:00 | 378 | 15:00 | Gopalganj | 411 | 0.625 | 389 | 0.91667
| Payra | 414 | 7:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 19:30 | 214 | 16:00
| Ishurdi | 235 | 6:00 | 226 | 21:00 | Megnaghat | 230 | 17:00 | 223 | 11:00
| Ashuganj | 236 | 19:00 | 231 | 9:00 | Fenchuganj | 236 | 5:00 | 232 | 3:00
| Serajganj | 231 | 19:00 | 226 | 23:00 | Siddhirganj | 229 | 7:00 | 222 | 11:00
| Baghabari | 233 | 6:00 | 227 | 11:00 | Maniknagar | 227 | 7:00 | 220 | 15:00
| Barapukuria | 236 | 6:00 | 228 | 19:30 | Agargaon | 224 | 7:00 | 215 | 15:00
| Bogra | 226 | 19:00 | 217 | 21:00 | Barisal | 243 | 20:00 | 231 | 21:00
| Rajshahi | 234 | 18:00 | 223 | 13:00 | Bhola 225 MW | 246 | 8:00 | 236 | 22:00
| Khulna South | 229 | 18:00 | 213 | 21:00 | AKSML | 224 | 20:00 | 214 | 4:00
| Rampura | 226 | 1:00 | 221 | 14:00 | BSRM | 224 | 20:00 | 216 | 16:00
| Haripur | 226 | 5:00 | 220 | 16:00 | Bibiyana | 237 | 5:00 | 232 | 13:00
| Hasnabad | 225 | 1:00 | 218 | 15:00 | Bhulta | 228 | 2:00 | 223 | 11:00
| Shyampur | 224 | 7:00 | 220 | 16:00 | Ashuganj (S) | 234 | 19:00 | 229 | 10:00
| Aminbazar | 225 | 1:00 | 217 | 2:00 | Kaliakoir | 225 | 5:00 | 217 | 15:00
| Tongi | 221 | 1:00 | 215 | 15:00 | GPH | 224 | 20:00 | 216 | 3:00
| Comilla (N) | 226 | 7:00 | 220 | 16:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 131 | 1:00 | 127 | 11:00 | Madanhat | 133 | 0.8125 | 128 | 0.29167
| Munsiganj | 131 | 5:00 | 126 | 10:00 | Hathazari | 132 | 0.77083 | 128 | 0.083333
| Sonargaon | 137 | 13:00 | 126 | 0:00 | Khulshi | 130 | 0.79167 | 125 | 0.375
| Shyampur | 134 | 6:00 | 129 | 11:00 | Halishahar | 131 | 0.8125 | 126 | 0.16667
| Bhulta | 125 | 18:00 | 120 | 15:00 | Baraulia | 131 | 0.83333 | 126 | 0.375
| Madanganj | 130 | 19:00 | 125 | 11:00 | Sikalbaha | 134 | 0.83333 | 128 | 0.125
| Shitalakhya | 137 | 4:00 | 129 | 16:00 | Dohazari | 130 | 0.8125 | 126 | 0.041667
| Rahim steal | 131 | 4:00 | 128 | 10:00 | Cox'sbazar | 123 | 0.83333 | 118 | 0.041667
| Matuail | 131 | 1:00 | 127 | 11:00 | Chandraghona | 132 | 0.83333 | 127 | 0.16667
| Ghorasal | 137 | 8:00 | 136 | 1:00 | Kaptai | 132 | 0.91667 | 128 | 0.29167
| Narsinghdi | 134 | 6:00 | 127 | 22:00 | A. Khaer Stl. | 130 | 0.8125 | 126 | 0.125
| Haripur (SBU) | 132 | 6:00 | 128 | 11:00 | Bakulia | 132 | 0.8125 | 126 | 0.125
| Sreenagar | 128 | 5:00 | 123 | 11:00 | Julda | 133 | 0.79167 | 128 | 0.70833
| Ullon | 136 | 3:00 | 131 | 15:00 | TK Chemical | 132 | 0.79167 | 127 | 0.29167
| Hasnabad | 136 | 3:00 | 130 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 137 | 4:00 | 132 | 11:00 | Shahmirpur | 132 | 0.83333 | 127 | 0.25
| Maniknagar | 137 | 5:00 | 132 | 12:00 | Khagrachhari | 131 | 0.8125 | 127 | 0.125
| Bangabhaban | 137 | 5:00 | 132 | 12:00 | Matarbari | 126 | 0.41667 | 120 | 0
| Motijheel | 137 | 5:00 | 132 | 12:00 | Baroiar Hat | 135 | 0.83333 | 128 | 0.041667
| Narinda | 137 | 5:00 | 132 | 12:00 | Rangamati | 131 | 19:30 | 126 | 4:00
| Kazla | 137 | 5:00 | 132 | 12:00 | Agrabad | 130 | 18:30 | 126 | 3:00
| Dhanmondi | 132 | 4:00 | 128 | 10:00 | Goalpara S/S | 138 | 18:30 | 127 | 0.125
| Lalbag | 137 | 5:00 | 129 | 11:00 | Khulna Central S/S | 137 | 18:30 | 126 | 0.041667
| Madartek | 136 | 5:00 | 131 | 15:00 | Noapara | 136 | 18:30 | 124 | 0.875
| Dhaka University | 136 | 1:00 | 132 | 11:00 | Jessore | 131 | 6:00 | 117 | 0.8125
| Aftabnagar | 136 | 1:00 | 131 | 14:00 | Benapol | 133 | 0.25 | 117 | 0.875
| Fatullah | 134 | 7:00 | 129 | 10:00 | Jhenida | 129 | 6:00 | 112 | 0.875
| Nawabganj | 128 | 5:00 | 122 | 15:00 | Bottail | 133 | 0.25 | 123 | 0.8125
| Keraniganj | 128 | 5:00 | 123 | 11:00 | G.K Project | 139 | 0.75 | 133 | 0.875
| Mirpur | 134 | 5:00 | 127 | 11:00 | Faridpur | 138 | 0.29167 | 128 | 0.875
| Kalyanpur | 134 | 2:00 | 128 | 15:00 | Rajbari | 137 | 0.29167 | 128 | 0.95833
| Gulshan | 136 | 4:00 | 131 | 14:00 | Madaripur | 141 | 0.25 | 132 | 0.875
| Uttara | 133 | 1:00 | 127 | 11:00 | Shariyatpur S/S | 141 | 7:00 | 130 | 0.91667
| Uttara New | 135 | 14:00 | 126 | 11:00 | Gopalganj | 145 | 0.25 | 133 | 0.91667
| Kamrangirchar | 137 | 1:00 | 129 | 16:00 | Bagerhat | 135 | 18:00 | 124 | 0.041667
| Savar | 126 | 5:00 | 125 | 11:00 | Mongla | 135 | 18:00 | 123 | 0.875
| Bhasantec | 135 | 5:00 | 128 | 15:00 | Satkhira | 137 | 18:00 | 123 | 21:00
| Agargaon | 133 | 6:00 | 129 | 15:00 | Gallamari | 138 | 0.25 | 128 | 21:00
| Satmosjid | 136 | 6:00 | 129 | 15:00 | Magura | 130 | 6:00 | 110 | 0.8125
| Tongi | 135 | 1:00 | 131 | 11:00 | Narail | 127 | 0.75 | 111 | 0.8125
| Kabirpur | 135 | 7:00 | 129 | 12:00 | Chuadanga | 124 | 6:00 | 102 | 0.83333
| Basundhara | 134 | 18:30 | 127 | 12:00 | Borguna | 140 | 16:00 | 127 | 0.875
| Manikganj | 138 | 1:00 | 132 | 11:00 | Barisal(N) | 142 | 7:00 | 132 | 20:00
| Joydevpur | 140 | 19:00 | 129 | 11:00 | Barisal (S) | 139 | 0.25 | 130 | 0.83333
| New Tongi | 135 | 6:00 | 132 | 8:00 | Patuakhali(S) | 138 | 0.16667 | 125 | 0.91667
| Kodda | 132 | 13:00 | 125 | 11:00 | Bhandaria | 139 | 0.25 | 125 | 0.91667
| Dhamrai | 134 | 6:00 | 127 | 21:00 | Ishurdi | 136 | 6:00 | 131 | 13:00
| Rajendrapur | 129 | 8:00 | 123 | 12:00 | Ruppur Paromanobik | 135 | 3:00 | 131 | 23:00
| Valuka | 125 | 6:00 | 114 | 23:00 | Natore | 135 | 18:30 | 128 | 13:00
| Tangail | 133 | 7:00 | 123 | 23:00 | Bogra | 134 | 18:00 | 127 | 23:00
| Mymensing | 129 | 7:00 | 119 | 22:00 | Noagaon | 131 | 18:00 | 122 | 23:00
| Kishorganj | 131 | 23:00 | 121 | 23:00 | Rajshahi | 133 | 18:00 | 126 | 13:00
| Netrokona | 127 | 18:00 | 115 | 23:00 | Rajshahi New | 135 | 18:00 | 125 | 12:00
| Jamalpur | 132 | 19:00 | 119 | 11:00 | C.Nawabganj | 134 | 18:30 | 124 | 10:00
| Sherpur | 132 | 19:00 | 116 | 11:00 | Amnura | 134 | 18:30 | 122 | 10:00
| Srimongal | 138 | 9:00 | 134 | 21:00 | Pabna | 135 | 4:00 | 130 | 21:00
| Shahjibazar | 135 | 6:00 | 130 | 23:00 | Shahjadpur | 140 | 18:00 | 136 | 8:00
| Fenchuganj | 137 | 8:00 | 134 | 2:00 | Serajganj | 133 | 18:00 | 128 | 20:00
| Khulawara | 136 | 7:00 | 133 | 23:00 | Niyamatpur | 128 | 19:00 | 119 | 21:00
| Sylhet | 135 | 11:00 | 133 | 1:00 | Joypurhat | 131 | 18:00 | 121 | 23:00
| Chatak | 134 | 7:00 | 131 | 21:00 | Sherpur(Bogura) | 135 | 19:00 | 128 | 23:00
| Sunamganj | 134 | 8:00 | 130 | 21:00 | Mohastangor | 133 | 18:30 | 125 | 23:00
| Biani Bazar | 134 | 9:00 | 131 | 18:30 | Bangura | 137 | 5:00 | 133 | 13:00
| Comilla(s) | 129 | 4:00 | 123 | 19:00 | Rangpur | 130 | 5:00 | 121 | 20:00
| Comilla(n) | 137 | 18:30 | 130 | 23:00 | Lalmonirhat | 131 | 6:00 | 122 | 19:30
| Chandpur | 132 | 6:00 | 123 | 23:00 | Saidpur | 131 | 18:00 | 120 | 21:00
| Feni | 137 | 19:30 | 127 | 16:00 | Purbasadipur | 129 | 7:00 | 113 | 19:30
| Chowmuhani | 137 | 12:00 | 124 | 23:00 | Thakurgaon | 129 | 6:00 | 113 | 20:00
| Ashuganj | 140 | 6:00 | 135 | 22:00 | Palashbari | 130 | 6:00 | 121 | 23:00
| Daudkandi | 131 | 6:00 | 125 | 0:00 | Barapukuria | 136 | 6:00 | 128 | 19:30
| B.Baria | 134 | 6:00 | 129 | 22:00 | Panchagar | 129 | 6:00 | 111 | 20:00
| Ramganj | 136 | 19:00 | 117 | 3:00 | Joldhaka | 130 | 0.25 | 116 | 0.83333
| Chaddagram | 136 | 19:00 | 129 | 23:00 | Kurigram | 130 | 0.20833 | 119 | 0.83333
| PHP | 135 | 19:00 | 126 | 3:00 | Mithapukur | 133 | 0.79167 | 124 | 0.95833
| Kochua | 133 | 7:00 | 123 | 0:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-03
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 104 | 7201 | 3613 | 10814 |  |  |  | QF-LDC-11
0:30 | 75 | 6629.5 | 3156.5 | 9786 | Date: | 2021-07-03
1:00 | 46 | 6058 | 2700 | 8758
1:30 | 55 | 5987.5 | 2647.5 | 8635
2:00 | 64 | 5917 | 2595 | 8512
2:30 | 56 | 5816 | 2573.5 | 8389.5 | [5 empty] | Gen. at Eve. Peak | 11515 | 11515 MW (21:00 )
3:00 | 48 | 5715 | 2552 | 8267 | [6 empty] | 21:00
3:30 | 29 | 5659.5 | 2555 | 8214.5 | [5 empty] | Gen. at Day Peak | 9422 | 9422 MW (12:00 )
4:00 | 10 | 5604 | 2558 | 8162 | [6 empty] | 12:00
4:30 | 22 | 5559.5 | 2540 | 8099.5 | [5 empty] | Highest Generation | 11515
5:00 | 34 | 5515 | 2522 | 8037 | [6 empty] | 21:00
5:30 | 63 | 5375.5 | 2440 | 7815.5
6:00 | 92 | 5236 | 2358 | 7594
6:30 | 57 | 5285.5 | 2392 | 7677.5
7:00 | 22 | 5335 | 2426 | 7761
7:30 | 35 | 5474 | 2397.5 | 7871.5
8:00 | 48 | 5613 | 2369 | 7982
8:30 | 82 | 5767.5 | 2447 | 8214.5
9:00 | 116 | 5922 | 2525 | 8447
9:30 | 134 | 6008 | 2614 | 8622
10:00 | 152 | 6094 | 2703 | 8797
10:30 | 100 | 6270 | 2654 | 8924
11:00 | 48 | 6446 | 2605 | 9051
11:30 | 57 | 6467.5 | 2769 | 9236.5
12:00 | 66 | 6489 | 2933 | 9422
12:30 | 53 | 6688 | 2917.5 | 9605.5
13:00 | 40 | 6887 | 2902 | 9789
13:30 | 42 | 6867 | 2888 | 9755
14:00 | 44 | 6847 | 2874 | 9721
14:30 | 146 | 6875 | 2951 | 9826
15:00 | 248 | 6903 | 3028 | 9931
15:30 | 291 | 6753.5 | 2990 | 9743.5
16:00 | 334 | 6604 | 2952 | 9556
16:30 | 340 | 6372 | 2893.5 | 9265.5
17:00 | 346 | 6140 | 2835 | 8975
17:30 | 328 | 6082 | 2805 | 8887
18:00 | 310 | 6024 | 2775 | 8799
18:30 | 267 | 6353 | 2929.5 | 9282.5
19:00 | 224 | 6682 | 3084 | 9766
19:30 | 128 | 7542 | 3548 | 11090
20:00 | 82 | 7590 | 3753 | 11343 |  |  |  | Executive Engineer
20:30 | 48 | 7619.5 | 3809.5 | 11429 |  |  |  | Network Operation Division
21:00 | 14 | 7649 | 3866 | 11515
21:30 | 47 | 7597 | 3872.5 | 11469.5
22:00 | 80 | 7545 | 3879 | 11424 |  |  |  |  | Page 6 of 7
22:30 | 109 | 7414.5 | 3801.5 | 11216
23:00 | 138 | 7284 | 3724 | 11008
23:30 | 121 | 7242.5 | 3668.5 | 10911
24:00 | 104 | 7201 | 3613 | 10814
11515 MW (21:00 )
9422 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-03 |  | Energy | 226523219
[11 empty] | 2021-07-03 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4940 | 804 | 2039 | 2077 | 619 | 26 | 337 | 0 | 124 | 0
0:30 | 4801.5 | 708.5 | 1940 | 1487.5 | 599.5 | 26.5 | 185.5 | 0 | 113 | 0 | Date: | 2021-07-03
1:00 | 4663 | 613 | 1841 | 898 | 580 | 27 | 34 | 0 | 102 | 0
1:30 | 4657 | 590 | 1824 | 835.5 | 575 | 27 | 25.5 | 0 | 101 | 0 | [7 empty] | Total Energy | 226.5232 | Total Energy Gen 226.523 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.523 MKWHr
2:00 | 4651 | 567 | 1807 | 773 | 570 | 27 | 17 | 0 | 100 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4668 | 567 | 1734 | 717.5 | 560 | 27 | 17 | 0 | 99 | 0 | [7 empty] | Energy Requirement | 226.5232
3:00 | 4685 | 567 | 1661 | 662 | 550 | 27 | 17 | 0 | 98 | 0
3:30 | 4657 | 566.5 | 1662 | 635.5 | 550 | 27.5 | 17 | 0 | 99 | 0 | [6 empty] | Shortage
4:00 | 4629 | 566 | 1663 | 609 | 550 | 28 | 17 | 0 | 100 | 0
4:30 | 4609 | 566.5 | 1646.5 | 594.5 | 540 | 28 | 17 | 0 | 98 | 0
5:00 | 4589 | 567 | 1630 | 580 | 530 | 28 | 17 | 0 | 96 | 0
5:30 | 4476.5 | 573 | 1562.5 | 558 | 510 | 28 | 17 | 0 | 90 | 0.5
6:00 | 4364 | 579 | 1495 | 536 | 490 | 28 | 17 | 0 | 84 | 1
6:30 | 4346 | 627 | 1493 | 591 | 485 | 28 | 17 | 0 | 85 | 5.5 |  |  |  |  | Coal
7:00 | 4328 | 675 | 1491 | 646 | 480 | 28 | 17 | 0 | 86 | 10
7:30 | 4367.5 | 621 | 1538.5 | 717.5 | 480 | 27.5 | 17 | 0 | 87 | 15.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4407 | 567 | 1586 | 789 | 480 | 27 | 17 | 0 | 88 | 21
8:30 | 4518.5 | 613 | 1612.5 | 834 | 480 | 27 | 17 | 0 | 85 | 27.5
9:00 | 4630 | 659 | 1639 | 879 | 480 | 27 | 17 | 0 | 82 | 34
9:30 | 4653 | 684 | 1703 | 924 | 479.5 | 26.5 | 17 | 0 | 87 | 48
10:00 | 4676 | 709 | 1767 | 969 | 479 | 26 | 17 | 0 | 92 | 62
10:30 | 4783.5 | 637.5 | 1827.5 | 1004 | 479.5 | 26 | 8.5 | 0 | 90 | 67.5
11:00 | 4891 | 566 | 1888 | 1039 | 480 | 26 | 0 | 0 | 88 | 73
11:30 | 4847 | 638 | 1924 | 1185 | 475 | 26.5 | 8 | 0 | 67 | 66
12:00 | 4803 | 710 | 1960 | 1331 | 470 | 27 | 16 | 0 | 46 | 59
12:30 | 4823.5 | 710 | 1921.5 | 1460 | 465 | 27 | 51 | 0 | 79 | 68.5
13:00 | 4844 | 710 | 1883 | 1589 | 460 | 27 | 86 | 0 | 112 | 78
13:30 | 4844 | 710 | 1883 | 1589 | 460 | 27 | 86 | 0 | 112 | 78
14:00 | 4844 | 710 | 1883 | 1589 | 460 | 27 | 86 | 0 | 112 | 78
14:30 | 4842.5 | 710 | 1919 | 1613.5 | 470 | 27.5 | 92 | 0 | 115 | 70.5
15:00 | 4841 | 710 | 1955 | 1638 | 480 | 28 | 98 | 0 | 118 | 63
15:30 | 4846.5 | 710 | 1884 | 1538 | 475 | 28 | 98 | 0 | 113 | 51
16:00 | 4852 | 710 | 1813 | 1438 | 470 | 28 | 98 | 0 | 108 | 39
16:30 | 4771.5 | 710 | 1738 | 1319.5 | 470 | 28 | 100.5 | 0 | 106 | 22
17:00 | 4691 | 710 | 1663 | 1201 | 470 | 28 | 103 | 0 | 104 | 5
17:30 | 4608.5 | 709.5 | 1681.5 | 1177.5 | 470 | 28 | 109 | 0 | 100 | 3
18:00 | 4526 | 709 | 1700 | 1154 | 470 | 28 | 115 | 0 | 96 | 1
18:30 | 4541 | 709 | 1718.5 | 1401.5 | 480 | 28 | 291 | 0 | 113 | 0.5
19:00 | 4556 | 709 | 1737 | 1649 | 490 | 28 | 467 | 0 | 130 | 0
19:30 | 4733 | 804 | 1879 | 2444 | 580 | 28 | 494 | 0 | 128 | 0
20:00 | 4846 | 805 | 1998 | 2430 | 600 | 28 | 506 | 0 | 130 | 0
20:30 | 4879 | 804.5 | 2014.5 | 2478.5 | 625 | 28 | 470.5 | 0 | 129 | 0
21:00 | 4912 | 804 | 2031 | 2527 | 650 | 28 | 435 | 0 | 128 | 0
21:30 | 4907 | 804 | 2024 | 2493 | 660 | 28 | 432.5 | 0 | 121 | 0
22:00 | 4902 | 804 | 2017 | 2459 | 670 | 28 | 430 | 0 | 114 | 0
22:30 | 4908 | 804 | 2031 | 2268 | 659.5 | 28 | 395.5 | 0 | 122 | 0
23:00 | 4914 | 804 | 2045 | 2077 | 649 | 28 | 361 | 0 | 130 | 0
23:30 | 4927 | 804 | 2042 | 2077 | 634 | 27 | 349 | 0 | 127 | 0 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4940 | 804 | 2039 | 2077 | 619 | 26 | 337 | 0 | 124 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 226.523 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.523 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-03
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 27 | 27 | 27 | 28 | 28 | 28 | 28 | 27 | 27 | 26 | 26 | 27 | 27 | 27 | 28 | 28 | 28 | 28 |  | 28 | 28 | 28 | 28 | 28 | 28 | 26 | 576600
2 | Karnaphuli Hydro PP Unit-4 & 5
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [11 empty] | 7 | 18 | 25 | 25 | 8 | 8 | 8 |  | 10 | 25 | 25 | 25 | 25 |  |  | 223122
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 4 | 9 | 11 | 7 | 8 | 18 | 18 | 9 | 10 | 0 | 0 | [8 empty] | 105570
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 211 | 203 | 203 | 203 | 203 | 203 | 217 | 215 | 215 | 204 | 204 | 204 | 203 | 202 | 203 | 203 |  | 206 | 203 | 203 | 203 | 203 | 203 | 203 | 4883660
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 100 | 110 | 110 | 115 | 115 | 115 | 100 | 102 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2534616
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 12 | 12 | 12 | 17 | 17 |  | 63 | 68 | 68 | 68 | 68 | 34 | 17 | 573601
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | [6 empty] | 3 | 17 | 17 | 17 | 23 | 76 | 105 | 105 | 105 | 51 | 17 | 17 |  | 30 | 105 | 105 | 105 | 105 | 105 | 105 | 1206872
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 42 | 50 | 42 |  |  |  |  | 80936
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 221 | 221 | 220 | 221 | 222 | 222 | 180 | 180 | 180 | 218 | 214 | 103 | 215 | 212 | 215 | 218 | 175 | 175 |  | 175 | 220 | 225 | 222 | 220 | 220 | 220 | 5034493
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 6 | 15 | 15 | 15 | 15 |  |  | 57709
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 451636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7101055
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2056288
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 23 | 23 | 20 | 26 | 26 | 23 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 547200
33 | Ashuganj 225 MW CCPP | 183 | 185 | 193 | 185 | 182 | 182 | 189 | 200 | 203 | 213 | 215 | 214 | 215 | 214 | 213 | 214 | 215 | 183 |  | 191 | 182 | 182 | 182 | 182 | 187 | 183 | 4753000
34 | Ashuganj 450 MW CCPP(South) | 265 | 270 | 280 | 265 | 265 | 265 | 265 | 280 | 315 | 300 | 300 | 275 | 275 | 265 | 275 | 275 | 275 | 275 |  | 285 | 275 | 300 | 300 | 300 | 300 | 300 | 6901000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 275 | 260 | 260 | 260 | 260 | 265 | 300 | 280 | 330 | 310 | 310 | 260 | 275 | 275 | 275 | 275 |  | 285 | 275 | 275 | 315 | 320 | 310 | 310 | 7187000
35 | Ashuganj 55 MW PP (Precision) | 57 | 57 | 57 | 57 | 57 | 57 | 56 | 57 | 56 | 55 | 55 | 54 | 53 | 53 | 53 | 52 | 52 | 53 |  | 54 | 55 | 55 | 57 | 56 | 56 | 57 | 1323360
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 317 | 317 | 325 | 324 | 318 | 316 | 317 | 339 | 377 | 375 | 367 | 360 | 340 | 340 | 366 | 339 | 339 | 339 |  | 340 | 339 | 349 | 340 | 321 | 318 | 324 | 8224770
40 | Meghnaghat 450 MW CCPP(MPL) | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7365750
41 | Haripur 360MW CCPP(HPL) | 296 | 323 | 350 | 351 | 354 | 282 | 283 | 282 | 281 | 344 | 345 | 343 | 343 | 321 | 316 | 316 | 336 | 346 |  | 350 | 351 | 355 | 341 | 332 | 350 | 353 | 7866000
42 | RPCL 210MW CCPP | 203 | 204 | 204 | 204 | 203 | 204 | 204 | 204 | 203 | 203 | 201 | 201 | 162 | 161 | 162 | 177 | 177 | 183 |  | 170 | 170 | 169 | 167 | 169 | 183 | 186 | 4419120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 2 | 4 | 6 | 22 | 34 | 24 | 35 | 40 | 38 | 22 | 1 | 0 | [8 empty] | 217020
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 43 | 43 |  | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 1038000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 707400
46 | Shajibazar 330 MW CCPP | 110 | 110 | 111 | 110 | 109 | 109 | 110 | 111 | 110 | 110 | 110 | 110 | 112 | 110 | 110 | 110 | 111 | 111 |  | 110 | 110 | 111 | 110 | 109 | 110 | 110 | 2444000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 40 | 40 | 40 | 40 | 40 | 63 | 60 | 61 | 61 | 61 | 61 | 60 | 61 | 60 | 60 | 61 |  | 61 | 61 | 62 | 61 | 61 | 56 | 62 | 1351488
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 50 | 10 | 10 | 10 | 10 | 10 | 60 | 81 | 81 | 81 | 81 | 84 | 84 | 83 | 30 | 30 | 30 |  | 30 | 30 | 84 | 84 | 84 | 84 | 84 | 1428480
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 178 | 178 | 178 | 178 | 178 | 218 | 218 | 218 | 218 | 218 | 218 | 191 | 184 |  | 184 | 218 | 218 | 218 | 218 | 218 | 218 | 5046600
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 402000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [13 empty] | 9 | [5 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 62100
54 | Hobiganj 11MW PP Cofidence-E | 11 | 0 | [5 empty] | 11 | 11 | 11 | [5 empty] | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 138048
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 14 | 14 | 14 | 14 | 14 | 14 | 30 | 45 | 45 | 47 | 47 | 49 | 50 | 50 | 50 | 14 | 14 |  | 14 | 49 | 49 | 50 | 50 | 50 | 50 | 841200
56 | Shahjahanulla 25 MW PP | 8 | 8 | 0 | [5 empty] | 8 | 8 | 8 | 8 | 8 | 8 | [5 empty] | 16 | 16 | 14 | 14 | 14 | 14 | 14 | 212496
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 300 | 300 | 295 | 275 | 290 | 290 | 320 | 310 | 310 | 300 | 280 | 280 | 310 | 290 | 280 | 290 |  | 290 | 295 | 300 | 285 | 290 | 285 | 295 | 7208000
| Bibiyana South 400 MW | 350 | 380 | 401 | 401 | 380 | 320 | 320 | 320 | 320 | 320 | 394 | 401 | 397 | 394 | 392 | 396 | 350 | 350 |  | 350 | 395 | 401 | 400 | 392 | 400 | 401 | 8865000
58 | Nababganj 55 MW PP (Southern power ) | [8 empty] | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 746
59 | Tangail Palli Power Gen 22 MW | [19 empty] | 4 | 10 |  | 10 | 11 |  |  | 46560
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 15 | 15 | 15 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 366960
61 | Narshingdi 22 MW PP (Doreen) | 17 | 0 | [6 empty] | 17 | 15 | 15 | 15 | 15 | 15 | 17 | 17 | 17 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 273672
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 479412
63 | Impoprt (Tripura) | 102 | 100 | 98 | 100 | 96 | 84 | 86 | 88 | 82 | 92 | 88 | 46 | 112 | 116 | 118 | 108 | 104 | 96 |  | 130 | 128 | 130 | 128 | 114 | 130 | 124 | 2540160
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 17 | 3 | 5 | 3 | 4 | 2 | 3 | 3 | 8 | 8 | 6 |  | 6 | 10 | 14 | 24 | 29 | 33 | 32 | 523200
65 | Feni 22MW PP (Doreen) | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 385740
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 252180
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817500
68 | Cumilla 25 MW PP (Summit) | 11 | 12 | 12 | 17 | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  |  |  | 12 | 20 | 20 | 21 | 20 | 432450
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 16 | 16 | 29 | 30 | 30 | 30 | 30 | 639360
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 12 | 33 | 33 | 33 | 33 | 815300
73 | Ghorashal 108MW PP (Regent) | 97 | 97 | 12 | 12 | 12 | 12 | 12 | 13 | 13 | 13 | 79 | 89 | 92 | 89 | 88 | 91 | 47 | 47 |  | 47 | 91 | 91 | 98 | 99 | 99 | 99 | 1453181
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1521900
| Chowmuhani 113 MW | 94 | 45 | 36 | 36 | 36 | 78 | 118 | 121 | 120 | 120 | 119 | 116 | 117 | 118 | 119 | 55 | 55 | 55 |  | 72 | 120 | 117 | 116 | 115 | 117 | 116 | 2341920
| Manikgonj 162MW PP(MPGL) | [11 empty] | 14 | 35 | 35 | 35 | 35 | 35 | 35 |  | 48 | 100 | 106 | 108 | 35 |  |  | 635040
77 | Siddhirganj 100 PP(Dutch Bangla) | [19 empty] | 7 | 40 | 65 | 95 | 100 | 100 | 100 | 488640
78 | Gazipur 52 MW PP | [8 empty] | 13 | 41 | 42 | 37 | 42 | 42 | 42 | 25 | 30 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 13 | 601440
79 | Kodda 150MW PP | [11 empty] | 16 | 32 | 32 | 32 | 32 | 32 | 32 |  | 150 | 150 | 150 | 150 | 150 | 115 | 115 | 953760
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 184320
81 | Jangalia 52 MW PP (Lakdanavi) | [7 empty] | 7 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 |  |  | 389659
| Gazipur 100 MW PP | 50 | 34 | 34 | 34 | 34 | 34 | 37 | 61 | 76 | 85 | 85 | 85 | 68 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 1677600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 6 |  |  | 2 | 2 | 1 | 1 | [9 empty] | 17879
| Jodiac Power | [11 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 |  |  | 202513
| Karnaphuli Power Ltd. | [11 empty] | 18 | 51 | 51 | 51 | 17 | 17 | 17 |  | 21 | 85 | 75 | 85 | 85 | 85 | 68 | 704215
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 270 | 275 | 275 | 275 | 250 | 260 | 260 | 280 | 300 | 285 | 285 | 265 | 265 | 270 | 275 | 265 | 255 | 265 |  | 290 | 275 | 240 | 270 | 270 | 270 | 250 | 6503564
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 4 | 34 | 17 | 17 | 17 | 17 | 17 |  | 17 | [6 empty] | 158400
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 40 | 0 |  |  |  |  | 50 | 50 | 50 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 20 | 20 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1455240
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 51 | 51 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 22 | 43 | 51 | 51 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 952629
94 | Gagnagar 102 MW PP (Digital Power) | [10 empty] | 3 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 |  |  |  |  | 160128
95 | Patenga 50MW PP (Baraka) | [26 empty] | 0
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 90 | 55 | 51 | 52 | 53 | 95 | 96 | 96 | 85 | 85 | 90 | 89 | 90 | 94 | 97 | 97 |  | 97 | 97 | 97 | 97 | 97 | 97 | 91 | 2085120
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [26 empty] | 0
100 | Manikganj 55 MW PP (Northern) | [26 empty] | 0
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 8900
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 35 | 35 | 35 | 35 | 758880
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | [19 empty] | 15 | 80 | 70 | 90 | 90 | 32 | 32 | 376800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [8 empty] | 7 | 30 | 30 | 30 | 49 | 65 | 65 | 65 | 65 | 65 |  | 59 | 80 | 76 | 80 | 80 | 67 | 55 | 909940
115 | Juldah 100 MW PP Unit-3 (Acorn) | [26 empty] | 0
116 | Chandpur 200MW (Desh energy) | [11 empty] | 24 | 34 | 34 | 34 | 17 | 17 | 17 |  | 28 | 68 | 68 | 34 | 34 | 17 | 17 | 408960
117 | Ashuganj 150MW PP (Midland) | [11 empty] | 3 | 23 | 30 | 36 | 36 | 10 | 10 |  | 36 | 148 | 128 | 150 | 150 | 148 | 150 | 955127
118 | Bibiyana-III 400 MW CCPP | 376 | 376 | 376 | 376 | 353 | 322 | 324 | 324 | 323 | 322 | 389 | 402 | 403 | 404 | 404 | 403 | 353 | 304 |  | 324 | 400 | 400 | 401 | 401 | 402 | 402 | 8890000
| Jamalpur 115 MW PP (United) | 55 | 55 | 35 | 35 | 35 | 35 | 35 | 8 | 8 | 8 | 8 | 48 | 115 | 115 | 115 | 105 | 85 | 55 |  | 73 | 115 | 115 | 115 | 115 | 115 | 115 | 1724400
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | [19 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 65280
| Anlima Energy Ltd. | 110 | 110 | 35 | 17 | 17 | 17 | 30 | 90 | 90 | 90 | 101 | 111 | 112 | 111 | 112 | 112 | 72 | 53 |  | 71 | 112 | 112 | 112 | 112 | 111 | 112 | 2126455
| Bhairob 54.5 MW | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 35 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 720720
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 10 | 15 | 21 | 21 | 21 | 18 | 17 | 8 |  |  | 1 | [8 empty] | 139846
120 | Eastern Zone Total | 6058 | 5917 | 5715 | 5604 | 5515 | 5236 | 5335 | 5613 | 5922 | 6094 | 6446 | 6489 | 6887 | 6847 | 6903 | 6604 | 6140 | 6024 |  | 6682 | 7542 | 7590 | 7649 | 7545 | 7284 | 7201 | 154384486
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | [11 empty] | 25 | 53 | 53 | 53 | 53 | 17 | 17 |  | 20 | 90 | 85 | 90 | 90 | 90 | 91 | 792480
130
131
132 | United Payra Power Ltd. | [26 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 170 | 170 | 170 | 170 | 170 | 132 | 130 | 130 | 131 | 131 | 171 | 221 | 221 | 220 | 220 | 180 | 151 | 152 |  | 152 | 220 | 220 | 223 | 223 | 221 | 223 | 4358291
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [26 empty] | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 10 | 11 | 11 | 11 | 277012
| Bhola 225 MW CCPP | 86 | 86 | 86 | 86 | 86 | 87 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 85 | 86 | 85 | 86 | 85 | 86 | 86 | 2109108
140 | Bhola 33 MW PP (Venture) | 26 | 24 | 22 | 23 | 18 | 15 | 14 | 14 | 14 | 15 | 19 | 19 | 20 | 21 | 18 | 17 | 17 | 17 |  | 24 | 25 | 28 | 29 | 30 | 30 | 28 | 493663
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 65 | 70 | 100 | 100 | 100 | 100 | 476160
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 613 | 567 | 567 | 566 | 567 | 579 | 675 | 567 | 659 | 709 | 566 | 710 | 710 | 709 | 710 | 710 | 710 | 709 |  | 709 | 804 | 805 | 804 | 804 | 804 | 804 | 16307636
147 | Bheramara 410 MW CCPP | 360 | 360 | 360 | 360 | 360 | 300 | 300 | 300 | 300 | 300 | 330 | 400 | 400 | 350 | 390 | 395 | 400 | 330 |  | 330 | 330 | 395 | 400 | 400 | 400 | 405 | 8951904
148 | Payra 1320 MW | 430 | 420 | 400 | 400 | 380 | 340 | 330 | 330 | 330 | 330 | 330 | 320 | 310 | 320 | 330 | 320 | 320 | 320 |  | 340 | 430 | 450 | 500 | 520 | 500 | 470 | 9951200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 3682200
153 | Baghabari 71 MW GTPP | 70 | 70 | 50 | 50 | 50 | 50 | 60 | 60 | 65 | 65 | 65 | 60 | 60 | 60 | 65 | 70 | 65 | 65 |  | 65 | 65 | 65 | 70 | 70 | 65 | 65 | 1485000
156 | Baghabari 100 MW GTPP | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 | 80 | 60 | 60 | 60 | 65 | 70 | 75 | 75 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1729000
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 43 | 50 | 50 | 50 | 50 | 257872
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 3 | 3 | 3 | 3 | 2 | 0 | 1 | 0 | 0
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 164 | 164 | 171 | 170 | 166 | 163 | 150 | 136 | 174 | 195 | 182 | 174 | 163 | 164 | 184 | 187 | 184 | 162 |  | 169 | 182 | 177 | 181 | 192 | 193 | 196 | 4388264
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 148 | 148 | 155 | 162 | 180 | 149 | 147 | 145 | 163 | 191 | 196 | 188 | 181 | 172 | 189 | 181 | 184 | 185 |  | 185 | 180 | 186 | 183 | 186 | 189 | 196 | 4440818
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 341 | 342 | 342 | 342 | 316 | 314 | 305 | 336 | 338 | 411 | 409 | 394 | 323 | 340 | 399 | 366 | 312 | 329 |  | 344 | 327 | 376 | 415 | 398 | 411 | 392 | 8668909
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 10 |  | 10 | 13 | 32 |  |  |  |  | 45359
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 3 | 3 | 3 | 3 | 3 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 15 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 338400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 170226
165 | Amnura 50 MW PP(Sinha) | [19 empty] | 12 | 12 | 12 | 12 | 12 |  |  | 53230
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [19 empty] | 30 | 30 | 33 | 30 | 30 | 30 | 30 | 148081
168 | Santahar 50 MW Peaking PP | [19 empty] | 27 | 37 | 43 | 42 | 36 | 36 | 29 | 257705
169 | Natore 52 MW PP (Rajlanka) | 25 | 0 | [17 empty] | 7 | 23 | 48 | 52 | 52 | 52 | 52 | 308160
170 | Chapainawabganj 100 MW Peaking PP | [12 empty] | 54 | 54 | 54 | 54 | 54 | 56 |  | 95 | 96 | 95 | 95 | 96 | 96 | 96 | 862160
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 18 | 35 | 35 | 35 | 35 |  |  | 151968
172 | Confidence Power Bogura Unit-1 113 MW | [11 empty] | 50 | 35 | 35 | 35 | 35 | 35 | 35 |  | 50 | 70 | 90 | 90 | 90 | 35 |  | 629664
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP
176 | Rangpur 113 MW PP (Confidence) | [11 empty] | 34 | 34 | 34 | 34 | 34 | 35 | 35 |  | 95 | 111 | 113 | 113 | 113 | 70 | 34 | 780912
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 5 | 4 | 3 | [9 empty] | 23351
178
178