## Forecast
0 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-08 | Thursday
|  |  | Date (day): | 2021-07-08 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13848.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15050 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-07 | 2021-07-08 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint.
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 92 | 96 | 100 | 100
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 322 | 324 | 350 | 360 |  |  | FGMO
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 316 | 351 | 360 | 360
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 260 | 260 | 260 | 190 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 280 | 300 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 70 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 100 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 331 | 332 | 330 | 330
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 16 | 24 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 64 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 30 | 0 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 53 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 46 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 16 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 25 | 25 | 25 |  | 27 | Fuel shortage
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 95 | 195 | 250 | 250 |  | 50 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 100 | 130 | 135 |  | 14 | Engine problem
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 50 | 105 | 50 | 50 |  | 55 | Fuel shortage
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 126 | 126 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 7 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5819 | 2780 | 2991 | 3781 | 4048 | 559 | 1016
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 2 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 54 | 55 | 55 | 55 | 175 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 210 | 210 | 215
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 100 | 110 | 110 | 110 |  | 40 | Machine problem
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 90 | 88 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 50 | 70 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 16 | 16 | 16 |  | 6 | Engine problem
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 7 | 20 | 5 | 15
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 12 | 12 | 96 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 82 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 94 | 91 | 112 | 112
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 983 | 1151 | 1540 | 1630 | 531 | 195
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 110 | 110 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 196 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 325 | 350 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 290 | 330 | 350 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 53 | 49 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 26 | 26 | 169 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 34 | 43 | 43 | 43 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 135 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 50 | 50 | 0 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 100 | 100 | 170 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 102 | 114 | 148 | 172
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 21 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 114 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 118 | 118 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 18 | 36 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1593 | 1826 | 2111 | 2370 | 298 | 351
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 161 | 157 | 190 | 190
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 120 | 175 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 1 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 289 | 445 | 582.6 | 556 | 0 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 163 | 162 | 160 | 160 |  | 170 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 56 | 62 | 63
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 81 | 81 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 218 | 225 | 225 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 290 | 315 | 341 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 0 | 0 | 0 | 0 |  | 400 | Under maint.
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1368 | 1377 | 1425 | 1452 | 0 | 929
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 799 | 800 | 807 | 807
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 3 | 0 | 0 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 100 | 220
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 350 | 410 | 400 | 400
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 40 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 53 | 90 | 90 | 90 |  | 15 | Engine problem
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2129 | 1205 | 1340 | 1547 | 1797 | 0 | 98
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 29 | 25 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 86 | 85 | 86 |  | 108 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 11 | 11 | 11 | 84 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 490 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 220 | 221 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 708 | 837 | 1073 | 1192 | 84 | 108
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 60 | 60 | 60 | 65
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 0 | 43 |  | 9 | Engine problem
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 20 | 40 | 0 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 18 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 43 | 50 | 50
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 35 |  | 15 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 171 | 182 | 210 | 210 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 183 | 168 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 394 | 418 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 44 | 0 | 42 |  | 8 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 18 | 18
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 48 | 87 | 50 | 95
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 112 | 113 | 113
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 35 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1087 | 1468 | 1518 | 1722 | 310 | 78
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 152 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21060 | 10165 | 11698 | 13848.6 | 15050 | 1906 | 3052
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9740.0825 | 11209 | 13269.7006 | 14420.8796
| A. |  | 2021-07-07 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11741 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9247 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11698 | MW
| 3 | Day peak Generation : |  |  | 10165 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11209 | MW
| 4 | Evening peak Generation : |  |  | 11698 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 252.6279 | MKWHr | By Solar | 0.27793 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 152.0745 | MKWHr |  | By Oil: | 62.238 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.6646 | MKWHr |  | By Hydro: | 1.2319 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1906 | MW | Dhaka | 3934 | 3934 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3052 | MW | Chittagong | 1100 | 1100 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4958 | MW | Khulna | 1320 | 1320 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1153.8 | MMCFD |  |  | Rajshahi | 1235 | 1235 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 158446609.838 | ii) Oil : | Taka | 450679630.22 | Comilla | 1098 | 1098 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 68168509 | Total | Taka | 677294749.058 | Mymensingh | 956 | 956 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.265 | MKWHr. | Sylhet | 443 | 443 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 56 | MW (E to W) at | 21:00 | hrs | Barisal | 319 | 319 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -28 | MW at | 20:00 | hrs | Rangpur | 804 | 804 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.1° C |  |  | Total | 11209 | 11209 |  | 0
| B. |  | 2021-07-08 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15050 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10400 | MW
| 4 | Reserve(Generation end) |  |  |  | 3050 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 258.2007 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8693 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.4596 | MKWHr. | ii) HVDC Flow at Peak Time |  | 800 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6813 | MKWHr. | iii) Maximum HVDC Flow : |  | 814 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 79.9 |  | (b) Today: | 80 |  | (c) Rule Curve: |  | 85.12
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-07
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 319 | 352 |  | 0 | 260 | 275 | 0 | 0 | 0 | 333 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 18 | 0 | 51 | 100 | 6 | 0 | 16 | 30 | 80 | 0 | 0 | 260 | 270 | 182 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 126 | 173 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 162 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 110 | 0 | 0 | 180 | 0 | 64 | 0 | 60 | 100 | 137 | 0 | 106 | 50 | 105 | 0 | 0 | 0 | 68 | 114 | 109 | 100 | 401 | 0 | 0 | 126 | 112 | 0 | 36 | 0 |  | 813 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 86 | 31 | 0 | 0 | 0 | 60 | 50 | 41 | 92 | 35 | 43 | 23 | 43 | 28 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 100 | 189 | 0 | 415 | 90 | 0 | 113 | 0 | 75 | 0 | 0 | 113 | 510 | 221 | 0 | 0 | 0 |  | 7590 | 3959 | 11549 | 4502 | 813 | 1992 | 2898 | 660 | 53 | 505 | 126 | 0 | 0 | 79.88
2:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 317 | 348 |  | 0 | 260 | 280 | 0 | 0 | 0 | 331 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 21 | 0 | 51 | 100 | 12 | 0 | 16 | 30 | 80 | 0 | 0 | 270 | 280 | 186 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 124 | 174 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 163 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 130 | 0 | 69 | 0 | 20 | 68 | 140 | 0 | 106 | 50 | 105 | 0 | 0 | 0 | 68 | 114 | 109 | 100 | 400 | 0 | 0 | 126 | 112 | 0 | 36 | 0 |  | 814 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 50 | 50 | 0 | 92 | 35 | 0 | 23 | 43 | 28 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 100 | 187 | 0 | 413 | 70 | 0 | 0 | 0 | 70 | 0 | 0 | 70 | 480 | 221 | 0 | 0 | 0 |  | 7371 | 3631 | 11002 | 4509 | 814 | 1979 | 2445 | 630 | 53 | 448 | 124 | 0 | 0 | 79.88
3:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 322 | 350 |  | 0 | 260 | 265 | 0 | 0 | 0 | 330 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 16 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 206 | 0 | 50 | 0 |  | 24 | 0 | 51 | 100 | 12 | 0 | 16 | 30 | 80 | 0 | 0 | 265 | 280 | 187 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 120 | 176 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 163 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 65 | 0 | 0 | 68 | 142 | 0 | 115 | 50 | 105 | 0 | 0 | 0 | 68 | 114 | 109 | 100 | 400 | 0 | 0 | 126 | 112 | 0 | 36 | 0 |  | 813 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 50 | 50 | 0 | 94 | 35 | 0 | 23 | 52 | 28 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 70 | 190 | 0 | 410 | 53 | 0 | 0 | 0 | 50 | 0 | 0 | 35 | 480 | 221 | 0 | 0 | 0 |  | 7269 | 3544 | 10813 | 4466 | 813 | 1983 | 2297 | 630 | 54 | 450 | 120 | 0 | 0 | 79.89
4:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 322 | 349 |  | 0 | 260 | 275 | 0 | 0 | 0 | 330 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 16 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 50 | 0 |  | 0 | 0 | 51 | 100 | 12 | 0 | 16 | 5 | 80 | 0 | 0 | 265 | 275 | 185 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 33 | 21 | 118 | 183 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 163 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 60 | 0 | 65 | 0 | 0 | 68 | 142 | 0 | 115 | 50 | 105 | 0 | 0 | 0 | 51 | 110 | 107 | 40 | 400 | 0 | 0 | 72 | 112 | 0 | 36 | 0 |  | 813 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 50 | 50 | 0 | 94 | 0 | 0 | 23 | 52 | 28 | 19 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 30 | 191 | 0 | 412 | 53 | 0 | 0 | 0 | 35 | 0 | 0 | 35 | 480 | 221 | 0 | 0 | 0 |  | 6994 | 3461 | 10455 | 4465 | 813 | 1959 | 2016 | 630 | 54 | 400 | 118 | 0 | 0 | 79.89
5:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 321 | 350 |  | 0 | 260 | 275 | 0 | 0 | 0 | 330 | 0 | 0 | 100 | 0 | 150 | 0 | 0 | 0 | 0 | 35 | 0 | 55 | 16 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 50 | 0 |  | 0 | 0 | 51 | 100 | 12 | 0 | 16 | 0 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 0 | 43 | 19 | 11 | 25 | 21 | 114 | 186 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 163 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 65 | 0 | 0 | 34 | 142 | 0 | 115 | 50 | 105 | 0 | 0 | 0 | 17 | 110 | 108 | 10 | 400 | 0 | 0 | 72 | 112 | 0 | 36 | 0 |  | 813 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 26 | 0 | 0 | 0 | 50 | 50 | 0 | 94 | 0 | 0 | 23 | 52 | 28 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 0 | 191 | 0 | 412 | 53 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 480 | 221 | 0 | 0 | 0 |  | 6819 | 3360 | 10179 | 4440 | 813 | 1953 | 1775 | 630 | 54 | 400 | 114 | 0 | 0 | 79.9
6:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 318 | 349 |  | 0 | 260 | 285 | 0 | 0 | 0 | 330 | 0 | 0 | 80 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 16 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 60 | 0 |  | 0 | 0 | 0 | 80 | 11 | 0 | 16 | 0 | 80 | 0 | 0 | 270 | 280 | 192 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 108 | 186 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 178 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 17 | 50 | 0 | 55 | 50 | 85 | 0 | 0 | 0 | 17 | 110 | 94 | 10 | 401 | 0 | 0 | 0 | 112 | 0 | 36 | 1 |  | 814 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 23 | 0 | 0 | 0 | 60 | 0 | 0 | 94 | 0 | 0 | 0 | 52 | 28 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 0 | 188 | 0 | 409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 221 | 0 | 0 | 0 |  | 6230 | 3181 | 9411 | 4437 | 814 | 1937 | 1322 | 580 | 54 | 158 | 108 | 1 | 0 | 79.9
7:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 341 | 350 |  | 0 | 260 | 300 | 0 | 0 | 0 | 326 | 0 | 0 | 16 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 8 | 215 | 0 | 60 | 0 |  | 0 | 0 | 0 | 80 | 12 | 0 | 16 | 0 | 80 | 0 | 0 | 295 | 305 | 204 | 8 | 0 | 26 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 104 | 187 | 8 | 0 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 205 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 1 | 0 | 17 | 20 | 0 | 35 | 50 | 93 | 1 | 0 | 0 | 17 | 54 | 99 | 10 | 398 | 0 | 0 | 0 | 112 | 0 | 36 | 2 |  | 814 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 60 | 0 | 0 | 48 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 192 | 0 | 11 | 0 | 201 | 0 | 416 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 221 | 0 | 0 | 0 |  | 6141 | 3106 | 9247 | 4544 | 814 | 1962 | 1146 | 550 | 54 | 68 | 104 | 5 | 0 | 79.91
8:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 349 | 310 |  | 0 | 260 | 260 | 0 | 0 | 0 | 300 | 0 | 0 | 40 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 40 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 19 | 203 | 0 | 60 | 0 |  | 3 | 0 | 0 | 100 | 12 | 0 | 16 | 6 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 0 | 23 | 56 | 0 | 43 | 0 | 0 | 4 | 22 | 11 | 25 | 21 | 110 | 191 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 161 | 62 | 84 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 2 | 0 | 0 | 0 | 0 | 78 | 1 | 50 | 30 | 55 | 0 | 48 | 50 | 105 | 1 | 0 | 0 | 33 | 0 | 110 | 50 | 400 | 0 | 1 | 52 | 112 | 0 | 36 | 4 |  | 808 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 48 | 0 | 16 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 205 | 0 | 11 | 0 | 197 | 0 | 333 | 35 | 0 | 10 | 0 | 0 | 0 | 1 | 15 | 400 | 221 | 0 | 0 | 0 |  | 6336 | 3046 | 9382 | 4408 | 808 | 1824 | 1504 | 550 | 54 | 116 | 110 | 8 | 0 | 79.91
9:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 320 | 305 |  | 0 | 260 | 280 | 0 | 0 | 0 | 300 | 0 | 0 | 90 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 53 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 207 | 0 | 60 | 0 |  | 24 | 0 | 0 | 100 | 12 | 0 | 16 | 3 | 80 | 0 | 0 | 265 | 275 | 191 | 8 | 0 | 23 | 57 | 0 | 43 | 0 | 0 | 39 | 22 | 8 | 25 | 21 | 100 | 185 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 161 | 61 | 81 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 5 | 0 | 85 | 0 | 0 | 0 | 0 | 149 | 0 | 50 | 100 | 135 | 0 | 75 | 50 | 105 | 3 | 0 | 0 | 51 | 8 | 115 | 50 | 398 | 0 | 0 | 126 | 99 | 0 | 36 | 6 |  | 808 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 55 | 0 | 0 | 48 | 0 | 43 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 172 | 0 | 358 | 53 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 400 | 221 | 0 | 0 | 0 |  | 6885 | 3105 | 9990 | 4335 | 808 | 1839 | 2179 | 550 | 54 | 115 | 100 | 10 | 0 | 79.92
10:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 326 | 330 |  | 0 | 260 | 275 | 0 | 0 | 0 | 301 | 0 | 0 | 100 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 53 | 16 | 25 | 28 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 228 | 0 | 20 | 0 |  | 24 | 0 | 0 | 100 | 0 | 0 | 16 | 3 | 80 | 0 | 0 | 265 | 275 | 187 | 8 | 0 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 8 | 25 | 21 | 94 | 165 | 8 | 21 | 0 | 44 | 30 | 47 | 0 | 0 | 160 | 61 | 78 | 0 | 218 | 18 | 0 | 9 | 305 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 145 | 1 | 50 | 100 | 142 | 0 | 75 | 50 | 105 | 5 | 0 | 0 | 53 | 46 | 117 | 50 | 399 | 0 | 1 | 126 | 94 | 0 | 36 | 5 |  | 808 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 55 | 0 | 10 | 48 | 0 | 43 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 173 | 0 | 394 | 53 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 380 | 220 | 0 | 0 | 1 |  | 6955 | 3132 | 10087 | 4316 | 808 | 1904 | 2242 | 530 | 54 | 125 | 94 | 14 | 0 | 79.92
11:00 | 0 | 0 | 0 | 0 | 300 | 99 | 0 | 317 | 351 |  | 0 | 260 | 260 | 0 | 0 | 0 | 300 | 0 | 0 | 100 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 17 | 53 | 16 | 25 | 28 | 33 | 25 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 204 | 0 | 20 | 0 |  | 22 | 0 | 0 | 100 | 0 | 0 | 16 | 4 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 0 | 23 | 53 | 0 | 34 | 0 | 0 | 43 | 22 | 8 | 25 | 14 | 98 | 161 | 8 | 19 | 0 | 44 | 30 | 47 | 0 | 0 | 161 | 61 | 84 | 0 | 218 | 18 | 0 | 9 | 285 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 3 | 50 | 100 | 142 | 0 | 75 | 50 | 105 | 4 | 0 | 0 | 82 | 34 | 117 | 50 | 401 | 0 | 7 | 126 | 94 | 0 | 36 | 8 |  | 799 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 60 | 0 | 10 | 48 | 0 | 43 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 173 | 0 | 366 | 53 | 0 | 35 | 0 | 0 | 0 | 1 | 35 | 380 | 220 | 0 | 0 | 0 |  | 6903 | 3087 | 9990 | 4246 | 799 | 1869 | 2246 | 530 | 54 | 125 | 98 | 23 | 0 | 79.93
12:00 | 0 | 0 | 0 | 0 | 300 | 92 | 0 | 322 | 316 |  | 0 | 260 | 260 | 0 | 0 | 0 | 331 | 0 | 0 | 100 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 53 | 19 | 25 | 28 | 33 | 25 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 90 | 0 | 0 | 16 | 7 | 80 | 0 | 0 | 260 | 270 | 186 | 8 | 0 | 26 | 53 | 0 | 34 | 0 | 50 | 43 | 22 | 8 | 25 | 14 | 102 | 161 | 8 | 19 | 1 | 43 | 30 | 47 | 0 | 0 | 163 | 61 | 81 | 0 | 218 | 0 | 0 | 9 | 295 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 2 | 50 | 100 | 142 | 0 | 75 | 50 | 105 | 4 | 0 | 0 | 82 | 34 | 118 | 50 | 400 | 0 | 1 | 126 | 94 | 0 | 18 | 7 |  | 799 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 60 | 0 | 20 | 48 | 18 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 12 | 0 | 183 | 0 | 394 | 53 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 370 | 220 | 0 | 0 | 0 |  | 7013 | 3152 | 10165 | 4368 | 799 | 1868 | 2252 | 520 | 54 | 185 | 102 | 17 | 0 | 79.93
13:00 | 0 | 0 | 0 | 0 | 300 | 95 | 0 | 319 | 286 |  | 0 | 260 | 240 | 0 | 0 | 0 | 335 | 0 | 0 | 100 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 53 | 19 | 25 | 24 | 33 | 25 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 24 | 0 | 0 | 90 | 0 | 0 | 14 | 7 | 80 | 0 | 0 | 310 | 270 | 184 | 8 | 0 | 26 | 53 | 0 | 34 | 0 | 49 | 43 | 22 | 8 | 25 | 12 | 102 | 138 | 8 | 21 | 1 | 43 | 30 | 50 | 0 | 0 | 162 | 62 | 84 | 0 | 218 | 0 | 0 | 9 | 300 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 5 | 50 | 68 | 142 | 0 | 75 | 50 | 105 | 2 | 0 | 0 | 85 | 17 | 110 | 50 | 400 | 0 | 8 | 126 | 94 | 0 | 18 | 19 |  | 800 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 50 | 17 | 47 | 48 | 35 | 43 | 4 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 12 | 0 | 190 | 0 | 365 | 55 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 360 | 220 | 0 | 0 | 1 |  | 6997 | 3227 | 10224 | 4432 | 800 | 1823 | 2234 | 510 | 53 | 232 | 102 | 38 | 0 | 79.94
14:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 316 | 286 |  | 0 | 260 | 260 | 0 | 0 | 0 | 331 | 0 | 0 | 100 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 53 | 19 | 25 | 24 | 33 | 25 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 100 | 0 |  | 24 | 0 | 0 | 90 | 0 | 0 | 16 | 8 | 80 | 0 | 0 | 310 | 270 | 183 | 8 | 0 | 26 | 52 | 0 | 34 | 0 | 50 | 43 | 22 | 8 | 25 | 15 | 110 | 135 | 8 | 21 | 1 | 43 | 30 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 177 | 0 | 0 | 9 | 265 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 4 | 50 | 68 | 142 | 0 | 75 | 50 | 105 | 1 | 0 | 0 | 85 | 17 | 111 | 50 | 360 | 0 | 16 | 126 | 105 | 0 | 18 | 16 |  | 801 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 50 | 34 | 41 | 48 | 35 | 43 | 29 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 165 | 0 | 11 | 0 | 200 | 0 | 309 | 53 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 340 | 160 | 0 | 0 | 1 |  | 6942 | 3128 | 10070 | 4350 | 801 | 1672 | 2284 | 490 | 53 | 269 | 110 | 41 | 0 | 0
15:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 317 | 291 |  | 0 | 260 | 270 | 0 | 0 | 0 | 328 | 0 | 0 | 100 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 24 | 33 | 25 | 25 | 0 | 27 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 88 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 310 | 270 | 187 | 8 | 0 | 26 | 52 | 0 | 34 | 0 | 50 | 43 | 22 | 11 | 25 | 15 | 108 | 141 | 8 | 21 | 1 | 43 | 30 | 53 | 0 | 0 | 161 | 60 | 84 | 0 | 177 | 0 | 0 | 9 | 285 | 16 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 149 | 4 | 20 | 68 | 140 | 0 | 75 | 50 | 105 | 0 | 0 | 0 | 85 | 17 | 114 | 50 | 350 | 0 | 13 | 126 | 114 | 0 | 18 | 8 |  | 800 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 50 | 50 | 41 | 47 | 35 | 25 | 29 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 188 | 0 | 353 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 340 | 122 | 0 | 0 | 2 |  | 6898 | 3015 | 9913 | 4298 | 800 | 1697 | 2153 | 490 | 52 | 284 | 108 | 31 | 0 | 0
16:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 318 | 317 |  | 0 | 260 | 260 | 0 | 0 | 0 | 332 | 0 | 0 | 100 | 48 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 17 | 88 | 0 | 0 | 16 | 3 | 80 | 0 | 0 | 310 | 270 | 184 | 8 | 0 | 26 | 51 | 0 | 34 | 0 | 50 | 25 | 22 | 11 | 25 | 15 | 110 | 154 | 8 | 21 | 1 | 43 | 30 | 53 | 0 | 0 | 163 | 61 | 84 | 0 | 177 | 0 | 0 | 9 | 285 | 16 | 5 | 0 | 45 | 0 | 0 | 0 | 0 | 140 | 0 | 20 | 51 | 80 | 0 | 75 | 50 | 105 | 1 | 0 | 0 | 51 | 34 | 110 | 50 | 350 | 0 | 17 | 72 | 114 | 0 | 18 | 2 |  | 800 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 50 | 50 | 41 | 47 | 18 | 16 | 29 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 11 | 0 | 190 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 340 | 122 | 0 | 0 | 2 |  | 6757 | 2952 | 9709 | 4335 | 800 | 1710 | 1883 | 490 | 53 | 301 | 110 | 27 | 0 | 0
17:00 | 0 | 0 | 0 | 0 | 300 | 52 | 0 | 317 | 345 |  | 0 | 260 | 260 | 0 | 0 | 0 | 300 | 0 | 0 | 50 | 48 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 17 | 50 | 0 | 0 | 16 | 8 | 80 | 0 | 0 | 310 | 270 | 184 | 8 | 0 | 26 | 50 | 0 | 34 | 0 | 50 | 8 | 22 | 11 | 25 | 15 | 104 | 158 | 8 | 21 | 0 | 43 | 30 | 19 | 0 | 0 | 161 | 56 | 84 | 0 | 177 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 80 | 0 | 0 | 0 | 0 | 100 | 1 | 10 | 51 | 40 | 0 | 55 | 50 | 51 | 0 | 0 | 0 | 51 | 34 | 25 | 20 | 335 | 0 | 7 | 35 | 72 | 0 | 18 | 2 |  | 800 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 16 | 0 | 0 | 0 | 50 | 50 | 41 | 47 | 18 | 16 | 31 | 8 | 0 | 0 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 185 | 0 | 334 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 340 | 122 | 0 | 0 | 0 |  | 6205 | 2839 | 9044 | 4244 | 800 | 1642 | 1412 | 490 | 53 | 287 | 104 | 12 | 0 | 0
18:00 | 0 | 0 | 0 | 0 | 300 | 52 | 0 | 324 | 350 |  | 0 | 260 | 270 | 0 | 0 | 0 | 300 | 0 | 0 | 32 | 48 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 19 | 25 | 9 | 33 | 33 | 25 | 0 | 28 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 10 | 0 | 17 | 30 | 0 | 0 | 16 | 5 | 80 | 0 | 0 | 310 | 265 | 184 | 8 | 0 | 26 | 52 | 0 | 34 | 0 | 50 | 8 | 22 | 11 | 32 | 14 | 100 | 162 | 8 | 21 | 0 | 43 | 30 | 19 | 0 | 0 | 162 | 45 | 50 | 0 | 177 | 0 | 0 | 9 | 290 | 16 | 5 | 0 | 95 | 0 | 0 | 3 | 0 | 100 | 0 | 10 | 34 | 40 | 0 | 35 | 50 | 34 | 0 | 0 | 0 | 34 | 34 | 25 | 10 | 320 | 2 | 3 | 35 | 53 | 0 | 18 | 3 |  | 801 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 60 | 50 | 41 | 47 | 18 | 8 | 31 | 8 | 44 | 21 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 11 | 0 | 170 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 340 | 122 | 0 | 0 | 0 |  | 5995 | 2841 | 8836 | 4178 | 801 | 1650 | 1229 | 490 | 53 | 328 | 100 | 7 | 0 | 0
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 70 | 0 | 322 | 351 |  | 0 | 260 | 270 | 0 | 0 | 14 | 300 | 0 | 0 | 55 | 48 | 125 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 213 | 0 | 110 | 0 |  | 16 | 0 | 40 | 88 | 0 | 12 | 16 | 6 | 80 | 0 | 0 | 340 | 295 | 200 | 8 | 0 | 26 | 51 | 0 | 43 | 0 | 50 | 16 | 22 | 11 | 25 | 21 | 122 | 163 | 8 | 21 | 0 | 43 | 30 | 19 | 0 | 0 | 161 | 45 | 50 | 0 | 190 | 0 | 0 | 9 | 295 | 16 | 8 | 0 | 100 | 0 | 0 | 26 | 0 | 100 | 0 | 30 | 39 | 65 | 0 | 56 | 84 | 60 | 0 | 0 | 0 | 47 | 114 | 70 | 30 | 350 | 17 | 0 | 49 | 72 | 0 | 18 | 0 |  | 800 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 60 | 50 | 41 | 75 | 18 | 8 | 31 | 8 | 44 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 11 | 0 | 172 | 0 | 350 | 0 | 0 | 6 | 0 | 40 | 0 | 0 | 20 | 350 | 120 | 0 | 0 | 0 |  | 6809 | 2961 | 9770 | 4330 | 800 | 1690 | 1818 | 500 | 54 | 456 | 122 | 0 | 0 | 0
19:30 | 0 | 0 | 0 | 0 | 300 | 80 | 0 | 313 | 352 |  | 0 | 260 | 250 | 0 | 0 | 30 | 335 | 0 | 0 | 90 | 48 | 150 | 20 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 8 | 33 | 33 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 202 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 18 | 16 | 6 | 110 | 0 | 0 | 310 | 270 | 184 | 8 | 0 | 26 | 52 | 0 | 43 | 0 | 50 | 35 | 22 | 11 | 25 | 21 | 128 | 164 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 57 | 84 | 0 | 225 | 0 | 0 | 10 | 275 | 16 | 11 | 0 | 150 | 0 | 0 | 80 | 0 | 100 | 0 | 70 | 100 | 140 | 0 | 115 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 118 | 100 | 380 | 25 | 0 | 126 | 94 | 0 | 18 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 60 | 50 | 41 | 85 | 35 | 43 | 31 | 16 | 44 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 40 | 194 | 0 | 370 | 35 | 0 | 55 | 0 | 107 | 0 | 0 | 70 | 440 | 170 | 0 | 0 | 0 |  | 7714 | 3582 | 11296 | 4521 | 800 | 1825 | 2876 | 590 | 54 | 502 | 128 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 95 | 0 | 323 | 352 |  | 0 | 260 | 255 | 0 | 0 | 30 | 334 | 0 | 0 | 100 | 48 | 150 | 14 | 0 | 0 | 0 | 54 | 35 | 55 | 19 | 25 | 8 | 33 | 16 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 18 | 16 | 12 | 110 | 0 | 0 | 310 | 270 | 184 | 8 | 0 | 26 | 52 | 0 | 43 | 0 | 50 | 37 | 22 | 11 | 30 | 21 | 112 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 84 | 0 | 225 | 0 | 0 | 10 | 280 | 16 | 11 | 0 | 190 | 0 | 0 | 108 | 0 | 100 | 0 | 70 | 80 | 135 | 0 | 115 | 105 | 105 | 0 | 0 | 0 | 110 | 100 | 117 | 100 | 400 | 30 | 0 | 124 | 95 | 0 | 18 | 0 |  | 801 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 60 | 50 | 40 | 86 | 35 | 43 | 38 | 35 | 44 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 30 | 185 | 0 | 342 | 70 | 0 | 85 | 0 | 107 | 0 | 0 | 100 | 460 | 172 | 0 | 0 | 0 |  | 7776 | 3678 | 11454 | 4520 | 801 | 1825 | 3023 | 610 | 54 | 509 | 112 | 0 | 0 | 0
21:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 324 | 351 |  | 0 | 260 | 280 | 0 | 0 | 0 | 332 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 21 | 33 | 16 | 25 | 0 | 30 | 25 | 100 | 0 | 25 | 210 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 0 | 16 | 20 | 110 | 0 | 0 | 325 | 290 | 196 | 8 | 0 | 26 | 49 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 114 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 81 | 0 | 225 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 120 | 0 | 100 | 0 | 70 | 100 | 135 | 0 | 115 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 118 | 100 | 400 | 0 | 0 | 126 | 91 | 0 | 18 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 60 | 50 | 40 | 87 | 35 | 43 | 31 | 52 | 44 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 40 | 168 | 0 | 418 | 90 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 490 | 221 | 0 | 0 | 0 |  | 7790 | 3908 | 11698 | 4578 | 800 | 1962 | 3046 | 640 | 55 | 503 | 114 | 0 | 0 | 0
22:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 319 | 354 |  | 0 | 260 | 250 | 0 | 0 | 0 | 334 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 25 | 0 | 30 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 6 | 0 | 16 | 28 | 110 | 0 | 0 | 310 | 270 | 218 | 8 | 0 | 26 | 49 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 116 | 159 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 62 | 84 | 0 | 225 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 195 | 0 | 0 | 151 | 0 | 100 | 0 | 70 | 100 | 142 | 0 | 115 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 120 | 100 | 400 | 0 | 0 | 126 | 94 | 0 | 29 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 30 | 0 | 0 | 0 | 50 | 50 | 40 | 95 | 35 | 43 | 31 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 40 | 193 | 0 | 388 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 222 | 0 | 0 | 0 |  | 7843 | 3898 | 11741 | 4608 | 800 | 1943 | 3077 | 640 | 55 | 502 | 116 | 0 | 0 | 79.98
23:00 | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 319 | 353 |  | 0 | 260 | 270 | 0 | 0 | 0 | 334 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 8 | 0 | 30 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 34 | 88 | 6 | 0 | 16 | 29 | 110 | 0 | 0 | 260 | 270 | 217 | 8 | 0 | 26 | 50 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 118 | 159 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 161 | 62 | 84 | 0 | 225 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 170 | 0 | 120 | 0 | 70 | 100 | 140 | 0 | 115 | 53 | 105 | 0 | 0 | 0 | 110 | 114 | 117 | 100 | 400 | 0 | 0 | 126 | 94 | 0 | 36 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 30 | 0 | 0 | 0 | 50 | 50 | 42 | 87 | 35 | 43 | 31 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 166 | 0 | 328 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 490 | 222 | 0 | 0 | 0 |  | 7773 | 3749 | 11522 | 4512 | 800 | 1889 | 3029 | 640 | 55 | 479 | 118 | 0 | 0 | 79.99
24:00 | 0 | 0 | 0 | 0 | 300 | 93 | 0 | 318 | 353 |  | 0 | 260 | 260 | 0 | 0 | 0 | 334 | 0 | 0 | 100 | 7 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 30 | 33 | 33 | 8 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 17 | 88 | 6 | 0 | 16 | 37 | 110 | 0 | 0 | 260 | 270 | 217 | 8 | 0 | 26 | 48 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 114 | 174 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 62 | 84 | 0 | 225 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 140 | 0 | 149 | 0 | 70 | 100 | 148 | 0 | 107 | 53 | 105 | 0 | 0 | 0 | 110 | 114 | 118 | 100 | 401 | 0 | 0 | 126 | 94 | 0 | 36 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 0 | 50 | 50 | 35 | 87 | 35 | 43 | 31 | 52 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 145 | 0 | 316 | 90 | 0 | 35 | 0 | 113 | 0 | 0 | 113 | 450 | 222 | 0 | 0 | 0 |  | 7652 | 3588 | 11240 | 4503 | 800 | 1890 | 2824 | 600 | 54 | 455 | 114 | 0 | 0 | 79.99
KWH | 0 | 0 | 0 | 0 | 7255936 | 2169319 | 0 | 7829500 | 8038000 |  | 0 | 6128500 | 6523636 | 0 | 0 | 67103 | 7823767 | 0 | 0 | 2118720 | 531504 | 2304480 | 18236 | 0 | 0 | 0 | 1135800 | 506379 | 1213076 | 356652 | 600000 | 606600 | 812200 | 747500 | 588480 | 0 | 623880 | 608000 | 2400000 | 0 | 600921 | 4862719 | 0 | 2171379 | 0 |  | 442320 | 0 | 560621 | 2090040 | 136320 | 35520 | 380544 | 304800 | 2155148 | 0 | 0 | 7241000 | 6724000 | 4649000 | 217454 | 0 | 580896 | 1272960 | 0 | 969549 | 0 | 774728 | 838190 | 486144 | 234540 | 682500 | 434020 | 2681280 | 3899760 | 190080 | 457956 | 3500 | 1029000 | 706920 | 1173000 | 0 | 0 | 3650000 | 1429632 | 1947840 | 0 | 5090060 | 190000 | 0 | 232380 | 7227500 | 382248 | 192384 | 0 | 2072508 | 0 | 0 | 1363200 | 0 | 2608850 | 22815 | 934080 | 1777440 | 2900509 | 0 | 2064000 | 1461600 | 2374436 | 22201 | 0 | 0 | 1759701 | 1678080 | 2558640 | 1433280 | 9158900 | 56640 | 83470 | 2417760 | 2409982 | 0 | 711000 | 84432 |  | 19459636 | 0 | 9397440 | 0 | 0 | 0 | 0 | 0 | 83050 | 0 | 0 | 2077363 | 567528 | 0 | 0 | 0 | 1290000 | 817856 | 584443 | 1623376 | 480920 | 590880 | 400954 | 1129920 | 421230 | 448320 | 0 | 198144 | 0 | 0 | 3680500 | 0 | 0 | 0 | 0 | 4405309 | 0 | 285108 | 507840 | 4658982 | 0 | 9112600 | 1214880 | 0 | 956160 | 0 | 884764 | 0 | 26709 | 1283904 | 10984100 | 4731518 | 0 | 0 | 34800 |  | 170289645 | 82338234 | 252627879 | 107248143 | 19459636 | 44826376 | 54667299 | 14664600 | 1231880 | 7570738 | 2681280 | 277927 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8054088.96 | 2863501.08 | 0 | 7907795 | 8279140 |  | 0 | 6680065 | 7241235.96 | 0 | 0 | 567691.38 | 8136717.68 | 0 | 0 | 15953961.6 | 4847316.48 | 22676083.2 | 168135.92 | 0 | 0 | 0 | 8291340 | 3914309.67 | 11960929.36 | 267489 | 450000 | 0 | 0 | 0 | 5690601.6 | 0 | 168447.6 | 164160 | 4344000 | 0 | 5582556.09 | 5300363.71 | 0 | 3691344.3 | 0 |  | 0 | 0 | 5438023.7 | 19959882 | 1185984 | 281318.4 | 479485.44 | 905256 | 3189619.04 | 0 | 0 | 5358340 | 6724000 | 4277080 | 280515.66 | 0 | 656412.48 | 1782144 | 0 | 1657928.79 | 0 | 7824752.8 | 8004714.5 | 617402.88 | 175905 | 1194375 | 325515 | 20109600 | 4133745.6 | 1725926.4 | 581604.12 | 55790 | 1687560 | 1131072 | 2087940 | 0 | 0 | 3796000 | 2816375.04 | 3720374.4 | 0 | 8805803.8 | 416100 | 0 | 474055.2 | 7299775 | 286686 | 146211.84 | 0 | 15668160.48 | 0 | 0 | 7088640 | 0 | 25671084 | 266707.35 | 7612752 | 19285224 | 20448588.45 | 0 | 18823680 | 13812120 | 20681337.56 | 0 | 0 | 0 | 15467771.79 | 16747238.4 | 21927544.8 | 9545644.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112087503.36 | 0 | 9867312 | 0 | 0 | 0 | 0 | 0 | 871194.5 | 0 | 0 | 2347420.19 | 879668.4 | 0 | 0 | 0 | 2644500 | 8047703.04 | 5937940.88 | 14366877.6 | 3703084 | 7988697.6 | 3885244.26 | 10948924.8 | 4085931 | 860774.4 | 0 | 149995.008 | 0 | 0 | 19948310 | 0 | 0 | 0 | 0 | 5815007.88 | 0 | 427662 | 8638358.4 | 5451008.94 | 0 | 9021474 | 12683347.2 | 0 | 9073958.4 | 0 | 6865768.64 | 0 | 295134.45 | 9488050.56 | 48220199 | 0 | 0 | 0 | 0 |  | 485841041.31 | 324601050.508 | 810442091.818 | 111226335.908 | 112087503.36 | 47220273.93 | 377545879.24 | 68168509 | 332607.6 | 73133750.98 | 20109600 | 617631.8 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 92 | 0 | 322 | 316 |  | 0 | 260 | 260 | 0 | 0 | 0 | 331 | 0 | 0 | 100 | 16 | 64 | 0 | 0 | 0 | 0 | 54 | 30 | 53 | 19 | 25 | 28 | 33 | 25 | 25 | 0 | 29 | 25 | 100 | 0 | 25 | 204 | 0 | 100 | 0 |  | 24 | 0 | 0 | 90 | 0 | 0 | 16 | 7 | 80 | 0 | 0 | 260 | 270 | 186 | 8 | 0 | 26 | 53 | 0 | 34 | 0 | 50 | 43 | 22 | 8 | 25 | 14 | 102 | 161 | 8 | 19 | 1 | 43 | 30 | 47 | 0 | 0 | 163 | 61 | 81 | 0 | 218 | 0 | 0 | 9 | 295 | 16 | 5 | 0 | 95 | 0 | 0 | 0 | 0 | 149 | 2 | 50 | 100 | 142 | 0 | 75 | 50 | 105 | 4 | 0 | 0 | 82 | 34 | 118 | 50 | 400 | 0 | 1 | 126 | 94 | 0 | 18 | 7 |  | 799 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 60 | 0 | 20 | 48 | 18 | 43 | 0 | 52 | 0 | 20 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 12 | 0 | 183 | 0 | 394 | 53 | 0 | 35 | 0 | 0 | 0 | 2 | 35 | 370 | 220 | 0 | 0 | 0 |  | 10165 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 96 | 0 | 324 | 351 | 0 | 0 | 260 | 280 | 0 | 0 | 0 | 332 | 0 | 0 | 100 | 24 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 19 | 25 | 21 | 33 | 16 | 25 | 0 | 30 | 25 | 100 | 0 | 25 | 210 | 0 | 110 | 0 | 0 | 24 | 0 | 51 | 88 | 0 | 0 | 16 | 20 | 110 | 0 | 0 | 325 | 290 | 196 | 8 | 0 | 26 | 49 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 114 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 81 | 0 | 225 | 0 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 120 | 0 | 100 | 0 | 70 | 100 | 135 | 0 | 115 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 118 | 100 | 400 | 0 | 0 | 126 | 91 | 0 | 18 | 0 |  | 800 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 29 | 0 | 0 | 0 | 60 | 50 | 40 | 87 | 35 | 43 | 31 | 52 | 44 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 40 | 168 | 0 | 418 | 90 | 0 | 112 | 0 | 113 | 0 | 0 | 113 | 490 | 221 | 0 | 0 | 0 |  | 11698 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 360 | 360 | 0 | 0 | 260 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 25 | 0 | 30 | 25 | 100 | 0 | 25 | 215 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 12 | 50 | 16 | 15 | 135 | 0 | 0 | 360 | 350 | 210 | 26 | 0 | 26 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 190 | 8 | 21 | 0 | 43 | 30 | 51 | 0 | 0 | 160 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 250 | 300 | 100 | 200 | 100 | 135 | 0 | 100 | 200 | 150 | 0 | 115 | 50 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 112 | 0 | 36 |  |  | 807 | 0 | 400 | 0 | 0 | 220 | 0 | 0 | 20 | 60 | 0 | 86 | 33 | 110 | 0 | 0 | 65 | 43 | 40 | 95 | 35 | 50 | 35 | 52 | 42 | 18 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 210 | 0 | 11 | 100 | 200 | 0 | 400 | 90 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 350 | 360 | 0 | 0 | 260 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 100 | 100 | 150 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 25 | 0 | 30 | 25 | 100 | 0 | 25 | 210 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 12 | 50 | 16 | 5 | 110 | 0 | 0 | 350 | 330 | 210 | 26 | 0 | 26 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 148 | 190 | 8 | 21 | 1.6 | 43 | 30 | 51 | 0 | 0 | 160 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 315 | 16 | 11 | 100 | 250 | 100 | 100 | 175 | 100 | 130 | 20 | 100 | 170 | 150 | 0 | 115 | 50 | 105 | 5 | 200 | 54 | 110 | 114 | 113 | 100 | 400 | 90 | 50 | 126 | 112 | 0 | 36 | 30 |  | 807 | 0 | 400 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 85 | 25 | 110 | 0 | 0 | 60 | 0 | 0 | 50 | 35 | 50 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 210 | 0 | 11 | 50 | 200 | 0 | 400 | 90 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 93 | 0 | 331 | 306 | 0 | 0 | 260 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 60 | 7 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 35 | 19 | 25 | 25 | 33 |  | 8 | 0 | 29 | 25 | 100 | 0 | 25 | 214 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 76 | 6 | 0 | 16 | 6 | 110 | 0 | 0 | 280 | 295 | 197 | 8 | 0 | 23 | 46 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 96 | 185 | 8 | 21 | 0 | 44 | 30 | 53 | 0 | 0 | 162 | 62 | 84 | 0 | 225 | 0 | 0 | 9 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 9 | 0 | 0 | 1 | 0 | 65 | 17 | 34 | 3 | 0 | 0 | 17 | 114 | 100 | 0 | 350 | 0 | 15 | 0 | 114 | 0 | 18 | 5 | 0 | 792 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 17 | 0 | 0 | 0 | 65 | 0 | 0 | 24 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 175 | 0 | 341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300 | 221 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9247 | 7:00
| Highest Generation |  | 11741 | 22:00
| Day Peak Generation |  | 10165 | 12:00
| Evening Peak Generation |  | 11698 | 21:00
| HVDC Max Flow |  | 814 | 2:00
| HVDC EvPeak Flow |  | 800 | 21:00
| Load factor L.F |  | 89.65%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-08
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-07 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10165 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8693 | MW
Evening Peak Generation : |  | 11698 | MW Hour : | 21:00 | Available Max Generation : |  | 15050 | MW
E.P. Demand (at gen end) : |  | 11698 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12000 | MW
Maximum Generation : |  | 11741 | MW Hour : | 22:00 | Reserve(Generation end) |  | 3050 | MW
Total Gen. (MKWH) : |  | 252.6279 | System Load Factor : | 89.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -28 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-08
Actual : | 80 | Ft.(MSL) , | Rule curve : | 85.12 | Ft.( MSL )
Gas Consumed : | Total = | 1153.8 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 158446609.838
: |  | Coal : | 68168509 | Oil : | 450679630.22 | Total : | 677294749.058
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4276.4928 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1456.6262 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1305.5133 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1179.7921 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1066.0779 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 860.2932 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 477.9683 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.4212 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 663.5155 |  |  | 0 | 0%
Total | 0 |  | 11507.7004 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,5
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Chandpur-150 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar 400 kV Bus-1 & 2 were shutdown at 12:20 for Project work.
b) Barishal(S) 132/33 kV T2 transformer was under shut down from 11:38 to 12:36 for R/H maintenance |  |  |  |  | About 30 MW power interruption occurred under Barishal S/S area
at 132 kV side. |  |  |  |  | from 11:38 to 12:36.
c) Kaliakoir 230/132 New transformer tripped at 11:57 showing PRD. |  |  |  |  | About 100 MW power interruption occurred under Dhamrai S/S area
Dhamrai S/S power restored at 12:41 by rearranging Bus at Kaliakoir S/S. |  |  |  |  | from 11:57 to 12:41.
d) Rangpur 132/33 kV T2 transformer was under shut down from 11:07 to 12:05 for R/H maintenance
at 33 kV side.
e) Manikganj P.P.-Savar 132 kV Ckt-2 was under shut down from 13:11 to 16:41 for C/M.
f) Keraniganj-Hasnabad 230 kV Ckt-1 was under shut down from 09:42 to 17:54 due to R/H maintenance.
g) Khulna(S)-Satkhira 132 kV Ckt-2 tripped at 14:29 from both ends showing Dist. Z1 at Khulna(S) end &
Dist. Z1, A,B,C at Satkhira end and was switched on at 14:47.
h) Bogura(Old) 132/33 kV T3 transformer along with 33 kV Bus section were under shut down from 16:18 |  |  |  |  | About 22 MW power interruption occurred under Bogura(Old) S/S area
to 17:15 due to R/H maintenance. |  |  |  |  | from 16:18 to 17:15.
i) Dohazari-Cox's Bazar 132 kV Ckt-1 is under shut down since 06:08(08/07/2021) for D/W. |  |  |  |  | About 12 MW power interruption occurred under Matarbari S/S area
since 06:08(08/07/2021).
j) Madunaghat 132/33 kV T1 transformer was shut down at 07:13(08/07/2021) for C/M.
k) Tongi-Bashundhara 132 kV Ckt-1 is under shut down since 06:24(08/07/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-07 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7255936 | Gas shortage
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 96 | 2169319 | Gas shortage
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 324 | 7829500 | FGMO
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 351 | 8038000
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 260 | 6128500 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6523636 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 67103 | Reserve.
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 18236 | Reserve.
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 356652
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2118720
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7823767
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 24 | 531504 | Low demand
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1135800
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2304480
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 506379 | Reserve.
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1213076
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1206600 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 812200
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 16 | 747500 | Engine problem
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 588480 | Fuel shortage
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 195 | 2072508 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 100 | 2608850 | Low demand
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1461600
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 56640 | Reserve.
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2417760 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 84432
| Dhaka area Total |  |  |  | 5819 | 2991 | 66077178
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 600921
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 22815
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 35520 | Reserve.
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 55 | 1231880 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 210 | 4862719 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2171379 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2374436
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 560621 | Low demand
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 88 | 2090040 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 934080 | Low demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 16 | 380544 | Engine problem
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 304800
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 136320 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22201
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1759701
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1433280
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 91 | 2409982 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1151 | 23731239
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 110 | 2155148 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 196 | 4649000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 325 | 7241000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 290 | 6724000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 580896 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 49 | 1272960
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 969549 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 135 | 2900509 | Engine problem
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 774728
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 0 | Under maint
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1777440 | Low demand
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 486144
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 234540
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2681280
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 682500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 838190 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 434020
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1678080
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 118 | 2558640
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 18 | 711000 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1826 | 39567078
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3899760 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 457956
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 190080 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 3500
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 120 | 1363200 | Low demand
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2064000
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 83470
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 442320
| Mymensingh Area Total |  |  |  | 709 | 445 | 8504286
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 706920 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 3650000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1173000
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 192384
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 56 | 1429632
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1947840
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 225 | 5090060
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 190000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 382248 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7227500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 0 | 0 | Under maint.
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 232380
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9158900
| Sylhet Area Total |  |  |  | 2377 | 1377 | 32409864
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 800 | 19459636
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 83050 | Reserve.
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 0 | Reserve.
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9397440 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 40 | 507840 | Low demand
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 1214880 | Engine problem
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1340 | 30662846
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 567528
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2077363 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 285108 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 490 | 10984100
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 221 | 4731518 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 837 | 18645617
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 60 | 1290000
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage.
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 817856
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 40 | 584443 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 480920 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 590880 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 400954 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 182 | 4405309 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 168 | 4658982 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 418 | 9112600 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 44 | 421230 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 448320
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 198144
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1129920
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 87 | 1623376 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 112 | 956160
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1283904
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 34800
| Rajshahi Area Total |  |  |  | 2179 | 1468 | 28437798
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3680500 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 884764
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 26709
| Rangpur Area Total |  |  |  | 605 | 263 | 4591973
| Total |  |  |  | 21060 | 11698 | 252627879
| Eastern Grid Total |  |  |  | 14321 | 7790 | 170289645
| Western Grid Total |  |  |  | 6739 | 3908 | 82338234
| National Grid Total |  |  |  | 21060 | 11698 | 252627879
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-07
(a) ENTIRE EASTERN GRID : |  | 7531 | MW | (b) ENTIRE WESTERN GRID : |  | 3678 | MW
i) Dhaka area |  | 3934 | MW | i) Khulna area |  | 1320 | MW
ii) Chittagong area |  | 1100 | MW | ii) Rajshahi area |  | 1235 | MW
iii) Comilla area |  | 1098 | MW | iii) Barisal area |  | 319 | MW
iv) Mymensingh area |  | 956 | MW | iv) Rangpur area |  | 804 | MW
v) Sylhet area |  | 443 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11209 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 15:00 | Kishoreganj | 144 | 22:00 | Jessore | 97 | 20:00
Munsiganj | 96 | 1:00 | Netrokona | 101 | 22:00 | Benapol | 50 | 19:30
Sonargaon | 81 | 22:00 | Jamalpur | 128 | 1:00 | Jhenida | 95 | 19:30
Shyampur | 192 | 10:00 | Sherpur | 120 | 1:00 | Bottail | 126 | 20:00
Bhulta | 186 | 0:00 | Srimongal | 49 | 21:00 | G.K Project | 51 | 21:00
Madanganj | 55 | 14:00 | Shahjibazar | 99 | 20:00 | Faridpur | 136 | 22:00
Shitalakhya | 111 | 13:00 | Fenchuganj | 39 | 19:00 | Rajbari | 45 | 1:00
Rahim steel | 27 | 0:00 | Kulawara | 41 | 22:00 | Madaripur | 92 | 1:00
Matuail | 60 | 0:00 | Sylhet | 96 | 20:00 | Sariatpur | 62 | 1:00
Ghorasal | 76 | 22:00 | Chatak | 26 | 21:00 | Gopalganj | 81 | 1:00
Narsingdi | 160 | 22:00 | Sunamganj | 48 | 22:00 | Bagerhat | 88 | 1:00
Haripur (SBU) | 110 | 0:00 | Biani Bazar | 56 | 19:30 | Mongla | 40 | 20:00
Sreenagar | 39 | 20:00 | Comilla (S) | 128 | 19:30 | Satkhira | 87 | 20:00
Ullon | 62 | 22:00 | Comilla(N) | 128 | 20:00 | Gallamari | 0
Hasnabad | 74 | 1:00 | Chandpur | 74 | 1:00 | Magura | 50 | 1:00
Magbazar | 71 | 10:00 | Feni | 105 | 21:00 | Norail | 40 | 1:00
Maniknagar | 72 | 13:00 | Chowmuhani | 198 | 22:00 | Chuadanga | 89 | 1:00
Bangabhaban | 10 | 10:00 | Ashuganj | 39 | 21:00 | Borguna | 16 | 1:00
Motijheel | 21 | 13:00 | Daudkandi | 134 | 20:00 | Barisal(N) | 40 | 1:00
Narinda | 48 | 13:00 | B.Baria | 153 | 1:00 | Barisal (S) | 92 | 22:00
Kazla | 68 | 16:00 | Ramganj | 76 | 22:00 | Patuakhali | 101 | 1:00
Dhanmondi | 134 | 13:00 | Chaddagram | 41 | 23:00 | Bhandaria | 44 | 1:00
Lalbag | 83 | 13:00 | PHP | 3 | 12:00 | Borhan Uddin | 42 | 22:00
Madartek | 66 | 20:00 | Kochua | 64 | 21:00 | Ishurdi | 60 | 14:00
Dhaka University | 22 | 13:00 | Madunaghat | 62 | 16:00 | Ruppur Paromanobik | 3 | 7:00
Aftabnagar | 10 | 13:00 | Hathazari | 87 | 19:00 | Natore | 122 | 21:00
Fatullah | 56 | 11:00 | Khulshi | 190 | 10:00 | Bogra | 145 | 21:00
Nawabganj | 47 | 22:00 | Halishahar | 91 | 7:00 | Noagaon | 120 | 21:00
Keraniganj | 62 | 14:00 | Baraulia | 147 | 1:00 | Rajshahi | 148 | 21:00
Mirpur | 120 | 11:00 | Sikalbaha | 28 | 14:00 | Rajshahi New | 12 | 20:00
Kalyanpur | 96 | 15:00 | Dohazari | 78 | 22:00 | C.Nawabganj | 64 | 21:00
Gulshan | 82 | 13:00 | Cox'sbazar | 88 | 1:00 | Amnura | 48 | 21:00
Uttara | 83 | 13:00 | Chandraghona | 24 | 1:00 | Pabna | 91 | 1:00
Uttara New | 12 | 10:00 | Kaptai | 4 | 19:00 | Shahjadpur | 84 | 21:00
Kamrangirchar | 81 | 12:00 | A. Khaer Stl. | 5 | 5:00 | Serajganj | 91 | 20:00
Savar | 148 | 12:00 | Bakulia | 93 | 13:00 | Niyamatpur | 73 | 20:00
Bhasantec | 112 | 13:00 | Julda | 24 | 12:00 | Joypurhat | 53 | 20:00
Agargaon | 71 | 13:00 | TK chemical | 25.7 | 19:30 | Sherpur(Bogura) | 52 | 19:30
Satmosjid | 101 | 14:00 | Modern Steel | 0 | #N/A | Mohastangor | 60 | 19:30
Tongi | 104 | 11:00 | Shahmirpur | 33 | 1:00 | Bhangura | 27 | 21:00
Kabirpur | 246 | 9:00 | Khagrachhari | 22 | 8:00 | Rangpur | 132 | 19:30
Basundhara | 198 | 15:00 | Matarbari | 31.5 | 1:00 | Lalmonirhat | 43 | 20:00
Manikganj | 82 | 21:00 | Baroiar Hat | 38 | 1:00 | Saidpur | 104 | 21:00
Joydevpur | 154 | 11:00 | Rangamati | 10 | 12:00 | Purbasadipur | 107 | 20:00
New Tongi | 116 | 12:00 | Abul Khair 230 | 4 | 12:00 | Thakurgaon | 84 | 21:00
Kodda | 275 | 10:00 | BSRM | 156 | 1:00 | Palashbari | 102 | 20:00
Dhamrai | 108 | 15:00 | GPH Ispat | 87 | 0:00 | Barapukuria | 53 | 21:00
Rajendrapur | 102 | 22:00 | Agrabad | 54 | 11:00 | Panchagar | 53 | 20:00
Valuka | 114 | 19:30 | Goalpara | 32 | 13:00 | Joldhaka | 56 | 21:00
Tangail | 191 | 21:00 | Central S/S | 117 | 13:00 | Kurigram | 57 | 19:30
Mymensing | 202 | 1:00 | Noapara | 45 | 19:30 | Mithapukur | 30 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-07 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 19:30 | 397 | 11:00 | Kaliakoir | 392 | 0.625 | 385 | 0.625
| Bheramara | 401 | 8:00 | 395 | 1:00 | Bhulta | 383 | 0.79167 | 376 | 0.29167
| Ashuganj(N) | 391 | 18:30 | 384 | 11:00 | Gopalganj | 410 | 0.625 | 390 | 0.95833
| Payra | 413 | 19:30 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 224 | 20:00 | 217 | 18:00
| Ishurdi | 235 | 14:00 | 228 | 7:00 | Megnaghat | 230 | 13:00 | 224 | 18:30
| Ashuganj | 239 | 8:00 | 235 | 6:00 | Fenchuganj | 238 | 19:00 | 234 | 1:00
| Serajganj | 230 | 1:00 | 225 | 7:00 | Siddhirganj | 229 | 8:00 | 225 | 12:00
| Baghabari | 232 | 16:00 | 228 | 7:00 | Maniknagar | 227 | 8:00 | 223 | 12:00
| Barapukuria | 233 | 18:00 | 226 | 21:00 | Agargaon | 225 | 14:00 | 220 | 16:00
| Bogra | 225 | 19:00 | 218 | 21:00 | Barisal | 242 | 19:30 | 231 | 23:00
| Rajshahi | 237 | 17:00 | 227 | 7:00 | Bhola 225 MW | 246 | 15:00 | 237 | 23:00
| Khulna South | 231 | 14:00 | 206 | 7:00 | AKSML | 225 | 19:30 | 220 | 5:00
| Rampura | 228 | 3:00 | 224 | 11:00 | BSRM | 226 | 11:00 | 220 | 7:00
| Haripur | 227 | 18:30 | 223 | 11:00 | Bibiyana | 238 | 8:00 | 233 | 9:00
| Hasnabad | 226 | 3:00 | 220 | 12:00 | Bhulta | 230 | 19:30 | 225 | 12:00
| Shyampur | 225 | 19:30 | 220 | 11:00 | Ashuganj (S) | 235 | 8:00 | 231 | 7:00
| Aminbazar | 225 | 1:00 | 221 | 2:00 | Kaliakoir | 227 | 18:30 | 222 | 6:00
| Tongi | 227 | 23:00 | 220 | 11:00 | GPH | 225 | 11:00 | 220 | 6:00
| Comilla (N) | 228 | 8:00 | 225 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 19:00 | 129 | 12:00 | Madanhat | 132 | 0.041667 | 131 | 0.083333
| Munsiganj | 133 | 19:00 | 128 | 12:00 | Hathazari | 133 | 0.8125 | 130 | 0.041667
| Sonargaon | 132 | 19:00 | 127 | 7:00 | Khulshi | 131 | 0.91667 | 126 | 0.70833
| Shyampur | 134 | 19:00 | 131 | 10:00 | Halishahar | 133 | 0.83333 | 127 | 0.70833
| Bhulta | 125 | 7:00 | 121 | 12:00 | Baraulia | 133 | 0.8125 | 128 | 0.75
| Madanganj | 132 | 18:30 | 127 | 11:00 | Sikalbaha | 134 | 0.8125 | 129 | 0.70833
| Shitalakhya | 138 | 19:00 | 130 | 12:00 | Dohazari | 130 | 0.58333 | 126 | 0.25
| Rahim steal | 133 | 19:00 | 129 | 11:00 | Cox'sbazar | 123 | 0.33333 | 117 | 0.79167
| Matuail | 133 | 19:00 | 129 | 12:00 | Chandraghona | 134 | 0.79167 | 130 | 0.20833
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 132 | 0.77083 | 130 | 0.041667
| Narsinghdi | 134 | 8:00 | 128 | 23:00 | A. Khaer Stl. | 130 | 0.041667 | 129 | 0.125
| Haripur (SBU) | 132 | 8:00 | 129 | 12:00 | Bakulia | 133 | 0.875 | 128 | 0.70833
| Sreenagar | 129 | 20:00 | 125 | 11:00 | Julda | 133 | 0.54167 | 128 | 0.79167
| Ullon | 135 | 7:00 | 131 | 10:00 | TK Chemical | 134 | 0.77083 | 128 | 0.70833
| Hasnabad | 136 | 2:00 | 132 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 135 | 4:00 | 131 | 11:00 | Shahmirpur | 134 | 0.8125 | 128 | 0.75
| Maniknagar | 137 | 19:00 | 133 | 12:00 | Khagrachhari | 132 | 0.33333 | 128 | 0.75
| Bangabhaban | 137 | 19:00 | 133 | 12:00 | Matarbari | 128 | 0.58333 | 120 | 0.041667
| Motijheel | 137 | 19:00 | 133 | 12:00 | Baroiar Hat | 134 | 0.083333 | 130 | 0.75
| Narinda | 137 | 19:00 | 133 | 12:00 | Rangamati | 133 | 19:30 | 128 | 18:00
| Kazla | 137 | 19:00 | 133 | 12:00 | Agrabad | 132 | 19:30 | 126 | 17:00
| Dhanmondi | 132 | 7:00 | 129 | 10:00 | Goalpara S/S | 140 | 14:00 | 120 | 0.29167
| Lalbag | 137 | 8:00 | 130 | 12:00 | Khulna Central S/S | 137 | 17:00 | 120 | 0.29167
| Madartek | 136 | 21:00 | 131 | 11:00 | Noapara | 135 | 14:00 | 120 | 0.25
| Dhaka University | 135 | 18:30 | 132 | 10:00 | Jessore | 133 | 17:00 | 116 | 0.125
| Aftabnagar | 135 | 2:00 | 132 | 10:00 | Benapol | 134 | 0.70833 | 117 | 0.16667
| Fatullah | 134 | 8:00 | 130 | 12:00 | Jhenida | 132 | 17:00 | 113 | 0.16667
| Nawabganj | 128 | 19:30 | 124 | 12:00 | Bottail | 135 | 0.70833 | 124 | 0.16667
| Keraniganj | 129 | 20:00 | 125 | 12:00 | G.K Project | 140 | 0.66667 | 135 | 0.041667
| Mirpur | 136 | 19:30 | 132 | 11:00 | Faridpur | 136 | 0.66667 | 128 | 0.95833
| Kalyanpur | 137 | 20:00 | 133 | 6:00 | Rajbari | 134 | 0.33333 | 128 | 0.875
| Gulshan | 134 | 3:00 | 131 | 10:00 | Madaripur | 142 | 0.625 | 133 | 0.83333
| Uttara | 135 | 2:00 | 131 | 7:00 | Shariyatpur S/S | 141 | 15:00 | 130 | 0.91667
| Uttara New | 135 | 10:00 | 131 | 7:00 | Gopalganj | 144 | 0.33333 | 134 | 0.875
| Kamrangirchar | 137 | 2:00 | 130 | 12:00 | Bagerhat | 138 | 14:00 | 114 | 0.29167
| Savar | 131 | 3:00 | 131 | 7:00 | Mongla | 138 | 14:00 | 120 | 0.29167
| Bhasantec | 134 | 3:00 | 131 | 10:00 | Satkhira | 139 | 14:00 | 118 | 7:00
| Agargaon | 137 | 3:00 | 132 | 11:00 | Gallamari
| Satmosjid | 135 | 19:00 | 131 | 15:00 | Magura | 130 | 16:00 | 112 | 0.29167
| Tongi | 139 | 18:00 | 134 | 15:00 | Narail | 127 | 0.75 | 111 | 0.29167
| Kabirpur | 135 | 8:00 | 131 | 21:00 | Chuadanga | 128 | 17:00 | 107 | 0.29167
| Basundhara | 136 | 22:00 | 131 | 14:00 | Borguna | 139 | 16:00 | 127 | 0.95833
| Manikganj | 140 | 22:00 | 136 | 15:00 | Barisal(N) | 141 | 14:00 | 132 | 1:00
| Joydevpur | 141 | 0:00 | 132 | 16:00 | Barisal (S) | 140 | 0.58333 | 129 | 0.91667
| New Tongi | 138 | 20:00 | 132 | 16:00 | Patuakhali(S) | 139 | 0.54167 | 124 | 0.91667
| Kodda | 137 | 14:00 | 130 | 18:00 | Bhandaria | 141 | 0.54167 | 125 | 0.91667
| Dhamrai | 133 | 19:00 | 127 | 10:00 | Ishurdi | 136 | 17:00 | 132 | 7:00
| Rajendrapur | 136 | 14:00 | 128 | 17:00 | Ruppur Paromanobik | 136 | 18:00 | 132 | 21:00
| Valuka | 125 | 6:00 | 113 | 21:00 | Natore | 134 | 14:00 | 130 | 7:00
| Tangail | 131 | 6:00 | 123 | 21:00 | Bogra | 133 | 19:00 | 128 | 1:00
| Mymensing | 128 | 6:00 | 118 | 21:00 | Noagaon | 129 | 1:00 | 124 | 21:00
| Kishorganj | 131 | 21:00 | 120 | 21:00 | Rajshahi | 133 | 18:30 | 127 | 7:00
| Netrokona | 127 | 6:00 | 117 | 20:00 | Rajshahi New | 134 | 17:00 | 128 | 6:00
| Jamalpur | 133 | 19:30 | 123 | 21:00 | C.Nawabganj | 133 | 2:00 | 126 | 7:00
| Sherpur | 132 | 22:00 | 122 | 17:00 | Amnura | 134 | 14:00 | 126 | 7:00
| Srimongal | 139 | 13:00 | 134 | 21:00 | Pabna | 135 | 15:00 | 131 | 2:00
| Shahjibazar | 137 | 10:00 | 132 | 21:00 | Shahjadpur | 138 | 18:00 | 134 | 7:00
| Fenchuganj | 137 | 15:00 | 133 | 23:00 | Serajganj | 132 | 17:00 | 130 | 1:00
| Khulawara | 136 | 5:00 | 134 | 1:00 | Niyamatpur | 129 | 18:00 | 121 | 21:00
| Sylhet | 135 | 6:00 | 133 | 19:00 | Joypurhat | 130 | 18:00 | 124 | 1:00
| Chatak | 135 | 10:00 | 130 | 21:00 | Sherpur(Bogura) | 132 | 8:00 | 128 | 5:00
| Sunamganj | 134 | 8;00 | 128 | 21:00 | Mohastangor | 131 | 18:00 | 125 | 5:00
| Biani Bazar | 134 | 7:00 | 130 | 21:00 | Bangura | 137 | 18:00 | 133 | 21:00
| Comilla(s) | 130 | 18:30 | 126 | 19:30 | Rangpur | 128 | 18:30 | 119 | 21:00
| Comilla(n) | 137 | 14:00 | 134 | 23:00 | Lalmonirhat | 127 | 18:30 | 120 | 20:00
| Chandpur | 133 | 12:00 | 125 | 22:00 | Saidpur | 129 | 18:30 | 119 | 21:00
| Feni | 135 | 18:30 | 128 | 5:00 | Purbasadipur | 127 | 18:30 | 113 | 20:00
| Chowmuhani | 137 | 12:00 | 129 | 18:00 | Thakurgaon | 125 | 18:00 | 110 | 21:00
| Ashuganj | 140 | 17:00 | 136 | 21:00 | Palashbari | 129 | 19:00 | 120 | 7:00
| Daudkandi | 132 | 13:00 | 128 | 1:00 | Barapukuria | 133 | 18:00 | 126 | 21:00
| B.Baria | 136 | 8:00 | 130 | 22:00 | Panchagar | 125 | 18:00 | 108 | 21:00
| Ramganj | 139 | 11:00 | 128 | 18:00 | Joldhaka | 124 | 0.75 | 113 | 0.875
| Chaddagram | 136 | 19:00 | 133 | 23:00 | Kurigram | 125 | 0.77083 | 114 | 0.875
| PHP | 136 | 19:30 | 129 | 18:00 | Mithapukur | 129 | 0.77083 | 122 | 0.20833
| Kochua | 132 | 18:00 | 125 | 1:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-07
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 6 | 7652 | 3588 | 11240 |  |  |  | QF-LDC-11
0:30 | 42 | 7621 | 3773.5 | 11394.5 | Date: | 2021-07-07
1:00 | 78 | 7590 | 3959 | 11549
1:30 | 50 | 7480.5 | 3795 | 11275.5
2:00 | 22 | 7371 | 3631 | 11002
2:30 | 39 | 7320 | 3587.5 | 10907.5 | [5 empty] | Gen. at Eve. Peak | 11698 | 11698 MW (21:00 )
3:00 | 56 | 7269 | 3544 | 10813 | [6 empty] | 21:00
3:30 | 59 | 7131.5 | 3502.5 | 10634 | [5 empty] | Gen. at Day Peak | 10165 | 10165 MW (12:00 )
4:00 | 62 | 6994 | 3461 | 10455 | [6 empty] | 12:00
4:30 | 58 | 6906.5 | 3410.5 | 10317 | [5 empty] | Highest Generation | 11741
5:00 | 54 | 6819 | 3360 | 10179 | [6 empty] | 22:00
5:30 | 181 | 6524.5 | 3270.5 | 9795
6:00 | 308 | 6230 | 3181 | 9411
6:30 | 232 | 6185.5 | 3143.5 | 9329
7:00 | 156 | 6141 | 3106 | 9247
7:30 | 114 | 6238.5 | 3076 | 9314.5
8:00 | 72 | 6336 | 3046 | 9382
8:30 | 99 | 6610.5 | 3075.5 | 9686
9:00 | 126 | 6885 | 3105 | 9990
9:30 | 164 | 6920 | 3118.5 | 10038.5
10:00 | 202 | 6955 | 3132 | 10087
10:30 | 164 | 6929 | 3109.5 | 10038.5
11:00 | 126 | 6903 | 3087 | 9990
11:30 | 121 | 6958 | 3119.5 | 10077.5
12:00 | 116 | 7013 | 3152 | 10165
12:30 | 111 | 7005 | 3189.5 | 10194.5
13:00 | 106 | 6997 | 3227 | 10224
13:30 | 230 | 6969.5 | 3177.5 | 10147
14:00 | 354 | 6942 | 3128 | 10070
14:30 | 362 | 6920 | 3071.5 | 9991.5
15:00 | 370 | 6898 | 3015 | 9913
15:30 | 366 | 6827.5 | 2983.5 | 9811
16:00 | 362 | 6757 | 2952 | 9709
16:30 | 395 | 6481 | 2895.5 | 9376.5
17:00 | 428 | 6205 | 2839 | 9044
17:30 | 410 | 6100 | 2840 | 8940
18:00 | 392 | 5995 | 2841 | 8836
18:30 | 251 | 6402 | 2901 | 9303
19:00 | 110 | 6809 | 2961 | 9770
19:30 | 36 | 7714 | 3582 | 11296
20:00 | 28 | 7776 | 3678 | 11454 |  |  |  | Executive Engineer
20:30 | 42 | 7783 | 3793 | 11576 |  |  |  | Network Operation Division
21:00 | 56 | 7790 | 3908 | 11698
21:30 | 61 | 7816.5 | 3903 | 11719.5
22:00 | 66 | 7843 | 3898 | 11741 |  |  |  |  | Page 6 of 7
22:30 | 38 | 7808 | 3823.5 | 11631.5
23:00 | 10 | 7773 | 3749 | 11522
23:30 | 8 | 7712.5 | 3668.5 | 11381
24:00 | 6 | 7652 | 3588 | 11240
11698 MW (21:00 )
10165 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-07 |  | Energy | 252627879
[11 empty] | 2021-07-07 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4503 | 800 | 1890 | 3029 | 600 | 54 | 455 | 0 | 114 | 0
0:30 | 4502.5 | 806.5 | 1941 | 2963.5 | 630 | 53.5 | 480 | 0 | 120 | 0 | Date: | 2021-07-07
1:00 | 4502 | 813 | 1992 | 2898 | 660 | 53 | 505 | 0 | 126 | 0
1:30 | 4505.5 | 813.5 | 1985.5 | 2671.5 | 645 | 53 | 476.5 | 0 | 125 | 0 | [7 empty] | Total Energy | 252.6279 | Total Energy Gen 252.628 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.628 MKWHr
2:00 | 4509 | 814 | 1979 | 2445 | 630 | 53 | 448 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4487.5 | 813.5 | 1981 | 2371 | 630 | 53.5 | 449 | 0 | 122 | 0 | [7 empty] | Energy Requirement | 252.6279
3:00 | 4466 | 813 | 1983 | 2297 | 630 | 54 | 450 | 0 | 120 | 0
3:30 | 4465.5 | 813 | 1971 | 2156.5 | 630 | 54 | 425 | 0 | 119 | 0 | [6 empty] | Shortage
4:00 | 4465 | 813 | 1959 | 2016 | 630 | 54 | 400 | 0 | 118 | 0
4:30 | 4452.5 | 813 | 1956 | 1895.5 | 630 | 54 | 400 | 0 | 116 | 0
5:00 | 4440 | 813 | 1953 | 1775 | 630 | 54 | 400 | 0 | 114 | 0
5:30 | 4438.5 | 813.5 | 1945 | 1548.5 | 605 | 54 | 279 | 0 | 111 | 0.5
6:00 | 4437 | 814 | 1937 | 1322 | 580 | 54 | 158 | 0 | 108 | 1
6:30 | 4490.5 | 814 | 1949.5 | 1234 | 565 | 54 | 113 | 0 | 106 | 3 |  |  |  |  | Coal
7:00 | 4544 | 814 | 1962 | 1146 | 550 | 54 | 68 | 0 | 104 | 5
7:30 | 4476 | 811 | 1893 | 1325 | 550 | 54 | 92 | 0 | 107 | 6.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4408 | 808 | 1824 | 1504 | 550 | 54 | 116 | 0 | 110 | 8
8:30 | 4371.5 | 808 | 1831.5 | 1841.5 | 550 | 54 | 115.5 | 0 | 105 | 9
9:00 | 4335 | 808 | 1839 | 2179 | 550 | 54 | 115 | 0 | 100 | 10
9:30 | 4325.5 | 808 | 1871.5 | 2210.5 | 540 | 54 | 120 | 0 | 97 | 12
10:00 | 4316 | 808 | 1904 | 2242 | 530 | 54 | 125 | 0 | 94 | 14
10:30 | 4281 | 803.5 | 1886.5 | 2244 | 530 | 54 | 125 | 0 | 96 | 18.5
11:00 | 4246 | 799 | 1869 | 2246 | 530 | 54 | 125 | 0 | 98 | 23
11:30 | 4307 | 799 | 1868.5 | 2249 | 525 | 54 | 155 | 0 | 100 | 20
12:00 | 4368 | 799 | 1868 | 2252 | 520 | 54 | 185 | 0 | 102 | 17
12:30 | 4400 | 799.5 | 1845.5 | 2243 | 515 | 53.5 | 208.5 | 0 | 102 | 27.5
13:00 | 4432 | 800 | 1823 | 2234 | 510 | 53 | 232 | 0 | 102 | 38
13:30 | 4432 | 800 | 1823 | 2234 | 510 | 53 | 232 | 0 | 102 | 38
14:00 | 4432 | 800 | 1823 | 2234 | 510 | 53 | 232 | 0 | 102 | 38
14:30 | 4365 | 800 | 1760 | 2193.5 | 500 | 52.5 | 258 | 0 | 105 | 34.5
15:00 | 4298 | 800 | 1697 | 2153 | 490 | 52 | 284 | 0 | 108 | 31
15:30 | 4316.5 | 800 | 1703.5 | 2018 | 490 | 52.5 | 292.5 | 0 | 109 | 29
16:00 | 4335 | 800 | 1710 | 1883 | 490 | 53 | 301 | 0 | 110 | 27
16:30 | 4289.5 | 800 | 1676 | 1647.5 | 490 | 53 | 294 | 0 | 107 | 19.5
17:00 | 4244 | 800 | 1642 | 1412 | 490 | 53 | 287 | 0 | 104 | 12
17:30 | 4211 | 800.5 | 1646 | 1320.5 | 490 | 53 | 307.5 | 0 | 102 | 9.5
18:00 | 4178 | 801 | 1650 | 1229 | 490 | 53 | 328 | 0 | 100 | 7
18:30 | 4254 | 800.5 | 1670 | 1523.5 | 495 | 53.5 | 392 | 0 | 111 | 3.5
19:00 | 4330 | 800 | 1690 | 1818 | 500 | 54 | 456 | 0 | 122 | 0
19:30 | 4521 | 800 | 1825 | 2876 | 590 | 54 | 502 | 0 | 128 | 0
20:00 | 4520 | 801 | 1825 | 3023 | 610 | 54 | 509 | 0 | 112 | 0
20:30 | 4549 | 800.5 | 1893.5 | 3034.5 | 625 | 54.5 | 506 | 0 | 113 | 0
21:00 | 4578 | 800 | 1962 | 3046 | 640 | 55 | 503 | 0 | 114 | 0
21:30 | 4593 | 800 | 1952.5 | 3061.5 | 640 | 55 | 502.5 | 0 | 115 | 0
22:00 | 4608 | 800 | 1943 | 3077 | 640 | 55 | 502 | 0 | 116 | 0
22:30 | 4560 | 800 | 1916 | 3053 | 640 | 55 | 490.5 | 0 | 117 | 0
23:00 | 4512 | 800 | 1889 | 3029 | 640 | 55 | 479 | 0 | 118 | 0
23:30 | 4507.5 | 800 | 1889.5 | 3029 | 620 | 54.5 | 467 | 0 | 116 | 0 | Max Temp. in Dhaka |  | 31.1° C
24:00 | 4503 | 800 | 1890 | 3029 | 600 | 54 | 455 | 0 | 114 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 252.628 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 252.628 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-07
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 29 | 28 | 28 | 27 | 28 | 28 | 28 |  | 29 | 29 | 29 | 30 | 30 | 30 | 29 | 623880
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 608000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 8 | 19 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600921
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 1 |  | 1 | 3 | 2 | 5 | 4 | 4 | 0 | 1 | 0 | [8 empty] | 22815
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 206 | 203 | 203 | 203 | 215 | 203 | 207 | 228 | 204 | 204 | 203 | 203 | 203 | 203 | 203 | 203 |  | 213 | 202 | 203 | 210 | 203 | 203 | 203 | 4862719
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 100 | 100 | 50 | 50 | 50 | 60 | 60 | 60 | 60 | 20 | 20 | 100 | 100 | 100 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2171379
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 51 | 51 | 51 | [10 empty] | 17 | 17 | 17 |  | 40 | 51 | 51 | 51 | 51 | 34 | 17 | 560621
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 85 | 93 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 51 | 34 |  | 60 | 105 | 105 | 105 | 105 | 105 | 105 | 2374436
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | 50 | 50 | 50 | [8 empty] | 50 | 49 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 774728
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 333 | 331 | 330 | 330 | 330 | 330 | 326 | 300 | 300 | 301 | 300 | 331 | 335 | 331 | 328 | 332 | 300 | 300 |  | 300 | 335 | 334 | 332 | 334 | 334 | 334 | 7823767
18 | Kodda 300 MW PP Unit-2 (Summit) | 110 | [6 empty] | 2 | 85 | 95 | 95 | 95 | 95 | 95 | 45 | 45 | 80 | 95 |  | 100 | 150 | 190 | 195 | 195 | 195 | 95 | 2072508
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7255936
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 110 | 110 | 110 | 110 | 110 | 110 | 2155148
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 580896
33 | Ashuganj 225 MW CCPP | 182 | 186 | 187 | 185 | 183 | 192 | 204 | 183 | 191 | 187 | 183 | 186 | 184 | 183 | 187 | 184 | 184 | 184 |  | 200 | 184 | 184 | 196 | 218 | 217 | 217 | 4649000
34 | Ashuganj 450 MW CCPP(South) | 270 | 280 | 280 | 275 | 270 | 280 | 305 | 270 | 275 | 275 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 265 |  | 295 | 270 | 270 | 290 | 270 | 270 | 270 | 6724000
| Ashuganj 450 MW CCPP(North) | 260 | 270 | 265 | 265 | 260 | 270 | 295 | 260 | 265 | 265 | 260 | 260 | 310 | 310 | 310 | 310 | 310 | 310 |  | 340 | 310 | 310 | 325 | 310 | 260 | 260 | 7241000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 57 | 56 | 53 | 53 | 53 | 52 | 52 | 51 | 50 | 52 |  | 51 | 52 | 52 | 49 | 49 | 50 | 48 | 1272960
36 | Chandpur 150 MW CCPP
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 319 | 317 | 322 | 322 | 321 | 318 | 341 | 349 | 320 | 326 | 317 | 322 | 319 | 316 | 317 | 318 | 317 | 324 |  | 322 | 313 | 323 | 324 | 319 | 319 | 318 | 7829500
40 | Meghnaghat 450 MW CCPP(MPL) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 6128500
41 | Haripur 360MW CCPP(HPL) | 352 | 348 | 350 | 349 | 350 | 349 | 350 | 310 | 305 | 330 | 351 | 316 | 286 | 286 | 291 | 317 | 345 | 350 |  | 351 | 352 | 352 | 351 | 354 | 353 | 353 | 8038000
42 | RPCL 210MW CCPP | 173 | 174 | 176 | 183 | 186 | 186 | 187 | 191 | 185 | 165 | 161 | 161 | 138 | 135 | 141 | 154 | 158 | 162 |  | 163 | 164 | 157 | 157 | 159 | 159 | 174 | 3899760
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 0 | 1 | 0 | 1 | 7 | 1 | 8 | 16 | 13 | 17 | 7 | 3 | [8 empty] | 83470
44 | Fenchugonj CCPP Phase-1 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1029000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 706920
46 | Shajibazar 330 MW CCPP | 162 | 163 | 163 | 163 | 163 | 162 | 162 | 161 | 161 | 160 | 161 | 163 | 162 | 162 | 161 | 163 | 161 | 162 |  | 161 | 163 | 162 | 162 | 163 | 161 | 162 | 3650000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 61 | 61 | 61 | 61 | 61 | 62 | 61 | 61 | 61 | 61 | 62 | 61 | 60 | 61 | 56 | 45 |  | 45 | 57 | 56 | 56 | 62 | 62 | 62 | 1429632
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 78 | 84 | 81 | 84 | 84 | 84 | 84 | 84 | 50 |  | 50 | 84 | 84 | 81 | 84 | 84 | 84 | 1947840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 225 | 225 | 225 | 225 | 225 | 178 | 205 | 218 | 218 | 218 | 218 | 218 | 218 | 177 | 177 | 177 | 177 | 177 |  | 190 | 225 | 225 | 225 | 225 | 225 | 225 | 5090060
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | [15 empty] | 190000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 232380
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 192384
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 47 | 47 | 47 | 50 | 53 | 53 | 53 | 19 | 19 |  | 19 | 53 | 53 | 53 | 53 | 53 | 53 | 1173000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 382248
57 | Bibiana-II 341 MW CCPP (Summit) | 300 | 295 | 300 | 300 | 300 | 290 | 310 | 290 | 290 | 305 | 285 | 295 | 300 | 265 | 285 | 285 | 290 | 290 |  | 295 | 275 | 280 | 290 | 285 | 290 | 300 | 7227500
| Bibiyana South 400 MW | 401 | 400 | 400 | 400 | 400 | 401 | 398 | 400 | 398 | 399 | 401 | 400 | 400 | 360 | 350 | 350 | 335 | 320 |  | 350 | 380 | 400 | 400 | 400 | 400 | 401 | 9158900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 40 | 53 | 53 | 53 | 53 | 53 | 53 | 55 | 35 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1213076
59 | Tangail Palli Power Gen 22 MW | 18 | 21 | 24 |  |  |  |  | 3 | 24 | 24 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 10 |  | 16 | 24 | 24 | 24 | 24 | 24 | 24 | 442320
60 | Barabkunda 22 MW PP (Regent) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 14 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 380544
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 16 | 16 | 16 | 16 |  |  |  | 16 | 16 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 356652
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 457956
63 | Impoprt (Tripura) | 126 | 124 | 120 | 118 | 114 | 108 | 104 | 110 | 100 | 94 | 98 | 102 | 102 | 110 | 108 | 110 | 104 | 100 |  | 122 | 128 | 112 | 114 | 116 | 118 | 114 | 2681280
64 | Malancha, Ctg. EPZ (United) | 30 | 30 | 30 | 5 | 0 | 0 | 0 | 6 | 3 | 3 | 4 | 7 | 7 | 8 | 5 | 3 | 8 | 5 |  | 6 | 6 | 12 | 20 | 28 | 29 | 37 | 304800
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 486144
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 234540
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 |  | 25 | 25 | 30 | 33 | 33 | 33 | 33 | 682500
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 14 | 14 | 12 | 15 | 15 | 15 | 15 | 14 |  | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 434020
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 28 | 28 | 9 |  | 20 | 8 | 8 | 21 | 30 | 30 | 30 | 606600
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 812200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 |  | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 747500
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 99 | 92 | 95 | 96 | 96 | 96 | 52 | 52 |  | 70 | 80 | 95 | 96 | 96 | 96 | 93 | 2169319
| Feni Lanka Power | 114 | 114 | 114 | 110 | 110 | 110 | 54 | 0 | 8 | 46 | 34 | 34 | 17 | 17 | 17 | 34 | 34 | 34 |  | 114 | 114 | 100 | 114 | 114 | 114 | 114 | 1678080
| Chowmuhani 113 MW | 109 | 109 | 109 | 107 | 108 | 94 | 99 | 110 | 115 | 117 | 117 | 118 | 110 | 111 | 114 | 110 | 25 | 25 |  | 70 | 118 | 117 | 118 | 120 | 117 | 118 | 2558640
| Manikgonj 162MW PP(MPGL) | 126 | 126 | 126 | 72 | 72 |  |  | 52 | 126 | 126 | 126 | 126 | 126 | 126 | 126 | 72 | 35 | 35 |  | 49 | 126 | 124 | 126 | 126 | 126 | 126 | 2417760
77 | Siddhirganj 100 PP(Dutch Bangla) | 100 | 100 | 100 | 100 | 100 | 80 | 16 | 40 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 32 |  | 55 | 90 | 100 | 100 | 100 | 100 | 100 | 2118720
78 | Gazipur 52 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 588480
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 32 | 16 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 48 | 48 |  | 125 | 150 | 150 | 150 | 150 | 150 | 150 | 2304480
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 190080
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 |  |  | 4 | 39 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 8 | 8 |  | 16 | 35 | 37 | 43 | 43 | 43 | 43 | 838190
| Gazipur 100 MW PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |  | 84 | 105 | 105 | 105 | 105 | 53 | 53 | 1461600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 1 | 3 | 5 | 4 | 4 | 2 | 1 | 0 | 1 | 0 | [9 empty] | 22201
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 68 | 68 | 68 | 51 | 17 | 17 | 17 | 33 | 51 | 53 | 82 | 82 | 85 | 85 | 85 | 51 | 51 | 34 |  | 47 | 110 | 110 | 110 | 110 | 110 | 110 | 1759701
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [20 empty] | 20 | 14 |  |  |  | 0 | 18236
86 | Meghnaghat CCPP ( Summit) | 275 | 280 | 265 | 275 | 275 | 285 | 300 | 260 | 280 | 275 | 260 | 260 | 240 | 260 | 270 | 260 | 260 | 270 |  | 270 | 250 | 255 | 280 | 250 | 270 | 260 | 6523636
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [17 empty] | 2 |  | 17 | 25 | 30 |  |  |  | 0 | 56640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 100 | 100 | 100 | 100 | 90 | 90 | 90 | 88 | 88 | 50 | 30 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2090040
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 969549
94 | Gagnagar 102 MW PP (Digital Power) | [9 empty] | 16 | 16 | 16 | 48 | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 24 | 24 | 24 | 7 | 531504
95 | Patenga 50MW PP (Baraka) | [19 empty] | 12 | 18 | 18 |  |  |  | 0 | 35520
96 | Chattogram 108 MW PP (ECPV) | 6 | 12 | 12 | 12 | 12 | 11 | 12 | 12 | 12 | [14 empty] | 6 | 6 | 6 | 136320
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 14 | 30 | 30 |  |  |  | 0 | 67103
100 | Manikganj 55 MW PP (Northern) | [8 empty] | 17 | 17 | 17 | 30 | 35 | 55 | 55 | 55 | 55 | 55 |  | 55 | 35 | 35 |  |  |  | 0 | 506379
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [8 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 3500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1135800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 180 | 130 | 100 | 60 | 8 | [12 empty] | 3 |  | 26 | 80 | 108 | 120 | 151 | 170 | 140 | 1363200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 64 | 69 | 65 | 65 | 65 | 50 | 50 | 78 | 149 | 145 | 149 | 149 | 149 | 149 | 149 | 140 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 120 | 149 | 2608850
115 | Juldah 100 MW PP Unit-3 (Acorn) | 60 | 20 | [5 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 20 | 10 | 10 |  | 30 | 70 | 70 | 70 | 70 | 70 | 70 | 934080
116 | Chandpur 200MW (Desh energy) | 100 | 68 | 68 | 68 | 34 | 17 | 17 | 30 | 100 | 100 | 100 | 100 | 68 | 68 | 68 | 51 | 51 | 34 |  | 39 | 100 | 80 | 100 | 100 | 100 | 100 | 1777440
117 | Ashuganj 150MW PP (Midland) | 137 | 140 | 142 | 142 | 142 | 50 | 20 | 55 | 135 | 142 | 142 | 142 | 142 | 142 | 140 | 80 | 40 | 40 |  | 65 | 140 | 135 | 135 | 142 | 140 | 148 | 2900509
118 | Bibiyana-III 400 MW CCPP
| Jamalpur 115 MW PP (United) | 106 | 106 | 115 | 115 | 115 | 55 | 35 | 48 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 55 | 35 |  | 56 | 115 | 115 | 115 | 115 | 115 | 107 | 2064000
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 40 | 10 | 10 | 10 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 20 | 10 |  | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 1433280
| Anlima Energy Ltd. | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 99 | 94 | 94 | 94 | 94 | 105 | 114 | 114 | 72 | 53 |  | 72 | 94 | 95 | 91 | 94 | 94 | 94 | 2409982
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 29 | 36 | 36 | 711000
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 2 | 4 | 6 | 5 | 8 | 7 | 19 | 16 | 8 | 2 | 2 | 3 | [8 empty] | 84432
120 | Eastern Zone Total | 7590 | 7371 | 7269 | 6994 | 6819 | 6230 | 6141 | 6336 | 6885 | 6955 | 6903 | 7013 | 6997 | 6942 | 6898 | 6757 | 6205 | 5995 |  | 6809 | 7714 | 7776 | 7790 | 7843 | 7773 | 7652 | 170289645
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | [9 empty] | 83050
Khulna 225 MW CCPP
129 | Rupsha 105 MW PP (Orion rupsha) | 90 | 70 | 53 | 53 | 53 |  |  | 35 | 53 | 53 | 53 | 53 | 55 | 53 | [6 empty] | 35 | 70 | 90 | 90 | 90 | 90 | 1214880
130
131
132 | United Payra Power Ltd. | [25 empty] | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 221 | 220 | 220 | 220 | 220 | 160 | 122 | 122 | 122 | 122 |  | 120 | 170 | 172 | 221 | 222 | 222 | 222 | 4731518
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 12 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 285108
| Bhola 225 MW CCPP | 86 | 86 | 86 | 86 | 84 | 84 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 |  | 86 | 86 | 86 | 86 | 84 | 84 | 86 | 2077363
140 | Bhola 33 MW PP (Venture) | 31 | 29 | 29 | 29 | 26 | 23 | 21 | 20 | 20 | 20 | 20 | 20 | 19 | 16 | 16 | 16 | 16 | 17 |  | 26 | 29 | 29 | 29 | 30 | 30 | 30 | 567528
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 70 | 30 | [16 empty] | 40 | 30 | 40 | 40 |  | 0 | 507840
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 813 | 814 | 813 | 813 | 813 | 814 | 814 | 808 | 808 | 808 | 799 | 799 | 800 | 801 | 800 | 800 | 800 | 801 |  | 800 | 800 | 801 | 800 | 800 | 800 | 800 | 19459636
147 | Bheramara 410 MW CCPP | 400 | 400 | 400 | 400 | 400 | 405 | 400 | 350 | 350 | 350 | 350 | 350 | 400 | 400 | 350 | 350 | 320 | 320 |  | 320 | 410 | 410 | 410 | 410 | 410 | 410 | 9397440
148 | Payra 1320 MW | 510 | 480 | 480 | 480 | 480 | 430 | 400 | 400 | 400 | 380 | 380 | 370 | 360 | 340 | 340 | 340 | 340 | 340 |  | 350 | 440 | 460 | 490 | 490 | 490 | 450 | 10984100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3680500
153 | Baghabari 71 MW GTPP | 60 | 50 | 50 | 50 | 50 | 60 | 60 | 55 | 55 | 55 | 60 | 60 | 50 | 50 | 50 | 50 | 50 | 60 |  | 60 | 60 | 60 | 60 | 50 | 50 | 50 | 1290000
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | [7 empty] | 17 | 34 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 817856
| Sirajgonj 6.55 MW Solar | [7 empty] | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 2 | 2 | 0 | 0 | [8 empty] | 34800
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 180 | 178 | 183 | 187 | 182 | 179 | 192 | 205 | 175 | 175 | 166 | 171 | 169 | 165 | 166 | 168 | 166 | 145 |  | 143 | 177 | 176 | 182 | 187 | 171 | 166 | 4405309
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 189 | 187 | 190 | 191 | 191 | 188 | 201 | 197 | 172 | 173 | 173 | 183 | 190 | 200 | 188 | 190 | 185 | 170 |  | 172 | 194 | 185 | 168 | 193 | 166 | 145 | 4658982
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 413 | 410 | 412 | 412 | 409 | 416 | 333 | 358 | 394 | 366 | 394 | 365 | 309 | 353 | 340 | 334 | 350 |  | 350 | 370 | 342 | 418 | 388 | 328 | 316 | 9112600
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 41 | [8 empty] | 10 | 10 | 20 | 47 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 40 | 40 | 40 | 42 | 35 | 584443
162 | Bogra 22 MW PP (GBB) | 19 | 19 | 19 | 19 | 20 | 21 | 21 | 21 | 21 | 21 | 18 | 20 | 21 | 21 | 18 | 21 |  | 21 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 448320
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 8 | 0 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 198144
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | [8 empty] | 18 | 35 | 35 | 35 | 18 | 18 | 18 |  | 18 | 35 | 35 | 35 | 35 | 35 | 35 | 480920
166 | Katakhali 50 MW PP (Northern) | 43 | [6 empty] | 16 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 16 | 16 | 8 |  | 8 | 43 | 43 | 43 | 43 | 43 | 43 | 590880
167 | Katakhali 50 MW Peaking PP | 23 | 23 | 23 | 23 | 23 | [7 empty] | 4 | 29 | 29 | 29 | 31 | 31 |  | 31 | 31 | 38 | 31 | 31 | 31 | 31 | 400954
168 | Santahar 50 MW Peaking PP | 28 | 28 | 28 | 28 | 28 | 28 | [11 empty] | 44 |  | 44 | 44 | 44 | 44 | 35 | 35 | 35 | 421230
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 |  | 8 | 16 | 35 | 52 | 52 | 52 | 52 | 1129920
170 | Chapainawabganj 100 MW Peaking PP | 92 | 92 | 94 | 94 | 94 | 94 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 47 | 47 | 47 | 47 |  | 75 | 85 | 86 | 87 | 95 | 87 | 87 | 1623376
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | [6 empty] | 10 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  |  |  | 6 | 55 | 85 | 112 | 113 | 113 | 35 | 956160
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 70 | 35 | 35 |  |  |  | 15 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 20 | 70 | 100 | 113 | 113 | 113 | 113 | 1283904
173 | Rangpur 20 MW GTPP | 0 | 0 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 75 | 70 | 50 | 35 | 8 | [14 empty] | 40 | 107 | 107 | 113 | 113 | 113 | 113 | 884764
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 3 | 4 | 2 | 1 | [8 empty] | 26709
178
178