## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-13 | Tuesday
|  |  | Date (day): | 2021-07-13 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14244.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15331 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-12 | 2021-07-13 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 170 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 100 | 160 | 0 | 100 |  | 190 | Machine problem
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 96 | 105 | 100 | 100
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 327 | 326 | 325 | 325 | 87 |  | Gas shortage
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 232 | 225 | 300 | 300 | 60 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 285 | 275 | 300 | 300 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 84 | 84 | 85 |  | 15 | Engine problem
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 16 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 95 | 100 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 320 | 326 | 330 | 330
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 85 | 94 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 50 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 43 | 52 | 52
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 20 | 288 | 250 | 300
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 26 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 105 | 149 | 130 | 132 |  | 17 | Engine problem
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 100 | 100
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 11 | 104 | 90 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 126 | 126 | 126 | 126 |  | 36 | Engine problem
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 27 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5819 | 2846 | 3577 | 3767 | 4106 | 726 | 938
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 46 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 54 | 77 | 77 | 77 | 153 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 214 | 203 | 225 | 225
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 110 | 110 | 110 |  | 40 | Machine problem
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 89 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 83 | 85 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 30 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 19 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 26 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 95 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 92 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1011 | 1233 | 1580 | 1670 | 521 | 189
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 100
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 213 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 315 | 285 | 350 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 310 | 280 | 330 | 350 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 54 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 34 | 34 | 34 | 34 |  | 17 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 140 | 145 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 41 | 49 | 42 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 90 | 90 | 90 | 90 |  | 73 | ST under maint
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 51 | 160 | 170 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 138 | 148 | 172
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 90 | 52 | 100 | 100 |  | 14 | Engine problem
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 113 | 115 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1865 | 1894 | 2192 | 2384 | 316 | 284
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 144 | 144 | 160 | 160 | 42 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 60 | 192 | 175 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 95 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 56 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 417 | 482 | 552.6 | 526 | 42 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 161 | 160 | 160 |  | 170 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 62 | 63
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 82 | 83 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 225 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 405 | 404 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 390 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1794 | 1777 | 1810 | 1811 | 0 | 529
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 798 | 798 | 821 | 821
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 15 | 0 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 100 | 0 | 160 |  | 70 | ST not available
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 405 | 400 | 400
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 21 | 105 | 90 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2129 | 1214 | 1523 | 1461 | 1766 | 0 | 153
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 33 | 25 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 88 | 85 | 86 |  | 108 | GT-2 under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 11 | 11 | 84 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 520 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 220 | 221 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 0 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 688 | 943 | 1073 | 1192 | 84 | 108
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 50 | 43 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 21 | 48 | 30 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 |  | 50 | Fuel shortage
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 34 | 43 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 24 | 32 | 30 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 175 | 210 | 210 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 197 | 191 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 408 | 409 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 0 | 41 |  | 9 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 46 | 52 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 92 | 91 | 95 | 95
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 94 | 94 | 94 |  | 19 | Engine problem
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 55 | 95 | 95 | 95 |  | 18 | Engine problem
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1139 | 1330 | 1538 | 1593 | 380 | 144
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 45 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 202 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22023 | 21060 | 11176 | 13022 | 14244.6 | 15331 | 2193 | 2622
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10646.466 | 12405 | 13569.6716 | 14604.5965
| A. |  | 2021-07-12 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13022 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10089 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13022 | MW
| 3 | Day peak Generation : |  |  | 11176 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12405 | MW
| 4 | Evening peak Generation : |  |  | 13022 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 279.6463 | MKWHr | By Solar | 0.87688 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 164.3065 | MKWHr |  | By Oil: | 75.4993 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.9183 | MKWHr |  | By Hydro: | 1.5922 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2193 | MW | Dhaka | 4330 | 4330 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2622 | MW | Chittagong | 1212 | 1212 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4815 | MW | Khulna | 1545 | 1545 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1240.9 | MMCFD |  |  | Rajshahi | 1378 | 1378 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 168966750.452 | ii) Oil : | Taka | 549442351.26 | Comilla | 1212 | 1212 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69263300 | Total | Taka | 787672401.712 | Mymensingh | 1046 | 1046 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.836 | MKWHr. | Sylhet | 520 | 520 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -280 | MW (E to W) at | 21:00 | hrs | Barisal | 376 | 376 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -310 | MW at | 22:00 | hrs | Rangpur | 786 | 786 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.8° C |  |  | Total | 12405 | 12405 |  | 0
| B. |  | 2021-07-13 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.9° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13400 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15331 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
| 4 | Reserve(Generation end) |  |  |  | 1931 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 287.7638 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9837 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.264 | MKWHr. | ii) HVDC Flow at Peak Time |  | 798 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.1891 | MKWHr. | iii) Maximum HVDC Flow : |  | 798 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 80.46 |  | (b) Today: | 80.97 |  | (c) Rule Curve: |  | 85.92
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-12
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 80 | 300 | 102 | 0 | 326 | 343 |  | 0 | 240 | 280 | 0 | 0 | 55 | 328 | 0 | 0 | 99 | 16 | 150 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 33 | 51 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 21 | 39 | 80 | 0 | 0 | 270 | 280 | 212 | 8 | 90 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 0 | 5 | 33 | 20 | 160 | 169 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 56 | 81 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 282 | 0 | 0 | 194 | 0 | 115 | 0 | 0 | 22 | 148 | 404 | 106 | 105 | 89 | 0 | 0 | 0 | 110 | 100 | 117 | 100 | 390 | 100 | 0 | 126 | 96 | 0 | 36 | 0 |  | 796 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 85 | 32 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 43 | 32 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 177 | 0 | 11 | 100 | 187 | 0 | 407 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 220 | 0 | 35 | 0 |  | 8602 | 3885 | 12487 | 4999 | 796 | 1948 | 3406 | 679 | 54 | 445 | 160 | 0 | 0 | 80.44
2:00 | 0 | 0 | 0 | 90 | 300 | 99 | 0 | 326 | 346 |  | 0 | 240 | 280 | 0 | 0 | 15 | 328 | 0 | 0 | 99 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 25 | 33 | 33 | 51 | 0 | 29 | 25 | 100 | 0 | 25 | 214 | 0 | 110 | 0 |  | 24 | 0 | 38 | 88 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 285 | 290 | 212 | 8 | 90 | 26 | 56 | 0 | 34 | 0 | 41 | 40 | 22 | 11 | 33 | 20 | 136 | 169 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 81 | 0 | 218 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 145 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 93 | 147 | 404 | 106 | 105 | 89 | 0 | 0 | 0 | 110 | 80 | 117 | 100 | 394 | 0 | 0 | 126 | 96 | 0 | 36 | 0 |  | 798 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 32 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 43 | 31 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 11 | 100 | 190 | 0 | 415 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 490 | 222 | 0 | 35 | 0 |  | 8201 | 3856 | 12057 | 5083 | 798 | 1969 | 2954 | 639 | 54 | 424 | 136 | 0 | 0 | 80.44
3:00 | 0 | 0 | 0 | 90 | 300 | 99 | 0 | 326 | 345 |  | 0 | 240 | 265 | 0 | 0 | 15 | 328 | 0 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 29 | 25 | 100 | 0 | 25 | 205 | 0 | 110 | 0 |  | 24 | 0 | 0 | 88 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 270 | 280 | 213 | 8 | 90 | 26 | 55 | 0 | 34 | 0 | 41 | 34 | 22 | 11 | 33 | 20 | 138 | 173 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 81 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 45 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 100 | 147 | 404 | 106 | 105 | 89 | 0 | 0 | 0 | 110 | 80 | 118 | 100 | 394 | 0 | 0 | 126 | 95 | 0 | 36 | 0 |  | 797 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 31 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 43 | 31 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 50 | 194 | 0 | 412 | 53 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 470 | 223 | 0 | 35 | 0 |  | 8021 | 3740 | 11761 | 5081 | 797 | 1964 | 2722 | 619 | 54 | 386 | 138 | 0 | 0 | 80.45
4:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 326 | 347 |  | 0 | 240 | 280 | 0 | 0 | 0 | 328 | 0 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 27 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 72 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 265 | 275 | 214 | 8 | 91 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 138 | 187 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 161 | 56 | 81 | 0 | 219 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 70 | 148 | 403 | 106 | 105 | 89 | 0 | 0 | 0 | 110 | 90 | 117 | 100 | 396 | 0 | 0 | 126 | 96 | 0 | 36 | 0 |  | 797 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 31 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 0 | 31 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 50 | 194 | 0 | 416 | 53 | 0 | 35 | 0 | 70 | 0 | 0 | 113 | 470 | 223 | 0 | 35 | 0 |  | 7973 | 3599 | 11572 | 5095 | 797 | 1979 | 2506 | 619 | 52 | 386 | 138 | 0 | 0 | 0
5:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 327 | 348 |  | 0 | 240 | 280 | 0 | 0 | 0 | 333 | 0 | 0 | 99 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 27 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 72 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 260 | 270 | 216 | 8 | 90 | 26 | 55 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 134 | 185 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 70 | 148 | 402 | 106 | 105 | 89 | 0 | 0 | 0 | 110 | 90 | 115 | 100 | 401 | 0 | 0 | 90 | 94 | 0 | 36 | 0 |  | 797 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 28 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 190 | 0 | 404 | 53 | 0 | 35 | 0 | 60 | 0 | 0 | 35 | 450 | 223 | 0 | 35 | 0 |  | 7890 | 3416 | 11306 | 5086 | 797 | 1949 | 2304 | 599 | 52 | 385 | 134 | 0 | 0 | 80.46
6:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 326 | 350 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 0 | 90 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 27 | 25 | 100 | 0 | 25 | 208 | 0 | 110 | 0 |  | 24 | 0 | 0 | 72 | 0 | 0 | 21 | 40 | 80 | 0 | 0 | 265 | 270 | 216 | 8 | 90 | 26 | 56 | 0 | 34 | 0 | 41 | 8 | 22 | 0 | 33 | 20 | 118 | 184 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 62 | 81 | 0 | 218 | 18 | 0 | 10 | 270 | 16 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 2 | 0 | 84 | 147 | 402 | 115 | 105 | 89 | 0 | 0 | 0 | 51 | 68 | 114 | 10 | 400 | 0 | 2 | 17 | 95 | 0 | 36 | 2 |  | 797 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 26 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 0 | 30 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 157 | 0 | 366 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 370 | 223 | 0 | 0 | 0 |  | 7415 | 2897 | 10312 | 4859 | 797 | 1892 | 1683 | 520 | 52 | 385 | 118 | 6 | 0 | 80.46
7:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 327 | 349 |  | 0 | 240 | 275 | 0 | 0 | 0 | 270 | 0 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 28 | 25 | 100 | 0 | 25 | 206 | 0 | 110 | 0 |  | 20 | 0 | 0 | 70 | 0 | 0 | 21 | 35 | 80 | 0 | 0 | 265 | 270 | 216 | 8 | 90 | 26 | 57 | 0 | 34 | 0 | 41 | 8 | 22 | 8 | 33 | 20 | 112 | 181 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 40 | 20 | 0 | 218 | 18 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 5 | 0 | 51 | 143 | 402 | 115 | 105 | 89 | 0 | 0 | 0 | 51 | 72 | 85 | 10 | 400 | 0 | 10 | 17 | 95 | 0 | 36 | 5 |  | 797 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 25 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 0 | 30 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 170 | 0 | 358 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 350 | 222 | 0 | 0 | 0 |  | 7201 | 2888 | 10089 | 4861 | 797 | 1846 | 1550 | 500 | 53 | 350 | 112 | 20 | 0 | 80.37
8:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 327 | 348 |  | 0 | 240 | 295 | 0 | 0 | 0 | 270 | 0 | 0 | 50 | 0 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 25 | 33 | 33 | 51 | 0 | 28 | 25 | 100 | 0 | 25 | 216 | 0 | 110 | 0 |  | 18 | 0 | 0 | 70 | 0 | 0 | 21 | 4 | 80 | 0 | 0 | 280 | 290 | 214 | 8 | 91 | 23 | 56 | 0 | 34 | 0 | 41 | 8 | 19 | 8 | 33 | 20 | 122 | 170 | 8 | 17 | 1 | 43 | 30 | 17 | 0 | 0 | 162 | 40 | 20 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 9 | 0 | 51 | 140 | 404 | 115 | 105 | 89 | 0 | 0 | 0 | 51 | 72 | 85 | 10 | 397 | 0 | 25 | 17 | 96 | 0 | 36 | 18 |  | 797 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 0 | 30 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 182 | 0 | 356 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 222 | 0 | 0 | 2 |  | 7224 | 2872 | 10096 | 4893 | 797 | 1780 | 1566 | 480 | 53 | 350 | 122 | 55 | 0 | 80.37
9:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 327 | 312 |  | 0 | 240 | 280 | 0 | 0 | 0 | 332 | 0 | 0 | 60 | 16 | 115 | 11 | 0 | 0 | 0 | 54 | 0 | 40 | 16 | 25 | 25 | 33 | 33 | 42 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 18 | 0 | 0 | 70 | 0 | 0 | 21 | 2 | 80 | 0 | 0 | 290 | 285 | 213 | 8 | 91 | 23 | 56 | 0 | 34 | 0 | 41 | 10 | 19 | 8 | 33 | 20 | 130 | 159 | 8 | 19 | 2 | 44 | 30 | 47 | 0 | 0 | 163 | 61 | 78 | 0 | 219 | 18 | 0 | 9 | 310 | 16 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 17 | 10 | 51 | 142 | 403 | 115 | 105 | 89 | 2 | 0 | 0 | 65 | 54 | 102 | 10 | 396 | 0 | 42 | 63 | 96 | 0 | 36 | 8 |  | 797 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 8 | 26 | 16 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 199 | 0 | 404 | 17 | 0 | 0 | 0 | 12 | 0 | 3 | 20 | 330 | 221 | 0 | 0 | 3 |  | 7456 | 3034 | 10490 | 5025 | 797 | 1876 | 1705 | 480 | 54 | 346 | 130 | 77 | 0 | 80.38
10:00 | 0 | 0 | 0 | 100 | 300 | 102 | 0 | 327 | 282 |  | 0 | 240 | 265 | 0 | 0 | 0 | 329 | 0 | 0 | 80 | 50 | 133 | 50 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 25 | 33 | 33 | 42 | 0 | 29 | 25 | 100 | 0 | 25 | 202 | 0 | 110 | 0 |  | 18 | 0 | 0 | 70 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 310 | 295 | 214 | 8 | 90 | 23 | 56 | 0 | 34 | 0 | 41 | 28 | 19 | 8 | 33 | 20 | 130 | 156 | 0 | 19 | 2 | 44 | 30 | 47 | 0 | 0 | 161 | 60 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 16 | 0 | 0 | 15 | 0 | 0 | 60 | 0 | 0 | 18 | 10 | 51 | 142 | 404 | 115 | 105 | 89 | 3 | 0 | 0 | 92 | 72 | 114 | 10 | 398 | 0 | 53 | 86 | 96 | 0 | 36 | 30 |  | 797 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 8 | 24 | 48 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 198 | 0 | 379 | 17 | 0 | 0 | 0 | 35 | 0 | 5 | 35 | 340 | 220 | 0 | 0 | 3 |  | 7684 | 3155 | 10839 | 5117 | 797 | 1802 | 1973 | 490 | 54 | 362 | 130 | 114 | 0 | 80.38
11:00 | 0 | 0 | 0 | 100 | 300 | 100 | 0 | 327 | 251 |  | 0 | 240 | 260 | 0 | 0 | 0 | 327 | 0 | 0 | 90 | 60 | 133 | 50 | 0 | 0 | 0 | 54 | 0 | 35 | 18 | 25 | 25 | 33 | 33 | 42 | 0 | 29 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 19 | 0 | 0 | 83 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 310 | 295 | 213 | 8 | 84 | 26 | 54 | 0 | 34 | 0 | 41 | 43 | 19 | 8 | 33 | 20 | 132 | 150 | 0 | 19 | 3 | 44 | 30 | 50 | 0 | 0 | 161 | 61 | 81 | 0 | 219 | 18 | 0 | 9 | 290 | 16 | 8 | 0 | 15 | 0 | 0 | 60 | 0 | 43 | 19 | 10 | 51 | 140 | 403 | 106 | 0 | 85 | 6 | 0 | 0 | 95 | 100 | 115 | 27 | 392 | 0 | 54 | 126 | 96 | 0 | 36 | 14 |  | 797 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 20 | 0 | 0 | 0 | 0 | 50 | 21 | 93 | 0 | 8 | 24 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 0 | 200 | 0 | 362 | 17 | 0 | 0 | 0 | 10 | 0 | 7 | 35 | 350 | 220 | 0 | 0 | 5 |  | 7673 | 3136 | 10809 | 5116 | 797 | 1752 | 1988 | 500 | 54 | 362 | 132 | 108 | 0 | 80.39
12:00 | 0 | 0 | 0 | 100 | 300 | 96 | 0 | 327 | 232 |  | 0 | 240 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 95 | 85 | 150 | 50 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 9 | 33 | 33 | 33 | 0 | 29 | 25 | 100 | 0 | 0 | 214 | 0 | 110 | 0 |  | 24 | 0 | 0 | 83 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 315 | 310 | 210 | 16 | 90 | 26 | 50 | 0 | 34 | 0 | 41 | 43 | 19 | 8 | 33 | 20 | 140 | 144 | 8 | 19 | 0 | 44 | 30 | 50 | 0 | 0 | 160 | 60 | 82 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 20 | 0 | 0 | 60 | 0 | 105 | 20 | 30 | 51 | 140 | 405 | 106 | 0 | 89 | 5 | 0 | 0 | 95 | 90 | 113 | 90 | 390 | 11 | 56 | 126 | 96 | 0 | 36 | 27 |  | 798 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 50 | 21 | 92 | 0 | 34 | 24 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 197 | 0 | 408 | 21 | 0 | 0 | 0 | 45 | 0 | 7 | 55 | 350 | 220 | 0 | 0 | 5 |  | 7933 | 3243 | 11176 | 5097 | 798 | 1792 | 2297 | 500 | 54 | 378 | 140 | 120 | 0 | 80.39
13:00 | 0 | 0 | 0 | 100 | 300 | 96 | 0 | 327 | 232 |  | 0 | 240 | 280 | 0 | 0 | 11 | 322 | 0 | 0 | 100 | 85 | 147 | 50 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 24 | 33 | 33 | 33 | 0 | 59 | 25 | 100 | 0 | 0 | 205 | 0 | 110 | 0 |  | 24 | 0 | 0 | 78 | 0 | 0 | 22 | 5 | 80 | 0 | 0 | 310 | 295 | 210 | 16 | 89 | 26 | 50 | 0 | 34 | 0 | 49 | 43 | 22 | 8 | 33 | 20 | 144 | 143 | 8 | 17 | 1 | 44 | 30 | 50 | 0 | 0 | 161 | 60 | 82 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 104 | 0 | 0 | 60 | 0 | 100 | 17 | 100 | 51 | 138 | 411 | 95 | 0 | 89 | 5 | 0 | 0 | 89 | 90 | 107 | 90 | 390 | 21 | 55 | 126 | 96 | 0 | 36 | 21 |  | 797 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 92 | 0 | 43 | 24 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 0 | 196 | 0 | 407 | 70 | 0 | 67 | 0 | 70 | 0 | 7 | 70 | 380 | 220 | 0 | 0 | 5 |  | 8081 | 3411 | 11492 | 5076 | 797 | 1793 | 2602 | 530 | 84 | 355 | 144 | 111 | 0 | 80.4
14:00 | 0 | 0 | 0 | 100 | 300 | 98 | 0 | 327 | 231 |  | 0 | 240 | 240 | 0 | 0 | 14 | 323 | 0 | 0 | 100 | 85 | 147 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 13 | 25 | 24 | 33 | 33 | 33 | 0 | 58 | 25 | 100 | 0 | 9 | 204 | 0 | 110 | 0 |  | 24 | 0 | 0 | 78 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 310 | 295 | 200 | 16 | 87 | 26 | 52 | 0 | 34 | 0 | 49 | 43 | 21 | 8 | 33 | 20 | 150 | 145 | 8 | 17 | 2 | 44 | 30 | 53 | 0 | 0 | 161 | 60 | 81 | 0 | 219 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 121 | 0 | 0 | 115 | 0 | 100 | 5 | 100 | 51 | 140 | 413 | 95 | 0 | 89 | 5 | 0 | 0 | 75 | 68 | 105 | 100 | 389 | 64 | 51 | 126 | 96 | 0 | 36 | 28 |  | 797 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 24 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 43 | 24 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 173 | 0 | 11 | 0 | 196 | 0 | 384 | 70 | 0 | 79 | 0 | 92 | 0 | 7 | 95 | 390 | 218 | 0 | 0 | 1 |  | 8143 | 3450 | 11593 | 5077 | 797 | 1754 | 2740 | 540 | 83 | 353 | 150 | 99 | 0 | 80.4
15:00 | 0 | 0 | 0 | 100 | 300 | 97 | 0 | 327 | 232 |  | 0 | 240 | 305 | 0 | 0 | 30 | 318 | 0 | 0 | 100 | 93 | 147 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 17 | 25 | 24 | 33 | 33 | 26 | 0 | 58 | 25 | 100 | 0 | 25 | 217 | 0 | 110 | 0 |  | 24 | 0 | 0 | 78 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 320 | 320 | 176 | 16 | 90 | 26 | 53 | 0 | 34 | 0 | 48 | 43 | 21 | 8 | 33 | 20 | 136 | 142 | 8 | 17 | 2 | 42 | 30 | 52 | 0 | 0 | 160 | 59 | 81 | 0 | 220 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 180 | 0 | 0 | 130 | 0 | 100 | 2 | 100 | 51 | 138 | 372 | 95 | 0 | 89 | 4 | 0 | 0 | 75 | 80 | 110 | 100 | 376 | 104 | 30 | 126 | 96 | 0 | 36 | 26 |  | 797 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 24 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 43 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 0 | 196 | 0 | 396 | 70 | 0 | 94 | 0 | 110 | 0 | 6 | 95 | 410 | 218 | 0 | 0 | 0 |  | 8310 | 3516 | 11826 | 5037 | 797 | 1785 | 3000 | 560 | 83 | 358 | 136 | 70 | 0 | 80.4
16:00 | 0 | 0 | 0 | 100 | 300 | 98 | 0 | 327 | 241 |  | 0 | 240 | 250 | 0 | 0 | 30 | 319 | 0 | 0 | 100 | 64 | 147 | 40 | 0 | 0 | 0 | 54 | 55 | 55 | 17 | 25 | 24 | 33 | 33 | 26 | 0 | 54 | 25 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 24 | 0 | 0 | 78 | 0 | 0 | 21 | 2 | 80 | 0 | 0 | 280 | 295 | 181 | 16 | 86 | 26 | 51 | 0 | 34 | 0 | 48 | 43 | 21 | 11 | 33 | 20 | 132 | 148 | 8 | 17 | 1 | 43 | 30 | 52 | 0 | 0 | 160 | 60 | 81 | 0 | 220 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 195 | 0 | 0 | 158 | 0 | 114 | 11 | 100 | 67 | 140 | 405 | 95 | 0 | 89 | 3 | 0 | 0 | 88 | 80 | 107 | 100 | 388 | 104 | 29 | 126 | 96 | 0 | 36 | 9 |  | 797 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 83 | 24 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 50 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 200 | 0 | 391 | 70 | 0 | 70 | 0 | 110 | 0 | 6 | 95 | 420 | 218 | 0 | 0 | 0 |  | 8292 | 3515 | 11807 | 5026 | 797 | 1788 | 2994 | 570 | 79 | 362 | 132 | 59 | 0 | 80.56
17:00 | 0 | 0 | 0 | 160 | 300 | 98 | 0 | 326 | 252 |  | 0 | 240 | 275 | 0 | 0 | 30 | 290 | 0 | 0 | 70 | 64 | 115 | 20 | 0 | 0 | 0 | 35 | 17 | 55 | 17 | 25 | 24 | 33 | 33 | 34 | 0 | 56 | 25 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 24 | 0 | 0 | 78 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 275 | 270 | 171 | 16 | 89 | 26 | 50 | 0 | 34 | 0 | 48 | 25 | 21 | 11 | 33 | 20 | 116 | 144 | 8 | 17 | 0 | 42 | 30 | 52 | 0 | 0 | 159 | 60 | 81 | 0 | 220 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 145 | 0 | 0 | 120 | 0 | 118 | 2 | 50 | 70 | 70 | 405 | 105 | 0 | 51 | 1 | 0 | 0 | 51 | 62 | 65 | 50 | 383 | 104 | 6 | 54 | 96 | 0 | 36 | 1 |  | 798 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 25 | 30 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 199 | 0 | 409 | 53 | 0 | 35 | 0 | 70 | 0 | 2 | 50 | 420 | 153 | 0 | 0 | 0 |  | 7642 | 3306 | 10948 | 5015 | 798 | 1734 | 2292 | 570 | 81 | 330 | 116 | 12 | 0 | 80.58
18:00 | 0 | 0 | 0 | 160 | 300 | 74 | 0 | 326 | 252 |  | 0 | 240 | 270 | 0 | 0 | 30 | 250 | 0 | 0 | 50 | 64 | 115 | 20 | 0 | 0 | 0 | 35 | 17 | 55 | 17 | 25 | 24 | 33 | 33 | 42 | 0 | 58 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 50 | 0 | 0 | 22 | 7 | 80 | 0 | 0 | 275 | 270 | 206 | 8 | 90 | 26 | 51 | 0 | 34 | 0 | 48 | 25 | 22 | 11 | 33 | 20 | 104 | 168 | 8 | 17 | 0 | 43 | 30 | 14 | 0 | 0 | 161 | 40 | 50 | 0 | 180 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 160 | 0 | 0 | 120 | 0 | 96 | 0 | 10 | 51 | 70 | 352 | 95 | 0 | 51 | 0 | 0 | 0 | 34 | 80 | 65 | 10 | 350 | 104 | 2 | 54 | 96 | 0 | 36 | 2 |  | 798 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 84 | 18 | 0 | 0 | 0 | 0 | 43 | 0 | 90 | 0 | 25 | 30 | 25 | 18 | 0 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 11 | 0 | 191 | 0 | 323 | 35 | 0 | 35 | 0 | 69 | 0 | 1 | 35 | 410 | 130 | 0 | 0 | 0 |  | 7243 | 3047 | 10290 | 4819 | 798 | 1502 | 2071 | 560 | 83 | 348 | 104 | 5 | 0 | 80.61
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 160 | 300 | 94 | 0 | 326 | 232 |  | 0 | 240 | 305 | 0 | 0 | 30 | 250 | 0 | 0 | 55 | 75 | 144 | 32 | 0 | 0 | 0 | 44 | 17 | 55 | 0 | 25 | 24 | 33 | 33 | 44 | 0 | 49 | 25 | 100 | 0 | 23 | 217 | 0 | 110 | 0 |  | 24 | 0 | 51 | 67 | 0 | 1 | 22 | 6 | 80 | 0 | 0 | 330 | 325 | 210 | 8 | 90 | 26 | 51 | 0 | 34 | 0 | 48 | 25 | 22 | 11 | 33 | 20 | 134 | 153 | 8 | 19 | 0 | 44 | 30 | 20 | 0 | 0 | 160 | 60 | 70 | 0 | 212 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 160 | 10 | 0 | 136 | 0 | 139 | 0 | 30 | 57 | 83 | 379 | 95 | 0 | 58 | 0 | 0 | 0 | 42 | 70 | 71 | 40 | 370 | 104 | 0 | 66 | 95 | 0 | 36 | 0 |  | 797 | 0 | 370 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 85 | 28 | 0 | 0 | 0 | 0 | 43 | 14 | 91 | 0 | 25 | 30 | 25 | 29 | 9 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 1 | 180 | 0 | 370 | 39 | 0 | 40 | 0 | 100 | 0 | 0 | 50 | 410 | 152 | 0 | 17 | 0 |  | 7822 | 3302 | 11124 | 5035 | 797 | 1625 | 2394 | 560 | 74 | 505 | 134 | 0 | 0 | 80.7
19:30 | 0 | 0 | 0 | 160 | 300 | 95 | 0 | 326 | 232 |  | 0 | 240 | 250 | 0 | 0 | 55 | 326 | 0 | 0 | 80 | 93 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 24 | 33 | 33 | 43 | 0 | 40 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 86 | 0 | 28 | 22 | 6 | 80 | 0 | 0 | 275 | 270 | 215 | 8 | 90 | 26 | 51 | 0 | 34 | 0 | 49 | 35 | 22 | 11 | 33 | 20 | 140 | 152 | 8 | 19 | 0 | 44 | 30 | 53 | 0 | 0 | 163 | 61 | 79 | 0 | 220 | 18 | 0 | 10 | 265 | 16 | 11 | 60 | 200 | 61 | 25 | 190 | 52 | 149 | 0 | 100 | 99 | 100 | 402 | 95 | 20 | 85 | 0 | 0 | 0 | 95 | 70 | 114 | 100 | 398 | 104 | 0 | 126 | 95 | 0 | 36 | 0 |  | 798 | 0 | 410 | 0 | 0 | 60 | 0 | 0 | 15 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 43 | 18 | 91 | 0 | 43 | 34 | 25 | 30 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 100 | 199 | 0 | 379 | 105 | 60 | 94 | 0 | 113 | 0 | 0 | 90 | 470 | 220 | 0 | 35 | 0 |  | 8713 | 3920 | 12633 | 5122 | 798 | 1735 | 3612 | 620 | 65 | 541 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 160 | 300 | 105 | 0 | 327 | 230 |  | 0 | 240 | 240 | 0 | 0 | 55 | 326 | 0 | 0 | 80 | 94 | 150 | 79 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 33 | 43 | 0 | 49 | 25 | 100 | 0 | 22 | 204 | 0 | 110 | 0 |  | 24 | 0 | 51 | 85 | 0 | 36 | 22 | 16 | 80 | 0 | 0 | 275 | 270 | 216 | 8 | 89 | 26 | 55 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 140 | 149 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 61 | 80 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 11 | 30 | 265 | 26 | 0 | 192 | 27 | 149 | 0 | 100 | 135 | 133 | 402 | 95 | 65 | 86 | 0 | 0 | 0 | 91 | 70 | 113 | 100 | 399 | 104 | 0 | 126 | 94 | 0 | 36 | 0 |  | 797 | 0 | 410 | 0 | 0 | 85 | 0 | 0 | 15 | 0 | 0 | 85 | 32 | 16 | 0 | 0 | 0 | 43 | 35 | 91 | 0 | 43 | 39 | 46 | 30 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 11 | 90 | 198 | 0 | 379 | 105 | 40 | 91 | 0 | 113 | 0 | 0 | 95 | 480 | 218 | 0 | 54 | 0 |  | 8822 | 3990 | 12812 | 5109 | 797 | 1771 | 3703 | 630 | 74 | 588 | 140 | 0 | 0 | 80.67
21:00 | 0 | 0 | 0 | 160 | 300 | 105 | 0 | 326 | 225 |  | 0 | 240 | 275 | 0 | 0 | 55 | 326 | 0 | 0 | 100 | 94 | 150 | 84 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 33 | 33 | 43 | 0 | 52 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 85 | 0 | 46 | 19 | 26 | 80 | 0 | 0 | 285 | 280 | 213 | 8 | 90 | 26 | 54 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 138 | 144 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 161 | 60 | 83 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 288 | 26 | 0 | 192 | 0 | 149 | 0 | 100 | 160 | 145 | 404 | 95 | 105 | 89 | 0 | 0 | 0 | 110 | 52 | 115 | 100 | 390 | 104 | 0 | 126 | 92 | 0 | 36 | 0 |  | 798 | 0 | 405 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 88 | 33 | 16 | 0 | 0 | 0 | 43 | 48 | 91 | 0 | 43 | 32 | 46 | 30 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 100 | 191 | 0 | 409 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 54 | 0 |  | 8963 | 4059 | 13022 | 5110 | 798 | 1824 | 3796 | 670 | 77 | 609 | 138 | 0 | 0 | 80.7
22:00 | 0 | 0 | 0 | 160 | 300 | 105 | 0 | 326 | 225 |  | 0 | 240 | 260 | 0 | 0 | 55 | 330 | 0 | 0 | 100 | 94 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 25 | 33 | 33 | 43 | 0 | 52 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 85 | 0 | 46 | 19 | 35 | 80 | 0 | 0 | 260 | 270 | 214 | 8 | 91 | 26 | 53 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 132 | 144 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 61 | 83 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 288 | 0 | 0 | 192 | 0 | 147 | 0 | 100 | 179 | 147 | 401 | 95 | 105 | 89 | 0 | 0 | 0 | 110 | 70 | 115 | 100 | 394 | 104 | 0 | 126 | 82 | 0 | 36 | 0 |  | 797 | 0 | 405 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 85 | 34 | 16 | 0 | 0 | 0 | 43 | 48 | 91 | 0 | 43 | 30 | 52 | 28 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 100 | 193 | 0 | 405 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 222 | 0 | 54 | 0 |  | 8931 | 4061 | 12992 | 5082 | 797 | 1840 | 3789 | 670 | 77 | 605 | 132 | 0 | 0 | 80.73
23:00 | 0 | 0 | 0 | 160 | 300 | 105 | 0 | 326 | 226 |  | 0 | 240 | 290 | 0 | 0 | 55 | 329 | 0 | 0 | 100 | 94 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 33 | 33 | 43 | 0 | 56 | 25 | 100 | 0 | 25 | 205 | 0 | 110 | 0 |  | 24 | 0 | 51 | 85 | 0 | 46 | 21 | 37 | 80 | 0 | 0 | 265 | 275 | 214 | 8 | 91 | 26 | 55 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 124 | 144 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 162 | 56 | 83 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 288 | 0 | 0 | 182 | 0 | 149 | 0 | 100 | 180 | 147 | 404 | 86 | 105 | 105 | 0 | 0 | 0 | 110 | 52 | 107 | 100 | 393 | 104 | 0 | 126 | 95 | 0 | 36 | 0 |  | 797 | 0 | 400 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 86 | 34 | 32 | 0 | 0 | 0 | 43 | 42 | 91 | 0 | 43 | 30 | 52 | 28 | 22 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 100 | 194 | 0 | 410 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 54 | 0 |  | 8940 | 4071 | 13011 | 5089 | 797 | 1849 | 3803 | 669 | 81 | 599 | 124 | 0 | 0 | 80.76
24:00 | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 326 | 290 |  | 0 | 240 | 250 | 0 | 0 | 55 | 329 | 0 | 0 | 100 | 94 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 25 | 33 | 33 | 43 | 0 | 59 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 88 | 0 | 47 | 21 | 39 | 80 | 0 | 0 | 260 | 270 | 215 | 8 | 90 | 26 | 55 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 21 | 130 | 151 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 163 | 56 | 83 | 0 | 211 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 288 | 0 | 0 | 182 | 27 | 149 | 0 | 100 | 180 | 147 | 403 | 96 | 105 | 93 | 0 | 0 | 0 | 110 | 52 | 107 | 100 | 400 | 104 | 0 | 126 | 95 | 0 | 36 | 0 |  | 797 | 0 | 400 | 0 | 0 | 40 | 0 | 0 | 15 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 43 | 42 | 91 | 0 | 43 | 30 | 52 | 27 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 11 | 100 | 194 | 0 | 404 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 54 | 0 |  | 8855 | 3973 | 12828 | 4940 | 797 | 1909 | 3760 | 670 | 84 | 538 | 130 | 0 | 0 | 80.79
KWH | 0 | 0 | 0 | 2835000 | 7144091 | 2339727 | 0 | 7974910 | 6758000 |  | 0 | 5640050 | 6632029 | 0 | 0 | 577859 | 7565958 | 0 | 0 | 2152550 | 1286640 | 3323040 | 927468 | 0 | 0 | 0 | 1265760 | 581008 | 1217454 | 276192 | 600000 | 543420 | 822500 | 817600 | 1003200 | 0 | 992204 | 600000 | 2400000 | 0 | 566634 | 4825409 | 0 | 2615614 | 0 |  | 564000 | 0 | 387999 | 1829640 | 0 | 225120 | 505728 | 448320 | 1987086 | 0 | 0 | 7209000 | 6933000 | 5046000 | 267636 | 2127880 | 582192 | 1296480 | 0 | 798432 | 0 | 1078504 | 851443 | 482148 | 214380 | 815600 | 442050 | 3189120 | 3722880 | 168960 | 431496 | 13900 | 1032000 | 711480 | 1144800 | 0 | 0 | 3606000 | 1342 | 1773120 | 0 | 5225970 | 377000 | 0 | 238140 | 7221500 | 369000 | 184944 | 62592 | 3231708 | 110329 | 20104 | 3316800 | 57723 | 1828800 | 121230 | 1016640 | 2055840 | 3288581 | 9625000 | 2451600 | 1648800 | 2126027 | 34527 | 0 | 0 | 2182909 | 1836540 | 2561160 | 1661760 | 9377600 | 1314240 | 417270 | 2455200 | 2274491 | 0 | 883440 | 203700 |  | 19264000 | 0 | 9365760 | 0 | 0 | 444579 | 0 | 0 | 112320 | 0 | 0 | 2062599 | 625625 | 72576 | 0 | 0 | 0 | 1097440 | 455069 | 2183928 | 0 | 620746 | 628704 | 1051680 | 166829 | 452640 | 0 | 260046 | 0 | 0 | 3662100 | 0 | 0 | 0 | 0 | 4456555 | 0 | 281779 | 871680 | 4837527 | 0 | 9471800 | 1511040 | 52315 | 1332768 | 0 | 1768252 | 0 | 57509 | 1635552 | 11256200 | 5135482 | 0 | 469200 | 28740 |  | 193953218 | 85693040 | 279646258 | 120412957 | 19264000 | 43893531 | 65620858 | 14918300 | 1592204 | 9878412 | 3189120 | 876876 | 0
Fuel Cost | 0 | 0 | 0 | 4167450 | 7929941.01 | 3088439.64 | 0 | 8054659.1 | 6960740 |  | 0 | 6147654.5 | 7361552.19 | 0 | 0 | 4888687.14 | 7868596.32 | 0 | 0 | 16208701.5 | 11734156.8 | 32698713.6 | 8551254.96 | 0 | 0 | 0 | 9240048 | 4491191.84 | 12004096.44 | 207144 | 450000 | 0 | 0 | 0 | 9700944 | 0 | 267895.08 | 162000 | 4344000 | 0 | 5264029.86 | 5259695.81 | 0 | 4446543.8 | 0 |  | 0 | 0 | 3763590.3 | 17473062 | 0 | 1782950.4 | 637217.28 | 1331510.4 | 2940887.28 | 0 | 0 | 5334660 | 6933000 | 4642320 | 345250.44 | 2447062 | 657876.96 | 1815072 | 0 | 1365318.72 | 0 | 10892890.4 | 8131280.65 | 612327.96 | 160785 | 1427300 | 331537.5 | 23918400 | 3946252.8 | 1534156.8 | 547999.92 | 221566 | 1692480 | 1138368 | 2037744 | 0 | 0 | 3750240 | 2643.74 | 3386659.2 | 0 | 9040928.1 | 825630 | 0 | 485805.6 | 7293715 | 276750 | 140557.44 | 1064689.92 | 24431712.48 | 1873386.42 | 336138.88 | 17247360 | 965128.56 | 17995392 | 1417178.7 | 8285616 | 22305864 | 23184496.05 | 8951250 | 22358592 | 15581160 | 18517695.17 | 0 | 0 | 0 | 19187770.11 | 18328669.2 | 21949141.2 | 11067321.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110960640 | 0 | 9834048 | 0 | 0 | 6161864.94 | 0 | 0 | 1178236.8 | 0 | 0 | 2330736.87 | 969718.75 | 708341.76 | 0 | 0 | 0 | 10798809.6 | 4623501.04 | 19327762.8 | 0 | 8392485.92 | 6092141.76 | 10190779.2 | 1618241.3 | 869068.8 | 0 | 196854.822 | 0 | 0 | 19848582 | 0 | 0 | 0 | 0 | 5882652.6 | 0 | 422668.5 | 14827276.8 | 5659906.59 | 0 | 9377082 | 15775257.6 | 889878.15 | 12647968.32 | 0 | 13721635.52 | 0 | 635474.45 | 12086729.28 | 49414718 | 0 | 0 | 0 | 0 |  | 569812493.77 | 355443062.172 | 925255555.942 | 123070302.902 | 110960640 | 45896447.55 | 452286598.72 | 69263300 | 429895.08 | 97155752.54 | 23918400 | 2274219.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 100 | 300 | 96 | 0 | 327 | 232 |  | 0 | 240 | 285 | 0 | 0 | 0 | 320 | 0 | 0 | 95 | 85 | 150 | 50 | 0 | 0 | 0 | 54 | 17 | 55 | 18 | 25 | 9 | 33 | 33 | 33 | 0 | 29 | 25 | 100 | 0 | 0 | 214 | 0 | 110 | 0 |  | 24 | 0 | 0 | 83 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 315 | 310 | 210 | 16 | 90 | 26 | 50 | 0 | 34 | 0 | 41 | 43 | 19 | 8 | 33 | 20 | 140 | 144 | 8 | 19 | 0 | 44 | 30 | 50 | 0 | 0 | 160 | 60 | 82 | 0 | 219 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 20 | 0 | 0 | 60 | 0 | 105 | 20 | 30 | 51 | 140 | 405 | 106 | 0 | 89 | 5 | 0 | 0 | 95 | 90 | 113 | 90 | 390 | 11 | 56 | 126 | 96 | 0 | 36 | 27 |  | 798 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 50 | 21 | 92 | 0 | 34 | 24 | 52 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 197 | 0 | 408 | 21 | 0 | 0 | 0 | 45 | 0 | 7 | 55 | 350 | 220 | 0 | 0 | 5 |  | 11176 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 160 | 300 | 105 | 0 | 326 | 225 | 0 | 0 | 240 | 275 | 0 | 0 | 55 | 326 | 0 | 0 | 100 | 94 | 150 | 84 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 25 | 33 | 33 | 43 | 0 | 52 | 25 | 100 | 0 | 25 | 203 | 0 | 110 | 0 | 0 | 24 | 0 | 51 | 85 | 0 | 46 | 19 | 26 | 80 | 0 | 0 | 285 | 280 | 213 | 8 | 90 | 26 | 54 | 0 | 34 | 0 | 49 | 43 | 22 | 11 | 33 | 20 | 138 | 144 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 0 | 161 | 60 | 83 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 288 | 26 | 0 | 192 | 0 | 149 | 0 | 100 | 160 | 145 | 404 | 95 | 105 | 89 | 0 | 0 | 0 | 110 | 52 | 115 | 100 | 390 | 104 | 0 | 126 | 92 | 0 | 36 | 0 |  | 798 | 0 | 405 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 88 | 33 | 16 | 0 | 0 | 0 | 43 | 48 | 91 | 0 | 43 | 32 | 46 | 30 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 100 | 191 | 0 | 409 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 54 | 0 |  | 13022 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 100 | 300 | 100 | 0 | 325 | 300 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 100 | 102 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 52 | 25 | 100 | 0 | 25 | 225 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 0 | 50 | 22 | 25 | 100 | 0 | 0 | 360 | 350 | 210 | 8 | 90 | 26 | 55 | 0 | 34 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 160 | 8 | 21 | 0 | 43 | 30 | 51 | 0 | 0 | 160 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 132 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 126 | 116 | 0 | 36 |  |  | 821 | 0 | 400 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 86 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 95 | 0 | 43 | 40 | 52 | 41 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 0 | 0 | 210 | 0 | 11 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 100 | 0 | 325 | 300 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 330 | 0 | 0 | 100 | 100 | 150 | 84 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 52 | 25 | 100 | 0 | 25 | 225 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 0 | 50 | 22 | 10 | 100 | 0 | 0 | 350 | 330 | 210 | 8 | 90 | 26 | 55 | 0 | 34 | 0 | 42 | 43 | 22 | 11 | 33 | 21 | 148 | 160 | 8 | 21 | 1.6 | 43 | 30 | 51 | 0 | 0 | 160 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 100 | 250 | 100 | 100 | 175 | 100 | 130 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 100 | 113 | 100 | 400 | 90 | 50 | 126 | 116 | 0 | 36 | 30 |  | 821 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 25 | 110 | 0 | 0 | 0 | 50 | 30 | 95 | 0 | 43 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 210 | 0 | 11 | 50 | 200 | 0 | 400 | 90 | 100 | 94 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 105 | 0 | 315 | 302 | 0 | 0 | 240 | 230 | 0 | 0 | 0 | 240 | 0 | 0 | 91 | 5 | 100 | 0 | 0 | 0 | 0 | 35 | 12 | 35 | 13 | 25 | 25 | 33 |  | 43 | 0 | 53 | 25 | 100 | 0 | 25 | 216 | 0 | 110 | 0 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 22 | 7 | 80 | 0 | 0 | 300 | 295 | 160 | 8 | 90 | 20 | 56 | 0 | 34 | 0 | 0 | 1 | 22 | 11 | 33 | 21 | 110 | 169 | 8 | 19 | 1 | 43 | 30 | 53 | 0 | 0 | 163 | 61 | 84 | 0 | 192 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 0 | 85 | 81 | 343 | 115 | 105 | 90 | 2 | 0 | 0 | 94 | 54 | 109 | 30 | 350 | 0 | 11 | 54 | 116 | 0 | 36 | 10 | 0 | 806 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 0 | 43 | 28 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 191 | 0 | 10 | 0 | 193 | 0 | 0 | 17 | 0 | 70 | 0 | 34 | 0 | 1 | 95 | 360 | 222 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 10089 | 7:00
| Highest Generation |  | 13022 | 21:00
| Day Peak Generation |  | 11176 | 12:00
| Evening Peak Generation |  | 13022 | 21:00
| HVDC Max Flow |  | 798 | 2:00
| HVDC EvPeak Flow |  | 798 | 21:00
| Load factor L.F |  | 89.48%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-13
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-12 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11176 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9837 | MW
Evening Peak Generation : |  | 13022 | MW Hour : | 21:00 | Available Max Generation : |  | 15331 | MW
E.P. Demand (at gen end) : |  | 13022 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13400 | MW
Maximum Generation : |  | 13022 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1931 | MW
Total Gen. (MKWH) : |  | 279.6463 | System Load Factor : | 89.48% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -310 | MW at | 22:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-13
Actual : | 80.97 | Ft.(MSL) , | Rule curve : | 85.92 | Ft.( MSL )
Gas Consumed : | Total = | 1240.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 168966750.452
: |  | Coal : | 69263300 | Oil : | 549442351.26 | Total : | 787672401.712
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4742.396 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1618.4369 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1451.0922 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1311.5486 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1185.0265 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 956.289 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 527.2978 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 246.0225 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 737.573 |  |  | 0 | 0%
Total | 0 |  | 12775.6825 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW GT-2
7) Chandpur-150 MW ST
8) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aurahati-Keraniganj 132 kV Ckt was under shut down from 10:05 to 13:50 for D/W.
b) Bagherhat-Bhandaria 132 kV Ckt was under shut down from 10:43 to 12:20 for tree trimming.
c) Mymensingh-Bhaluka 132 kV Ckt-1 was under shut down from 10:25 to 15:47 for D/W.
d) Bogura-Sherpur 132 kV Ckt-2 was under shut down from 09:20 to 09:52 for C/M.
e) Gazipur 100 MW-Kodda 132 kV Ckt was under shut down from 11:14 to 18:24 for Bus bar protection test.
f) Shyampur-Hasnabad 230 kV Ckt was under shut down from 09:37 to 15:06 for R/H maintenance.
g) Jamalpur 132/33 kV T1 transformer was under shut down from 12:22 to 13:32 for R/H maintenance.
h) Kodda-Rajendrapur 132 kV Ckt-1 was under shut down from 12:15 to 21:10 for D/W.
i) Madunaghat 132/33 kV T1 transformer was under shut down from 11:51 to 13:05 for R/H maintenance. |  |  |  |  | About 18 MW power interruption occurred under Madunaghat S/S area
from 11:51 to 13:05.
j) Polashbari-Mahasthangar 132 kV Ckt-1 tripped at 10:40 from both ends showing Dist.Z1, A,B at both ends
and was switched on at 10:53.
k) Polashbari-Rangpur 132 kV Ckt-2 tripped at 10:40 from Polashbari end showing O/C and was switched
on at 10:48.
l) Savar 33 kV Bus-B was under shut down from 10:30 to 16:42 for D/W.
m) Sirajganj-Shahjadpur 132 kV Ckt tripped at 10:07 from Shahjadpur end showing Dist. C, Z1 and was switched
on at 10:22 and again tripped at 11:23 showing same relay.
n) Sirajganj-Shahjadpur 132 kV Ckt was under shutdown from 13:32 to 15:15 for C/M.
o) Polashbari-Mahasthangar 132 kV Ckt-1 was under shutdown from 14:40 to 15:50 for C/M.
p) B. Baria 132/33 kV T1 transformer was under shut down from 16:46 to 18:04 for C/M.
q) Kabirpur 132/33 kV T3 transformer tripped at 15:44 due to 33 kV Mouchak feeder fault and was switched
on at 18:10.
r) Ghorashal unit-5 tripped at 23:50 due to 6.6 kV CB Room on fire.
s) Sylhet-Chattak 132 kV Ckt-2 tripped at 00:01(13/07/2021) from Sylhet end showing Dist. A-phase and |  |  |  |  | About 33 MW power interruption occurred under Sunamganj S/S area
was switched on at 00:16(13/07/2021). |  |  |  |  | from 00:01(13/07/2021) to 00:16(13/07/2021).
t) Sirajganj Unit-4 tripped at 05:20(13/07/2021) due to electrical fault at GT.
u) Sherpur 132/33 kV T1 transformer is under shut down since 07:52(13/07/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-12 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 160 | 2835000 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7144091 | Gas shortage
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 105 | 2339727
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 326 | 7974910 | FGMO
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 225 | 6758000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5640050 | Dirty gas
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6632029 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 577859
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 84 | 927468 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 276192 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 100 | 2152550
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7565958
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 1286640
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1265760
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3323040
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 581008
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1217454
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 50 | 1143420 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 822500
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 817600
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 43 | 1003200 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 288 | 3231708
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 26 | 110329 | Low demand
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 20104 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 57723 | Reserve.
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1828800
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1648800
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 1314240
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 126 | 2455200 | Engine problem
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203700
| Dhaka area Total |  |  |  | 5819 | 3577 | 73155060
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 566634
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 121230
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 46 | 225120
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 77 | 1592204 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4825409
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 110 | 2615614 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 89 | 2126027 | Engine problem
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 387999 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 85 | 1829640 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1016640
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 505728
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 26 | 448320
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34527
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2182909
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1661760
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 92 | 2274491 | Transformer O/L.
| Chattogram area Total |  |  |  | 2382 | 1233 | 24814252
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1987086 | Gas Shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 5046000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 7209000 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6933000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 582192 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1296480
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 267636 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 34 | 798432 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 145 | 3288581
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 49 | 1078504
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2127880 | Machine problem
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 160 | 2055840 | Engine problem
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 482148
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214380
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 3189120
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 815600
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 851443 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 442050 | Engine problem
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 62592 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 52 | 1836540 | Engine problem
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 2561160
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 883440 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1894 | 44009104
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 144 | 3722880 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 431496
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 168960 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13900
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 192 | 3316800
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 95 | 2451600 | Engine problem
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 417270
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 564000
| Mymensingh Area Total |  |  |  | 709 | 482 | 11086906
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1032000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 711480 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3606000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1144800
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 184944
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1342
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1773120
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5225970
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 377000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 369000 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7221500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 404 | 9625000
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 238140
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 390 | 9377600
| Sylhet Area Total |  |  |  | 2377 | 1777 | 40887896
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 798 | 19264000
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 112320 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 100 | 444579 | Low demand
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 405 | 9365760 | FGMO
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 871680
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1511040
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1523 | 31569379
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 72576 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 625625
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2062599 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 281779 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 11256200
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 221 | 5135482 | On Test
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 469200 | Line O/L
| Barisal Area Total |  |  |  | 1826 | 943 | 19903461
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 1097440
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 48 | 455069 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 620746 | Engine problem
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 628704 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 175 | 4456555 | FGMO
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 191 | 4837527 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 409 | 9471800 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 166829 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 452640
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 260046
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 46 | 1051680
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 2183928 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 52315 | Reserve.
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1332768 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1635552 | Engine problem
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28740
| Rajshahi Area Total |  |  |  | 2179 | 1330 | 28732339
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3662100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1768252
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 57509
| Rangpur Area Total |  |  |  | 605 | 263 | 5487861
| Total |  |  |  | 21060 | 13022 | 279646258
| Eastern Grid Total |  |  |  | 14321 | 8963 | 193953218
| Western Grid Total |  |  |  | 6739 | 4059 | 85693040
| National Grid Total |  |  |  | 21060 | 13022 | 279646258
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-12
(a) ENTIRE EASTERN GRID : |  | 8320 | MW | (b) ENTIRE WESTERN GRID : |  | 4085 | MW
i) Dhaka area |  | 4330 | MW | i) Khulna area |  | 1545 | MW
ii) Chittagong area |  | 1212 | MW | ii) Rajshahi area |  | 1378 | MW
iii) Comilla area |  | 1212 | MW | iii) Barisal area |  | 376 | MW
iv) Mymensingh area |  | 1046 | MW | iv) Rangpur area |  | 786 | MW
v) Sylhet area |  | 520 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12405 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 9:00 | Kishoreganj | 140 | 1:00 | Jessore | 120 | 19:30
Munsiganj | 108 | 23:00 | Netrokona | 114 | 2:00 | Benapol | 62 | 20:00
Sonargaon | 69 | 20:00 | Jamalpur | 146 | 19:30 | Jhenida | 114 | 19:30
Shyampur | 190 | 10:00 | Sherpur | 136 | 19:30 | Bottail | 136 | 20:00
Bhulta | 193 | 0:00 | Srimongal | 60 | 22:00 | G.K Project | 56 | 21:00
Madanganj | 51 | 14:00 | Shahjibazar | 118 | 22:00 | Faridpur | 146 | 21:00
Shitalakhya | 121 | 12:00 | Fenchuganj | 50 | 19:00 | Rajbari | 58 | 23:00
Rahim steel | 22 | 0:00 | Kulawara | 46 | 23:00 | Madaripur | 109 | 22:00
Matuail | 60 | 0:00 | Sylhet | 123 | 20:00 | Sariatpur | 72 | 22:00
Ghorasal | 80 | 0:00 | Chatak | 34 | 21:00 | Gopalganj | 96 | 21:00
Narsingdi | 177 | 0:00 | Sunamganj | 55 | 21:00 | Bagerhat | 103 | 19:30
Haripur (SBU) | 117 | 23:00 | Biani Bazar | 72 | 20:00 | Mongla | 40 | 12:00
Sreenagar | 43 | 22:00 | Comilla (S) | 160 | 1:00 | Satkhira | 107 | 21:00
Ullon | 80 | 0:00 | Comilla(N) | 145 | 22:00 | Gallamari
Hasnabad | 81 | 19:30 | Chandpur | 81 | 23:00 | Magura | 56 | 21:00
Magbazar | 72 | 10:00 | Feni | 117 | 21:00 | Norail | 43 | 20:00
Maniknagar | 72 | 13:00 | Chowmuhani | 214 | 23:00 | Chuadanga | 91 | 20:00
Bangabhaban | 13 | 12:00 | Ashuganj | 35 | 22:00 | Borguna | 18 | 20:00
Motijheel | 23 | 12:00 | Daudkandi | 158 | 22:00 | Barisal(N) | 46 | 22:00
Narinda | 50 | 16:00 | B.Baria | 175 | 22:00 | Barisal (S) | 106 | 22:00
Kazla | 61 | 1:00 | Ramganj | 88 | 22:00 | Patuakhali | 116 | 22:00
Dhanmondi | 149 | 14:00 | Chaddagram | 46 | 20:00 | Bhandaria | 54 | 21:00
Lalbag | 86 | 13:00 | PHP | 4 | 19:30 | Borhan Uddin | 45 | 21:00
Madartek | 76 | 23:00 | Kochua | 64 | 22:00 | Ishurdi | 72 | 1:00
Dhaka University | 25 | 12:00 | Madunaghat | 54 | 18:30 | Ruppur Paromanobik | 3 | 7:00
Aftabnagar | 10 | 1:00 | Hathazari | 92 | 19:30 | Natore | 137 | 21:00
Fatullah | 56 | 10:00 | Khulshi | 182 | 12:00 | Bogra | 166 | 19:30
Nawabganj | 55 | 22:00 | Halishahar | 86 | 14:00 | Noagaon | 118 | 20:00
Keraniganj | 68 | 19:30 | Baraulia | 141 | 23:00 | Rajshahi | 154 | 21:00
Mirpur | 122 | 19:30 | Sikalbaha | 39 | 18:00 | Rajshahi New | 18 | 1:00
Kalyanpur | 105 | 19:30 | Dohazari | 82 | 19:00 | C.Nawabganj | 72 | 12:00
Gulshan | 96 | 14:00 | Cox'sbazar | 99 | 19:30 | Amnura | 50 | 20:00
Uttara | 98 | 1:00 | Chandraghona | 26 | 15:00 | Pabna | 106 | 21:00
Uttara New | 21 | 15:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 101 | 21:00
Kamrangirchar | 85 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 108 | 21:00
Savar | 173 | 11:00 | Bakulia | 111 | 15:00 | Niyamatpur | 84 | 20:00
Bhasantec | 118 | 14:00 | Julda | 24 | 13:00 | Joypurhat | 63 | 20:00
Agargaon | 78 | 13:00 | TK chemical | 30.5 | 21:00 | Sherpur(Bogura) | 55 | 19:30
Satmosjid | 112 | 24:00 | Modern Steel | 0 | #N/A | Mohastangor | 68 | 20:00
Tongi | 116 | 18:00 | Shahmirpur | 28.4 | 0:00 | Bhangura | 34 | 21:00
Kabirpur | 245 | 15:00 | Khagrachhari | 30 | 4:00 | Rangpur | 112 | 20:00
Basundhara | 236 | 14:00 | Matarbari | 36.5 | 20:00 | Lalmonirhat | 40 | 19:00
Manikganj | 92 | 19:30 | Baroiar Hat | 40 | 19:00 | Saidpur | 104 | 20:00
Joydevpur | 179 | 19:30 | Rangamati | 10 | 11:00 | Purbasadipur | 114 | 19:30
New Tongi | 111 | 14:00 | Abul Khair 230 | 138 | 23:00 | Thakurgaon | 83 | 1:00
Kodda | 294 | 15:00 | BSRM | 153 | 3:00 | Palashbari | 118 | 19:30
Dhamrai | 108 | 19:30 | GPH Ispat | 25 | 7:00 | Barapukuria | 58 | 21:00
Rajendrapur | 108 | 20:00 | Agrabad | 76 | 14:00 | Panchagar | 49 | 20:00
Valuka | 116 | 10:00 | Goalpara | 37 | 23:00 | Joldhaka | 61 | 21:00
Tangail | 224 | 22:00 | Central S/S | 120 | 22:00 | Kurigram | 54 | 1:00
Mymensing | 220 | 22:00 | Noapara | 50 | 19:30 | Mithapukur | 52 | 2:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-12 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 400 | 5:00 | 395 | 11:00 | Kaliakoir | 389 | 0.29167 | 378 | 0.5
| Bheramara | 402 | 1:00 | 395 | 1:00 | Bhulta | 385 | 0.25 | 376 | 0.41667
| Ashuganj(N) | 390 | 18:00 | 384 | 10:00 | Gopalganj | 409 | 0.625 | 388 | 0.875
| Payra | 415 | 21:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 223 | 19:30 | 217 | 7:00
| Ishurdi | 235 | 2:00 | 224 | 21:00 | Megnaghat | 230 | 16:00 | 228 | 19:00
| Ashuganj | 239 | 6:00 | 235 | 9:00 | Fenchuganj | 236 | 20:00 | 233 | 2:00
| Serajganj | 230 | 14:00 | 226 | 8:00 | Siddhirganj | 230 | 19:30 | 226 | 6:00
| Baghabari | 232 | 17:00 | 225 | 20:00 | Maniknagar | 229 | 19:30 | 224 | 10:00
| Barapukuria | 233 | 18:00 | 223 | 20:00 | Agargaon | 226 | 8:00 | 219 | 9:00
| Bogra | 223 | 18:00 | 212 | 21:00 | Barisal | 241 | 19:30 | 233 | 24:00
| Rajshahi | 234 | 3:00 | 222 | 19:30 | Bhola 225 MW | 245 | 8:00 | 239 | 1:00
| Khulna South | 225 | 18:00 | 210 | 5:00 | AKSML | 224 | 19:30 | 218 | 12:00
| Rampura | 229 | 3:00 | 222 | 12:00 | BSRM | 226 | 6:00 | 219 | 9:00
| Haripur | 229 | 20:00 | 223 | 10:00 | Bibiyana | 238 | 20:00 | 232 | 10:00
| Hasnabad | 228 | 1:00 | 225 | 3:00 | Bhulta | 231 | 6:00 | 225 | 10:00
| Shyampur | 227 | 21:00 | 220 | 9:00 | Ashuganj (S) | 235 | 6:00 | 231 | 11:00
| Aminbazar | 227 | 1:00 | 221 | 2:00 | Kaliakoir | 227 | 1:00 | 214 | 11:00
| Tongi | 227 | 19:30 | 213 | 9:00 | GPH | 224 | 6:00 | 220 | 13:00
| Comilla (N) | 228 | 6:00 | 225 | 15:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 20:00 | 130 | 10:00 | Madanhat | 134 | 0.83333 | 130 | 0.77083
| Munsiganj | 135 | 19:30 | 129 | 10:00 | Hathazari | 133 | 0.8125 | 129 | 0.29167
| Sonargaon | 133 | 19:00 | 128 | 10:00 | Khulshi | 130 | 0.8125 | 126 | 0.41667
| Shyampur | 135 | 22:00 | 131 | 10:00 | Halishahar | 132 | 0.83333 | 125 | 0.29167
| Bhulta | 130 | 19:30 | 122 | 9:00 | Baraulia | 132 | 0.8125 | 128 | 0.625
| Madanganj | 134 | 0:00 | 128 | 11:00 | Sikalbaha | 134 | 0.83333 | 131 | 0.041667
| Shitalakhya | 142 | 19:30 | 127 | 1:00 | Dohazari | 128 | 0.875 | 124 | 0.75
| Rahim steal | 133 | 19:00 | 130 | 9:00 | Cox'sbazar | 120 | 0.375 | 115 | 0.083333
| Matuail | 134 | 20:00 | 130 | 10:00 | Chandraghona | 133 | 0.8125 | 129 | 0.5
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 132 | 0.75 | 130 | 0.041667
| Narsinghdi | 132 | 7:00 | 126 | 21:00 | A. Khaer Stl. | 131 | 0.041667 | 128 | 0.41667
| Haripur (SBU) | 134 | 19:30 | 130 | 10:00 | Bakulia | 131 | 0.8125 | 127 | 0.375
| Sreenagar | 130 | 20:00 | 125 | 10:00 | Julda | 132 | 0.041667 | 128 | 0.77083
| Ullon | 136 | 4:00 | 130 | 12:00 | TK Chemical | 133 | 0.83333 | 128 | 0.41667
| Hasnabad | 138 | 1:00 | 133 | 9:00 | Modern Steel | 0 | #N/A |  | #N/A
| Magbazar | 136 | 6:00 | 130 | 10:00 | Shahmirpur | 134 | 0.8125 | 127 | 0.33333
| Maniknagar | 137 | 1:00 | 134 | 10:00 | Khagrachhari | 131 | 0.16667 | 127 | 0.5
| Bangabhaban | 137 | 1:00 | 134 | 10:00 | Matarbari | 121 | 0.20833 | 118 | 0.95833
| Motijheel | 137 | 1:00 | 134 | 10:00 | Baroiar Hat | 133 | 0.16667 | 130 | 0.58333
| Narinda | 137 | 1:00 | 134 | 10:00 | Rangamati | 132 | 19:30 | 128 | 12:00
| Kazla | 137 | 1:00 | 134 | 10:00 | Agrabad | 131 | 19:30 | 127 | 7:00
| Dhanmondi | 133 | 2:00 | 129 | 9:00 | Goalpara S/S | 135 | 19:00 | 125 | 0.20833
| Lalbag | 139 | 19:30 | 132 | 10:00 | Khulna Central S/S | 135 | 18:00 | 123 | 0.29167
| Madartek | 135 | 5:00 | 130 | 12:00 | Noapara | 132 | 18:00 | 121 | 0.29167
| Dhaka University | 135 | 1:00 | 130 | 12:00 | Jessore | 128 | 18:00 | 117 | 0.625
| Aftabnagar | 135 | 6:00 | 131 | 9:00 | Benapol | 127 | 0.75 | 116 | 0.125
| Fatullah | 135 | 5:00 | 131 | 12:00 | Jhenida | 125 | 18:00 | 108 | 0.875
| Nawabganj | 130 | 19:30 | 125 | 17:00 | Bottail | 130 | 0.70833 | 120 | 0.875
| Keraniganj | 130 | 19:30 | 125 | 10:00 | G.K Project | 137 | 0.75 | 132 | 0.83333
| Mirpur | 136 | 1:00 | 131 | 17:00 | Faridpur | 135 | 0.29167 | 127 | 0.875
| Kalyanpur | 136 | 1:00 | 131 | 16:00 | Rajbari | 134 | 0.29167 | 125 | 0.875
| Gulshan | 134 | 1:00 | 130 | 10:00 | Madaripur | 141 | 0.75 | 132 | 0.8125
| Uttara | 136 | 20:00 | 130 | 8:00 | Shariyatpur S/S | 140 | 8:00 | 130 | 0.875
| Uttara New | 135 | 17:00 | 130 | 9:00 | Gopalganj | 143 | 0.25 | 132 | 0.8125
| Kamrangirchar | 139 | 20:00 | 132 | 10:00 | Bagerhat | 133 | 19:00 | 120 | 0.20833
| Savar | 130 | 1:00 | 131 | 9:00 | Mongla | 131 | 19:00 | 118 | 0.29167
| Bhasantec | 134 | 1:00 | 129 | 12:00 | Satkhira | 134 | 18:00 | 122 | 7:00
| Agargaon | 138 | 1:00 | 131 | 10:00 | Gallamari
| Satmosjid | 135 | 6:00 | 130 | 12:00 | Magura | 125 | 18:00 | 105 | 0.875
| Tongi | 139 | 1:00 | 131 | 11:00 | Narail | 123 | 0.75 | 105 | 0.875
| Kabirpur | 132 | 4.00 | 128 | 12:00 | Chuadanga | 120 | 18:00 | 96 | 0.875
| Basundhara | 137 | 18:30 | 128 | 10:00 | Borguna | 137 | 8:00 | 131 | 0.8125
| Manikganj | 139 | 19:30 | 126 | 9:00 | Barisal(N) | 140 | 7:00 | 134 | 1:00
| Joydevpur | 139 | 1:00 | 132 | 15:00 | Barisal (S) | 139 | 0.77083 | 132 | 0.041667
| New Tongi | 138 | 19:30 | 132 | 8:00 | Patuakhali(S) | 136 | 0.33333 | 131 | 0.041667
| Kodda | 135 | 20:00 | 124 | 10:00 | Bhandaria | 139 | 0.33333 | 125 | 0.95833
| Dhamrai | 131 | 1:00 | 126 | 20:00 | Ishurdi | 136 | 18:00 | 129 | 21:00
| Rajendrapur | 136 | 1:00 | 119 | 15:00 | Ruppur Paromanobik | 134 | 2:00 | 130 | 19:30
| Valuka | 120 | 18:00 | 108 | 13:00 | Natore | 133 | 16:00 | 126 | 21:00
| Tangail | 130 | 6:00 | 120 | 21:00 | Bogra | 133 | 18:00 | 124 | 21:00
| Mymensing | 124 | 10:00 | 114 | 21:00 | Noagaon | 129 | 18:00 | 117 | 21:00
| Kishorganj | 128 | 18:00 | 119 | 1:00 | Rajshahi | 133 | 18:00 | 126 | 21:00
| Netrokona | 122 | 18:00 | 111 | 19:00 | Rajshahi New | 132 | 3:00 | 124 | 21:00
| Jamalpur | 133 | 18:00 | 120 | 22:00 | C.Nawabganj | 131 | 18:00 | 123 | 21:00
| Sherpur | 132 | 16:00 | 118 | 13:00 | Amnura | 133 | 18:00 | 122 | 21:00
| Srimongal | 136 | 20:00 | 133 | 1:00 | Pabna | 135 | 18:00 | 127 | 21:00
| Shahjibazar | 134 | 7:00 | 130 | 1:00 | Shahjadpur | 136 | 1:00 | 134 | 21:00
| Fenchuganj | 136 | 6:00 | 133 | 1:00 | Serajganj | 131 | 18:00 | 125 | 21:00
| Khulawara | 134 | 3;00 | 132 | 19:00 | Niyamatpur | 126 | 18:00 | 113 | 21:00
| Sylhet | 133 | 5:00 | 131 | 18:30 | Joypurhat | 129 | 18:00 | 114 | 21:00
| Chatak | 134 | 24:00 | 128 | 1:00 | Sherpur(Bogura) | 132 | 16:00 | 125 | 19:30
| Sunamganj | 129 | 5;00 | 125 | 1:00 | Mohastangor | 131 | 18:00 | 122 | 21:00
| Biani Bazar | 132 | 2:00 | 127 | 1:00 | Bangura | 135 | 6:00 | 130 | 20:00
| Comilla(s) | 130 | 6:00 | 123 | 1:00 | Rangpur | 125 | 6:00 | 130 | 20:00
| Comilla(n) | 137 | 6:00 | 134 | 21:00 | Lalmonirhat | 125 | 16:00 | 115 | 19:30
| Chandpur | 132 | 7:00 | 129 | 23:00 | Saidpur | 126 | 16:00 | 114 | 19:30
| Feni | 136 | 11:00 | 130 | 21:00 | Purbasadipur | 124 | 18:00 | 106 | 20:00
| Chowmuhani | 135 | 8:00 | 129 | 21:00 | Thakurgaon | 122 | 18:00 | 102 | 19:30
| Ashuganj | 138 | 18:00 | 135 | 21:00 | Palashbari | 126 | 18:00 | 116 | 19:30
| Daudkandi | 133 | 18:30 | 129 | 23:00 | Barapukuria | 133 | 18:00 | 123 | 20:00
| B.Baria | 133 | 8:00 | 128 | 1:00 | Panchagar | 120 | 6:00 | 100 | 20:00
| Ramganj | 138 | 11:00 | 130 | 15:00 | Joldhaka | 122 | 0.75 | 107 | 0.8125
| Chaddagram | 136 | 5:00 | 131 | 15:00 | Kurigram | 125 | 0.45833 | 111 | 0.875
| PHP | 135 | 11:00 | 128 | 22:00 | Mithapukur | 128 | 0.66667 | 118 | 0.8125
| Kochua | 136 | 3:00 | 128 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-12
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 264 | 8855 | 3973 | 12828 |  |  |  | QF-LDC-11
0:30 | 256 | 8728.5 | 3929 | 12657.5 | Date: | 2021-07-12
1:00 | 248 | 8602 | 3885 | 12487
1:30 | 222 | 8401.5 | 3870.5 | 12272
2:00 | 196 | 8201 | 3856 | 12057
2:30 | 190 | 8111 | 3798 | 11909 | [5 empty] | Gen. at Eve. Peak | 13022 | 13022 MW (21:00 )
3:00 | 184 | 8021 | 3740 | 11761 | [6 empty] | 21:00
3:30 | 178 | 7997 | 3669.5 | 11666.5 | [5 empty] | Gen. at Day Peak | 11176 | 11176 MW (12:00 )
4:00 | 172 | 7973 | 3599 | 11572 | [6 empty] | 12:00
4:30 | 180 | 7931.5 | 3507.5 | 11439 | [5 empty] | Highest Generation | 13022
5:00 | 188 | 7890 | 3416 | 11306 | [6 empty] | 21:00
5:30 | 241 | 7652.5 | 3156.5 | 10809
6:00 | 294 | 7415 | 2897 | 10312
6:30 | 285 | 7308 | 2892.5 | 10200.5
7:00 | 276 | 7201 | 2888 | 10089
7:30 | 242 | 7212.5 | 2880 | 10092.5
8:00 | 208 | 7224 | 2872 | 10096
8:30 | 130 | 7340 | 2953 | 10293
9:00 | 52 | 7456 | 3034 | 10490
9:30 | 29 | 7570 | 3094.5 | 10664.5
10:00 | 6 | 7684 | 3155 | 10839
10:30 | 9 | 7678.5 | 3145.5 | 10824
11:00 | 12 | 7673 | 3136 | 10809
11:30 | 14 | 7803 | 3189.5 | 10992.5
12:00 | 16 | 7933 | 3243 | 11176
12:30 | 38 | 8007 | 3327 | 11334
13:00 | 60 | 8081 | 3411 | 11492
13:30 | 64 | 8112 | 3430.5 | 11542.5
14:00 | 68 | 8143 | 3450 | 11593
14:30 | 42 | 8226.5 | 3483 | 11709.5
15:00 | 16 | 8310 | 3516 | 11826
15:30 | 11 | 8301 | 3515.5 | 11816.5
16:00 | 6 | 8292 | 3515 | 11807
16:30 | 54 | 7967 | 3410.5 | 11377.5
17:00 | 102 | 7642 | 3306 | 10948
17:30 | 101 | 7442.5 | 3176.5 | 10619
18:00 | 100 | 7243 | 3047 | 10290
18:30 | 85 | 7532.5 | 3174.5 | 10707
19:00 | 70 | 7822 | 3302 | 11124
19:30 | 292 | 8713 | 3920 | 12633
20:00 | 292 | 8822 | 3990 | 12812 |  |  |  | Executive Engineer
20:30 | 286 | 8892.5 | 4024.5 | 12917 |  |  |  | Network Operation Division
21:00 | 280 | 8963 | 4059 | 13022
21:30 | 295 | 8947 | 4060 | 13007
22:00 | 310 | 8931 | 4061 | 12992 |  |  |  |  | Page 6 of 7
22:30 | 265 | 8935.5 | 4066 | 13001.5
23:00 | 220 | 8940 | 4071 | 13011
23:30 | 242 | 8897.5 | 4022 | 12919.5
24:00 | 264 | 8855 | 3973 | 12828
13022 MW (21:00 )
11176 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-12 |  | Energy | 279646258
[11 empty] | 2021-07-12 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4940 | 797 | 1909 | 3803 | 670 | 84 | 538 | 0 | 130 | 0
0:30 | 4969.5 | 796.5 | 1928.5 | 3604.5 | 674.5 | 69 | 491.5 | 0 | 145 | 0 | Date: | 2021-07-12
1:00 | 4999 | 796 | 1948 | 3406 | 679 | 54 | 445 | 0 | 160 | 0
1:30 | 5041 | 797 | 1958.5 | 3180 | 659 | 54 | 434.5 | 0 | 148 | 0 | [7 empty] | Total Energy | 279.6463 | Total Energy Gen 279.646 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.646 MKWHr
2:00 | 5083 | 798 | 1969 | 2954 | 639 | 54 | 424 | 0 | 136 | 0 | [7 empty] | Energy not Served | 0
2:30 | 5082 | 797.5 | 1966.5 | 2838 | 629 | 54 | 405 | 0 | 137 | 0 | [7 empty] | Energy Requirement | 279.6463
3:00 | 5081 | 797 | 1964 | 2722 | 619 | 54 | 386 | 0 | 138 | 0
3:30 | 5088 | 797 | 1971.5 | 2614 | 619 | 53 | 386 | 0 | 138 | 0 | [6 empty] | Shortage
4:00 | 5095 | 797 | 1979 | 2506 | 619 | 52 | 386 | 0 | 138 | 0
4:30 | 5090.5 | 797 | 1964 | 2405 | 609 | 52 | 385.5 | 0 | 136 | 0
5:00 | 5086 | 797 | 1949 | 2304 | 599 | 52 | 385 | 0 | 134 | 0
5:30 | 4972.5 | 797 | 1920.5 | 1993.5 | 559.5 | 52 | 385 | 0 | 126 | 3
6:00 | 4859 | 797 | 1892 | 1683 | 520 | 52 | 385 | 0 | 118 | 6
6:30 | 4860 | 797 | 1869 | 1616.5 | 510 | 52.5 | 367.5 | 0 | 115 | 13 |  |  |  |  | Coal
7:00 | 4861 | 797 | 1846 | 1550 | 500 | 53 | 350 | 0 | 112 | 20
7:30 | 4877 | 797 | 1813 | 1558 | 490 | 53 | 350 | 0 | 117 | 37.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4893 | 797 | 1780 | 1566 | 480 | 53 | 350 | 0 | 122 | 55
8:30 | 4959 | 797 | 1828 | 1635.5 | 480 | 53.5 | 348 | 0 | 126 | 66
9:00 | 5025 | 797 | 1876 | 1705 | 480 | 54 | 346 | 0 | 130 | 77
9:30 | 5071 | 797 | 1839 | 1839 | 485 | 54 | 354 | 0 | 130 | 95.5
10:00 | 5117 | 797 | 1802 | 1973 | 490 | 54 | 362 | 0 | 130 | 114
10:30 | 5116.5 | 797 | 1777 | 1980.5 | 495 | 54 | 362 | 0 | 131 | 111
11:00 | 5116 | 797 | 1752 | 1988 | 500 | 54 | 362 | 0 | 132 | 108
11:30 | 5106.5 | 797.5 | 1772 | 2142.5 | 500 | 54 | 370 | 0 | 136 | 114
12:00 | 5097 | 798 | 1792 | 2297 | 500 | 54 | 378 | 0 | 140 | 120
12:30 | 5086.5 | 797.5 | 1792.5 | 2449.5 | 515 | 69 | 366.5 | 0 | 142 | 115.5
13:00 | 5076 | 797 | 1793 | 2602 | 530 | 84 | 355 | 0 | 144 | 111
13:30 | 5076 | 797 | 1793 | 2602 | 530 | 84 | 355 | 0 | 144 | 111
14:00 | 5076 | 797 | 1793 | 2602 | 530 | 84 | 355 | 0 | 144 | 111
14:30 | 5056.5 | 797 | 1789 | 2801 | 545 | 83.5 | 356.5 | 0 | 140 | 90.5
15:00 | 5037 | 797 | 1785 | 3000 | 560 | 83 | 358 | 0 | 136 | 70
15:30 | 5031.5 | 797 | 1786.5 | 2997 | 565 | 81 | 360 | 0 | 134 | 64.5
16:00 | 5026 | 797 | 1788 | 2994 | 570 | 79 | 362 | 0 | 132 | 59
16:30 | 5020.5 | 797.5 | 1761 | 2643 | 570 | 80 | 346 | 0 | 124 | 35.5
17:00 | 5015 | 798 | 1734 | 2292 | 570 | 81 | 330 | 0 | 116 | 12
17:30 | 4917 | 798 | 1618 | 2181.5 | 565 | 82 | 339 | 0 | 110 | 8.5
18:00 | 4819 | 798 | 1502 | 2071 | 560 | 83 | 348 | 0 | 104 | 5
18:30 | 4927 | 797.5 | 1563.5 | 2232.5 | 560 | 78.5 | 426.5 | 0 | 119 | 2.5
19:00 | 5035 | 797 | 1625 | 2394 | 560 | 74 | 505 | 0 | 134 | 0
19:30 | 5122 | 798 | 1735 | 3612 | 620 | 65 | 541 | 0 | 140 | 0
20:00 | 5109 | 797 | 1771 | 3703 | 630 | 74 | 588 | 0 | 140 | 0
20:30 | 5109.5 | 797.5 | 1797.5 | 3749.5 | 650 | 75.5 | 598.5 | 0 | 139 | 0
21:00 | 5110 | 798 | 1824 | 3796 | 670 | 77 | 609 | 0 | 138 | 0
21:30 | 5096 | 797.5 | 1832 | 3792.5 | 670 | 77 | 607 | 0 | 135 | 0
22:00 | 5082 | 797 | 1840 | 3789 | 670 | 77 | 605 | 0 | 132 | 0
22:30 | 5085.5 | 797 | 1844.5 | 3796 | 669.5 | 79 | 602 | 0 | 128 | 0
23:00 | 5089 | 797 | 1849 | 3803 | 669 | 81 | 599 | 0 | 124 | 0
23:30 | 5014.5 | 797 | 1879 | 3803 | 669.5 | 82.5 | 568.5 | 0 | 127 | 0 | Max Temp. in Dhaka |  | 35.8° C
24:00 | 4940 | 797 | 1909 | 3803 | 670 | 84 | 538 | 0 | 130 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 279.646 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 279.646 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-12
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 29 | 29 | 29 | 27 | 27 | 27 | 28 | 28 | 29 | 29 | 29 | 29 | 59 | 58 | 58 | 54 | 56 | 58 |  | 49 | 40 | 49 | 52 | 52 | 56 | 59 | 992204
2 | Karnaphuli Hydro PP Unit-4 & 5 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  |  | 9 | 25 | 25 | 25 | 25 |  | 23 | 25 | 22 | 25 | 25 | 25 | 25 | 566634
| Teknaf 20MW PP (Solartech) | [5 empty] | 2 | 5 | 9 | 17 | 18 | 19 | 20 | 17 | 5 | 2 | 11 | 2 | 0 | [8 empty] | 121230
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 214 | 205 | 203 | 203 | 208 | 206 | 216 | 203 | 202 | 203 | 214 | 205 | 204 | 217 | 204 | 204 | 203 |  | 217 | 203 | 204 | 203 | 203 | 205 | 203 | 4825409
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2615614
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 38 | [17 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 387999
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 85 | 89 | 89 | 89 | 89 | 89 | 51 | 51 |  | 58 | 85 | 86 | 89 | 89 | 105 | 93 | 2126027
| Daudkandi 200 MW PP (B.Trac) | [20 empty] | 60 | 30 |  |  |  |  | 62592
14 | Titas 50 MW Peaking PP | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 49 | 49 | 48 | 48 | 48 | 48 |  | 48 | 49 | 49 | 49 | 49 | 49 | 49 | 1078504
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 328 | 328 | 328 | 328 | 333 | 270 | 270 | 270 | 332 | 329 | 327 | 320 | 322 | 323 | 318 | 319 | 290 | 250 |  | 250 | 326 | 326 | 326 | 330 | 329 | 329 | 7565958
18 | Kodda 300 MW PP Unit-2 (Summit) | 282 | 145 | 45 | [6 empty] | 15 | 15 | 20 | 104 | 121 | 180 | 195 | 145 | 160 |  | 160 | 200 | 265 | 288 | 288 | 288 | 288 | 3231708
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 267636
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 80 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 160 | 160 |  | 160 | 160 | 160 | 160 | 160 | 160 | 0 | 2835000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7144091
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1987086
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 582192
33 | Ashuganj 225 MW CCPP | 212 | 212 | 213 | 214 | 216 | 216 | 216 | 214 | 213 | 214 | 213 | 210 | 210 | 200 | 176 | 181 | 171 | 206 |  | 210 | 215 | 216 | 213 | 214 | 214 | 215 | 5046000
34 | Ashuganj 450 MW CCPP(South) | 280 | 290 | 280 | 275 | 270 | 270 | 270 | 290 | 285 | 295 | 295 | 310 | 295 | 295 | 320 | 295 | 270 | 270 |  | 325 | 270 | 270 | 280 | 270 | 275 | 270 | 6933000
| Ashuganj 450 MW CCPP(North) | 270 | 285 | 270 | 265 | 260 | 265 | 265 | 280 | 290 | 310 | 310 | 315 | 310 | 310 | 320 | 280 | 275 | 275 |  | 330 | 275 | 275 | 285 | 260 | 265 | 260 | 7209000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 55 | 56 | 55 | 56 | 57 | 56 | 56 | 56 | 54 | 50 | 50 | 52 | 53 | 51 | 50 | 51 |  | 51 | 51 | 55 | 54 | 53 | 55 | 55 | 1296480
36 | Chandpur 150 MW CCPP | 90 | 90 | 90 | 91 | 90 | 90 | 90 | 91 | 91 | 90 | 84 | 90 | 89 | 87 | 90 | 86 | 89 | 90 |  | 90 | 90 | 89 | 90 | 91 | 91 | 90 | 2127880
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 326 | 326 | 326 | 326 | 327 | 326 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 327 | 326 | 326 |  | 326 | 326 | 327 | 326 | 326 | 326 | 326 | 7974910
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5640050
41 | Haripur 360MW CCPP(HPL) | 343 | 346 | 345 | 347 | 348 | 350 | 349 | 348 | 312 | 282 | 251 | 232 | 232 | 231 | 232 | 241 | 252 | 252 |  | 232 | 232 | 230 | 225 | 225 | 226 | 290 | 6758000
42 | RPCL 210MW CCPP | 169 | 169 | 173 | 187 | 185 | 184 | 181 | 170 | 159 | 156 | 150 | 144 | 143 | 145 | 142 | 148 | 144 | 168 |  | 153 | 152 | 149 | 144 | 144 | 144 | 151 | 3722880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 10 | 25 | 42 | 53 | 54 | 56 | 55 | 51 | 30 | 29 | 6 | 2 | [8 empty] | 417270
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 42 | 43 | 42 | 43 |  | 44 | 44 | 43 | 43 | 43 | 43 | 43 | 1032000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 711480
46 | Shajibazar 330 MW CCPP | 163 | 162 | 162 | 161 | 162 | 163 | 162 | 162 | 163 | 161 | 161 | 160 | 161 | 161 | 160 | 160 | 159 | 161 |  | 160 | 163 | 163 | 161 | 162 | 162 | 163 | 3606000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 56 | 56 | 56 | 56 | 62 | 40 | 40 | 61 | 60 | 61 | 60 | 60 | 60 | 59 | 60 | 60 | 40 |  | 60 | 61 | 61 | 60 | 61 | 56 | 56 | 1342
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 20 | 20 | 78 | 81 | 81 | 82 | 82 | 81 | 81 | 81 | 81 | 50 |  | 70 | 79 | 80 | 83 | 83 | 83 | 83 | 1773120
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 219 | 219 | 219 | 218 | 218 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 220 | 220 | 220 | 180 |  | 212 | 220 | 219 | 219 | 219 | 219 | 211 | 5225970
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 377000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 238140
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | [5 empty] | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 |  | 11 | 11 | 11 | 184944
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 17 | 47 | 47 | 50 | 50 | 50 | 53 | 52 | 52 | 52 | 14 |  | 20 | 53 | 53 | 53 | 53 | 53 | 53 | 1144800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 369000
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 300 | 305 | 290 | 270 | 300 | 310 | 310 | 290 | 290 | 300 | 300 | 280 | 300 | 300 | 285 | 280 |  | 290 | 265 | 280 | 290 | 300 | 300 | 300 | 7221500
| Bibiyana South 400 MW | 390 | 394 | 394 | 396 | 401 | 400 | 400 | 397 | 396 | 398 | 392 | 390 | 390 | 389 | 376 | 388 | 383 | 350 |  | 370 | 398 | 399 | 390 | 394 | 393 | 400 | 9377600
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 40 | 55 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 1217454
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 20 | 18 | 18 | 18 | 19 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 564000
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 19 | 21 | 22 | 22 |  | 22 | 22 | 22 | 19 | 19 | 21 | 21 | 505728
61 | Narshingdi 22 MW PP (Doreen) |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 18 | 18 |  | 13 | 17 | 17 | 17 | 17 |  |  |  |  | 16 |  |  | 16 | 276192
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 17 | 17 | 17 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 431496
63 | Impoprt (Tripura) | 160 | 136 | 138 | 138 | 134 | 118 | 112 | 122 | 130 | 130 | 132 | 140 | 144 | 150 | 136 | 132 | 116 | 104 |  | 134 | 140 | 140 | 138 | 132 | 124 | 130 | 3189120
64 | Malancha, Ctg. EPZ (United) | 39 | 40 | 40 | 40 | 40 | 40 | 35 | 4 | 2 | 2 | 2 | 3 | 5 | 3 | 2 | 2 | 2 | 7 |  | 6 | 6 | 16 | 26 | 35 | 37 | 39 | 448320
65 | Feni 22MW PP (Doreen) |  | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 22 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 482148
66 | Feni 11 MW PP (Doreen) | 5 | 11 | 11 | 11 | 11 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 214380
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 815600
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 442050
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 9 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 25 | 25 | 25 | 25 | 25 | 543420
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 822500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 817600
73 | Ghorashal 108MW PP (Regent) | 102 | 99 | 99 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 100 | 96 | 96 | 98 | 97 | 98 | 98 | 74 |  | 94 | 95 | 105 | 105 | 105 | 105 | 105 | 2339727
| Feni Lanka Power | 100 | 80 | 80 | 90 | 90 | 68 | 72 | 72 | 54 | 72 | 100 | 90 | 90 | 68 | 80 | 80 | 62 | 80 |  | 70 | 70 | 70 | 52 | 70 | 52 | 52 | 1836540
| Chowmuhani 113 MW | 117 | 117 | 118 | 117 | 115 | 114 | 85 | 85 | 102 | 114 | 115 | 113 | 107 | 105 | 110 | 107 | 65 | 65 |  | 71 | 114 | 113 | 115 | 115 | 107 | 107 | 2561160
| Manikgonj 162MW PP(MPGL) | 126 | 126 | 126 | 126 | 90 | 17 | 17 | 17 | 63 | 86 | 126 | 126 | 126 | 126 | 126 | 126 | 54 | 54 |  | 66 | 126 | 126 | 126 | 126 | 126 | 126 | 2455200
77 | Siddhirganj 100 PP(Dutch Bangla) | 99 | 99 | 99 | 99 | 99 | 90 | 50 | 50 | 60 | 80 | 90 | 95 | 100 | 100 | 100 | 100 | 70 | 50 |  | 55 | 80 | 80 | 100 | 100 | 100 | 100 | 2152550
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 42 | 42 | 42 | 33 | 33 | 33 | 26 | 26 | 34 | 42 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1003200
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 150 | 150 | 115 | 115 | 115 | 133 | 133 | 150 | 147 | 147 | 147 | 147 | 115 | 115 |  | 144 | 150 | 150 | 150 | 150 | 150 | 150 | 3323040
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 168960
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 40 | 34 | 43 | 43 | 8 | 8 | 8 | 10 | 28 | 43 | 43 | 43 | 43 | 43 | 43 | 25 | 25 |  | 25 | 35 | 43 | 43 | 43 | 43 | 43 | 851443
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | [10 empty] | 20 | 65 | 105 | 105 | 105 | 105 | 1648800
| Kaptai 7 MW Solar PP | [8 empty] | 2 | 3 | 6 | 5 | 5 | 5 | 4 | 3 | 1 | [9 empty] | 34527
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 51 | 51 | 51 | 65 | 92 | 95 | 95 | 89 | 75 | 75 | 88 | 51 | 34 |  | 42 | 95 | 91 | 110 | 110 | 110 | 110 | 2182909
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 40 | [7 empty] | 11 | 50 | 50 | 50 | 50 | 50 | 50 | 40 | 20 | 20 |  | 32 | 80 | 79 | 84 | 85 | 86 | 86 | 927468
86 | Meghnaghat CCPP ( Summit) | 280 | 280 | 265 | 280 | 280 | 280 | 275 | 295 | 280 | 265 | 260 | 285 | 280 | 240 | 305 | 250 | 275 | 270 |  | 305 | 250 | 240 | 275 | 260 | 290 | 250 | 6632029
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 100 | [10 empty] | 11 | 21 | 64 | 104 | 104 | 104 | 104 |  | 104 | 104 | 104 | 104 | 104 | 104 | 104 | 1314240
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 88 | 88 | 72 | 72 | 72 | 70 | 70 | 70 | 70 | 83 | 83 | 78 | 78 | 78 | 78 | 78 | 50 |  | 67 | 86 | 85 | 85 | 85 | 85 | 88 | 1829640
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 798432
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | [6 empty] | 16 | 50 | 60 | 85 | 85 | 85 | 93 | 64 | 64 | 64 |  | 75 | 93 | 94 | 94 | 94 | 94 | 94 | 1286640
95 | Patenga 50MW PP (Baraka) | [19 empty] | 1 | 28 | 36 | 46 | 46 | 46 | 47 | 225120
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 15 | 15 | [9 empty] | 11 | 14 | 30 | 30 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 577859
100 | Manikganj 55 MW PP (Northern) | 55 | [10 empty] | 17 | 17 | 35 | 35 | 55 | 17 | 17 |  | 17 | 55 | 55 | 55 | 55 | 55 | 55 | 581008
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 3 |  | 1 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 13900
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 35 |  | 44 | 54 | 54 | 54 | 54 | 54 | 54 | 1265760
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 10 | 61 | 26 | 26 |  |  | 0 | 110329
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 25 |  |  |  |  | 0 | 20104
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 194 | 194 | 170 | 80 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 115 | 130 | 158 | 120 | 120 |  | 136 | 190 | 192 | 192 | 192 | 182 | 182 | 3316800
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 52 | 27 |  |  |  | 27 | 57723
114 | Kodda 149 MW PP Unit-1 (Summit) | 115 | [9 empty] | 43 | 105 | 100 | 100 | 100 | 114 | 118 | 96 |  | 139 | 149 | 149 | 149 | 147 | 149 | 149 | 1828800
115 | Juldah 100 MW PP Unit-3 (Acorn) | [8 empty] | 10 | 10 | 10 | 30 | 100 | 100 | 100 | 100 | 50 | 10 |  | 30 | 100 | 100 | 100 | 100 | 100 | 100 | 1016640
116 | Chandpur 200MW (Desh energy) | 22 | 93 | 100 | 70 | 70 | 84 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 67 | 70 | 51 |  | 57 | 99 | 135 | 160 | 179 | 180 | 180 | 2055840
117 | Ashuganj 150MW PP (Midland) | 148 | 147 | 147 | 148 | 148 | 147 | 143 | 140 | 142 | 142 | 140 | 140 | 138 | 140 | 138 | 140 | 70 | 70 |  | 83 | 100 | 133 | 145 | 147 | 147 | 147 | 3288581
118 | Bibiyana-III 400 MW CCPP | 404 | 404 | 404 | 403 | 402 | 402 | 402 | 404 | 403 | 404 | 403 | 405 | 411 | 413 | 372 | 405 | 405 | 352 |  | 379 | 402 | 402 | 404 | 401 | 404 | 403 | 9625000
| Jamalpur 115 MW PP (United) | 106 | 106 | 106 | 106 | 106 | 115 | 115 | 115 | 115 | 115 | 106 | 106 | 95 | 95 | 95 | 95 | 105 | 95 |  | 95 | 95 | 95 | 95 | 95 | 86 | 96 | 2451600
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 10 | 10 | 10 | 10 | 10 | 27 | 90 | 90 | 100 | 100 | 100 | 50 | 10 |  | 40 | 100 | 100 | 100 | 100 | 100 | 100 | 1661760
| Anlima Energy Ltd. | 96 | 96 | 95 | 96 | 94 | 95 | 95 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 96 |  | 95 | 95 | 94 | 92 | 82 | 95 | 95 | 2274491
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 883440
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 18 | 8 | 30 | 14 | 27 | 21 | 28 | 26 | 9 | 1 | 2 | [8 empty] | 203700
120 | Eastern Zone Total | 8602 | 8201 | 8021 | 7973 | 7890 | 7415 | 7201 | 7224 | 7456 | 7684 | 7673 | 7933 | 8081 | 8143 | 8310 | 8292 | 7642 | 7243 |  | 7822 | 8713 | 8822 | 8963 | 8931 | 8940 | 8855 | 193953218
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 7 | [14 empty] | 4 | 4 | 4 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 112320
| Khulna 225 MW CCPP | [19 empty] | 40 | 60 | 85 | 100 | 100 | 100 | 40 | 444579
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 21 | 70 | 70 | 70 | 70 | 53 | 35 |  | 39 | 105 | 105 | 105 | 105 | 105 | 105 | 1511040
130
131
132 | United Payra Power Ltd. | 35 | 35 | 35 | 35 | 35 | [14 empty] | 17 | 35 | 54 | 54 | 54 | 54 | 54 | 469200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 222 | 223 | 223 | 223 | 223 | 222 | 222 | 221 | 220 | 220 | 220 | 220 | 218 | 218 | 218 | 153 | 130 |  | 152 | 220 | 218 | 221 | 222 | 221 | 221 | 5135482
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [21 empty] | 16 | 16 | 16 | 32 | 0 | 72576
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 281779
| Bhola 225 MW CCPP | 85 | 84 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 84 | 83 | 86 | 84 |  | 85 | 86 | 85 | 88 | 85 | 86 | 86 | 2062599
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 31 | 31 | 28 | 26 | 25 | 20 | 20 | 20 | 20 | 21 | 21 | 24 | 24 | 24 | 21 | 18 |  | 28 | 32 | 32 | 33 | 34 | 34 | 34 | 625625
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 50 | 50 | [15 empty] | 1 | 100 | 90 | 100 | 100 | 100 | 100 | 871680
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 796 | 798 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 797 | 798 | 797 | 797 | 797 | 797 | 798 | 798 |  | 797 | 798 | 797 | 798 | 797 | 797 | 797 | 19264000
147 | Bheramara 410 MW CCPP | 400 | 400 | 400 | 400 | 400 | 300 | 300 | 300 | 340 | 400 | 400 | 395 | 390 | 395 | 385 | 395 | 400 | 340 |  | 370 | 410 | 410 | 405 | 405 | 400 | 400 | 9365760
148 | Payra 1320 MW | 530 | 490 | 470 | 470 | 450 | 370 | 350 | 330 | 330 | 340 | 350 | 350 | 380 | 390 | 410 | 420 | 420 | 410 |  | 410 | 470 | 480 | 520 | 520 | 520 | 520 | 11256200
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 3662100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1097440
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 3 | 3 | 5 | 5 | 5 | 1 | 0 | 0 | 0 | 0 | [8 empty] | 28740
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 177 | 182 | 186 | 186 | 181 | 159 | 167 | 164 | 174 | 183 | 187 | 170 | 179 | 173 | 181 | 175 | 174 | 171 |  | 170 | 178 | 168 | 175 | 179 | 179 | 179 | 4456555
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 190 | 194 | 194 | 190 | 157 | 170 | 182 | 199 | 198 | 200 | 197 | 196 | 196 | 196 | 200 | 199 | 191 |  | 180 | 199 | 198 | 191 | 193 | 194 | 194 | 4837527
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 407 | 415 | 412 | 416 | 404 | 366 | 358 | 356 | 404 | 379 | 362 | 408 | 407 | 384 | 396 | 391 | 409 | 323 |  | 370 | 379 | 379 | 409 | 405 | 410 | 404 | 9471800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [7 empty] | 14 | 18 | 35 | 48 | 48 | 42 | 42 | 455069
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  |  | 9 | 20 | 20 | 22 | 22 | 22 | 22 | 452640
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 260046
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 43 | [5 empty] | 8 | 8 | 8 | 34 | 43 | 43 | 43 | 50 | 25 | 25 |  | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 620746
167 | Katakhali 50 MW Peaking PP | 32 | 31 | 31 | 31 | 30 | 30 | 30 | 30 | 26 | 24 | 24 | 24 | 24 | 24 | 30 | 30 | 30 | 30 |  | 30 | 34 | 39 | 32 | 30 | 30 | 30 | 628704
168 | Santahar 50 MW Peaking PP | [17 empty] | 18 |  | 29 | 30 | 30 | 30 | 28 | 28 | 27 | 166829
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 16 | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 |  | 25 | 25 | 46 | 46 | 52 | 52 | 52 | 1051680
170 | Chapainawabganj 100 MW Peaking PP | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 92 | 92 | 90 | 90 | 90 | 90 | 90 |  | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 2183928
171 | Baghabari 200 MW PP (Paramount) | [20 empty] | 60 | 40 |  |  |  | 0 | 52315
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 35 | 35 | [7 empty] | 67 | 79 | 94 | 70 | 35 | 35 |  | 40 | 94 | 91 | 94 | 94 | 94 | 94 | 1332768
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 35 |  |  |  | 20 | 35 | 35 | 55 | 70 | 95 | 95 | 95 | 50 | 35 |  | 50 | 90 | 95 | 95 | 95 | 95 | 95 | 1635552
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 70 | 60 |  |  |  | 12 | 35 | 10 | 45 | 70 | 92 | 110 | 110 | 70 | 69 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 1768252
177 | Sympa Solar Power 8MW | [5 empty] | 0 |  | 0 | 3 | 5 | 7 | 7 | 7 | 7 | 6 | 6 | 2 | 1 | [8 empty] | 57509
178
178