## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-18 | Sunday
|  |  | Date (day): | 2021-07-18 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14534.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15478 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-17 | 2021-07-18 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 103 | 189 | 190 | 190 |  | 70 | Machine problem
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 0 | 0 | 0 |  | 190 | Under maint
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 32 | 99 | 108 | 108
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 277 | 277 | 325 | 325 | 87 |  | Gas shortage
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 208 | 135 | 260 | 270 | 90 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 220 | 220 | 220 | 220 | 230 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 275 | 300 | 305 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 87 | 85 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 16 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 90 | 95 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 334 | 335 | 335
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 94 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 115 | 150 | 150 | 150
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 47 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 24 | 52 | 52
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 45 | 260 | 250 | 300
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 58 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 53 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 87 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 104 | 104 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 18 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5819 | 2834 | 3543 | 3980 | 4232 | 776 | 770
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 14 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 89 | 119 | 88 | 88 | 142 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 204 | 203 | 225 | 225 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 110 | 120 | 110 | 110 |  | 40 | Machine problem
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Engine problem
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 82 | 94 | 100 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 40 | 100 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 0 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 23 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 68 | 110 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 70 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 91 | 95 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1026 | 1295 | 1591 | 1681 | 510 | 189
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 100 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 212 | 194 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 285 | 360 | 360 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 275 | 275 | 300 | 320 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 56 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 34 | 34 | 34 | 34 |  | 17 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 135 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 41 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 135 | 136 | 135 | 135 |  | 28 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 51 | 200 | 170 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 94 | 122 | 148 | 172
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 14 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 100 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 34 | 114 | 34 | 114
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 104 | 117 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 36 | 36 |  | 18 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1662 | 2103 | 2159 | 2448 | 316 | 225
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 142 | 117 | 155 | 140 | 62 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 21 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 2 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 202 | 195 | 175 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 8 | 107 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 16 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 414 | 472 | 547.6 | 506 | 62 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 163 | 162 | 163 | 163 |  | 167 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 61 | 62 | 63
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 225 | 225 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 300 | 300 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 364 | 417 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 400 | 400 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1709 | 1787 | 1783 | 1784 | 0 | 556
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 791 | 791 | 823 | 823
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 15 | 0 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 130 | 0 | 160 |  | 70 | ST not available
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 315 | 260 | 350 | 350 | 60 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 70 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2129 | 1180 | 1401 | 1428 | 1718 | 60 | 153
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 64 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 26 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 72 | 81 | 70 | 70 | 25 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 280 | 280 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 181 | 221 | 220 | 220 |  |  | On Test
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 150 | 110 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 558 | 830 | 1158 | 1165 | 25 | 194
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 20 | 40 |  | 31 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 43 | 0 | 43 | 43 |  | 7 | Engine problem
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 40 | 40 |  | 10 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 210 | 210 |  |  | FGMO
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 182 | 175 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 414 | 410 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 16 | 8 | 8
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 60 | 91 | 95 | 95
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 5 | 94 | 94 | 94 |  | 19 | Engine problem
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 90 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1027 | 1291 | 1547 | 1591 | 380 | 102
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 72 | 70 | 70 |  | 15 | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 149 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 2 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 260 | 334 | 341 | 353 | 124 | 120
|  | Total |  |  |  |  | 22023 | 21060 | 10670 | 13056 | 14534.6 | 15478 | 2253 | 2396
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10216.4269 | 12501 | 13916.7459 | 14820.0427
| A. |  | 2021-07-17 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13056 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9712 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13056 | MW
| 3 | Day peak Generation : |  |  | 10670 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12501 | MW
| 4 | Evening peak Generation : |  |  | 13056 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 274.9918 | MKWHr | By Solar | 0.44592 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 159.7139 | MKWHr |  | By Oil: | 78.3618 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.7823 | MKWHr |  | By Hydro: | 1.9929 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2253 | MW | Dhaka | 4313 | 4313 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2396 | MW | Chittagong | 1307 | 1307 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4649 | MW | Khulna | 1626 | 1626 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1214.9 | MMCFD |  |  | Rajshahi | 1341 | 1341 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 167071641.664 | ii) Oil : | Taka | 561690930.74 | Comilla | 1209 | 1209 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 62651524.3 | Total | Taka | 791414096.704 | Mymensingh | 1022 | 1022 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.644 | MKWHr. | Sylhet | 500 | 500 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -526 | MW (E to W) at | 21:00 | hrs | Barisal | 397 | 397 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -560 | MW at | 19:30 | hrs | Rangpur | 786 | 786 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.4° C |  |  | Total | 12501 | 12501 |  | 0
| B. |  | 2021-07-18 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 33.3° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15478 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 2178 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 280.131 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9707 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.1673 | MKWHr. | ii) HVDC Flow at Peak Time |  | 791 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.5277 | MKWHr. | iii) Maximum HVDC Flow : |  | 798 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.58 |  | (b) Today: | 82.58 |  | (c) Rule Curve: |  | 86.72
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-17
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 103 | 0 | 110 | 300 | 31 | 0 | 277 | 332 |  | 0 | 220 | 280 | 0 | 0 | 45 | 338 | 0 | 0 | 95 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 17 | 25 | 22 | 33 | 33 | 51 | 0 | 56 | 30 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 25 | 270 | 216 | 73 | 138 | 26 | 56 | 0 | 34 | 0 | 48 | 43 | 22 | 11 | 25 | 20 | 128 | 154 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 162 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 245 | 0 | 0 | 194 | 0 | 123 | 0 | 20 | 194 | 150 | 367 | 102 | 105 | 85 | 0 | 0 | 0 | 110 | 34 | 109 | 100 | 400 | 104 | 0 | 162 | 111 | 0 | 36 | 0 |  | 798 | 0 | 325 | 0 | 0 | 40 | 0 | 0 | 4 | 0 | 0 | 0 | 34 | 110 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 43 | 29 | 25 | 27 | 22 | 0 | 11 | 48 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 71 | 100 | 187 | 0 | 306 | 105 | 0 | 94 | 40 | 113 | 0 | 0 | 113 | 280 | 220 | 0 | 150 | 0 |  | 8566 | 3779 | 12345 | 4711 | 798 | 1873 | 3763 | 477 | 86 | 509 | 128 | 0 | 0 | 82.53
2:00 | 0 | 103 | 0 | 110 | 300 | 31 | 0 | 277 | 346 |  | 0 | 220 | 275 | 0 | 0 | 15 | 338 | 0 | 0 | 95 | 16 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 17 | 25 | 22 | 33 | 33 | 51 | 0 | 58 | 30 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 51 | 100 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 30 | 270 | 216 | 73 | 137 | 26 | 56 | 0 | 34 | 0 | 48 | 43 | 22 | 11 | 25 | 20 | 126 | 153 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 195 | 0 | 0 | 194 | 0 | 56 | 0 | 20 | 189 | 147 | 365 | 102 | 105 | 85 | 0 | 0 | 0 | 85 | 34 | 108 | 100 | 400 | 0 | 0 | 162 | 111 | 0 | 36 | 0 |  | 798 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 34 | 97 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 43 | 29 | 25 | 21 | 22 | 0 | 11 | 77 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 100 | 187 | 0 | 362 | 105 | 0 | 94 | 40 | 113 | 0 | 0 | 113 | 280 | 222 | 0 | 150 | 0 |  | 8242 | 3811 | 12053 | 4718 | 798 | 1949 | 3405 | 506 | 88 | 463 | 126 | 0 | 0 | 82.54
3:00 | 0 | 103 | 0 | 110 | 300 | 31 | 0 | 277 | 346 |  | 0 | 220 | 280 | 0 | 0 | 15 | 334 | 0 | 0 | 95 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 17 | 25 | 22 | 28 | 33 | 51 | 0 | 58 | 30 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 80 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 60 | 270 | 217 | 73 | 138 | 26 | 56 | 0 | 34 | 0 | 32 | 43 | 22 | 11 | 25 | 20 | 124 | 153 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 163 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 23 | 0 | 20 | 193 | 147 | 365 | 103 | 105 | 85 | 0 | 0 | 0 | 85 | 34 | 106 | 100 | 400 | 0 | 0 | 162 | 93 | 0 | 36 | 0 |  | 798 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 34 | 80 | 0 | 0 | 0 | 50 | 0 | 90 | 35 | 0 | 29 | 25 | 20 | 22 | 0 | 11 | 78 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 70 | 187 | 0 | 359 | 105 | 0 | 94 | 46 | 70 | 0 | 0 | 113 | 280 | 223 | 0 | 150 | 0 |  | 7929 | 3667 | 11596 | 4747 | 798 | 1946 | 3010 | 508 | 88 | 375 | 124 | 0 | 0 | 82.55
4:00 | 0 | 104 | 0 | 110 | 300 | 31 | 0 | 277 | 346 |  | 0 | 220 | 285 | 0 | 0 | 0 | 334 | 0 | 0 | 95 | 0 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 17 | 25 | 22 | 28 | 33 | 51 | 0 | 58 | 30 | 100 | 0 | 25 | 213 | 0 | 110 | 0 |  | 22 | 0 | 0 | 92 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 140 | 270 | 212 | 73 | 138 | 26 | 55 | 0 | 34 | 0 | 0 | 16 | 22 | 11 | 25 | 20 | 122 | 153 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 162 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 17 | 0 | 20 | 100 | 147 | 377 | 103 | 105 | 85 | 0 | 0 | 0 | 85 | 34 | 108 | 100 | 400 | 0 | 0 | 108 | 93 | 0 | 36 | 0 |  | 798 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 29 | 25 | 20 | 22 | 0 | 11 | 75 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 20 | 187 | 0 | 362 | 105 | 0 | 94 | 46 | 70 | 0 | 0 | 113 | 280 | 224 | 0 | 150 | 0 |  | 7749 | 3571 | 11320 | 4848 | 798 | 1959 | 2693 | 504 | 88 | 308 | 122 | 0 | 0 | 82.56
5:00 | 0 | 103 | 0 | 110 | 300 | 31 | 0 | 277 | 346 |  | 0 | 220 | 265 | 0 | 0 | 0 | 334 | 0 | 0 | 95 | 0 | 115 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 22 | 28 | 33 | 51 | 0 | 28 | 30 | 100 | 0 | 23 | 203 | 0 | 110 | 0 |  | 22 | 0 | 0 | 92 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 160 | 270 | 217 | 73 | 132 | 26 | 56 | 0 | 34 | 0 | 0 | 16 | 22 | 11 | 25 | 18 | 114 | 153 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 16 | 0 | 0 | 50 | 147 | 364 | 103 | 105 | 85 | 0 | 0 | 0 | 85 | 34 | 106 | 100 | 400 | 0 | 0 | 108 | 93 | 0 | 36 | 0 |  | 798 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 32 | 64 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 22 | 25 | 20 | 22 | 0 | 11 | 79 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 187 | 0 | 332 | 105 | 0 | 70 | 50 | 70 | 0 | 0 | 70 | 280 | 222 | 0 | 150 | 0 |  | 7602 | 3452 | 11054 | 4843 | 798 | 1916 | 2515 | 509 | 58 | 301 | 114 | 0 | 0 | 82.57
6:00 | 0 | 103 | 0 | 110 | 300 | 31 | 0 | 277 | 346 |  | 0 | 220 | 260 | 0 | 0 | 0 | 336 | 0 | 0 | 90 | 0 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 22 | 28 | 25 | 51 | 0 | 27 | 30 | 100 | 0 | 25 | 202 | 0 | 110 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 42 | 135 | 0 | 0 | 365 | 270 | 189 | 8 | 134 | 26 | 56 | 0 | 34 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 106 | 165 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 163 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 16 | 1 | 0 | 17 | 20 | 367 | 65 | 105 | 85 | 0 | 0 | 0 | 85 | 34 | 108 | 20 | 350 | 0 | 0 | 17 | 92 | 0 | 36 | 1 |  | 798 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 22 | 25 | 21 | 22 | 0 | 11 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 189 | 0 | 330 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 222 | 0 | 100 | 0 |  | 7180 | 2990 | 10170 | 4990 | 798 | 1822 | 1692 | 502 | 57 | 201 | 106 | 2 | 0 | 82.58
7:00 | 0 | 104 | 0 | 110 | 300 | 31 | 0 | 277 | 336 |  | 0 | 220 | 285 | 0 | 0 | 0 | 333 | 0 | 0 | 85 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 18 | 25 | 22 | 28 | 25 | 51 | 0 | 27 | 30 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 34 | 100 | 0 | 0 | 360 | 270 | 179 | 8 | 138 | 26 | 56 | 0 | 34 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 100 | 190 | 8 | 21 | 0 | 43 | 0 | 53 | 0 | 0 | 162 | 40 | 20 | 0 | 219 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 15 | 2 | 0 | 17 | 10 | 382 | 8 | 105 | 85 | 0 | 0 | 0 | 51 | 34 | 106 | 10 | 350 | 0 | 0 | 17 | 92 | 0 | 36 | 4 |  | 791 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 22 | 25 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 0 | 194 | 0 | 355 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 224 | 0 | 0 | 0 |  | 6976 | 2879 | 9855 | 4976 | 791 | 1793 | 1481 | 503 | 57 | 148 | 100 | 6 | 0 | 82.59
8:00 | 0 | 104 | 0 | 110 | 300 | 32 | 0 | 277 | 313 |  | 0 | 220 | 270 | 0 | 0 | 0 | 332 | 0 | 0 | 87 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 45 | 20 | 25 | 22 | 28 | 33 | 51 | 0 | 27 | 30 | 100 | 0 | 10 | 202 | 0 | 110 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 365 | 270 | 201 | 8 | 130 | 26 | 30 | 0 | 34 | 0 | 0 | 0 | 19 | 0 | 25 | 18 | 100 | 173 | 8 | 21 | 0 | 43 | 0 | 50 | 0 | 0 | 163 | 40 | 20 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 16 | 11 | 0 | 17 | 35 | 366 | 8 | 105 | 92 | 0 | 0 | 0 | 51 | 34 | 108 | 10 | 348 | 0 | 1 | 20 | 92 | 0 | 36 | 8 |  | 792 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 22 | 25 | 0 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 0 | 193 | 0 | 312 | 53 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 280 | 190 | 0 | 0 | 0 |  | 6920 | 2792 | 9712 | 4925 | 792 | 1628 | 1537 | 503 | 57 | 149 | 100 | 21 | 0 | 82.6
9:00 | 0 | 104 | 0 | 110 | 300 | 32 | 0 | 277 | 270 |  | 0 | 220 | 280 | 0 | 0 | 0 | 327 | 0 | 0 | 87 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 18 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 30 | 100 | 0 | 25 | 213 | 0 | 110 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 280 | 290 | 201 | 8 | 136 | 26 | 30 | 0 | 34 | 0 | 0 | 0 | 19 | 0 | 33 | 12 | 92 | 151 | 8 | 21 | 1 | 43 | 0 | 47 | 0 | 0 | 163 | 40 | 81 | 0 | 218 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 202 | 0 | 16 | 17 | 10 | 17 | 128 | 366 | 8 | 105 | 105 | 2 | 0 | 0 | 51 | 34 | 106 | 50 | 400 | 0 | 3 | 58 | 92 | 0 | 36 | 12 |  | 792 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 0 | 0 | 22 | 25 | 0 | 22 | 0 | 11 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 34 | 0 | 191 | 0 | 393 | 70 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 280 | 182 | 0 | 0 | 0 |  | 7189 | 2837 | 10026 | 4904 | 792 | 1690 | 1789 | 500 | 58 | 165 | 92 | 36 | 0 | 82.61
10:00 | 0 | 103 | 0 | 110 | 300 | 32 | 0 | 277 | 239 |  | 0 | 220 | 275 | 0 | 0 | 0 | 327 | 0 | 0 | 87 | 24 | 64 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 22 | 33 | 33 | 51 | 0 | 29 | 30 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 0 | 0 | 0 | 92 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 270 | 280 | 211 | 8 | 139 | 26 | 30 | 0 | 34 | 0 | 0 | 20 | 19 | 0 | 33 | 14 | 100 | 151 | 0 | 18 | 1 | 43 | 0 | 47 | 0 | 0 | 164 | 40 | 81 | 0 | 218 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 202 | 0 | 40 | 17 | 10 | 17 | 145 | 351 | 8 | 105 | 105 | 2 | 0 | 0 | 51 | 34 | 105 | 70 | 400 | 0 | 12 | 143 | 92 | 0 | 36 | 14 |  | 791 | 0 | 340 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 22 | 25 | 0 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 34 | 0 | 187 | 0 | 416 | 70 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 280 | 181 | 0 | 0 | 1 |  | 7333 | 2857 | 10190 | 4858 | 791 | 1681 | 2001 | 502 | 59 | 150 | 100 | 48 | 0 | 82.62
11:00 | 0 | 103 | 0 | 110 | 300 | 32 | 0 | 277 | 218 |  | 0 | 220 | 280 | 0 | 0 | 0 | 327 | 0 | 0 | 87 | 32 | 98 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 29 | 60 | 100 | 0 | 25 | 231 | 0 | 110 | 0 |  | 6 | 0 | 0 | 92 | 0 | 0 | 22 | 2 | 80 | 0 | 0 | 260 | 275 | 215 | 8 | 137 | 23 | 30 | 0 | 34 | 0 | 0 | 43 | 19 | 11 | 33 | 12 | 90 | 150 | 0 | 18 | 1 | 43 | 0 | 47 | 0 | 0 | 162 | 40 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 5 | 0 | 0 | 202 | 0 | 59 | 5 | 10 | 41 | 140 | 366 | 8 | 105 | 105 | 4 | 0 | 0 | 67 | 34 | 104 | 70 | 400 | 0 | 17 | 162 | 92 | 0 | 36 | 14 |  | 791 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 35 | 24 | 15 | 25 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 36 | 0 | 186 | 0 | 402 | 70 | 0 | 0 | 0 | 0 | 0 | 3 | 50 | 280 | 181 | 0 | 0 | 2 |  | 7488 | 2912 | 10400 | 4859 | 791 | 1640 | 2204 | 504 | 89 | 177 | 90 | 46 | 0 | 82.63
12:00 | 0 | 103 | 0 | 110 | 300 | 32 | 0 | 277 | 208 |  | 0 | 220 | 265 | 0 | 0 | 0 | 324 | 0 | 0 | 90 | 48 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 29 | 60 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 24 | 0 | 0 | 82 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 290 | 275 | 212 | 8 | 135 | 26 | 30 | 0 | 34 | 0 | 0 | 43 | 20 | 8 | 33 | 14 | 94 | 142 | 2 | 18 | 2 | 43 | 0 | 47 | 0 | 0 | 163 | 40 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 202 | 0 | 87 | 14 | 40 | 51 | 135 | 364 | 8 | 105 | 105 | 3 | 0 | 0 | 68 | 34 | 104 | 70 | 400 | 17 | 16 | 162 | 91 | 0 | 36 | 18 |  | 791 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 35 | 43 | 0 | 25 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 72 | 0 | 182 | 0 | 414 | 70 | 0 | 5 | 0 | 34 | 0 | 2 | 90 | 280 | 181 | 0 | 0 | 3 |  | 7645 | 3025 | 10670 | 4829 | 791 | 1690 | 2436 | 504 | 89 | 179 | 94 | 58 | 0 | 82.64
13:00 | 0 | 185 | 0 | 0 | 300 | 32 | 0 | 276 | 152 |  | 0 | 220 | 265 | 0 | 0 | 10 | 320 | 0 | 0 | 92 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 16 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 60 | 100 | 0 | 25 | 206 | 0 | 110 | 0 |  | 24 | 0 | 0 | 82 | 0 | 11 | 22 | 7 | 80 | 0 | 0 | 310 | 295 | 213 | 8 | 137 | 26 | 30 | 0 | 34 | 0 | 0 | 43 | 21 | 8 | 33 | 14 | 96 | 129 | 8 | 18 | 2 | 43 | 0 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 95 | 0 | 0 | 202 | 0 | 87 | 8 | 70 | 97 | 137 | 386 | 8 | 105 | 105 | 3 | 0 | 0 | 82 | 34 | 104 | 100 | 400 | 35 | 22 | 162 | 92 | 0 | 36 | 17 |  | 791 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 35 | 43 | 0 | 25 | 0 | 21 | 0 | 8 | 78 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 72 | 0 | 179 | 0 | 408 | 89 | 0 | 50 | 0 | 38 | 0 | 1 | 113 | 280 | 181 | 0 | 0 | 3 |  | 7884 | 3090 | 10974 | 4874 | 791 | 1627 | 2747 | 508 | 88 | 187 | 96 | 56 | 0 | 82.65
14:00 | 0 | 189 | 0 | 0 | 300 | 32 | 0 | 276 | 153 |  | 0 | 220 | 230 | 0 | 0 | 15 | 325 | 0 | 0 | 94 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 60 | 100 | 0 | 25 | 203 | 0 | 110 | 0 |  | 24 | 0 | 0 | 92 | 0 | 25 | 22 | 4 | 80 | 0 | 0 | 290 | 275 | 217 | 8 | 131 | 26 | 30 | 0 | 34 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 0 | 129 | 8 | 18 | 2 | 43 | 0 | 50 | 0 | 0 | 162 | 62 | 84 | 0 | 218 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 135 | 0 | 0 | 202 | 0 | 89 | 9 | 100 | 116 | 143 | 366 | 14 | 105 | 105 | 4 | 0 | 0 | 85 | 34 | 114 | 100 | 400 | 37 | 31 | 162 | 92 | 0 | 36 | 8 |  | 792 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 34 | 0 | 51 | 35 | 43 | 0 | 25 | 0 | 21 | 0 | 8 | 79 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 79 | 0 | 178 | 0 | 333 | 105 | 0 | 68 | 0 | 90 | 0 | 1 | 113 | 280 | 176 | 0 | 0 | 4 |  | 7859 | 3127 | 10986 | 4808 | 792 | 1542 | 2967 | 509 | 88 | 221 | 0 | 59 | 0 | 82.66
15:00 | 0 | 188 | 0 | 0 | 300 | 32 | 0 | 275 | 151 |  | 0 | 220 | 250 | 0 | 0 | 41 | 334 | 0 | 0 | 94 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 22 | 0 | 0 | 80 | 0 | 25 | 22 | 4 | 80 | 0 | 0 | 305 | 275 | 218 | 8 | 136 | 26 | 31 | 0 | 34 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 106 | 129 | 8 | 18 | 2 | 43 | 0 | 50 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 275 | 16 | 5 | 0 | 145 | 0 | 0 | 170 | 0 | 100 | 11 | 100 | 120 | 150 | 366 | 59 | 105 | 105 | 2 | 0 | 0 | 85 | 34 | 110 | 100 | 400 | 72 | 22 | 162 | 92 | 0 | 36 | 4 |  | 792 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 50 | 0 | 51 | 35 | 50 | 0 | 25 | 0 | 21 | 0 | 11 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 80 | 0 | 178 | 0 | 348 | 105 | 0 | 94 | 0 | 113 | 0 | 2 | 113 | 280 | 181 | 0 | 0 | 4 |  | 8094 | 3213 | 11307 | 4846 | 792 | 1557 | 3131 | 503 | 88 | 237 | 106 | 47 | 0 | 82.67
16:00 | 0 | 189 | 0 | 0 | 300 | 32 | 0 | 276 | 153 |  | 0 | 220 | 265 | 0 | 0 | 30 | 334 | 0 | 0 | 95 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 23 | 0 | 0 | 80 | 0 | 25 | 22 | 2 | 80 | 0 | 0 | 305 | 275 | 215 | 8 | 137 | 26 | 31 | 0 | 34 | 0 | 0 | 43 | 21 | 8 | 33 | 20 | 94 | 129 | 8 | 18 | 1 | 43 | 0 | 50 | 0 | 0 | 163 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 145 | 0 | 0 | 100 | 0 | 100 | 0 | 50 | 120 | 140 | 367 | 95 | 105 | 105 | 1 | 0 | 0 | 85 | 34 | 106 | 100 | 400 | 35 | 17 | 126 | 92 | 0 | 36 | 14 |  | 791 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 50 | 0 | 51 | 35 | 24 | 0 | 16 | 0 | 0 | 0 | 11 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 178 | 0 | 358 | 105 | 0 | 94 | 0 | 60 | 0 | 1 | 70 | 280 | 181 | 0 | 14 | 3 |  | 7860 | 3068 | 10928 | 4830 | 791 | 1538 | 2811 | 502 | 88 | 237 | 94 | 37 | 0 | 82.68
17:00 | 0 | 187 | 0 | 0 | 300 | 32 | 0 | 275 | 153 |  | 0 | 220 | 260 | 0 | 0 | 30 | 335 | 0 | 0 | 95 | 48 | 132 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 28 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 80 | 0 | 25 | 22 | 5 | 80 | 0 | 0 | 300 | 275 | 215 | 8 | 135 | 26 | 31 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 102 | 132 | 8 | 18 | 1 | 43 | 0 | 52 | 0 | 0 | 163 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 145 | 0 | 0 | 100 | 0 | 84 | 4 | 50 | 120 | 140 | 367 | 105 | 105 | 105 | 1 | 0 | 0 | 68 | 34 | 106 | 50 | 400 | 35 | 10 | 72 | 92 | 0 | 36 | 5 |  | 791 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 5 | 51 | 35 | 24 | 0 | 16 | 0 | 0 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 78 | 0 | 178 | 0 | 361 | 105 | 0 | 35 | 0 | 34 | 0 | 1 | 35 | 280 | 181 | 0 | 17 | 0 |  | 7728 | 2957 | 10685 | 4823 | 791 | 1553 | 2563 | 501 | 88 | 242 | 102 | 22 | 0 | 82.69
18:00 | 0 | 189 | 0 | 0 | 300 | 53 | 0 | 276 | 153 |  | 0 | 220 | 270 | 0 | 0 | 30 | 280 | 0 | 0 | 55 | 48 | 98 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 16 | 25 | 22 | 33 | 33 | 25 | 0 | 61 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 50 | 0 | 25 | 22 | 2 | 80 | 0 | 0 | 275 | 275 | 216 | 8 | 137 | 26 | 31 | 0 | 34 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 100 | 135 | 8 | 18 | 0 | 43 | 0 | 14 | 0 | 0 | 162 | 40 | 40 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 145 | 0 | 0 | 100 | 0 | 80 | 1 | 50 | 68 | 150 | 367 | 106 | 105 | 68 | 0 | 0 | 0 | 68 | 34 | 65 | 50 | 360 | 35 | 1 | 72 | 81 | 0 | 36 | 2 |  | 791 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 0 | 50 | 5 | 59 | 35 | 16 | 35 | 16 | 15 | 0 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 0 | 178 | 0 | 364 | 53 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 280 | 181 | 0 | 17 | 0 |  | 7280 | 2960 | 10240 | 4706 | 791 | 1504 | 2246 | 501 | 121 | 267 | 100 | 4 | 0 | 82.7
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 189 | 0 | 0 | 300 | 65 | 0 | 277 | 152 |  | 0 | 220 | 295 | 0 | 0 | 30 | 330 | 0 | 0 | 55 | 64 | 150 | 33 | 0 | 0 | 0 | 54 | 17 | 40 | 0 | 25 | 17 | 33 | 33 | 25 | 0 | 59 | 60 | 100 | 0 | 25 | 214 | 0 | 120 | 0 |  | 24 | 0 | 51 | 80 | 0 | 26 | 22 | 4 | 100 | 0 | 0 | 340 | 325 | 216 | 8 | 137 | 26 | 30 | 0 | 34 | 0 | 33 | 25 | 22 | 11 | 33 | 20 | 124 | 136 | 8 | 21 | 0 | 44 | 0 | 21 | 0 | 0 | 160 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 5 | 40 | 145 | 59 | 0 | 132 | 27 | 85 | 0 | 90 | 85 | 150 | 410 | 106 | 105 | 70 | 0 | 0 | 0 | 72 | 34 | 71 | 90 | 385 | 45 | 0 | 73 | 81 | 0 | 36 | 0 |  | 791 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 34 | 7 | 0 | 0 | 0 | 50 | 25 | 91 | 35 | 50 | 28 | 16 | 29 | 18 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 4 | 177 | 0 | 381 | 77 | 0 | 40 | 0 | 113 | 0 | 0 | 70 | 280 | 219 | 0 | 19 | 0 |  | 8147 | 3309 | 11456 | 4978 | 791 | 1641 | 2828 | 501 | 119 | 474 | 124 | 0 | 0 | 82.73
19:30 | 0 | 189 | 0 | 0 | 300 | 95 | 0 | 277 | 147 |  | 0 | 220 | 250 | 0 | 0 | 55 | 334 | 0 | 0 | 70 | 94 | 150 | 85 | 0 | 0 | 0 | 54 | 40 | 55 | 0 | 25 | 17 | 33 | 33 | 32 | 0 | 59 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 45 | 22 | 5 | 100 | 0 | 0 | 285 | 300 | 204 | 8 | 130 | 26 | 30 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 124 | 134 | 8 | 21 | 0 | 43 | 0 | 52 | 0 | 0 | 162 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 260 | 16 | 11 | 100 | 202 | 217 | 25 | 194 | 99 | 149 | 0 | 100 | 150 | 150 | 415 | 106 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 117 | 100 | 400 | 104 | 0 | 162 | 95 | 0 | 36 | 0 |  | 791 | 0 | 270 | 0 | 0 | 60 | 0 | 0 | 23 | 0 | 0 | 0 | 34 | 48 | 0 | 0 | 0 | 50 | 27 | 91 | 35 | 50 | 30 | 16 | 29 | 21 | 0 | 11 | 70 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 100 | 175 | 0 | 374 | 105 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 280 | 204 | 0 | 150 | 0 |  | 9155 | 3784 | 12939 | 4887 | 791 | 1659 | 4308 | 499 | 119 | 552 | 124 | 0 | 0 | 0
20:00 | 0 | 189 | 0 | 0 | 300 | 97 | 0 | 277 | 141 |  | 0 | 220 | 275 | 0 | 0 | 55 | 334 | 0 | 0 | 70 | 94 | 150 | 83 | 0 | 0 | 0 | 54 | 52 | 55 | 0 | 25 | 22 | 33 | 33 | 46 | 0 | 59 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 49 | 22 | 12 | 80 | 0 | 0 | 285 | 295 | 201 | 8 | 130 | 26 | 47 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 122 | 129 | 8 | 21 | 0 | 43 | 0 | 50 | 0 | 0 | 162 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 280 | 16 | 11 | 100 | 225 | 51 | 25 | 194 | 100 | 142 | 0 | 100 | 178 | 150 | 416 | 106 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 117 | 100 | 400 | 104 | 0 | 158 | 94 | 0 | 36 | 0 |  | 791 | 0 | 265 | 0 | 0 | 130 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 48 | 0 | 0 | 0 | 50 | 22 | 91 | 35 | 50 | 38 | 16 | 30 | 22 | 0 | 11 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 82 | 100 | 175 | 0 | 378 | 105 | 50 | 93 | 0 | 113 | 0 | 0 | 113 | 280 | 217 | 0 | 150 | 0 |  | 9091 | 3873 | 12964 | 4855 | 791 | 1716 | 4234 | 502 | 119 | 625 | 122 | 0 | 0 | 82.72
21:00 | 0 | 189 | 0 | 0 | 300 | 99 | 0 | 277 | 135 |  | 0 | 220 | 275 | 0 | 0 | 55 | 334 | 0 | 0 | 95 | 94 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 24 | 0 | 59 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 50 | 0 | 23 | 80 | 0 | 0 | 285 | 275 | 194 | 8 | 136 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 122 | 117 | 8 | 21 | 0 | 43 | 0 | 50 | 0 | 0 | 162 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 16 | 11 | 100 | 260 | 58 | 25 | 195 | 53 | 149 | 0 | 100 | 200 | 150 | 417 | 107 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 117 | 100 | 400 | 104 | 0 | 162 | 95 | 0 | 36 | 0 |  | 791 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 20 | 91 | 35 | 0 | 35 | 16 | 29 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 100 | 175 | 0 | 410 | 105 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 280 | 221 | 0 | 150 | 0 |  | 9200 | 3856 | 13056 | 4811 | 791 | 1777 | 4323 | 501 | 119 | 612 | 122 | 0 | 0 | 82.73
22:00 | 0 | 189 | 0 | 0 | 300 | 104 | 0 | 277 | 132 |  | 0 | 220 | 275 | 0 | 0 | 55 | 335 | 0 | 0 | 96 | 94 | 150 | 86 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 52 | 0 | 59 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 50 | 21 | 33 | 80 | 0 | 0 | 285 | 275 | 200 | 8 | 130 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 122 | 118 | 8 | 21 | 0 | 43 | 0 | 50 | 0 | 0 | 162 | 62 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 11 | 60 | 268 | 30 | 0 | 195 | 52 | 149 | 0 | 100 | 195 | 150 | 402 | 107 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 115 | 100 | 400 | 104 | 0 | 162 | 107 | 0 | 36 | 0 |  | 791 | 0 | 255 | 0 | 0 | 140 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 20 | 91 | 35 | 0 | 35 | 16 | 29 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 82 | 100 | 172 | 0 | 394 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 280 | 220 | 0 | 150 | 0 |  | 9161 | 3813 | 12974 | 4805 | 791 | 1773 | 4235 | 502 | 119 | 627 | 122 | 0 | 0 | 82.74
23:00 | 0 | 189 | 0 | 0 | 300 | 103 | 0 | 277 | 150 |  | 0 | 220 | 300 | 0 | 0 | 30 | 330 | 0 | 0 | 96 | 72 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 28 | 33 | 33 | 52 | 0 | 27 | 60 | 100 | 0 | 26 | 217 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 50 | 21 | 33 | 80 | 0 | 0 | 305 | 295 | 196 | 8 | 136 | 26 | 57 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 124 | 133 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 162 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 270 | 0 | 0 | 196 | 0 | 115 | 0 | 80 | 198 | 150 | 402 | 107 | 105 | 105 | 0 | 0 | 0 | 110 | 105 | 108 | 100 | 398 | 90 | 0 | 162 | 112 | 0 | 36 | 0 |  | 791 | 0 | 255 | 0 | 0 | 140 | 0 | 0 | 22 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 21 | 91 | 35 | 0 | 28 | 16 | 29 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 82 | 100 | 169 | 0 | 418 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 280 | 221 | 0 | 150 | 0 |  | 8944 | 3832 | 12776 | 4872 | 791 | 1813 | 3963 | 503 | 87 | 623 | 124 | 0 | 0 | 82.74
24:00 | 0 | 189 | 0 | 0 | 300 | 105 | 0 | 277 | 234 |  | 0 | 220 | 255 | 0 | 0 | 30 | 335 | 0 | 0 | 95 | 48 | 150 | 20 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 28 | 33 | 33 | 52 | 0 | 28 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 51 | 94 | 0 | 24 | 22 | 33 | 80 | 0 | 0 | 260 | 260 | 211 | 8 | 130 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 120 | 147 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 268 | 0 | 0 | 196 | 0 | 115 | 0 | 50 | 198 | 150 | 402 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 108 | 100 | 400 | 70 | 0 | 162 | 111 | 0 | 36 | 0 |  | 791 | 0 | 255 | 0 | 0 | 140 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 12 | 90 | 35 | 0 | 28 | 16 | 29 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 100 | 167 | 0 | 395 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 280 | 222 | 0 | 150 | 0 |  | 8790 | 3789 | 12579 | 4809 | 791 | 1870 | 3793 | 502 | 88 | 606 | 120 | 0 | 0 | 82.76
KWH | 0 | 3670300 | 0 | 1449000 | 7121082 | 1117590 | 0 | 6772740 | 5536000 |  | 0 | 5518250 | 6617978 | 0 | 0 | 558998 | 7894649 | 0 | 0 | 2158742 | 967392 | 2738880 | 403525 | 0 | 0 | 0 | 1281240 | 664288 | 1151503 | 317700 | 600000 | 529380 | 710300 | 811700 | 1148160 | 0 | 868904 | 1124000 | 2300000 | 0 | 589874 | 4911838 | 0 | 2816483 | 0 |  | 451680 | 0 | 398798 | 2101920 | 0 | 418560 | 499728 | 458880 | 2372640 | 0 | 0 | 6366300 | 6853000 | 5039000 | 585454 | 3235110 | 586584 | 1047840 | 0 | 833240 | 0 | 364304 | 807394 | 495000 | 214380 | 749500 | 437440 | 2527680 | 3373280 | 165120 | 450504 | 10800 | 1038000 | 0 | 1161000 | 0 | 0 | 3635000 | 1284096 | 1789440 | 0 | 5273580 | 400000 | 0 | 257220 | 7136500 | 365856 | 192336 | 289152 | 2852835 | 240616 | 59340 | 4459200 | 246401 | 1834560 | 92475 | 1118400 | 2716320 | 3198254 | 9076000 | 1658400 | 2553600 | 2370254 | 22201 | 0 | 0 | 2129372 | 1158240 | 2540160 | 1931520 | 9409500 | 961920 | 160130 | 3130560 | 2304600 | 0 | 891000 | 125945 |  | 19167273 | 0 | 7669152 | 0 | 0 | 682196 | 0 | 0 | 176640 | 0 | 0 | 0 | 691924 | 777216 | 0 | 0 | 0 | 760032 | 174165 | 1796672 | 628950 | 415137 | 426310 | 546240 | 309220 | 440400 | 0 | 250452 | 1686110 | 0 | 3662100 | 0 | 0 | 0 | 0 | 3681491 | 0 | 1708608 | 868800 | 4617827 | 0 | 9072873 | 2214720 | 114540 | 1400256 | 302400 | 1528444 | 0 | 11510 | 1847616 | 7434100 | 4887709 | 0 | 1759200 | 22860 |  | 193258615 | 81733143 | 274991758 | 117470928 | 19167273 | 42242928 | 70534597 | 12782310 | 1992904 | 7827217 | 2527680 | 445921 | 0
Fuel Cost | 0 | 5432044 | 0 | 2130030 | 7904401.02 | 1475218.8 | 0 | 6840467.4 | 5702080 |  | 0 | 6014892.5 | 7345955.58 | 0 | 0 | 4729123.08 | 8210434.96 | 0 | 0 | 16255327.26 | 8822615.04 | 26950579.2 | 3720500.5 | 0 | 0 | 0 | 9353052 | 5134946.24 | 11353819.58 | 238275 | 450000 | 0 | 0 | 0 | 11102707.2 | 0 | 234604.08 | 303480 | 4163000 | 0 | 5479929.46 | 5353903.42 | 0 | 4788021.1 | 0 |  | 0 | 0 | 3868340.6 | 20073336 | 0 | 3314995.2 | 629657.28 | 1362873.6 | 3511507.2 | 0 | 0 | 4711062 | 6853000 | 4635880 | 755235.66 | 3720376.5 | 662839.92 | 1466976 | 0 | 1424840.4 | 0 | 3679470.4 | 7710612.7 | 628650 | 160785 | 1311625 | 328080 | 18957600 | 3575676.8 | 1499289.6 | 572140.08 | 172152 | 1702320 | 0 | 2066580 | 0 | 0 | 3780400 | 2529669.12 | 3417830.4 | 0 | 9123293.4 | 876000 | 0 | 524728.8 | 7207865 | 274392 | 146175.36 | 4918475.52 | 21567432.6 | 4085659.68 | 992164.8 | 23187840 | 4119824.72 | 18052070.4 | 1081032.75 | 9114960 | 29472072 | 22547690.7 | 8440680 | 15124608 | 24131520 | 20644912.34 | 0 | 0 | 0 | 18717179.88 | 11559235.2 | 21769171.2 | 12863923.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110403492.48 | 0 | 8052609.6 | 0 | 0 | 9455236.56 | 0 | 0 | 1852953.6 | 0 | 0 | 0 | 1072482.2 | 7585628.16 | 0 | 0 | 0 | 7478714.88 | 1769516.4 | 15900547.2 | 4842915 | 5612652.24 | 4130943.9 | 5293065.6 | 2999434 | 845568 | 0 | 189592.164 | 10167243.3 | 0 | 19848582 | 0 | 0 | 0 | 0 | 4859568.12 | 0 | 2562912 | 14778288 | 5402857.59 | 0 | 8982144.27 | 23121676.8 | 1948325.4 | 13288429.44 | 2854656 | 11860725.44 | 0 | 127185.5 | 13653882.24 | 32635699 | 0 | 0 | 0 | 0 |  | 569116116.43 | 353577527.084 | 922693643.514 | 122189414.034 | 110403492.48 | 44882227.63 | 483605194 | 62651524.3 | 538084.08 | 78085736.74 | 18957600 | 1380370.25 | 0
Yesterday Day Peak | 0 | 103 | 0 | 110 | 300 | 32 | 0 | 277 | 208 |  | 0 | 220 | 265 | 0 | 0 | 0 | 324 | 0 | 0 | 90 | 48 | 115 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 29 | 60 | 100 | 0 | 25 | 204 | 0 | 110 | 0 |  | 24 | 0 | 0 | 82 | 0 | 0 | 22 | 3 | 80 | 0 | 0 | 290 | 275 | 212 | 8 | 135 | 26 | 30 | 0 | 34 | 0 | 0 | 43 | 20 | 8 | 33 | 14 | 94 | 142 | 2 | 18 | 2 | 43 | 0 | 47 | 0 | 0 | 163 | 40 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 45 | 0 | 0 | 202 | 0 | 87 | 14 | 40 | 51 | 135 | 364 | 8 | 105 | 105 | 3 | 0 | 0 | 68 | 34 | 104 | 70 | 400 | 17 | 16 | 162 | 91 | 0 | 36 | 18 |  | 791 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 35 | 43 | 0 | 25 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 72 | 0 | 182 | 0 | 414 | 70 | 0 | 5 | 0 | 34 | 0 | 2 | 90 | 280 | 181 | 0 | 0 | 3 |  | 10670 | DayPeak
Yesterday Evening Peak | 0 | 189 | 0 | 0 | 300 | 99 | 0 | 277 | 135 | 0 | 0 | 220 | 275 | 0 | 0 | 55 | 334 | 0 | 0 | 95 | 94 | 150 | 87 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 24 | 0 | 59 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 | 0 | 24 | 0 | 51 | 94 | 0 | 50 | 0 | 23 | 80 | 0 | 0 | 285 | 275 | 194 | 8 | 136 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 122 | 117 | 8 | 21 | 0 | 43 | 0 | 50 | 0 | 0 | 162 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 16 | 11 | 100 | 260 | 58 | 25 | 195 | 53 | 149 | 0 | 100 | 200 | 150 | 417 | 107 | 105 | 105 | 0 | 0 | 0 | 110 | 114 | 117 | 100 | 400 | 104 | 0 | 162 | 95 | 0 | 36 | 0 |  | 791 | 0 | 260 | 0 | 0 | 130 | 0 | 0 | 15 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 20 | 91 | 35 | 0 | 35 | 16 | 29 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 100 | 175 | 0 | 410 | 105 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 280 | 221 | 0 | 150 | 0 |  | 13056 | EvPeak
Forecast for Evening | 0 | 190 | 0 | 0 | 300 | 108 | 0 | 325 | 270 | 0 | 0 | 220 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 100 | 102 | 150 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 28 | 60 | 100 | 0 | 25 | 225 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 0 | 50 | 22 | 25 | 135 | 0 | 0 | 360 | 320 | 210 | 8 | 135 | 26 | 55 | 0 | 34 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 140 | 8 | 21 | 0 | 43 | 0 | 51 | 0 | 0 | 163 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 36 |  |  | 823 | 0 | 350 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 95 | 35 | 43 | 40 | 8 | 30 | 22 | 0 | 11 | 70 | 0 | 150 | 10 | 10 | 0 | 0 | 210 | 0 | 70 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 190 | 0 | 0 | 300 | 108 | 0 | 325 | 260 | 0 | 0 | 220 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 100 | 100 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 28 | 60 | 100 | 0 | 25 | 225 | 0 | 110 | 0 | 0 | 22 |  | 51 | 100 | 0 | 50 | 22 | 10 | 100 | 0 | 0 | 360 | 300 | 210 | 8 | 135 | 26 | 55 | 0 | 34 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 148 | 155 | 8 | 21 | 1.6 | 43 | 0 | 51 | 0 | 0 | 163 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 100 | 250 | 100 | 100 | 175 | 100 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 34 | 113 | 100 | 400 | 104 | 50 | 162 | 116 | 0 | 36 | 30 |  | 823 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 20 | 95 | 35 | 43 | 40 | 8 | 0 | 22 | 0 | 11 | 70 | 0 | 150 | 0 | 0 | 0 | 0 | 210 | 0 | 70 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 110 | 6
Generation at 08:00(Today) | 0 | 189 | 0 | 0 | 300 | 105 | 0 | 277 | 177 | 0 | 0 | 220 | 290 | 0 | 0 | 0 | 330 | 0 | 0 | 24 | 3 | 10 | 0 | 0 | 0 | 0 | 35 | 0 | 45 | 16 | 25 | 22 | 33 |  | 20 | 0 | 27 | 60 | 100 | 0 | 25 | 210 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 270 | 275 | 214 | 8 | 137 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 19 | 0 | 33 | 20 | 76 | 148 | 8 | 21 | 1 | 43 | 0 | 47 | 0 | 0 | 162 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 21 | 11 | 0 | 18 | 13 | 403 | 107 | 84 | 105 | 1 | 0 | 0 | 34 | 17 | 107 | 6 | 400 | 0 | 13 | 17 | 112 | 0 | 17 | 12 | 0 | 807 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 24 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 186 | 0 | 400 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 221 | 0 | 54 | 1 | 0
199
| Minimum Generation |  | 9712 | 8:00
| Highest Generation |  | 13056 | 21:00
| Day Peak Generation |  | 10670 | 12:00
| Evening Peak Generation |  | 13056 | 21:00
| HVDC Max Flow |  | 798 | 1:00
| HVDC EvPeak Flow |  | 791 | 21:00
| Load factor L.F |  | 87.76%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-18
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-17 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10670 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9707 | MW
Evening Peak Generation : |  | 13056 | MW Hour : | 21:00 | Available Max Generation : |  | 15478 | MW
E.P. Demand (at gen end) : |  | 13056 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13300 | MW
Maximum Generation : |  | 13056 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2178 | MW
Total Gen. (MKWH) : |  | 274.9918 | System Load Factor : | 87.76% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -560 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-18
Actual : | 82.58 | Ft.(MSL) , | Rule curve : | 86.72 | Ft.( MSL )
Gas Consumed : | Total = | 1214.9 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 167071641.664
: |  | Coal : | 62651524.3 | Oil : | 561690930.74 | Total : | 791414096.704
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4730.7567 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1614.3945 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1447.4553 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1308.257 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1182.0549 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 953.8908 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 526.0654 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 245.4079 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 735.7229 |  |  | 0 | 0%
Total | 0 |  | 12744.0055 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-4 & 5
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7)Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Manikganj PP 132 kV Ckt-2 was under shut down from 08:39 to 17:57 for D/W.
b) Kallyanpur 132 kV main Bus was under shut down from 10:53 to 15:01 for C/M.
c) Khulshi-AKSM 132 kV Ckt was under shut down from 11:21 to 12:44 to attend R/H at Khulshi end.
d) Savar 132/33 kV T3 transformer was under shut down from 09:53 to 12:44 for C/M.
e) Jamalpur 132/33 kV T3 transformer was under shut down from 08:58 to 16:48 due to R/H maintenance.
f) Pabna 132/33 kV T1 & T2 transformers tripped at 12:05 showing O/C, E/F due to 33 kV Kashinathpur |  |  |  |  | About 94 MW power interruption occurred under Pabna S/S area
feeder fault and were switched on at 12:28. |  |  |  |  | from 12:05 to 12:28.
g) Bhandaria 132/33 kV T1 transformer was under shut down from 10:32 to 13:21 for C/M.
h) Ghorashal unit-5 was shutdown at 12:40 for emergency maintenance.
i) Tripura-Cumilla(S) 132 kV both Ckts tripped at 13:41 from Tripura end due to CT burst of Laksham REB feeder |  |  |  |  | About 96 MW power interruption occurred under Cumilla(S) S/S area
and were switched on at 14:19. |  |  |  |  | from 13:41 to 14:19.
j) Cox's Bazar 132/33 kV T3 transformer was under shut down from 15:15 to 16:21 for C/M.
k) Dohazari 132/33 kV T2 transformer is under shut down since 06:13(18/07/2021) for C/M.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-17 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 189 | 3670300 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 1449000 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7121082 | Machine problem
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 1117590 | Gas shortage
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 277 | 6772740 | Gas shortage
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 135 | 5536000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 220 | 5518250 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6617978 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 558998
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 87 | 403525 | Engine problem
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 16 | 317700 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 95 | 2158742
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 334 | 7894649
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 967392 | Engine problem
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1281240
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2738880
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 664288
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1151503
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1129380 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 710300
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811700
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 24 | 1148160 | Engine problem
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 260 | 2852835 | Engine problem
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 58 | 240616 | Low demand
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 59340 | Low demand
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 53 | 246401 | Low demand
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1834560
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2553600
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 961920
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3130560
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 125945
| Dhaka area Total |  |  |  | 5819 | 3543 | 71745174
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 589874
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 92475
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 418560
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 119 | 1992904 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4911838 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2816483 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2370254
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 398798 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 94 | 2101920 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1118400
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 0 | 499728
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 23 | 458880
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22201
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2129372
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1931520
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 95 | 2304600 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1295 | 26457807
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2372640 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 194 | 5039000 | FGMO
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 6366300 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 6853000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 586584 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1047840 | Engine problem
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 585454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 34 | 833240 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3198254
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 41 | 364304
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3235110
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2716320
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 495000
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214380
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 122 | 2527680
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 749500
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 807394 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 437440
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 100 | 289152 | Low demand
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1158240
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 117 | 2540160
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 891000 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2103 | 43307992
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 117 | 3373280 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 450504
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 165120 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10800
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 195 | 4459200 | Engine problem
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 107 | 1658400 | Engine problem
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 160130
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 451680
| Mymensingh Area Total |  |  |  | 709 | 472 | 10729114
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1038000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 162 | 3635000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1161000
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 192336
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1284096
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1789440
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 225 | 5273580
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 400000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 365856 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7136500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 417 | 9076000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 257220
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 9409500 | FGMO
| Sylhet Area Total |  |  |  | 2377 | 1787 | 41018528
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 791 | 19167273
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 176640 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 130 | 682196 | Low demand
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7669152 | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 868800
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2214720
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 302400 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1401 | 31081181
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 64 | 777216 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 691924
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Machine problem
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 81 | 1708608 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 280 | 7434100 | Boiler problem
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 221 | 4887709
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 150 | 1759200
| Barisal Area Total |  |  |  | 1826 | 830 | 17258757
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 760032
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 174165 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 628950 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 415137
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 426310 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3681491 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 175 | 4617827 | Gas shortage
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 9072873 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 309220 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 440400
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 250452
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 16 | 546240 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 91 | 1796672 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 114540 | Low demand
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1400256 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1847616
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 22860
| Rajshahi Area Total |  |  |  | 2179 | 1291 | 26505041
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1686110 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 149 | 3662100 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1528444
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11510
| Rangpur Area Total |  |  |  | 605 | 334 | 6888164
| Total |  |  |  | 21060 | 13056 | 274991758
| Eastern Grid Total |  |  |  | 14321 | 9200 | 193258615
| Western Grid Total |  |  |  | 6739 | 3856 | 81733143
| National Grid Total |  |  |  | 21060 | 13056 | 274991758
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-17
(a) ENTIRE EASTERN GRID : |  | 8351 | MW | (b) ENTIRE WESTERN GRID : |  | 4150 | MW
i) Dhaka area |  | 4313 | MW | i) Khulna area |  | 1626 | MW
ii) Chittagong area |  | 1307 | MW | ii) Rajshahi area |  | 1341 | MW
iii) Comilla area |  | 1209 | MW | iii) Barisal area |  | 397 | MW
iv) Mymensingh area |  | 1022 | MW | iv) Rangpur area |  | 786 | MW
v) Sylhet area |  | 500 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12501 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 15:00 | Kishoreganj | 148 | 1:00 | Jessore | 116 | 21:00
Munsiganj | 106 | 1:00 | Netrokona | 111 | 22:00 | Benapol | 62 | 22:00
Sonargaon | 73 | 23:00 | Jamalpur | 152 | 20:00 | Jhenida | 120 | 20:00
Shyampur | 188 | 10:00 | Sherpur | 126 | 21:00 | Bottail | 144 | 21:00
Bhulta | 175 | 1:00 | Srimongal | 53 | 21:00 | G.K Project | 60 | 22:00
Madanganj | 52 | 10:00 | Shahjibazar | 111 | 22:00 | Faridpur | 151 | 21:00
Shitalakhya | 125 | 12:00 | Fenchuganj | 44 | 19:00 | Rajbari | 54 | 19:30
Rahim steel | 25 | 0:00 | Kulawara | 48 | 19:30 | Madaripur | 108 | 22:00
Matuail | 60 | 0:00 | Sylhet | 116 | 19:00 | Sariatpur | 74 | 22:00
Ghorasal | 76 | 22:00 | Chatak | 29 | 21:00 | Gopalganj | 102 | 22:00
Narsingdi | 172 | 22:00 | Sunamganj | 47 | 20:00 | Bagerhat | 109 | 21:00
Haripur (SBU) | 100 | 10:00 | Biani Bazar | 62 | 19:30 | Mongla | 40 | 19:30
Sreenagar | 44 | 2:00 | Comilla (S) | 128 | 1:00 | Satkhira | 109 | 22:00
Ullon | 67 | 21:00 | Comilla(N) | 137 | 22:00 | Gallamari | 32 | 1:00
Hasnabad | 82 | 20:00 | Chandpur | 84 | 23:00 | Magura | 58 | 22:00
Magbazar | 87 | 16:00 | Feni | 126 | 19:00 | Norail | 44 | 19:30
Maniknagar | 62 | 19:30 | Chowmuhani | 226 | 23:00 | Chuadanga | 93 | 20:00
Bangabhaban | 7 | 10:00 | Ashuganj | 30 | 1:00 | Borguna | 20 | 21:00
Motijheel | 21 | 12:00 | Daudkandi | 161 | 21:00 | Barisal(N) | 45 | 23:00
Narinda | 52 | 12:00 | B.Baria | 160 | 21:00 | Barisal (S) | 114 | 23:00
Kazla | 80 | 12:00 | Ramganj | 88 | 22:00 | Patuakhali | 126 | 22:00
Dhanmondi | 173 | 13:00 | Chaddagram | 61 | 21:00 | Bhandaria | 58 | 22:00
Lalbag | 90 | 13:00 | PHP | 3 | 10:00 | Borhan Uddin | 48 | 21:00
Madartek | 72 | 23:00 | Kochua | 68 | 21:00 | Ishurdi | 72 | 19:30
Dhaka University | 30 | 13:00 | Madunaghat | 56 | 19:30 | Ruppur Paromanobik | 3 | 21:00
Aftabnagar | 10 | 14:00 | Hathazari | 90 | 21:00 | Natore | 134 | 21:00
Fatullah | 54 | 9:00 | Khulshi | 174 | 16:00 | Bogra | 158 | 19:30
Nawabganj | 54 | 21:00 | Halishahar | 80 | 8:00 | Noagaon | 120 | 1:00
Keraniganj | 64 | 19:30 | Baraulia | 142 | 0:00 | Rajshahi | 163 | 21:00
Mirpur | 124 | 19:30 | Sikalbaha | 36 | 1:00 | Rajshahi New | 16 | 1:00
Kalyanpur | 117 | 20:00 | Dohazari | 92 | 19:30 | C.Nawabganj | 72 | 21:00
Gulshan | 92 | 13:00 | Cox'sbazar | 100 | 23:00 | Amnura | 60 | 1:00
Uttara | 87 | 14:00 | Chandraghona | 28 | 19:30 | Pabna | 106 | 21:00
Uttara New | 19 | 10:00 | Kaptai | 4 | 18:30 | Shahjadpur | 104 | 21:00
Kamrangirchar | 84 | 19:30 | A. Khaer Stl. | 3 | 15:00 | Serajganj | 96 | 20:00
Savar | 152 | 15:00 | Bakulia | 105 | 19:30 | Niyamatpur | 84 | 1:00
Bhasantec | 125 | 20:00 | Julda | 22 | 11:00 | Joypurhat | 66 | 21:00
Agargaon | 70 | 13:00 | TK chemical | 29.5 | 22:00 | Sherpur(Bogura) | 56 | 1:00
Satmosjid | 97 | 19:30 | Modern Steel | 0 | #N/A | Mohastangor | 78 | 19:30
Tongi | 111 | 11:00 | Shahmirpur | 26 | 0:00 | Bhangura | 34 | 21:00
Kabirpur | 246 | 12:00 | Khagrachhari | 30 | 16:00 | Rangpur | 134 | 21:00
Basundhara | 217 | 12:00 | Matarbari | 37 | 20:00 | Lalmonirhat | 40 | 21:00
Manikganj | 76 | 22:00 | Baroiar Hat | 44 | 21:00 | Saidpur | 106 | 20:00
Joydevpur | 162 | 19:30 | Rangamati | 12 | 19:00 | Purbasadipur | 110 | 20:00
New Tongi | 110 | 12:00 | Abul Khair 230 | 134 | 0:00 | Thakurgaon | 86 | 21:00
Kodda | 281 | 15:00 | BSRM | 150 | 18:30 | Palashbari | 117 | 1:00
Dhamrai | 110 | 19:30 | GPH Ispat | 87 | 16:00 | Barapukuria | 56 | 21:00
Rajendrapur | 112 | 19:30 | Agrabad | 75 | 19:00 | Panchagar | 49 | 21:00
Valuka | 136 | 15:00 | Goalpara | 25 | 1:00 | Joldhaka | 54 | 21:00
Tangail | 233 | 21:00 | Central S/S | 111 | 20:00 | Kurigram | 59 | 20:00
Mymensing | 212 | 1:00 | Noapara | 59 | 19:30 | Mithapukur | 33 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-17 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 19:30 | 396 | 5:00 | Kaliakoir | 389 | 0.33333 | 384 | 0.375
| Bheramara | 401 | 19:30 | 394 | 1:00 | Bhulta | 386 | 0.33333 | 376 | 0.083333
| Ashuganj(N) | 392 | 6:00 | 381 | 2:00 | Gopalganj | 411 | 0.625 | 397 | 0.875
| Payra | 4412 | 20:00 | 408 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 12:00 | 219 | 2:00
| Ishurdi | 235 | 8:00 | 224 | 21:00 | Megnaghat | 234 | 14:00 | 228 | 10:00
| Ashuganj | 240 | 19:00 | 234 | 7:00 | Fenchuganj | 237 | 4:00 | 233 | 1:00
| Serajganj | 231 | 18:00 | 225 | 19:30 | Siddhirganj | 230 | 19:30 | 226 | 11:00
| Baghabari | 233 | 19:00 | 227 | 1:00 | Maniknagar | 229 | 19:30 | 224 | 12:00
| Barapukuria | 235 | 14:00 | 226 | 1:00 | Agargaon | 227 | 8:00 | 221 | 9:00
| Bogra | 225 | 14:00 | 215 | 1:00 | Barisal | 243 | 5:00 | 237 | 19:00
| Rajshahi | 235 | 18:00 | 224 | 21:00 | Bhola 225 MW | 245 | 4:00 | 241 | 21:00
| Khulna South | 225 | 18:30 | 213 | 4:00 | AKSML | 226 | 5:00 | 220 | 9:00
| Rampura | 229 | 21:00 | 221 | 12:00 | BSRM | 227 | 14:00 | 220 | 2:00
| Haripur | 228 | 1:00 | 223 | 11:00 | Bibiyana | 238 | 6:00 | 233 | 12:00
| Hasnabad | 230 | 1:00 | 224 | 12:00 | Bhulta | 232 | 20:00 | 227 | 9:00
| Shyampur | 227 | 20:00 | 220 | 10:00 | Ashuganj (S) | 236 | 8:00 | 232 | 13:00
| Aminbazar | 228 | 1:00 | 222 | 2:00 | Kaliakoir | 228 | 14:00 | 222 | 9:00
| Tongi | 228 | 1:00 | 127 | 13:00 | GPH | 225 | 14:00 | 220 | 1:00
| Comilla (N) | 229 | 19:30 | 225 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:30 | 130 | 11:00 | Madanhat | 133 | 0.083333 | 131 | 0.33333
| Munsiganj | 135 | 19:30 | 129 | 12:00 | Hathazari | 133 | 0.66667 | 131 | 0.083333
| Sonargaon | 134 | 19:30 | 129 | 9:00 | Khulshi | 131 | 0.58333 | 128 | 0.041667
| Shyampur | 136 | 18:30 | 131 | 12:00 | Halishahar | 133 | 0.91667 | 129 | 0.33333
| Bhulta | 126 | 1:00 | 122 | 10:00 | Baraulia | 133 | 0.91667 | 129 | 0.041667
| Madanganj | 134 | 19:30 | 128 | 11:00 | Sikalbaha | 133 | 0.54167 | 130 | 0.29167
| Shitalakhya | 141 | 19:30 | 132 | 10:00 | Dohazari | 128 | 0.58333 | 126 | 0.083333
| Rahim steal | 134 | 20:00 | 130 | 9:00 | Cox'sbazar | 125 | 0.66667 | 115 | 0.083333
| Matuail | 134 | 19:30 | 130 | 11:00 | Chandraghona | 133 | 0.58333 | 130 | 0.25
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 132 | 0.29167 | 130 | 0.041667
| Narsinghdi | 134 | 6:00 | 126 | 21:00 | A. Khaer Stl. | 131 | 0.875 | 129 | 0.70833
| Haripur (SBU) | 134 | 21:00 | 130 | 11:00 | Bakulia | 132 | 0.58333 | 129 | 0.29167
| Sreenagar | 132 | 19:30 | 125 | 11:00 | Julda | 134 | 0.58333 | 131 | 0.16667
| Ullon | 134 | 1:00 | 129 | 12:00 | TK Chemical | 133 | 0.95833 | 130 | 0.29167
| Hasnabad | 140 | 20:00 | 134 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 134 | 1:00 | 130 | 10:00 | Shahmirpur | 133 | 0.54167 | 130 | 0.29167
| Maniknagar | 137 | 1:00 | 134 | 10:00 | Khagrachhari | 132 | 0.66667 | 130 | 0.041667
| Bangabhaban | 137 | 1:00 | 134 | 10:00 | Matarbari | 130 | 0.70833 | 119 | 0.83333
| Motijheel | 137 | 1:00 | 134 | 10:00 | Baroiar Hat | 134 | 0.875 | 130 | 0.79167
| Narinda | 137 | 1:00 | 134 | 10:00 | Rangamati | 132 | 14:00 | 130 | 8:00
| Kazla | 137 | 1:00 | 134 | 10:00 | Agrabad | 131 | 13:00 | 129 | 6:00
| Dhanmondi | 133 | 5:00 | 129 | 11:00 | Goalpara S/S | 135 | 8:00 | 126 | 0.54167
| Lalbag | 139 | 20:00 | 131 | 12:00 | Khulna Central S/S | 134 | 8:00 | 126 | 0.54167
| Madartek | 134 | 1:00 | 129 | 13:00 | Noapara | 133 | 18:30 | 122 | 0.16667
| Dhaka University | 135 | 1:00 | 129 | 13:00 | Jessore | 125 | 8:00 | 113 | 0.54167
| Aftabnagar | 135 | 5:00 | 130 | 10:00 | Benapol | 128 | 0.77083 | 115 | 0.875
| Fatullah | 136 | 19:00 | 131 | 12:00 | Jhenida | 123 | 18:00 | 107 | 0.875
| Nawabganj | 130 | 19:30 | 124 | 12:00 | Bottail | 130 | 0.45833 | 120 | 0.8125
| Keraniganj | 131 | 19:30 | 125 | 12:00 | G.K Project | 138 | 0.75 | 132 | 0.91667
| Mirpur | 137 | 19:30 | 133 | 8:00 | Faridpur | 136 | 0.70833 | 130 | 0.875
| Kalyanpur | 138 | 22:00 | 134 | 18:00 | Rajbari | 136 | 0.75 | 128 | 0.91667
| Gulshan | 133 | 1:00 | 129 | 12:00 | Madaripur | 141 | 0.33333 | 135 | 0.83333
| Uttara | 136 | 1:00 | 132 | 9:00 | Shariyatpur S/S | 140 | 9:00 | 133 | 0.875
| Uttara New | 137 | 12:00 | 132 | 8:00 | Gopalganj | 145 | 0.33333 | 134 | 0.875
| Kamrangirchar | 140 | 1:00 | 133 | 10:00 | Bagerhat | 134 | 18:30 | 122 | 0.29167
| Savar | 132 | 20:00 | 132 | 7:00 | Mongla | 131 | 17:00 | 124 | 0.54167
| Bhasantec | 135 | 1:00 | 131 | 12:00 | Satkhira | 134 | 8:00 | 124 | 4:00
| Agargaon | 140 | 1:00 | 132 | 12:00 | Gallamari | 136 | 0.77083 | 129 | 7:00
| Satmosjid | 136 | 1:00 | 132 | 12:00 | Magura | 122 | 11:00 | 106 | 0.8125
| Tongi | 139 | 1:00 | 134 | 12:00 | Narail | 123 | 0.77083 | 104 | 0.875
| Kabirpur | 138 | 8:00 | 135 | 9:00 | Chuadanga | 117 | 11:00 | 95 | 0.875
| Basundhara | 137 | 18:30 | 131 | 9:00 | Borguna | 140 | 2:00 | 134 | 0.58333
| Manikganj | 140 | 1:00 | 133 | 10:00 | Barisal(N) | 140 | 8:00 | 137 | 19:00
| Joydevpur | 139 | 4:00 | 135 | 8:00 | Barisal (S) | 139 | 0.29167 | 135 | 0.79167
| New Tongi | 139 | 6:00 | 132 | 9:00 | Patuakhali(S) | 140 | 0.041667 | 129 | 0.54167
| Kodda | 136 | 20:00 | 128 | 10:00 | Bhandaria | 136 | 0.375 | 130 | 0.79167
| Dhamrai | 131 | 1:00 | 127 | 19:30 | Ishurdi | 136 | 18:00 | 130 | 21:00
| Rajendrapur | 134 | 1:00 | 125 | 11:00 | Ruppur Paromanobik | 135 | 18:30 | 130 | 21:00
| Valuka | 127 | 6:00 | 109 | 21:00 | Natore | 134 | 14:00 | 127 | 21:00
| Tangail | 135 | 7:00 | 125 | 20:00 | Bogra | 134 | 19:00 | 124 | 1:00
| Mymensing | 132 | 8:00 | 114 | 21:00 | Noagaon | 129 | 18:00 | 117 | 1:00
| Kishorganj | 132 | 21:00 | 118 | 21:00 | Rajshahi | 132 | 18:00 | 125 | 21:00
| Netrokona | 130 | 7:00 | 109 | 22:00 | Rajshahi New | 133 | 18:00 | 125 | 21:00
| Jamalpur | 137 | 6:00 | 123 | 21:00 | C.Nawabganj | 132 | 18:30 | 124 | 21:00
| Sherpur | 137 | 6:00 | 120 | 21:00 | Amnura | 133 | 18:00 | 125 | 21:00
| Srimongal | 138 | 6:00 | 134 | 1:00 | Pabna | 135 | 18:00 | 129 | 21:00
| Shahjibazar | 137 | 8:00 | 132 | 22:00 | Shahjadpur | 137 | 18:00 | 134 | 20:00
| Fenchuganj | 137 | 13:00 | 133 | 1:00 | Serajganj | 132 | 14:00 | 126 | 1:00
| Khulawara | 136 | 5:00 | 133 | 22:00 | Niyamatpur | 128 | 18:30 | 112 | 1:00
| Sylhet | 135 | 7:00 | 131 | 23:00 | Joypurhat | 128 | 18:30 | 114 | 1:00
| Chatak | 134 | 6:00 | 129 | 20:00 | Sherpur(Bogura) | 134 | 14:00 | 126 | 1:00
| Sunamganj | 133 | 7:00 | 127 | 21:00 | Mohastangor | 133 | 15:00 | 123 | 1:00
| Biani Bazar | 135 | 8:00 | 129 | 1:00 | Bangura | 136 | 18:00 | 130 | 21:00
| Comilla(s) | 129 | 5:00 | 124 | 19:00 | Rangpur | 131 | 15:00 | 118 | 1:00
| Comilla(n) | 138 | 21:00 | 134 | 13:00 | Lalmonirhat | 130 | 15:00 | 117 | 19:30
| Chandpur | 138 | 1:00 | 132 | 7:00 | Saidpur | 130 | 15:00 | 117 | 1:00
| Feni | 134 | 7:00 | 130 | 2:00 | Purbasadipur | 127 | 14:00 | 112 | 1:00
| Chowmuhani | 134 | 1:00 | 130 | 6:00 | Thakurgaon | 125 | 15:00 | 111 | 1:00
| Ashuganj | 140 | 7:00 | 135 | 1:00 | Palashbari | 130 | 15:00 | 120 | 20:00
| Daudkandi | 135 | 19:30 | 128 | 2:00 | Barapukuria | 135 | 18:00 | 126 | 1:00
| B.Baria | 135 | 6:00 | 128 | 22:00 | Panchagar | 125 | 15:00 | 107 | 19:30
| Ramganj | 134 | 1:00 | 130 | 4:00 | Joldhaka | 128 | 0.625 | 114 | 0.83333
| Chaddagram | 136 | 21:00 | 132 | 4:00 | Kurigram | 129 | 0.625 | 113 | 0.041667
| PHP | 133 | 8:00 | 130 | 1:00 | Mithapukur | 132 | 0.625 | 121 | 0.041667
| Kochua | 135 | 5:00 | 131 | 23:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-17
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 362 | 8790 | 3789 | 12579 |  |  |  | QF-LDC-11
0:30 | 396 | 8678 | 3784 | 12462 | Date: | 2021-07-17
1:00 | 430 | 8566 | 3779 | 12345
1:30 | 383 | 8404 | 3795 | 12199
2:00 | 336 | 8242 | 3811 | 12053
2:30 | 321 | 8085.5 | 3739 | 11824.5 | [5 empty] | Gen. at Eve. Peak | 13056 | 13056 MW (21:00 )
3:00 | 306 | 7929 | 3667 | 11596 | [6 empty] | 21:00
3:30 | 285 | 7839 | 3619 | 11458 | [5 empty] | Gen. at Day Peak | 10670 | 10670 MW (12:00 )
4:00 | 264 | 7749 | 3571 | 11320 | [6 empty] | 12:00
4:30 | 264 | 7675.5 | 3511.5 | 11187 | [5 empty] | Highest Generation | 13056
5:00 | 264 | 7602 | 3452 | 11054 | [6 empty] | 21:00
5:30 | 267 | 7391 | 3221 | 10612
6:00 | 270 | 7180 | 2990 | 10170
6:30 | 273 | 7078 | 2934.5 | 10012.5
7:00 | 276 | 6976 | 2879 | 9855
7:30 | 265 | 6948 | 2835.5 | 9783.5
8:00 | 254 | 6920 | 2792 | 9712
8:30 | 188 | 7054.5 | 2814.5 | 9869
9:00 | 122 | 7189 | 2837 | 10026
9:30 | 117 | 7261 | 2847 | 10108
10:00 | 112 | 7333 | 2857 | 10190
10:30 | 111 | 7410.5 | 2884.5 | 10295
11:00 | 110 | 7488 | 2912 | 10400
11:30 | 105 | 7566.5 | 2968.5 | 10535
12:00 | 100 | 7645 | 3025 | 10670
12:30 | 159 | 7764.5 | 3057.5 | 10822
13:00 | 218 | 7884 | 3090 | 10974
13:30 | 212 | 7871.5 | 3108.5 | 10980
14:00 | 206 | 7859 | 3127 | 10986
14:30 | 226 | 7976.5 | 3170 | 11146.5
15:00 | 246 | 8094 | 3213 | 11307
15:30 | 224 | 7977 | 3140.5 | 11117.5
16:00 | 202 | 7860 | 3068 | 10928
16:30 | 164 | 7794 | 3012.5 | 10806.5
17:00 | 126 | 7728 | 2957 | 10685
17:30 | 92 | 7504 | 2958.5 | 10462.5
18:00 | 58 | 7280 | 2960 | 10240
18:30 | 133 | 7713.5 | 3134.5 | 10848
19:00 | 208 | 8147 | 3309 | 11456
19:30 | 560 | 9155 | 3784 | 12939
20:00 | 486 | 9091 | 3873 | 12964 |  |  |  | Executive Engineer
20:30 | 506 | 9145.5 | 3864.5 | 13010 |  |  |  | Network Operation Division
21:00 | 526 | 9200 | 3856 | 13056
21:30 | 496 | 9180.5 | 3834.5 | 13015
22:00 | 466 | 9161 | 3813 | 12974 |  |  |  |  | Page 6 of 7
22:30 | 410 | 9052.5 | 3822.5 | 12875
23:00 | 354 | 8944 | 3832 | 12776
23:30 | 358 | 8867 | 3810.5 | 12677.5
24:00 | 362 | 8790 | 3789 | 12579
13056 MW (21:00 )
10670 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-17 |  | Energy | 274991758
[11 empty] | 2021-07-17 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4809 | 791 | 1870 | 3963 | 502 | 88 | 606 | 0 | 120 | 0
0:30 | 4760 | 794.5 | 1871.5 | 3863 | 489.5 | 87 | 557.5 | 0 | 124 | 0 | Date: | 2021-07-17
1:00 | 4711 | 798 | 1873 | 3763 | 477 | 86 | 509 | 0 | 128 | 0
1:30 | 4714.5 | 798 | 1911 | 3584 | 491.5 | 87 | 486 | 0 | 127 | 0 | [7 empty] | Total Energy | 274.9918 | Total Energy Gen 274.992 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 274.992 MKWHr
2:00 | 4718 | 798 | 1949 | 3405 | 506 | 88 | 463 | 0 | 126 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4732.5 | 798 | 1947.5 | 3207.5 | 507 | 88 | 419 | 0 | 125 | 0 | [7 empty] | Energy Requirement | 274.9918
3:00 | 4747 | 798 | 1946 | 3010 | 508 | 88 | 375 | 0 | 124 | 0
3:30 | 4797.5 | 798 | 1952.5 | 2851.5 | 506 | 88 | 341.5 | 0 | 123 | 0 | [6 empty] | Shortage
4:00 | 4848 | 798 | 1959 | 2693 | 504 | 88 | 308 | 0 | 122 | 0
4:30 | 4845.5 | 798 | 1937.5 | 2604 | 506.5 | 73 | 304.5 | 0 | 118 | 0
5:00 | 4843 | 798 | 1916 | 2515 | 509 | 58 | 301 | 0 | 114 | 0
5:30 | 4916.5 | 798 | 1869 | 2103.5 | 505.5 | 57.5 | 251 | 0 | 110 | 1
6:00 | 4990 | 798 | 1822 | 1692 | 502 | 57 | 201 | 0 | 106 | 2
6:30 | 4983 | 794.5 | 1807.5 | 1586.5 | 502.5 | 57 | 174.5 | 0 | 103 | 4 |  |  |  |  | Coal
7:00 | 4976 | 791 | 1793 | 1481 | 503 | 57 | 148 | 0 | 100 | 6
7:30 | 4950.5 | 791.5 | 1710.5 | 1509 | 503 | 57 | 148.5 | 0 | 100 | 13.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4925 | 792 | 1628 | 1537 | 503 | 57 | 149 | 0 | 100 | 21
8:30 | 4914.5 | 792 | 1659 | 1663 | 501.5 | 57.5 | 157 | 0 | 96 | 28.5
9:00 | 4904 | 792 | 1690 | 1789 | 500 | 58 | 165 | 0 | 92 | 36
9:30 | 4881 | 791.5 | 1685.5 | 1895 | 501 | 58.5 | 157.5 | 0 | 96 | 42
10:00 | 4858 | 791 | 1681 | 2001 | 502 | 59 | 150 | 0 | 100 | 48
10:30 | 4858.5 | 791 | 1660.5 | 2102.5 | 503 | 74 | 163.5 | 0 | 95 | 47
11:00 | 4859 | 791 | 1640 | 2204 | 504 | 89 | 177 | 0 | 90 | 46
11:30 | 4844 | 791 | 1665 | 2320 | 504 | 89 | 178 | 0 | 92 | 52
12:00 | 4829 | 791 | 1690 | 2436 | 504 | 89 | 179 | 0 | 94 | 58
12:30 | 4851.5 | 791 | 1658.5 | 2591.5 | 506 | 88.5 | 183 | 0 | 95 | 57
13:00 | 4874 | 791 | 1627 | 2747 | 508 | 88 | 187 | 0 | 96 | 56
13:30 | 4874 | 791 | 1627 | 2747 | 508 | 88 | 187 | 0 | 96 | 56
14:00 | 4874 | 791 | 1627 | 2747 | 508 | 88 | 187 | 0 | 96 | 56
14:30 | 4860 | 791.5 | 1592 | 2939 | 505.5 | 88 | 212 | 0 | 101 | 51.5
15:00 | 4846 | 792 | 1557 | 3131 | 503 | 88 | 237 | 0 | 106 | 47
15:30 | 4838 | 791.5 | 1547.5 | 2971 | 502.5 | 88 | 237 | 0 | 100 | 42
16:00 | 4830 | 791 | 1538 | 2811 | 502 | 88 | 237 | 0 | 94 | 37
16:30 | 4826.5 | 791 | 1545.5 | 2687 | 501.5 | 88 | 239.5 | 0 | 98 | 29.5
17:00 | 4823 | 791 | 1553 | 2563 | 501 | 88 | 242 | 0 | 102 | 22
17:30 | 4764.5 | 791 | 1528.5 | 2404.5 | 501 | 104.5 | 254.5 | 0 | 101 | 13
18:00 | 4706 | 791 | 1504 | 2246 | 501 | 121 | 267 | 0 | 100 | 4
18:30 | 4842 | 791 | 1572.5 | 2537 | 501 | 120 | 370.5 | 0 | 112 | 2
19:00 | 4978 | 791 | 1641 | 2828 | 501 | 119 | 474 | 0 | 124 | 0
19:30 | 4887 | 791 | 1659 | 4308 | 499 | 119 | 552 | 0 | 124 | 0
20:00 | 4855 | 791 | 1716 | 4234 | 502 | 119 | 625 | 0 | 122 | 0
20:30 | 4833 | 791 | 1746.5 | 4278.5 | 501.5 | 119 | 618.5 | 0 | 122 | 0
21:00 | 4811 | 791 | 1777 | 4323 | 501 | 119 | 612 | 0 | 122 | 0
21:30 | 4808 | 791 | 1775 | 4279 | 501.5 | 119 | 619.5 | 0 | 122 | 0
22:00 | 4805 | 791 | 1773 | 4235 | 502 | 119 | 627 | 0 | 122 | 0
22:30 | 4838.5 | 791 | 1793 | 4099 | 502.5 | 103 | 625 | 0 | 123 | 0
23:00 | 4872 | 791 | 1813 | 3963 | 503 | 87 | 623 | 0 | 124 | 0
23:30 | 4840.5 | 791 | 1841.5 | 3963 | 502.5 | 87.5 | 614.5 | 0 | 122 | 0 | Max Temp. in Dhaka |  | 33.4° C
24:00 | 4809 | 791 | 1870 | 3963 | 502 | 88 | 606 | 0 | 120 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 274.992 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 274.992 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-17
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 56 | 58 | 58 | 58 | 28 | 27 | 27 | 27 | 28 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 | 61 |  | 59 | 59 | 59 | 59 | 59 | 27 | 28 | 868904
2 | Karnaphuli Hydro PP Unit-4 & 5 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1124000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 23 | 25 | 25 | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 26 | 25 | 589874
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 2 | 11 | 17 | 17 | 5 | 14 | 8 | 9 | 11 |  | 4 | 1 | [8 empty] | 92475
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 213 | 203 | 202 | 204 | 202 | 213 | 204 | 231 | 204 | 206 | 203 | 204 | 203 | 203 | 203 |  | 214 | 203 | 203 | 203 | 203 | 217 | 204 | 4911838
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2816483
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 51 | 51 | 0 | [16 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 398798
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 92 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 68 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 2370254
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 40 | 100 | 100 | 100 | 60 |  |  | 289152
14 | Titas 50 MW Peaking PP | 48 | 48 | 32 | 0 | [15 empty] | 33 | 41 | 41 | 41 | 41 | 41 | 41 | 364304
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 338 | 338 | 334 | 334 | 334 | 336 | 333 | 332 | 327 | 327 | 327 | 324 | 320 | 325 | 334 | 334 | 335 | 280 |  | 330 | 334 | 334 | 334 | 335 | 330 | 335 | 7894649
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 195 | 0 | [7 empty] | 5 | 45 | 95 | 135 | 145 | 145 | 145 | 145 |  | 145 | 202 | 225 | 260 | 268 | 270 | 268 | 2852835
19 | Ashuganj 195MW PP (APSCL-United) | 73 | 73 | 73 | 73 | 73 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 585454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT | 103 | 103 | 103 | 104 | 104 | 103 | 104 | 104 | 104 | 103 | 103 | 103 | 185 | 189 | 188 | 189 | 187 | 189 |  | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 3670300
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | [13 empty] | 0 | 1449000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7121082
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 2372640
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 586584
33 | Ashuganj 225 MW CCPP | 216 | 216 | 217 | 212 | 217 | 189 | 179 | 201 | 201 | 211 | 215 | 212 | 213 | 217 | 218 | 215 | 215 | 216 |  | 216 | 204 | 201 | 194 | 200 | 196 | 211 | 5039000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 290 | 280 | 275 | 275 | 295 | 275 | 275 | 275 | 275 | 275 |  | 325 | 300 | 295 | 275 | 275 | 295 | 260 | 6853000
| Ashuganj 450 MW CCPP(North) | 25 | 30 | 60 | 140 | 160 | 365 | 360 | 365 | 280 | 270 | 260 | 290 | 310 | 290 | 305 | 305 | 300 | 275 |  | 340 | 285 | 285 | 285 | 285 | 305 | 260 | 6366300
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 55 | 56 | 56 | 56 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 31 | 31 | 31 | 31 |  | 30 | 30 | 47 | 56 | 56 | 57 | 56 | 1047840
36 | Chandpur 150 MW CCPP | 138 | 137 | 138 | 138 | 132 | 134 | 138 | 130 | 136 | 139 | 137 | 135 | 137 | 131 | 136 | 137 | 135 | 137 |  | 137 | 130 | 130 | 136 | 130 | 136 | 130 | 3235110
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 276 | 276 | 275 | 276 | 275 | 276 |  | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 6772740
40 | Meghnaghat 450 MW CCPP(MPL) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5518250
41 | Haripur 360MW CCPP(HPL) | 332 | 346 | 346 | 346 | 346 | 346 | 336 | 313 | 270 | 239 | 218 | 208 | 152 | 153 | 151 | 153 | 153 | 153 |  | 152 | 147 | 141 | 135 | 132 | 150 | 234 | 5536000
42 | RPCL 210MW CCPP | 154 | 153 | 153 | 153 | 153 | 165 | 190 | 173 | 151 | 151 | 150 | 142 | 129 | 129 | 129 | 129 | 132 | 135 |  | 136 | 134 | 129 | 117 | 118 | 133 | 147 | 3373280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 0 | 1 | 3 | 12 | 17 | 16 | 22 | 31 | 22 | 17 | 10 | 1 | [8 empty] | 160130
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1038000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 162 | 162 | 163 | 162 | 162 | 163 | 162 | 163 | 163 | 164 | 162 | 163 | 162 | 162 | 162 | 163 | 163 | 162 |  | 160 | 162 | 162 | 162 | 162 | 162 | 162 | 3635000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 57 | 57 | 56 | 57 | 57 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 62 | 62 | 61 | 61 | 40 |  | 61 | 62 | 62 | 61 | 62 | 61 | 62 | 1284096
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 20 | 20 | 81 | 81 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 40 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1789440
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 218 | 218 | 219 | 219 | 219 | 218 | 219 | 219 | 219 | 219 |  | 219 | 225 | 225 | 225 | 218 | 219 | 219 | 5273580
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 400000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 257220
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 11 | 11 | 11 | 11 | 11 | 11 | 192336
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 47 | 47 | 47 | 47 | 53 | 50 | 50 | 50 | 52 | 14 |  | 21 | 52 | 50 | 50 | 50 | 47 | 47 | 1161000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 365856
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 290 | 290 | 300 | 290 | 265 | 295 | 290 | 300 | 300 | 290 | 300 | 290 | 280 | 275 | 280 | 280 | 290 |  | 280 | 260 | 280 | 290 | 290 | 290 | 285 | 7136500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 350 | 350 | 348 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 360 |  | 385 | 400 | 400 | 400 | 400 | 398 | 400 | 9409500
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 1151503
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 22 | 22 | 0 |  |  |  |  | 6 | 24 | 24 | 24 | 22 | 23 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 451680
60 | Barabkunda 22 MW PP (Regent) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 |  | 21 | 21 | 22 | 499728
61 | Narshingdi 22 MW PP (Doreen) | 17 | 17 | 17 | 17 | 18 | 18 | 18 | 20 | 18 | 18 |  |  | 16 | 16 | 16 |  |  | 16 |  |  |  |  | 16 | 16 | 16 | 16 | 317700
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 450504
63 | Impoprt (Tripura) | 128 | 126 | 124 | 122 | 114 | 106 | 100 | 100 | 92 | 100 | 90 | 94 | 96 |  | 106 | 94 | 102 | 100 |  | 124 | 124 | 122 | 122 | 122 | 124 | 120 | 2527680
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 34 | 3 | 2 | 2 | 2 | 3 | 7 | 4 | 4 | 2 | 5 | 2 |  | 4 | 5 | 12 | 23 | 33 | 33 | 33 | 458880
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 20 | 21 | 21 | 21 | 21 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495000
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  | 11 | 8 | 8 | 8 | 8 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 214380
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 749500
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 18 | 20 | 20 | 18 | 12 | 14 | 12 | 14 | 14 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 437440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 17 | 17 | 22 | 22 | 22 | 28 | 28 | 529380
71 | Maona 33 MW PP(Summit) | 33 | 33 | 28 | 28 | 28 | 28 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 710300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811700
73 | Ghorashal 108MW PP (Regent) | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 53 |  | 65 | 95 | 97 | 99 | 104 | 103 | 105 | 1117590
| Feni Lanka Power | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 114 | 114 | 105 | 114 | 1158240
| Chowmuhani 113 MW | 109 | 108 | 106 | 108 | 106 | 108 | 106 | 108 | 106 | 105 | 104 | 104 | 104 | 114 | 110 | 106 | 106 | 65 |  | 71 | 117 | 117 | 117 | 115 | 108 | 108 | 2540160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 108 | 108 | 17 | 17 | 20 | 58 | 143 | 162 | 162 | 162 | 162 | 162 | 126 | 72 | 72 |  | 73 | 162 | 158 | 162 | 162 | 162 | 162 | 3130560
77 | Siddhirganj 100 PP(Dutch Bangla) | 95 | 95 | 95 | 95 | 95 | 90 | 85 | 87 | 87 | 87 | 87 | 90 | 92 | 94 | 94 | 95 | 95 | 55 |  | 55 | 70 | 70 | 95 | 96 | 96 | 95 | 2158742
78 | Gazipur 52 MW PP | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 25 |  | 25 | 32 | 46 | 24 | 52 | 52 | 52 | 1148160
79 | Kodda 150MW PP | 150 | 150 | 150 | 115 | 115 | 64 | 32 | 48 | 64 | 64 | 98 | 115 | 132 | 132 | 132 | 132 | 132 | 98 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2738880
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 2 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 165120
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 16 | 16 | 0 |  |  |  | 20 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 25 |  | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 807394
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2553600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 | 2 | 2 | 4 | 3 | 3 | 4 | 2 | 1 | 1 | 0 | [8 empty] | 22201
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 110 | 85 | 85 | 85 | 85 | 85 | 51 | 51 | 51 | 51 | 67 | 68 | 82 | 85 | 85 | 85 | 68 | 68 |  | 72 | 110 | 110 | 110 | 110 | 110 | 110 | 2129372
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 33 | 85 | 83 | 87 | 86 | 50 | 20 | 403525
86 | Meghnaghat CCPP ( Summit) | 280 | 275 | 280 | 285 | 265 | 260 | 285 | 270 | 280 | 275 | 280 | 265 | 265 | 230 | 250 | 265 | 260 | 270 |  | 295 | 250 | 275 | 275 | 275 | 300 | 255 | 6617978
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 0 | [9 empty] | 17 | 35 | 37 | 72 | 35 | 35 | 35 |  | 45 | 104 | 104 | 104 | 104 | 90 | 70 | 961920
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 100 | 80 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 82 | 82 | 92 | 80 | 80 | 80 | 50 |  | 80 | 94 | 94 | 94 | 94 | 94 | 94 | 2101920
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 833240
94 | Gagnagar 102 MW PP (Digital Power) | 16 | 16 | 0 |  |  |  |  | 16 | 24 | 24 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 64 | 94 | 94 | 94 | 94 | 72 | 48 | 967392
95 | Patenga 50MW PP (Baraka) | [12 empty] | 11 | 25 | 25 | 25 | 25 | 25 |  | 26 | 45 | 49 | 50 | 50 | 50 | 24 | 418560
96 | Chattogram 108 MW PP (ECPV) | [25 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 15 | 15 | 0 | [8 empty] | 10 | 15 | 41 | 30 | 30 | 30 |  | 30 | 55 | 55 | 55 | 55 | 30 | 30 | 558998
100 | Manikganj 55 MW PP (Northern) | 55 | 0 | [7 empty] | 35 | 35 | 35 | 35 | 55 | 55 | 17 | 17 | 17 |  | 17 | 40 | 52 | 55 | 55 | 55 | 55 | 664288
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 10800
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1281240
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 59 | 217 | 51 | 58 | 30 |  | 0 | 240616
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 25 | 25 | 25 |  |  | 0 | 59340
106 | Mymensingh 200 MW PP (United) | 194 | 194 | 200 | 200 | 200 | 200 | 200 | 202 | 202 | 202 | 202 | 202 | 202 | 202 | 170 | 100 | 100 | 100 |  | 132 | 194 | 194 | 195 | 195 | 196 | 196 | 4459200
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 27 | 99 | 100 | 53 | 52 |  | 0 | 246401
114 | Kodda 149 MW PP Unit-1 (Summit) | 123 | 56 | 23 | 17 | 16 | 16 | 15 | 16 | 16 | 40 | 59 | 87 | 87 | 89 | 100 | 100 | 84 | 80 |  | 85 | 149 | 142 | 149 | 149 | 115 | 115 | 1834560
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | 20 | 20 | 20 | 0 |  |  |  | 10 | 10 | 10 | 40 | 70 | 100 | 100 | 50 | 50 | 50 |  | 90 | 100 | 100 | 100 | 100 | 80 | 50 | 1118400
116 | Chandpur 200MW (Desh energy) | 194 | 189 | 193 | 100 | 50 | 17 | 17 | 17 | 17 | 17 | 41 | 51 | 97 | 116 | 120 | 120 | 120 | 68 |  | 85 | 150 | 178 | 200 | 195 | 198 | 198 | 2716320
117 | Ashuganj 150MW PP (Midland) | 150 | 147 | 147 | 147 | 147 | 20 | 10 | 35 | 128 | 145 | 140 | 135 | 137 | 143 | 150 | 140 | 140 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3198254
118 | Bibiyana-III 400 MW CCPP | 367 | 365 | 365 | 377 | 364 | 367 | 382 | 366 | 366 | 351 | 366 | 364 | 386 | 366 | 366 | 367 | 367 | 367 |  | 410 | 415 | 416 | 417 | 402 | 402 | 402 | 9076000
| Jamalpur 115 MW PP (United) | 102 | 102 | 103 | 103 | 103 | 65 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 14 | 59 | 95 | 105 | 106 |  | 106 | 106 | 106 | 107 | 107 | 107 | 108 | 1658400
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 20 | 10 | 10 | 50 | 70 | 70 | 70 | 100 | 100 | 100 | 100 | 50 | 50 |  | 90 | 100 | 100 | 100 | 100 | 100 | 100 | 1931520
| Anlima Energy Ltd. | 111 | 111 | 93 | 93 | 93 | 92 | 92 | 92 | 92 | 92 | 92 | 91 | 92 | 92 | 92 | 92 | 92 | 81 |  | 81 | 95 | 94 | 95 | 107 | 112 | 111 | 2304600
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 891000
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 8 | 12 | 14 | 14 | 18 | 17 | 8 | 4 | 14 | 5 | 2 | [8 empty] | 125945
120 | Eastern Zone Total | 8566 | 8242 | 7929 | 7749 | 7603 | 7180 | 6976 | 6920 | 7189 | 7333 | 7488 | 7645 | 7884 | 7859 | 8094 | 7860 | 7728 | 7280 |  | 8147 | 9155 | 9091 | 9200 | 9161 | 8944 | 8790 | 193258615
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 5 |  | 17 | 23 | 22 | 15 | 20 | 22 | 15 | 176640
| Khulna 225 MW CCPP | 40 | 0 | [18 empty] | 60 | 130 | 130 | 140 | 140 | 140 | 682196
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 70 | 53 | 53 | 70 | 70 | 70 | 70 | 89 | 105 | 105 | 105 | 105 | 53 |  | 77 | 105 | 105 | 105 | 105 | 105 | 105 | 2214720
130
131
132 | United Payra Power Ltd. | 150 | 150 | 150 | 150 | 150 | 100 | [9 empty] | 14 | 17 | 17 |  | 19 | 150 | 150 | 150 | 150 | 150 | 150 | 1759200
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 222 | 223 | 224 | 222 | 222 | 224 | 190 | 182 | 181 | 181 | 181 | 181 | 176 | 181 | 181 | 181 | 181 |  | 219 | 204 | 217 | 221 | 220 | 221 | 222 | 4887709
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 110 | 97 | 80 | 64 | 64 | 0 | [13 empty] | 7 | 48 | 48 | 64 | 64 | 64 | 64 | 777216
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 71 | 70 | 69 | 70 | 69 | 69 | 70 | 70 | 34 | 34 | 36 | 72 | 72 | 79 | 80 | 69 | 78 | 81 |  | 81 | 81 | 82 | 81 | 82 | 82 | 81 | 1708608
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 33 | 32 | 30 | 25 | 24 | 25 | 25 | 24 | 25 | 25 | 28 | 28 | 26 | 24 | 23 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 691924
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 70 | 20 | 0 | [14 empty] | 4 | 100 | 100 | 100 | 100 | 100 | 100 | 868800
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 40 | 40 | 46 | 46 | 50 | 0 | [17 empty] | 15 | 15 | 15 | 302400
146 | Bheramara HVDC | 798 | 798 | 798 | 798 | 798 | 798 | 791 | 792 | 792 | 791 | 791 | 791 | 791 | 792 | 792 | 791 | 791 | 791 |  | 791 | 791 | 791 | 791 | 791 | 791 | 791 | 19167273
147 | Bheramara 410 MW CCPP | 325 | 330 | 335 | 340 | 340 | 345 | 350 | 355 | 350 | 340 | 330 | 315 | 305 | 290 | 285 | 285 | 280 | 280 |  | 285 | 270 | 265 | 260 | 255 | 255 | 255 | 7669152
148 | Payra 1320 MW | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7434100
149
150 | Barapukuria TPP Unit-1 | 48 | 77 | 78 | 75 | 79 | 73 | 73 | 73 | 70 | 72 | 74 | 74 | 78 | 79 | 74 | 73 | 72 | 72 |  | 72 | 70 | 73 | 72 | 72 | 73 | 72 | 1686110
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 149 | 149 | 150 | 149 | 150 | 149 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 150 | 150 | 150 | 3662100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | 50 | 0 | [7 empty] | 34 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 760032
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 3 | 4 | 4 | 3 | 0 | 0 | [8 empty] | 22860
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3681491
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 187 | 187 | 187 | 187 | 187 | 189 | 194 | 193 | 191 | 187 | 186 | 182 | 179 | 178 | 178 | 178 | 178 | 178 |  | 177 | 175 | 175 | 175 | 172 | 169 | 167 | 4617827
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 306 | 362 | 359 | 362 | 332 | 330 | 355 | 312 | 393 | 416 | 402 | 414 | 408 | 333 | 348 | 358 | 361 | 364 |  | 381 | 374 | 378 | 410 | 394 | 418 | 395 | 9072873
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 20 | 20 | 0 | [13 empty] | 5 | 5 |  | 25 | 27 | 22 | 20 | 20 | 21 | 12 | 174165
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 0 | 0 | 0 |  | 18 | 21 | 22 | 22 | 22 | 22 | 22 | 440400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 250452
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 0 | [5 empty] | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 628950
166 | Katakhali 50 MW PP (Northern) | 43 | 43 | 0 | [7 empty] | 24 | 43 | 43 | 43 | 50 | 24 | 24 | 16 |  | 50 | 50 | 50 |  |  |  | 0 | 415137
167 | Katakhali 50 MW Peaking PP | 29 | 29 | 29 | 29 | 22 | 22 | 22 | 22 | 22 | 22 | 15 | [6 empty] | 35 |  | 28 | 30 | 38 | 35 | 35 | 28 | 28 | 426310
168 | Santahar 50 MW Peaking PP | 27 | 21 | 20 | 20 | 20 | 21 | [11 empty] | 15 |  | 29 | 29 | 30 | 29 | 29 | 29 | 29 | 309220
169 | Natore 52 MW PP (Rajlanka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 546240
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 75 | 75 | 60 | 60 | 60 | 51 | 51 | 51 | 51 | 51 | 59 |  | 91 | 91 | 91 | 91 | 91 | 91 | 90 | 1796672
171 | Baghabari 200 MW PP (Paramount) | [20 empty] | 50 | 50 | 50 |  |  | 0 | 114540
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 70 | 0 | [5 empty] | 5 | 50 | 68 | 94 | 94 | 35 | 35 |  | 40 | 94 | 93 | 94 | 94 | 94 | 94 | 1400256
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 70 | 0 |  |  |  |  | 50 | 90 | 113 | 113 | 113 | 70 | 35 | 35 |  | 70 | 113 | 113 | 113 | 113 | 113 | 113 | 1847616
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 70 | 70 | 70 | 0 | [5 empty] | 34 | 38 | 90 | 113 | 60 | 34 | 34 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1528444
177 | Sympa Solar Power 8MW | [5 empty] | 0 |  | 1 | 1 | 1 | 3 | 2 | 1 | 1 | 2 | 1 | 1 | 0 | [8 empty] | 11510
178
178