## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-19 | Monday
|  |  | Date (day): | 2021-07-19 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13966.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14920 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-18 | 2021-07-19 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 133 | 133 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
| 4 | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 78 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 5 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 108 | 108
| 6 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 7 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 276 | 276 | 280 | 280 | 132 |  | Gas shortage
| 8 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 106 | 145 | 190 | 190 | 170 |  | Gas shortage
| 9 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 220 | 220 | 220 | 220 | 230 |  | Gas shortage
| 10 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 11 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 285 | 300 | 305 |  |  | FGMO
| 12 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 13 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 18 | 55 | 55 | 55
| 14 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 1 | 75 | 70 | 100
| 15 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 20 | 20
| 16 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 17 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 18 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 80 | 95 | 100 | 100
| 19 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 323 | 333 | 335 | 335
| 20 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 48 | 100 | 100 | 102
| 21 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 22 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 23 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 133 | 133 | 133 | 133 |  | 16 | Engine problem
| 24 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 17 | 55 | 55
| 25 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 26 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 27 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 46 | 55 | 55 |  | 25 | Engine problem
| 28 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 0 | 33 | 33
| 30 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 51 | 52 | 52
| 31 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 32 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 201 | 268 | 270 | 270 |  | 30 | Engine problem
| 33 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 300 | 100 | 300
| 34 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 35 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 102 | 100 | 100
| 36 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 55 | 149 | 149 | 149
| 37 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| 38 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 17 | 92 | 92 | 104
| 39 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 40 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6256 | 5819 | 2826 | 3603 | 3651 | 3870 | 901 | 1006
| 41 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 42 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 43 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 10 | 0 | 20 | 0
| 44 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 45 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 123 | 120 | 120 | 110 |  | Low water lavel
| 46 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 217 | 203 | 225 | 225 |  |  | FGMO
| 47 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 49 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 50 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 51 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 70 | 82 | 82 | 100
| 52 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 70 | 70 | 100 | 100
| 53 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 20 | 10 | 25
| 54 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 55 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 56 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 57 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 58 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 85 | 51 | 110 | 110
| 59 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 60 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 112 | 112 | 112 | 112
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1159 | 1232 | 1611 | 1719 | 478 | 179
| 61 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 70 | 120 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 62 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 211 | 131 | 210 | 210 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 260 | 300 | 320 |  |  | FGMO
| 64 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 260 | 300 | 320 |  |  | FGMO
| 65 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 66 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 50 | 30 | 55 | 55
| 67 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 68 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 34 | 43 | 43 | 43 |  | 8 | Engine problem
| 69 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 142 | 150 | 150 | 150
| 70 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 71 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 0 | 90 | 90 |  | 73 | Machine problem
| 72 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 180 | 0 | 170 | 200
| 73 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 22 | 22 | 22
| 74 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 140 | 148 | 172
| 75 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 76 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 77 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 20 | 21 | 21
| 78 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 79 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 100 | 17 | 100 |  |  | Fuel shortage
| 80 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 110 | 116 | 113 | 113
| 81 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1813 | 1730 | 2047 | 2339 | 316 | 280
| 82 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 114 | 132 | 155 | 150 | 52 |  | Gas shortage
| 83 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 84 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 85 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 86 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 194 | 175 | 200
| 87 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 106 | 115 | 115
| 88 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 52 | 0 | 50 | 0
| 89 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 436 | 485 | 547.6 | 516 | 52 | 87
| 90 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 91 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 28 | 22 | 22 | 22 |  | 68 | Machine problem.
| 92 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 93 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 163 | 163 | 163 |  | 167 | GT-1 Under maint
| 94 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 53 | 51 | 51
| 95 | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 44 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 96 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 97 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 61 | 62 | 63
| 98 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 83 | 84 | 84
| 99 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 100 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 225 | 225
| 101 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
| 102 | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 50 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 103 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 104 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 310 | 300 | 310 |  |  | FGMO
| 105 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 368 | 400 | 400
| 106 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 107 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 393 | 397 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2516 | 2377 | 1783 | 1775 | 1805 | 1816 | 0 | 534
| 108 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 807 | 807 | 824 | 824
| 109 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 110 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 0 | 20 |  | 34 | Engine problem
| 111 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 155 | 0 | 160 |  | 70 | ST not available
| 112 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 113 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 270 | 265 | 270 | 270 | 140 |  | Gas shortage
| 114 | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 40 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 115 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 116 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 90 | 105 | 105 | 105
| 117 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2288 | 2129 | 1167 | 1452 | 1349 | 1639 | 140 | 153
| 118 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 119 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 26 | 33
| 120 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 121 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 69 | 76 | 76 | 76 | 19 |  | Gas shortage
| 122 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 280 | 500 | 622 | 622
|  | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 0 | 0 | 218 | 220 | 220 | 220
| 123 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 72 | 81 | 110 | 110
|  | Barisal Area Total |  |  |  |  | 1826 | 1826 | 664 | 927 | 1164 | 1171 | 19 | 194
| 124 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 125 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 126 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 20 | 20 | 20 |  | 51 | Engine problem
| 127 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
| 128 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 129 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 31 | 31 |  | 19 | Engine problem
| 130 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 131 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 140 | 140 | 140 | 140 |  |  | Gas shortage
| 132 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 181 | 170 | 200 | 200 |  |  | FGMO
| 133 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 412 | 408 | 400 | 400 |  |  | FGMO
| 134 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 30 |  | 20 | Engine problem
| 135 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 20 | 21 | 22 | 22
| 136 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 137 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 5 | 11 | 11
| 138 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 8 | 30 | 52
| 139 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 47 | 90 | 95 | 95 |  | 9 | Engine problem
| 140 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 200 | 200 | 200
| 141 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 75 | 94 | 94 | 94 |  | 19 | Engine problem
| 142 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 143 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1042 | 1411 | 1447 | 1493 | 430 | 133
| 144 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 75 | 74 | 74 |  | 15 | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 145 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 146 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 147 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 148 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 90 | 113 | 113 | 113
| 149 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 320 | 338 | 345 | 357 | 124 | 120
|  | Total |  |  |  |  | 22023 | 21060 | 11210 | 12953 | 13966.6 | 14920 | 2460 | 2686
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10678.6219 | 12339 | 13304.5532 | 14212.76
| A. |  | 2021-07-18 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12953 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9707 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12953 | MW
| 3 | Day peak Generation : |  |  | 11210 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12339 | MW
| 4 | Evening peak Generation : |  |  | 12953 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 274.612 | MKWHr | By Solar | 0.67405 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 155.4122 | MKWHr |  | By Oil: | 79.131 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.6342 | MKWHr |  | By Hydro: | 2.5186 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2460 | MW | Dhaka | 4126 | 4126 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2686 | MW | Chittagong | 1308 | 1308 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5146 | MW | Khulna | 1621 | 1621 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1174.67 | MMCFD |  |  | Rajshahi | 1384 | 1384 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 161926511.23 | ii) Oil : | Taka | 578596592.08 | Comilla | 1161 | 1161 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 70927520 | Total | Taka | 811450623.31 | Mymensingh | 1024 | 1024 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.8225 | MKWHr. | Sylhet | 531 | 531 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -316 | MW (E to W) at | 21:00 | hrs | Barisal | 392 | 392 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -460 | MW at | 19:30 | hrs | Rangpur | 792 | 792 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.8° C |  |  | Total | 12339 | 12339 |  | 0
| B. |  | 2021-07-19 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14920 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1920 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 275.6084 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9616 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.504 | MKWHr. | ii) HVDC Flow at Peak Time |  | 807 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7379 | MKWHr. | iii) Maximum HVDC Flow : |  | 809 | MW at | 4:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 82.58 |  | (b) Today: | 82.98 |  | (c) Rule Curve: |  | 86.88
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-18
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 189 | 0 | 0 | 300 | 105 | 0 | 277 | 247 |  | 0 | 220 | 275 | 0 | 0 | 15 | 335 | 0 | 0 | 96 | 7 | 150 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 16 | 25 | 30 | 33 | 33 | 52 | 0 | 28 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 19 | 0 | 36 | 94 | 0 | 0 | 22 | 33 | 80 | 0 | 0 | 260 | 260 | 218 | 8 | 137 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 120 | 147 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 160 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 275 | 16 | 11 | 0 | 225 | 0 | 0 | 196 | 0 | 50 | 0 | 50 | 198 | 150 | 401 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 105 | 106 | 100 | 400 | 0 | 0 | 162 | 112 | 0 | 36 | 0 |  | 807 | 0 | 255 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 50 | 8 | 90 | 35 | 0 | 22 | 16 | 28 | 22 | 0 | 11 | 76 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 81 | 100 | 166 | 0 | 389 | 105 | 0 | 35 | 15 | 113 | 0 | 0 | 113 | 280 | 215 | 0 | 150 | 0 |  | 8480 | 3609 | 12089 | 4820 | 807 | 1859 | 3424 | 506 | 88 | 465 | 120 | 0 | 0 | 82.53
2:00 | 0 | 189 | 0 | 0 | 300 | 106 | 0 | 277 | 271 |  | 0 | 220 | 300 | 0 | 0 | 15 | 335 | 0 | 0 | 96 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 16 | 25 | 30 | 33 | 33 | 52 | 0 | 28 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 20 | 0 | 0 | 94 | 0 | 0 | 20 | 33 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 130 | 26 | 56 | 0 | 34 | 0 | 41 | 43 | 22 | 11 | 33 | 20 | 118 | 147 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 275 | 16 | 11 | 0 | 95 | 0 | 0 | 195 | 0 | 35 | 0 | 10 | 198 | 145 | 402 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 107 | 100 | 400 | 0 | 0 | 162 | 112 | 0 | 17 | 0 |  | 808 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 64 | 0 | 0 | 0 | 50 | 0 | 90 | 35 | 0 | 22 | 16 | 20 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 82 | 100 | 168 | 0 | 362 | 105 | 0 | 0 | 15 | 70 | 0 | 0 | 90 | 280 | 221 | 0 | 150 | 0 |  | 8182 | 3435 | 11617 | 4817 | 808 | 1865 | 3045 | 503 | 88 | 373 | 118 | 0 | 0 | 82.54
3:00 | 0 | 169 | 0 | 0 | 300 | 106 | 0 | 277 | 277 |  | 0 | 220 | 275 | 0 | 0 | 0 | 335 | 0 | 0 | 96 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 30 | 33 | 33 | 52 | 0 | 29 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 94 | 0 | 0 | 20 | 33 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 136 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 116 | 153 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 196 | 0 | 16 | 0 | 0 | 198 | 147 | 401 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 107 | 60 | 400 | 0 | 0 | 162 | 112 | 0 | 17 | 0 |  | 808 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 64 | 0 | 0 | 0 | 50 | 0 | 93 | 35 | 0 | 22 | 16 | 22 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 83 | 60 | 169 | 0 | 385 | 105 | 0 | 0 | 15 | 34 | 0 | 0 | 50 | 280 | 222 | 0 | 150 | 0 |  | 7930 | 3349 | 11279 | 4809 | 808 | 1905 | 2712 | 503 | 89 | 337 | 116 | 0 | 0 | 82.55
4:00 | 0 | 189 | 0 | 0 | 300 | 106 | 0 | 277 | 287 |  | 0 | 220 | 275 | 0 | 0 | 0 | 334 | 0 | 0 | 96 | 0 | 150 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 30 | 33 | 33 | 52 | 0 | 29 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 94 | 0 | 0 | 21 | 33 | 80 | 0 | 0 | 260 | 260 | 217 | 8 | 137 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 112 | 153 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 161 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 195 | 0 | 16 | 0 | 0 | 85 | 147 | 401 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 107 | 0 | 400 | 0 | 0 | 162 | 112 | 0 | 17 | 0 |  | 809 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 64 | 0 | 0 | 0 | 50 | 0 | 93 | 35 | 0 | 22 | 16 | 21 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 71 | 10 | 172 | 0 | 367 | 105 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 280 | 223 | 0 | 150 | 0 |  | 7783 | 3236 | 11019 | 4848 | 809 | 1884 | 2438 | 503 | 89 | 336 | 112 | 0 | 0 | 82.56
5:00 | 0 | 189 | 0 | 0 | 300 | 106 | 0 | 277 | 292 |  | 0 | 220 | 275 | 0 | 0 | 0 | 334 | 0 | 0 | 96 | 0 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 35 | 16 | 25 | 27 | 33 | 33 | 52 | 0 | 29 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 94 | 0 | 0 | 21 | 33 | 80 | 0 | 0 | 260 | 260 | 218 | 8 | 132 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 108 | 154 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 161 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 195 | 0 | 16 | 0 | 0 | 85 | 100 | 403 | 108 | 105 | 105 | 0 | 0 | 0 | 110 | 34 | 107 | 0 | 400 | 0 | 0 | 108 | 112 | 0 | 17 | 0 |  | 808 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 64 | 0 | 0 | 0 | 0 | 0 | 93 | 35 | 0 | 22 | 16 | 22 | 22 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 10 | 177 | 0 | 357 | 105 | 0 | 0 | 15 | 34 | 0 | 0 | 0 | 280 | 222 | 0 | 150 | 0 |  | 7637 | 3178 | 10815 | 4849 | 808 | 1887 | 2337 | 502 | 89 | 235 | 108 | 0 | 0 | 82.57
6:00 | 0 | 189 | 0 | 0 | 300 | 106 | 0 | 277 | 272 |  | 0 | 220 | 275 | 0 | 0 | 0 | 334 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 16 | 25 | 26 | 33 | 33 | 16 | 0 | 28 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 94 | 0 | 0 | 21 | 33 | 80 | 0 | 0 | 260 | 260 | 216 | 8 | 137 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 98 | 153 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 162 | 62 | 81 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 16 | 1 | 0 | 17 | 10 | 403 | 108 | 70 | 105 | 0 | 0 | 0 | 51 | 34 | 107 | 0 | 400 | 0 | 1 | 17 | 112 | 0 | 17 | 1 |  | 808 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 16 | 22 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 181 | 0 | 389 | 105 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 280 | 221 | 0 | 100 | 0 |  | 6901 | 3017 | 9918 | 4849 | 808 | 1875 | 1585 | 504 | 88 | 108 | 98 | 3 | 0 | 82.58
7:00 | 0 | 189 | 0 | 0 | 300 | 106 | 0 | 277 | 216 |  | 0 | 220 | 300 | 0 | 0 | 0 | 334 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 16 | 25 | 26 | 33 | 33 | 16 | 0 | 27 | 60 | 100 | 0 | 25 | 212 | 0 | 120 | 0 |  | 0 | 0 | 0 | 50 | 0 | 0 | 21 | 33 | 80 | 0 | 0 | 295 | 295 | 214 | 8 | 136 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 68 | 152 | 8 | 21 | 0 | 43 | 0 | 47 | 0 | 0 | 163 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 16 | 7 | 0 | 17 | 10 | 403 | 108 | 70 | 105 | 0 | 0 | 0 | 34 | 34 | 107 | 0 | 400 | 0 | 8 | 17 | 112 | 0 | 17 | 5 |  | 809 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 24 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 70 | 0 | 186 | 0 | 372 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 221 | 0 | 54 | 0 |  | 6815 | 2903 | 9718 | 4933 | 809 | 1812 | 1424 | 503 | 87 | 62 | 68 | 20 | 0 | 82.59
8:00 | 0 | 189 | 0 | 0 | 300 | 105 | 0 | 277 | 177 |  | 0 | 220 | 290 | 0 | 0 | 0 | 330 | 0 | 0 | 24 | 3 | 10 | 0 | 0 | 0 | 0 | 35 | 0 | 45 | 16 | 25 | 22 | 33 | 33 | 20 | 0 | 27 | 60 | 100 | 0 | 25 | 210 | 0 | 120 | 0 |  | 0 | 0 | 0 | 80 | 0 | 0 | 19 | 7 | 80 | 0 | 0 | 270 | 275 | 214 | 8 | 137 | 26 | 56 | 0 | 34 | 0 | 0 | 43 | 19 | 0 | 33 | 20 | 76 | 148 | 8 | 21 | 1 | 43 | 0 | 47 | 0 | 0 | 162 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 21 | 11 | 0 | 18 | 13 | 403 | 107 | 84 | 105 | 1 | 0 | 0 | 34 | 17 | 107 | 6 | 400 | 0 | 13 | 17 | 112 | 0 | 17 | 12 |  | 807 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 24 | 0 | 0 | 16 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 186 | 0 | 400 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 221 | 0 | 54 | 1 |  | 6791 | 2916 | 9707 | 4863 | 807 | 1783 | 1475 | 505 | 87 | 72 | 76 | 39 | 0 | 82.6
9:00 | 0 | 189 | 0 | 0 | 300 | 102 | 0 | 277 | 155 |  | 0 | 220 | 245 | 0 | 0 | 0 | 330 | 0 | 0 | 60 | 24 | 98 | 0 | 0 | 0 | 0 | 54 | 0 | 55 | 0 | 25 | 22 | 33 | 33 | 42 | 0 | 26 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 9 | 0 | 0 | 80 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 260 | 265 | 214 | 8 | 137 | 26 | 55 | 0 | 34 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 76 | 131 | 8 | 21 | 2 | 44 | 0 | 47 | 0 | 0 | 161 | 61 | 81 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 5 | 0 | 0 | 0 | 0 | 60 | 0 | 45 | 15 | 10 | 55 | 61 | 403 | 97 | 105 | 105 | 2 | 0 | 0 | 57 | 17 | 108 | 50 | 400 | 0 | 17 | 39 | 112 | 0 | 17 | 22 |  | 807 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 24 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 68 | 0 | 182 | 0 | 419 | 90 | 0 | 8 | 0 | 0 | 0 | 0 | 25 | 280 | 220 | 0 | 72 | 1 |  | 7121 | 2955 | 10076 | 4811 | 807 | 1779 | 1810 | 503 | 86 | 145 | 76 | 59 | 0 | 82.85
10:00 | 0 | 189 | 0 | 0 | 300 | 102 | 0 | 274 | 133 |  | 0 | 220 | 275 | 0 | 0 | 0 | 328 | 0 | 0 | 80 | 24 | 133 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 26 | 60 | 100 | 0 | 25 | 208 | 0 | 120 | 0 |  | 22 | 0 | 0 | 80 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 275 | 280 | 212 | 8 | 137 | 26 | 52 | 0 | 34 | 0 | 0 | 43 | 19 | 11 | 33 | 20 | 96 | 116 | 8 | 21 | 2 | 43 | 0 | 47 | 0 | 0 | 160 | 60 | 81 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 5 | 0 | 11 | 0 | 0 | 60 | 0 | 45 | 19 | 10 | 121 | 130 | 402 | 97 | 105 | 105 | 2 | 0 | 0 | 85 | 17 | 108 | 100 | 400 | 0 | 26 | 135 | 112 | 0 | 17 | 33 |  | 807 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 8 | 0 | 12 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 68 | 0 | 181 | 0 | 397 | 90 | 0 | 35 | 0 | 34 | 0 | 0 | 70 | 280 | 218 | 0 | 72 | 4 |  | 7592 | 3039 | 10631 | 4818 | 807 | 1720 | 2336 | 502 | 86 | 180 | 96 | 86 | 0 | 82.62
11:00 | 0 | 133 | 0 | 0 | 300 | 102 | 0 | 276 | 121 |  | 0 | 220 | 275 | 0 | 0 | 9 | 327 | 0 | 0 | 70 | 32 | 133 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 16 | 25 | 22 | 33 | 33 | 51 | 0 | 58 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 0 | 19 | 2 | 80 | 0 | 0 | 270 | 280 | 212 | 8 | 137 | 26 | 50 | 0 | 34 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 104 | 117 | 8 | 21 | 2 | 43 | 0 | 47 | 0 | 0 | 161 | 60 | 82 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 5 | 0 | 60 | 0 | 0 | 75 | 0 | 45 | 10 | 70 | 178 | 142 | 402 | 65 | 105 | 105 | 3 | 0 | 0 | 85 | 17 | 108 | 100 | 400 | 0 | 27 | 162 | 112 | 0 | 17 | 28 |  | 807 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 8 | 0 | 21 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 181 | 0 | 408 | 90 | 0 | 62 | 0 | 34 | 0 | 4 | 90 | 280 | 218 | 0 | 72 | 2 |  | 7740 | 3100 | 10840 | 4764 | 807 | 1717 | 2570 | 504 | 118 | 180 | 104 | 76 | 0 | 82.63
12:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 106 |  | 0 | 220 | 280 | 0 | 0 | 18 | 323 | 0 | 0 | 80 | 48 | 133 | 1 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 42 | 0 | 58 | 60 | 100 | 0 | 25 | 217 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 0 | 21 | 2 | 80 | 0 | 0 | 280 | 285 | 211 | 8 | 137 | 26 | 50 | 0 | 34 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 108 | 114 | 8 | 21 | 2 | 43 | 28 | 47 | 0 | 0 | 160 | 60 | 79 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 201 | 0 | 0 | 100 | 0 | 55 | 10 | 70 | 180 | 142 | 402 | 115 | 105 | 105 | 4 | 0 | 0 | 85 | 17 | 110 | 100 | 393 | 17 | 52 | 162 | 112 | 0 | 17 | 33 |  | 807 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 181 | 0 | 412 | 90 | 0 | 75 | 0 | 90 | 0 | 5 | 113 | 280 | 218 | 0 | 72 | 3 |  | 8017 | 3193 | 11210 | 4804 | 807 | 1600 | 2979 | 505 | 118 | 180 | 108 | 109 | 0 | 82.88
13:00 | 0 | 134 | 0 | 0 | 300 | 0 | 0 | 276 | 106 |  | 0 | 220 | 275 | 0 | 0 | 48 | 326 | 0 | 0 | 88 | 48 | 118 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 42 | 0 | 59 | 60 | 100 | 0 | 25 | 205 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 13 | 20 | 10 | 80 | 0 | 0 | 260 | 265 | 209 | 8 | 136 | 26 | 52 | 0 | 34 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 122 | 112 | 8 | 21 | 2 | 43 | 28 | 47 | 0 | 0 | 162 | 60 | 80 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 260 | 0 | 0 | 100 | 0 | 100 | 7 | 100 | 198 | 142 | 403 | 115 | 105 | 105 | 5 | 0 | 0 | 85 | 17 | 108 | 100 | 395 | 70 | 42 | 162 | 112 | 0 | 17 | 33 |  | 808 | 0 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 8 | 0 | 19 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 67 | 0 | 178 | 0 | 407 | 90 | 0 | 90 | 0 | 113 | 0 | 5 | 113 | 280 | 218 | 0 | 72 | 4 |  | 8215 | 3218 | 11433 | 4747 | 808 | 1594 | 3275 | 505 | 119 | 165 | 122 | 98 | 0 | 82.89
14:00 | 0 | 135 | 0 | 0 | 300 | 0 | 0 | 275 | 109 |  | 0 | 220 | 240 | 0 | 0 | 55 | 325 | 0 | 0 | 87 | 48 | 125 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 46 | 0 | 61 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 82 | 0 | 17 | 20 | 5 | 80 | 0 | 0 | 260 | 265 | 215 | 8 | 136 | 26 | 53 | 0 | 34 | 0 | 2 | 43 | 21 | 11 | 33 | 20 | 120 | 112 | 8 | 21 | 2 | 43 | 28 | 50 | 0 | 0 | 162 | 60 | 80 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 8 | 0 | 265 | 0 | 0 | 112 | 0 | 106 | 6 | 90 | 198 | 145 | 403 | 115 | 105 | 105 | 4 | 0 | 0 | 85 | 17 | 110 | 100 | 400 | 92 | 48 | 162 | 112 | 0 | 17 | 4 |  | 808 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 19 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 68 | 0 | 178 | 0 | 380 | 90 | 0 | 94 | 0 | 106 | 0 | 5 | 113 | 280 | 218 | 0 | 72 | 4 |  | 8244 | 3186 | 11430 | 4751 | 808 | 1560 | 3316 | 505 | 121 | 176 | 120 | 73 | 0 | 82.9
15:00 | 0 | 135 | 0 | 0 | 300 | 0 | 0 | 275 | 122 |  | 0 | 220 | 280 | 0 | 0 | 55 | 325 | 0 | 0 | 87 | 48 | 132 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 21 | 33 | 33 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 0 | 82 | 0 | 22 | 20 | 5 | 80 | 0 | 0 | 260 | 270 | 215 | 8 | 137 | 26 | 54 | 0 | 34 | 0 | 41 | 43 | 21 | 11 | 33 | 20 | 128 | 115 | 8 | 21 | 2 | 44 | 28 | 50 | 0 | 0 | 160 | 61 | 79 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 8 | 0 | 268 | 0 | 0 | 140 | 0 | 132 | 9 | 90 | 197 | 150 | 405 | 115 | 105 | 105 | 2 | 0 | 0 | 85 | 17 | 108 | 100 | 390 | 94 | 42 | 162 | 112 | 0 | 17 | 2 |  | 808 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 46 | 0 | 45 | 35 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 67 | 0 | 175 | 0 | 408 | 105 | 0 | 94 | 0 | 113 | 0 | 4 | 113 | 280 | 218 | 0 | 72 | 4 |  | 8428 | 3277 | 11705 | 4748 | 808 | 1610 | 3450 | 505 | 123 | 268 | 128 | 65 | 0 | 82.91
16:00 | 0 | 134 | 0 | 0 | 300 | 0 | 0 | 275 | 136 |  | 0 | 220 | 265 | 0 | 0 | 15 | 339 | 0 | 0 | 80 | 48 | 132 | 10 | 0 | 0 | 0 | 54 | 17 | 55 | 0 | 25 | 21 | 33 | 0 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 19 | 20 | 5 | 80 | 0 | 0 | 260 | 265 | 212 | 8 | 137 | 26 | 54 | 0 | 34 | 0 | 46 | 34 | 21 | 11 | 33 | 20 | 118 | 130 | 8 | 21 | 1 | 44 | 28 | 50 | 0 | 0 | 161 | 61 | 79 | 0 | 190 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 220 | 0 | 0 | 100 | 0 | 100 | 12 | 90 | 197 | 150 | 404 | 115 | 105 | 105 | 2 | 0 | 0 | 85 | 17 | 105 | 100 | 392 | 54 | 30 | 162 | 112 | 0 | 17 | 1 |  | 807 | 0 | 255 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 50 | 5 | 45 | 35 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 66 | 0 | 173 | 0 | 319 | 105 | 0 | 50 | 0 | 58 | 0 | 3 | 113 | 310 | 218 | 0 | 72 | 1 |  | 8071 | 3119 | 11190 | 4687 | 807 | 1534 | 3050 | 535 | 123 | 286 | 118 | 50 | 0 | 82.92
17:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 275 | 156 |  | 0 | 220 | 255 | 0 | 0 | 15 | 300 | 0 | 0 | 92 | 48 | 132 | 0 | 0 | 0 | 0 | 35 | 17 | 55 | 16 | 25 | 21 | 33 | 0 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 12 | 20 | 8 | 80 | 0 | 0 | 260 | 265 | 189 | 8 | 138 | 26 | 54 | 0 | 34 | 0 | 48 | 36 | 21 | 11 | 33 | 20 | 102 | 135 | 8 | 21 | 1 | 44 | 0 | 50 | 0 | 0 | 162 | 61 | 83 | 0 | 190 | 18 | 0 | 10 | 295 | 16 | 11 | 0 | 200 | 0 | 0 | 100 | 0 | 56 | 4 | 50 | 155 | 150 | 405 | 115 | 105 | 105 | 1 | 0 | 0 | 85 | 17 | 105 | 50 | 400 | 17 | 5 | 162 | 112 | 0 | 17 | 1 |  | 807 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 5 | 45 | 35 | 0 | 0 | 8 | 0 | 21 | 0 | 0 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 66 | 0 | 173 | 0 | 310 | 105 | 0 | 50 | 0 | 36 | 0 | 2 | 50 | 380 | 151 | 0 | 35 | 1 |  | 7731 | 2983 | 10714 | 4625 | 807 | 1490 | 2663 | 605 | 123 | 284 | 102 | 15 | 0 | 82.92
18:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 275 | 162 |  | 0 | 220 | 255 | 0 | 0 | 15 | 270 | 0 | 0 | 95 | 48 | 82 | 0 | 0 | 0 | 0 | 54 | 17 | 55 | 16 | 25 | 21 | 33 | 0 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 12 | 20 | 5 | 80 | 0 | 0 | 260 | 265 | 158 | 8 | 136 | 26 | 56 | 0 | 43 | 0 | 48 | 43 | 21 | 11 | 33 | 20 | 98 | 138 | 8 | 21 | 0 | 44 | 22 | 14 | 0 | 0 | 163 | 40 | 20 | 0 | 190 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 190 | 0 | 0 | 100 | 0 | 56 | 0 | 10 | 155 | 150 | 315 | 107 | 105 | 105 | 0 | 0 | 0 | 85 | 17 | 113 | 10 | 350 | 17 | 0 | 108 | 112 | 0 | 17 | 1 |  | 808 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 50 | 18 | 51 | 35 | 0 | 21 | 8 | 3 | 21 | 0 | 0 | 76 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 68 | 0 | 173 | 0 | 272 | 105 | 0 | 50 | 0 | 34 | 0 | 1 | 50 | 380 | 151 | 0 | 35 | 0 |  | 7263 | 2988 | 10251 | 4427 | 808 | 1364 | 2546 | 606 | 123 | 277 | 98 | 2 | 0 | 82.92
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 160 |  | 0 | 220 | 300 | 0 | 0 | 20 | 300 | 0 | 0 | 95 | 84 | 133 | 8 | 0 | 0 | 0 | 54 | 17 | 55 | 16 | 25 | 16 | 33 | 17 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 215 | 0 | 120 | 0 |  | 24 | 0 | 51 | 70 | 0 | 17 | 20 | 5 | 80 | 0 | 0 | 285 | 295 | 152 | 8 | 137 | 26 | 30 | 0 | 43 | 0 | 49 | 40 | 21 | 11 | 33 | 20 | 138 | 132 | 8 | 21 | 0 | 44 | 22 | 21 | 0 | 0 | 161 | 61 | 30 | 0 | 217 | 18 | 0 | 10 | 280 | 16 | 11 | 45 | 215 | 35 | 36 | 130 | 48 | 64 | 0 | 54 | 160 | 150 | 379 | 105 | 105 | 105 | 0 | 0 | 0 | 85 | 36 | 114 | 80 | 375 | 53 | 0 | 135 | 112 | 0 | 17 | 0 |  | 807 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 50 | 18 | 90 | 35 | 0 | 21 | 8 | 26 | 21 | 0 | 11 | 76 | 0 | 150 | 15 | 0 | 0 | 0 | 140 | 0 | 77 | 5 | 160 | 0 | 377 | 105 | 0 | 56 | 0 | 100 | 0 | 0 | 90 | 390 | 151 | 0 | 58 | 0 |  | 8141 | 3375 | 11516 | 4669 | 807 | 1465 | 3225 | 616 | 123 | 473 | 138 | 0 | 0 | 82.94
19:30 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 155 |  | 0 | 220 | 255 | 0 | 0 | 55 | 333 | 0 | 0 | 95 | 94 | 133 | 73 | 0 | 0 | 0 | 54 | 35 | 55 | 16 | 25 | 16 | 33 | 17 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 70 | 0 | 40 | 20 | 11 | 80 | 0 | 0 | 260 | 265 | 148 | 8 | 131 | 26 | 30 | 0 | 43 | 0 | 50 | 43 | 21 | 11 | 33 | 20 | 138 | 132 | 8 | 21 | 0 | 44 | 22 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 145 | 230 | 110 | 50 | 192 | 100 | 100 | 0 | 90 | 180 | 150 | 366 | 105 | 105 | 105 | 0 | 0 | 0 | 85 | 100 | 116 | 100 | 400 | 92 | 0 | 162 | 112 | 0 | 17 | 0 |  | 807 | 0 | 270 | 0 | 0 | 60 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 0 | 28 | 8 | 28 | 21 | 0 | 11 | 75 | 0 | 150 | 17 | 0 | 0 | 0 | 140 | 0 | 77 | 100 | 170 | 0 | 406 | 105 | 50 | 90 | 0 | 107 | 0 | 0 | 113 | 420 | 200 | 0 | 100 | 0 |  | 8881 | 3818 | 12699 | 4650 | 807 | 1642 | 4147 | 645 | 123 | 547 | 138 | 0 | 0 | 0
20:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 150 |  | 0 | 220 | 285 | 0 | 0 | 55 | 331 | 0 | 0 | 95 | 94 | 133 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 21 | 33 | 17 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 210 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 47 | 20 | 7 | 80 | 0 | 0 | 285 | 290 | 132 | 8 | 0 | 26 | 30 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 136 | 132 | 8 | 21 | 0 | 43 | 22 | 53 | 0 | 0 | 163 | 61 | 83 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 195 | 268 | 102 | 0 | 193 | 100 | 146 | 0 | 70 | 0 | 150 | 382 | 105 | 105 | 105 | 0 | 0 | 0 | 51 | 100 | 114 | 100 | 392 | 93 | 0 | 162 | 112 | 0 | 17 | 0 |  | 807 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 0 | 31 | 8 | 29 | 21 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 79 | 170 | 0 | 409 | 105 | 50 | 94 | 0 | 113 | 0 | 0 | 113 | 430 | 220 | 0 | 81 | 0 |  | 8711 | 3866 | 12577 | 4574 | 807 | 1664 | 4025 | 654 | 123 | 594 | 136 | 0 | 0 | 82.93
21:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 145 |  | 0 | 220 | 285 | 0 | 0 | 55 | 333 | 0 | 0 | 95 | 100 | 133 | 75 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 21 | 33 | 0 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 50 | 20 | 20 | 70 | 0 | 0 | 260 | 260 | 131 | 8 | 0 | 26 | 30 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 140 | 132 | 8 | 21 | 0 | 44 | 22 | 53 | 0 | 0 | 163 | 61 | 83 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 11 | 200 | 268 | 300 | 0 | 194 | 102 | 149 | 0 | 70 | 0 | 150 | 368 | 106 | 105 | 105 | 0 | 0 | 0 | 51 | 100 | 116 | 100 | 397 | 92 | 0 | 162 | 112 | 0 | 17 | 0 |  | 807 | 0 | 265 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 0 | 28 | 8 | 29 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 100 | 170 | 0 | 408 | 105 | 200 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 220 | 0 | 81 | 0 |  | 8825 | 4128 | 12953 | 4468 | 807 | 1681 | 4383 | 725 | 123 | 626 | 140 | 0 | 0 | 82.94
22:00 | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 145 |  | 0 | 220 | 275 | 0 | 0 | 55 | 335 | 0 | 0 | 95 | 100 | 133 | 73 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 61 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 50 | 20 | 29 | 70 | 0 | 0 | 260 | 260 | 156 | 8 | 90 | 26 | 20 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 140 | 132 | 8 | 21 | 0 | 43 | 22 | 53 | 0 | 0 | 162 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 200 | 265 | 157 | 0 | 195 | 102 | 149 | 0 | 70 | 45 | 150 | 366 | 106 | 105 | 105 | 0 | 0 | 0 | 51 | 100 | 115 | 100 | 400 | 93 | 0 | 162 | 112 | 0 | 17 | 0 |  | 807 | 0 | 260 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 0 | 90 | 35 | 0 | 28 | 8 | 20 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 100 | 170 | 0 | 404 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 510 | 220 | 0 | 81 | 0 |  | 8850 | 3900 | 12750 | 4612 | 807 | 1667 | 4071 | 735 | 121 | 597 | 140 | 0 | 0 | 82.94
23:00 | 0 | 30 | 0 | 0 | 300 | 0 | 0 | 276 | 142 |  | 0 | 220 | 250 | 0 | 0 | 55 | 334 | 0 | 0 | 95 | 88 | 133 | 68 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 59 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 50 | 20 | 38 | 70 | 0 | 0 | 260 | 265 | 168 | 8 | 90 | 23 | 20 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 138 | 132 | 8 | 21 | 0 | 43 | 22 | 53 | 0 | 0 | 162 | 56 | 84 | 0 | 218 | 18 | 0 | 10 | 300 | 16 | 11 | 200 | 265 | 108 | 0 | 184 | 52 | 149 | 0 | 100 | 132 | 150 | 368 | 106 | 105 | 105 | 0 | 0 | 0 | 55 | 100 | 104 | 100 | 398 | 93 | 0 | 162 | 112 | 0 | 17 | 0 |  | 808 | 0 | 260 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 0 | 90 | 35 | 0 | 28 | 8 | 20 | 21 | 0 | 0 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 75 | 100 | 170 | 0 | 413 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 550 | 220 | 0 | 81 | 0 |  | 8715 | 3943 | 12658 | 4512 | 808 | 1681 | 4029 | 774 | 119 | 597 | 138 | 0 | 0 | 82.95
24:00 | 0 | 23 | 0 | 0 | 300 | 0 | 0 | 276 | 175 |  | 0 | 220 | 250 | 0 | 0 | 55 | 334 | 0 | 0 | 95 | 102 | 133 | 69 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 0 | 25 | 204 | 0 | 120 | 0 |  | 24 | 0 | 51 | 82 | 0 | 50 | 20 | 38 | 70 | 0 | 0 | 260 | 260 | 186 | 8 | 87 | 23 | 20 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 132 | 147 | 8 | 21 | 0 | 43 | 22 | 53 | 0 | 0 | 162 | 52 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 5 | 150 | 268 | 0 | 0 | 185 | 26 | 149 | 0 | 100 | 180 | 150 | 365 | 106 | 105 | 105 | 0 | 0 | 0 | 85 | 114 | 107 | 100 | 397 | 92 | 0 | 162 | 112 | 0 | 17 | 0 |  | 808 | 0 | 260 | 0 | 0 | 160 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 0 | 90 | 35 | 0 | 29 | 8 | 20 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 100 | 170 | 0 | 397 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 220 | 0 | 81 | 0 |  | 8695 | 3926 | 12621 | 4528 | 808 | 1680 | 3996 | 754 | 120 | 603 | 132 | 0 | 0 | 82.95
KWH | 0 | 3851600 | 0 | 0 | 7265973 | 1174045 | 0 | 6754300 | 4312000 |  | 0 | 5519250 | 6652771 | 0 | 0 | 602816 | 7787594 | 0 | 0 | 2009558 | 1002672 | 2665920 | 458260 | 0 | 0 | 0 | 1250640 | 546234 | 1190534 | 320976 | 600000 | 553860 | 805600 | 656900 | 1113605 | 0 | 1062627 | 1456000 | 2400000 | 0 | 618586 | 4883284 | 0 | 2886693 | 0 |  | 517920 | 0 | 356267 | 1902840 | 0 | 377760 | 468432 | 423360 | 1957428 | 0 | 0 | 6797900 | 6635000 | 4745000 | 217454 | 2900670 | 594936 | 1162560 | 0 | 887384 | 0 | 546688 | 1035835 | 499824 | 243900 | 801300 | 476930 | 2737920 | 3170960 | 187200 | 475416 | 14800 | 1023000 | 299400 | 1109400 | 0 | 0 | 3617000 | 1427424 | 1849920 | 0 | 5205760 | 392000 | 0 | 256320 | 7220500 | 375264 | 204240 | 927744 | 3630653 | 814942 | 54558 | 3350400 | 433535 | 1789920 | 106245 | 1083840 | 3238560 | 3081163 | 9411000 | 2497200 | 2516400 | 2504072 | 26039 | 0 | 0 | 2088390 | 1055640 | 2619120 | 1662720 | 9405100 | 907200 | 301660 | 3251520 | 2703545 | 0 | 466920 | 160099 |  | 19504000 | 0 | 5851008 | 0 | 0 | 786339 | 0 | 0 | 132000 | 0 | 0 | 0 | 687185 | 44448 | 0 | 0 | 0 | 660928 | 103265 | 1656392 | 803930 | 0 | 225932 | 264480 | 275948 | 481200 | 0 | 165240 | 1766400 | 0 | 3676200 | 12000 | 0 | 0 | 0 | 3713245 | 0 | 1743158 | 790080 | 4448345 | 0 | 9222582 | 2431200 | 287584 | 1277184 | 122400 | 1583289 | 0 | 34666 | 1768224 | 9191600 | 5073382 | 0 | 2191200 | 30540 |  | 193606395 | 81005574 | 274611969 | 114072502 | 19504000 | 41339700 | 71709292 | 14634200 | 2518627 | 7421679 | 2737920 | 674049 | 0
Fuel Cost | 0 | 5700368 | 0 | 0 | 8065230.03 | 1549739.4 | 0 | 6821843 | 4441360 |  | 0 | 6015982.5 | 7384575.81 | 0 | 0 | 5099823.36 | 8099097.76 | 0 | 0 | 15131971.74 | 9144368.64 | 26232652.8 | 4225157.2 | 0 | 0 | 0 | 9129672 | 4222388.82 | 11738665.24 | 240732 | 450000 | 0 | 0 | 0 | 10768560.35 | 0 | 286909.29 | 393120 | 4344000 | 0 | 5746663.94 | 5322779.56 | 0 | 4907378.1 | 0 |  | 0 | 0 | 3455789.9 | 18172122 | 0 | 2991859.2 | 590224.32 | 1257379.2 | 2896993.44 | 0 | 0 | 5030446 | 6635000 | 4365400 | 280515.66 | 3335770.5 | 672277.68 | 1627584 | 0 | 1517426.64 | 0 | 5521548.8 | 9892224.25 | 634776.48 | 182925 | 1402275 | 357697.5 | 20534400 | 3361217.6 | 1699776 | 603778.32 | 235912 | 1677720 | 479040 | 1974732 | 0 | 0 | 3761680 | 2812025.28 | 3533347.2 | 0 | 9005964.8 | 858480 | 0 | 522892.8 | 7292705 | 281448 | 155222.4 | 15780925.44 | 27447736.68 | 13837715.16 | 912209.76 | 17422080 | 7248705.2 | 17612812.8 | 1242004.05 | 8833296 | 35138376 | 21722199.15 | 8752230 | 22774464 | 23779980 | 21810467.12 | 0 | 0 | 0 | 18356948.1 | 10535287.2 | 22445858.4 | 11073715.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112343040 | 0 | 6143558.4 | 0 | 0 | 10898658.54 | 0 | 0 | 1384680 | 0 | 0 | 0 | 1065136.75 | 433812.48 | 0 | 0 | 0 | 6503531.52 | 1049172.4 | 14659069.2 | 6190261 | 0 | 2189281.08 | 2562811.2 | 2676695.6 | 923904 | 0 | 125086.68 | 10651392 | 0 | 19925004 | 415800 | 0 | 0 | 0 | 4901483.4 | 0 | 2614737 | 13439260.8 | 5204563.65 | 0 | 9130356.18 | 25381728 | 4891803.84 | 12120476.16 | 1155456 | 12286322.64 | 0 | 383059.3 | 13067175.36 | 40351124 | 0 | 0 | 0 | 0 |  | 601800626.77 | 345068441.18 | 946869067.95 | 118178712.9 | 112343040 | 43747798.33 | 503609712.24 | 70927520 | 680029.29 | 74986879.84 | 20534400 | 1860975.35 | 0
Yesterday Day Peak | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 106 |  | 0 | 220 | 280 | 0 | 0 | 18 | 323 | 0 | 0 | 80 | 48 | 133 | 1 | 0 | 0 | 0 | 54 | 55 | 55 | 16 | 25 | 22 | 33 | 33 | 42 | 0 | 58 | 60 | 100 | 0 | 25 | 217 | 0 | 120 | 0 |  | 24 | 0 | 0 | 70 | 0 | 0 | 21 | 2 | 80 | 0 | 0 | 280 | 285 | 211 | 8 | 137 | 26 | 50 | 0 | 34 | 0 | 0 | 43 | 21 | 11 | 33 | 20 | 108 | 114 | 8 | 21 | 2 | 43 | 28 | 47 | 0 | 0 | 160 | 60 | 79 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 8 | 0 | 201 | 0 | 0 | 100 | 0 | 55 | 10 | 70 | 180 | 142 | 402 | 115 | 105 | 105 | 4 | 0 | 0 | 85 | 17 | 110 | 100 | 393 | 17 | 52 | 162 | 112 | 0 | 17 | 33 |  | 807 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 8 | 0 | 20 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 69 | 0 | 181 | 0 | 412 | 90 | 0 | 75 | 0 | 90 | 0 | 5 | 113 | 280 | 218 | 0 | 72 | 3 |  | 11210 | DayPeak
Yesterday Evening Peak | 0 | 133 | 0 | 0 | 300 | 0 | 0 | 276 | 145 | 0 | 0 | 220 | 285 | 0 | 0 | 55 | 333 | 0 | 0 | 95 | 100 | 133 | 75 | 0 | 0 | 0 | 54 | 17 | 55 | 19 | 25 | 21 | 33 | 0 | 51 | 0 | 63 | 60 | 100 | 0 | 25 | 203 | 0 | 120 | 0 | 0 | 24 | 0 | 51 | 82 | 0 | 50 | 20 | 20 | 70 | 0 | 0 | 260 | 260 | 131 | 8 | 0 | 26 | 30 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 20 | 140 | 132 | 8 | 21 | 0 | 44 | 22 | 53 | 0 | 0 | 163 | 61 | 83 | 0 | 219 | 18 | 0 | 10 | 310 | 16 | 11 | 200 | 268 | 300 | 0 | 194 | 102 | 149 | 0 | 70 | 0 | 150 | 368 | 106 | 105 | 105 | 0 | 0 | 0 | 51 | 100 | 116 | 100 | 397 | 92 | 0 | 162 | 112 | 0 | 17 | 0 |  | 807 | 0 | 265 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 0 | 34 | 16 | 0 | 0 | 0 | 50 | 20 | 90 | 35 | 0 | 28 | 8 | 29 | 21 | 0 | 5 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 100 | 170 | 0 | 408 | 105 | 200 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 220 | 0 | 81 | 0 |  | 12953 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 108 | 0 | 280 | 190 | 0 | 0 | 220 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 100 | 102 | 133 | 100 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 0 | 50 | 22 | 25 | 135 | 0 | 0 | 320 | 320 | 210 | 8 | 90 | 26 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 150 | 8 | 21 | 0 | 43 | 22 | 51 | 0 | 0 | 163 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 310 | 16 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 100 | 113 | 100 | 400 | 104 | 0 | 162 | 112 | 0 | 17 |  |  | 824 | 0 | 270 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 20 | 95 | 35 | 0 | 31 | 52 | 30 | 22 | 0 | 11 | 74 | 0 | 150 | 10 | 10 | 0 | 0 | 140 | 0 | 76 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 108 | 0 | 280 | 190 | 0 | 0 | 220 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 100 | 100 | 133 | 70 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 225 | 0 | 120 | 0 | 0 | 22 |  | 51 | 82 | 0 | 50 | 22 | 10 | 120 | 0 | 0 | 300 | 300 | 210 | 8 | 90 | 26 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 148 | 155 | 8 | 21 | 1.6 | 43 | 22 | 51 | 0 | 0 | 163 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 16 | 11 | 100 | 270 | 100 | 100 | 175 | 100 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 17 | 113 | 100 | 400 | 92 | 50 | 162 | 112 | 0 | 17 | 30 |  | 824 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 110 | 0 | 0 | 0 | 50 | 20 | 95 | 35 | 0 | 31 | 30 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 110 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 277 | 330 | 0 | 0 | 220 | 260 | 0 | 0 | 0 | 339 | 0 | 0 | 95 | 0 | 82 | 0 | 0 | 0 | 0 | 35 | 0 | 17 | 0 | 25 | 21 | 33 |  | 22 | 0 | 60 | 60 | 100 | 0 | 6 | 204 | 0 | 120 | 0 | 0 | 1 | 0 | 0 | 82 | 0 | 0 | 20 | 4 | 70 | 0 | 0 | 260 | 260 | 206 | 8 | 88 | 23 | 20 | 0 | 43 | 0 | 0 | 3 | 18 | 0 | 33 | 20 | 102 | 155 | 8 | 21 | 1 | 43 | 22 | 53 | 0 | 0 | 162 | 62 | 81 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 5 | 0 | 0 | 0 | 0 | 70 | 0 | 16 | 6 | 10 | 34 | 110 | 388 | 115 | 105 | 105 | 0 | 0 | 0 | 51 | 17 | 107 | 10 | 370 | 0 | 3 | 13 | 112 | 0 | 17 | 8 | 0 | 809 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 76 | 0 | 173 | 0 | 359 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 220 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 9707 | 8:00
| Highest Generation |  | 12953 | 21:00
| Day Peak Generation |  | 11210 | 12:00
| Evening Peak Generation |  | 12953 | 21:00
| HVDC Max Flow |  | 809 | 4:00
| HVDC EvPeak Flow |  | 807 | 21:00
| Load factor L.F |  | 88.34%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-19
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-18 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11210 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9616 | MW
Evening Peak Generation : |  | 12953 | MW Hour : | 21:00 | Available Max Generation : |  | 14920 | MW
E.P. Demand (at gen end) : |  | 12953 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12953 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1920 | MW
Total Gen. (MKWH) : |  | 274.612 | System Load Factor : | 88.34% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -460 | MW at | 19:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-19
Actual : | 82.98 | Ft.(MSL) , | Rule curve : | 86.88 | Ft.( MSL )
Gas Consumed : | Total = | 1174.67 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 161926511.23
: |  | Coal : | 70927520 | Oil : | 578596592.08 | Total : | 811450623.31
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4602.3018 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1569.7814 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1407.3175 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1271.9302 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1149.2594 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 927.4236 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 512.4647 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 238.6251 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 715.3044 |  |  | 0 | 0%
Total | 0 |  | 12394.4081 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-4 & 5
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7)Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Aminbazar-Kallyanpur 132 kV Ckt-1 was under shut down from 08:45 to 19:24 for C/M.
b) After maintenance Comilla(S) 132/33 kV T-2 transformer was switched on at 09:15.
c) Bheramara 132/33 kV T-2 transformer was under shut down from 08:30 to 09:39 for GK project work.
d) Kallyanpur 132 kV reserve Bus was under shut down from 08:42 to 18:40 for C/M.
e) Manikganj-Kabirpur 132 kV Ckt-2 and GT-2 132/33 kV transformer were under shut down from 09:22 to
13:43 for oil leakage of GT-3 transformer.
f) Rampura 132 kV Bus-1 was under shut down from 20:15 to 13:45 for C/M.
g) Baghabari-Shahjadpur 132 kV Ckt-1 tripped at 09:39 showing Dist. Z1,Z2 at Baghabari end and Dist. C at
Shahjadpur end and was switched on at 10:03.
h) Pabna 132/33 kV T-2 transformer and its associated 33 kV Bus were under shut down from 12:50 to 14:37
for maintenance of kashinathpur feeder.
i) Payra unit01 was synchronized at 15:15.
j) Fenchuhganj GT-3 was shut down at 15:20 due to high vibration.
k) Chandpur 132/33 kV T-1, T-2 and T-5 transformers tripped at 19:44 due to 33 kV Matlab feeder loop fault |  |  |  |  | About 30 MW power interruption occurred under Chandpur S/S area
and were switched on T-1 & T-2 at 19:58 and T-5 at 22:52. |  |  |  |  | from 19:44 to 19:58.
l) Chandpur 150 MW CCPP and Chandpur DESH 200 MW tripped at 19:41 due to voltage fluctuation.
m) Chandpur DESH 200 MW synchronized at 21:03.
n) Chandpur 150 MW CCPP GT was synchronized at 21:21.
o) Payra unit-2 was shut down at 21:53 due to boiler problem.
p) Bakulia-Khulshi 132 kV Ckt-1 was under shut down from 21:33 to 22:36 for R/H maintenance at Bakulia end.
q)Ghorashal unit-3 GT tripped at due to cooling system problem 22:44 and was synchronized at 22:50.
r) Ghorashal unit-3 GT was forced shut down at 00:48(19/7/2021) for cooling system problem.
s) Sirajganj 132/33 kV T-4 transformer was under down from 07:43(19/7/2021) to 10:27 for R/H maintenance.
t) Chatak 132/33 kV T-2 transformer tripped at 02:15(19/7/2021) due to 33 kV feeder fault and was switched
on at 02:22.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-18 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 133 | 3851600 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7265973 | Machine problem
4 | Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
5 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 1174045 | Gas shortage
6 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
7 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 276 | 6754300 | Gas shortage
8 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 145 | 4312000 | Gas shortage
9 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 220 | 5519250 | Gas shortage
10 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
11 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6652771 | FGMO
12 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
13 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 602816
14 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 75 | 458260 | Low demand
15 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 320976 | Engine problem
16 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
17 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
18 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 95 | 2009558 | Engine problem
19 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 333 | 7787594
20 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 100 | 1002672
21 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
22 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1250640
23 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 2665920 | Engine problem
24 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 546234 | Low demand
25 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1190534
26 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
27 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 46 | 1153860 | Engine problem
28 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805600
29 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 0 | 656900 | Engine problem
30 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 1113605
31 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
32 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 268 | 3630653 | Low demand
33 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 300 | 814942
34 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 54558 | Reserve.
35 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 102 | 433535
36 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1789920
37 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2516400
38 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 907200 | Engine problem
39 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3251520
40 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 160099
| Dhaka area Total |  |  |  | 5819 | 3603 | 70653935
41 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
42 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 618586
43 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 106245
44 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 377760
45 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 123 | 2518627 | Low water level & Unit-2 under maint
46 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 203 | 4883284 | FGMO
47 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2886693 | Machine problem
48 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2504072
49 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
50 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 356267 | Fuel shortage
51 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 82 | 1902840 | Engine problem
52 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 70 | 1083840 | Low demand
53 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 468432
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 20 | 423360
54 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
55 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26039
56 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Transformer O/L
57 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
58 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 51 | 2088390 | Low demand
59 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1662720
60 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 112 | 2703545
| Chattogram area Total |  |  |  | 2382 | 1232 | 27010700
61 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1957428 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
62 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 131 | 4745000 | Gas shortage
63 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6797900 | FGMO
64 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 260 | 6635000 | FGMO
65 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 594936 | Engine problem
66 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 1162560 | Gas shortage
67 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
68 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 887384 | Engine problem
69 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3081163
70 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 546688
71 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 0 | 2900670 | Tripped at 19:40
72 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 0 | 3238560 | Tripped at 19:41
73 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499824
74 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 243900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2737920
75 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 801300
76 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 1035835 | Engine problem
77 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 476930
78 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 927744 | Reserve.
79 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 1055640 | Fuel shortage
80 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 116 | 2619120
81 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 466920 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1730 | 43629876
82 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 132 | 3170960 | Gas shortage
83 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 475416
84 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 187200 | Engine problem
85 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14800
86 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 194 | 3350400 | Engine problem
87 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 2497200 | Engine problem
88 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 301660
89 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 517920
| Mymensingh Area Total |  |  |  | 709 | 485 | 10515556
90 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1023000 | Machine problem
91 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 22 | 299400 | Machine problem
92 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
93 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 163 | 3617000 | GT-1 under maint
94 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1109400
95 | Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
96 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 204240
97 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1427424
98 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 83 | 1849920
99 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
100 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 5205760
101 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 392000
102 | Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
103 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 375264 | Engine problem
104 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7220500 | FGMO
105 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 368 | 9411000 | FGMO
106 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 256320
107 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 397 | 9405100
| Sylhet Area Total |  |  |  | 2377 | 1775 | 41796328
108 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 807 | 19504000
109 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
110 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 132000 | Engine problem
111 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 155 | 786339 | ST not available
112 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
113 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 265 | 5851008 | Gas shortage
114 | Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
115 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 790080
116 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2431200
117 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 122400 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1452 | 29617027
118 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 44448 | Line O/L
119 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 687185
120 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
121 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 76 | 1743158 | Gas shortage
122 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 9191600
| Bhola Nutan Biddut BD LTD |  | IPP | 220 | 0 | 220 | 5073382
123 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 81 | 2191200 | Low demand
| Barisal Area Total |  |  |  | 1826 | 927 | 18930973
124 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
125 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 660928
126 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 20 | 103265 | Engine problem
127 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 803930 | Engine problem
128 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
129 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 225932 | Engine problem
130 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
131 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 140 | 3713245 | Gas shortage
132 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 170 | 4448345 | FGMO
133 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 408 | 9222582 | FGMO
134 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 275948 | Engine problem
135 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 481200
136 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
137 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 5 | 165240
138 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 264480 | Fuel shortage
139 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 1656392 | Engine problem
140 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 200 | 287584
141 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1277184 | Engine problem
142 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 1768224
143 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30540
| Rajshahi Area Total |  |  |  | 2179 | 1411 | 25385019
144 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 75 | 1766400 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
145 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3676200 | Coal shortage
146 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 12000
147 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
148 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1583289
149 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 34666
| Rangpur Area Total |  |  |  | 605 | 338 | 7072555
| Total |  |  |  | 21060 | 12953 | 274611969
| Eastern Grid Total |  |  |  | 14321 | 8825 | 193606395
| Western Grid Total |  |  |  | 6739 | 4128 | 81005574
| National Grid Total |  |  |  | 21060 | 12953 | 274611969
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-18
(a) ENTIRE EASTERN GRID : |  | 8150 | MW | (b) ENTIRE WESTERN GRID : |  | 4189 | MW
i) Dhaka area |  | 4126 | MW | i) Khulna area |  | 1621 | MW
ii) Chittagong area |  | 1308 | MW | ii) Rajshahi area |  | 1384 | MW
iii) Comilla area |  | 1161 | MW | iii) Barisal area |  | 392 | MW
iv) Mymensingh area |  | 1024 | MW | iv) Rangpur area |  | 792 | MW
v) Sylhet area |  | 531 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12339 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 12:00 | Kishoreganj | 136 | 1:00 | Jessore | 122 | 22:00
Munsiganj | 106 | 0:00 | Netrokona | 114 | 20:00 | Benapol | 74 | 19:30
Sonargaon | 75 | 21:00 | Jamalpur | 148 | 21:00 | Jhenida | 117 | 22:00
Shyampur | 170 | 7:00 | Sherpur | 124 | 23:00 | Bottail | 143 | 21:00
Bhulta | 175 | 11:00 | Srimongal | 56 | 21:00 | G.K Project | 61 | 22:00
Madanganj | 53 | 22:00 | Shahjibazar | 117 | 22:00 | Faridpur | 149 | 21:00
Shitalakhya | 122 | 16:00 | Fenchuganj | 48 | 20:00 | Rajbari | 52 | 19:30
Rahim steel | 25 | 0:00 | Kulawara | 48 | 19:00 | Madaripur | 108 | 22:00
Matuail | 54 | 0:00 | Sylhet | 121 | 19:00 | Sariatpur | 70 | 21:00
Ghorasal | 74 | 22:00 | Chatak | 32 | 22:00 | Gopalganj | 96 | 21:00
Narsingdi | 166 | 22:00 | Sunamganj | 54 | 21:00 | Bagerhat | 106 | 21:00
Haripur (SBU) | 98 | 10:00 | Biani Bazar | 70 | 19:00 | Mongla | 42 | 20:00
Sreenagar | 41 | 21:00 | Comilla (S) | 140 | 21:00 | Satkhira | 114 | 21:00
Ullon | 63 | 22:00 | Comilla(N) | 131 | 21:00 | Gallamari | 38 | 13:00
Hasnabad | 78 | 19:30 | Chandpur | 84 | 24:00 | Magura | 56 | 21:00
Magbazar | 90 | 12:00 | Feni | 125 | 19:30 | Norail | 42 | 1:00
Maniknagar | 76 | 13:00 | Chowmuhani | 220 | 1:00 | Chuadanga | 92 | 20:00
Bangabhaban | 13 | 10:00 | Ashuganj | 42 | 23:00 | Borguna | 20 | 22:00
Motijheel | 27 | 12:00 | Daudkandi | 158 | 22:00 | Barisal(N) | 47 | 21:00
Narinda | 54 | 14:00 | B.Baria | 159 | 21:00 | Barisal (S) | 114 | 23:00
Kazla | 73 | 1:00 | Ramganj | 86 | 19:30 | Patuakhali | 124 | 23:00
Dhanmondi | 196 | 13:00 | Chaddagram | 56 | 1:00 | Bhandaria | 54 | 1:00
Lalbag | 91 | 13:00 | PHP | 3 | 15:00 | Borhan Uddin | 47 | 19:00
Madartek | 70 | 23:00 | Kochua | 72 | 22:00 | Ishurdi | 65 | 20:00
Dhaka University | 34 | 13:00 | Madunaghat | 60 | 19:30 | Ruppur Paromanobik | 3 | 21:00
Aftabnagar | 10 | 12:00 | Hathazari | 92 | 21:00 | Natore | 140 | 21:00
Fatullah | 52 | 10:00 | Khulshi | 170 | 13:00 | Bogra | 157 | 21:00
Nawabganj | 55 | 22:00 | Halishahar | 87 | 14:00 | Noagaon | 120 | 21:00
Keraniganj | 60 | 21:00 | Baraulia | 142 | 1:00 | Rajshahi | 161 | 21:00
Mirpur | 119 | 19:00 | Sikalbaha | 32 | 23:00 | Rajshahi New | 14 | 21:00
Kalyanpur | 111 | 14:00 | Dohazari | 88 | 20:00 | C.Nawabganj | 66 | 21:00
Gulshan | 102 | 13:00 | Cox'sbazar | 105 | 20:00 | Amnura | 50 | 21:00
Uttara | 93 | 13:00 | Chandraghona | 28 | 19:00 | Pabna | 105 | 21:00
Uttara New | 12 | 12:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 104 | 21:00
Kamrangirchar | 82 | 19:00 | A. Khaer Stl. | 3 | 16:00 | Serajganj | 105 | 21:00
Savar | 150 | 9:00 | Bakulia | 105 | 12:00 | Niyamatpur | 77 | 21:00
Bhasantec | 133 | 13:00 | Julda | 24 | 10:00 | Joypurhat | 65 | 21:00
Agargaon | 81 | 13:00 | TK chemical | 30 | 21:00 | Sherpur(Bogura) | 56 | 21:00
Satmosjid | 95 | 13:00 | Modern Steel | 0 | #N/A | Mohastangor | 72 | 21:00
Tongi | 111 | 9:00 | Shahmirpur | 29.5 | 19:00 | Bhangura | 32 | 21:00
Kabirpur | 239 | 11:00 | Khagrachhari | 28 | 7:00 | Rangpur | 127 | 19:30
Basundhara | 229 | 12:00 | Matarbari | 40 | 21:00 | Lalmonirhat | 48 | 21:00
Manikganj | 82 | 22:00 | Baroiar Hat | 44 | 19:30 | Saidpur | 98 | 19:30
Joydevpur | 157 | 11:00 | Rangamati | 12 | 19:00 | Purbasadipur | 112 | 21:00
New Tongi | 107 | 12:00 | Abul Khair 230 | 107 | 23:00 | Thakurgaon | 91 | 20:00
Kodda | 267 | 12:00 | BSRM | 165 | 19:30 | Palashbari | 121 | 21:00
Dhamrai | 102 | 11:00 | GPH Ispat | 87 | 19:30 | Barapukuria | 56 | 21:00
Rajendrapur | 108 | 15:00 | Agrabad | 80 | 15:00 | Panchagar | 51 | 20:00
Valuka | 122 | 15:00 | Goalpara | 27 | 23:00 | Joldhaka | 64 | 19:30
Tangail | 224 | 21:00 | Central S/S | 102 | 1:00 | Kurigram | 54 | 21:00
Mymensing | 199 | 19:30 | Noapara | 52 | 20:00 | Mithapukur | 35 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-18 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 18:00 | 396 | 9:00 | Kaliakoir | 391 | 0.75 | 382 | 0.41667
| Bheramara | 404 | 24:00 | 395 | 23:00 | Bhulta | 384 | 0.83333 | 375 | 0.5
| Ashuganj(N) | 389 | 13:00 | 383 | 11:00 | Gopalganj | 410 | 0.625 | 385 | 0.91667
| Payra | 416 | 22:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 222 | 1:00 | 220 | 8:00
| Ishurdi | 235 | 18:00 | 225 | 19:30 | Megnaghat | 232 | 14:00 | 227 | 9:00
| Ashuganj | 240 | 18:30 | 235 | 2:00 | Fenchuganj | 236 | 18:30 | 233 | 5:00
| Serajganj | 230 | 6:00 | 223 | 22:00 | Siddhirganj | 231 | 19:30 | 226 | 11:00
| Baghabari | 232 | 16:00 | 225 | 20:00 | Maniknagar | 229 | 19:30 | 223 | 11:00
| Barapukuria | 234 | 18:00 | 224 | 21:00 | Agargaon | 228 | 24:00 | 219 | 12:00
| Bogra | 223 | 18:00 | 212 | 22:00 | Barisal | 232 | 1:00 | 232 | 22:00
| Rajshahi | 233 | 18:00 | 222 | 20:00 | Bhola 225 MW | 245 | 11:00 | 238 | 22:00
| Khulna South | 226 | 18:00 | 206 | 13:00 | AKSML | 225 | 1:00 | 220 | 2:00
| Rampura | 229 | 1:00 | 222 | 11:00 | BSRM | 225 | 13:00 | 221 | 15:00
| Haripur | 229 | 20:00 | 223 | 9:00 | Bibiyana | 238 | 1:00 | 233 | 24:00
| Hasnabad | 230 | 21:00 | 220 | 10:00 | Bhulta | 232 | 19:30 | 226 | 9:00
| Shyampur | 228 | 22:00 | 220 | 11:00 | Ashuganj (S) | 235 | 18:00 | 231 | 6:00
| Aminbazar | 229 | 1:00 | 221 | 2:00 | Kaliakoir | 229 | 21:00 | 221 | 9:00
| Tongi | 228 | 19:30 | 220 | 7:00 | GPH | 229 | 5:00 | 220 | 3:00
| Comilla (N) | 229 | 18:30 | 225 | 8:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 22:00 | 129 | 9:00 | Madanhat | 133 | 0.95833 | 131 | 0.041667
| Munsiganj | 136 | 19:30 | 130 | 6:00 | Hathazari | 132 | 0.041667 | 130 | 0.83333
| Sonargaon | 134 | 19:00 | 127 | 11:00 | Khulshi | 130 | 0.041667 | 128 | 0.16667
| Shyampur | 137 | 22:00 | 131 | 10:00 | Halishahar | 132 | 0.041667 | 129 | 0.20833
| Bhulta | 127 | 19:00 | 123 | 7:00 | Baraulia | 131 | 0.125 | 129 | 0.375
| Madanganj | 134 | 20:00 | 126 | 7:00 | Sikalbaha | 133 | 0.79167 | 129 | 0.16667
| Shitalakhya | 143 | 22:00 | 132 | 10:00 | Dohazari | 130 | 0.79167 | 125 | 0.16667
| Rahim steal | 134 | 19:00 | 130 | 12:00 | Cox'sbazar | 122 | 0.41667 | 110 | 0.83333
| Matuail | 134 | 22:00 | 129 | 9:00 | Chandraghona | 133 | 0.375 | 131 | 0.125
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 132 | 0.29167 | 130 | 0.041667
| Narsinghdi | 132 | 16:00 | 124 | 22:00 | A. Khaer Stl. | 130 | 0.041667 | 129 | 0.29167
| Haripur (SBU) | 134 | 19:00 | 130 | 9:00 | Bakulia | 132 | 0.041667 | 129 | 0.25
| Sreenagar | 133 | 19:30 | 125 | 9:00 | Julda | 133 | 0.041667 | 130 | 0.29167
| Ullon | 134 | 1:00 | 128 | 10:00 | TK Chemical | 132 | 0.041667 | 130 | 0.5
| Hasnabad | 140 | 18:30 | 133 | 10:00 | Modern Steel
| Magbazar | 135 | 2:00 | 128 | 11:00 | Shahmirpur | 133 | 0.625 | 130 | 0.25
| Maniknagar | 137 | 1:00 | 132 | 11:00 | Khagrachhari | 131 | 0.29167 | 130 | 0.041667
| Bangabhaban | 137 | 1:00 | 132 | 11:00 | Matarbari | 130 | 0.79167 | 114 | 0.83333
| Motijheel | 137 | 1:00 | 132 | 11:00 | Baroiar Hat | 132 | 0.54167 | 129 | 0.83333
| Narinda | 137 | 1:00 | 132 | 11:00 | Rangamati | 132 | 9:00 | 130 | 4:00
| Kazla | 137 | 1:00 | 132 | 11:00 | Agrabad | 131 | 0:00 | 129 | 3:00
| Dhanmondi | 134 | 23:00 | 128 | 10:00 | Goalpara S/S | 136 | 18:00 | 124 | 0.16667
| Lalbag | 140 | 19:30 | 131 | 10:00 | Khulna Central S/S | 136 | 18:00 | 123 | 0.54167
| Madartek | 134 | 3:00 | 128 | 11:00 | Noapara | 132 | 17:00 | 119 | 0.79167
| Dhaka University | 134 | 3:00 | 128 | 12:00 | Jessore | 129 | 18:00 | 114 | 0.125
| Aftabnagar | 134 | 1:00 | 128 | 11:00 | Benapol | 129 | 0.75 | 113 | 0.54167
| Fatullah | 137 | 19:30 | 131 | 9:00 | Jhenida | 125 | 18:00 | 108 | 0.8125
| Nawabganj | 131 | 19:30 | 124 | 10:00 | Bottail | 130 | 0.75 | 120 | 0.83333
| Keraniganj | 133 | 19:30 | 125 | 10:00 | G.K Project | 138 | 0.75 | 132 | 0.8125
| Mirpur | 137 | 19:30 | 132 | 7:00 | Faridpur | 136 | 0.75 | 128 | 0.91667
| Kalyanpur | 138 | 19:30 | 133 | 8:00 | Rajbari | 135 | 0.75 | 124 | 0.91667
| Gulshan | 133 | 1:00 | 127 | 12:00 | Madaripur | 141 | 0.75 | 132 | 0.875
| Uttara | 137 | 18:30 | 131 | 8:00 | Shariyatpur S/S | 140 | 17:00 | 132 | 0.875
| Uttara New | 137 | 12:00 | 131 | 8:00 | Gopalganj | 145 | 0.70833 | 132 | 0.91667
| Kamrangirchar | 141 | 18:30 | 132 | 10:00 | Bagerhat | 134 | 18:00 | 120 | 0.54167
| Savar | 131 | 18:30 | 130 | 8:00 | Mongla | 132 | 18:00 | 119 | 0.5
| Bhasantec | 136 | 19:30 | 131 | 9:00 | Satkhira | 135 | 18:00 | 121 | 13:00
| Agargaon | 140 | 22:00 | 131 | 12:00 | Gallamari | 137 | 0.75 | 124 | 15:00
| Satmosjid | 136 | 19:30 | 131 | 10:00 | Magura | 124 | 18:00 | 105 | 0.8125
| Tongi | 140 | 00:00 | 133 | 11:00 | Narail | 123 | 0.75 | 105 | 0.875
| Kabirpur | 139 | 18:30 | 135 | 10:00 | Chuadanga | 118 | 18:00 | 95 | 0.875
| Basundhara | 138 | 19:30 | 130 | 10:00 | Borguna | 140 | 6:00 | 132 | 0.91667
| Manikganj | 140 | 1:00 | 128 | 10:00 | Barisal(N) | 141 | 17:00 | 132 | 22:00
| Joydevpur | 139 | 13:00 | 133 | 5.00 | Barisal (S) | 139 | 0.70833 | 131 | 0.91667
| New Tongi | 138 | 1:00 | 131 | 10:00 | Patuakhali(S) | 139 | 0.8125 | 134 | 0.91667
| Kodda | 137 | 23:00 | 128 | 9:00 | Bhandaria | 139 | 0.70833 | 126 | 0.91667
| Dhamrai | 132 | 19:30 | 127 | 15:00 | Ishurdi | 136 | 18:00 | 130 | 20:00
| Rajendrapur | 136 | 20:00 | 125 | 10:00 | Ruppur Paromanobik | 134 | 6:00 | 130 | 21:00
| Valuka | 122 | 8:00 | 109 | 20:00 | Natore | 133 | 18:00 | 126 | 21:00
| Tangail | 134 | 5:00 | 125 | 21:00 | Bogra | 133 | 18:30 | 124 | 21:00
| Mymensing | 126 | 7:00 | 113 | 23:00 | Noagaon | 130 | 18:00 | 117 | 21:00
| Kishorganj | 128 | 7:00 | 118 | 21:00 | Rajshahi | 132 | 18:00 | 125 | 21:00
| Netrokona | 125 | 8:00 | 110 | 20:00 | Rajshahi New | 134 | 18:00 | 125 | 21:00
| Jamalpur | 135 | 19:00 | 122 | 21:00 | C.Nawabganj | 132 | 18:00 | 125 | 21:00
| Sherpur | 132 | 15:00 | 119 | 23:00 | Amnura | 133 | 18:00 | 125 | 21:00
| Srimongal | 137 | 9:00 | 133 | 19:30 | Pabna | 135 | 18:00 | 128 | 21:00
| Shahjibazar | 136 | 7:00 | 130 | 22:00 | Shahjadpur | 139 | 18:00 | 134 | 21:00
| Fenchuganj | 136 | 6:00 | 133 | 1:00 | Serajganj | 132 | 14:00 | 126 | 21:00
| Khulawara | 135 | 4:00 | 133 | 18:30 | Niyamatpur | 127 | 18:30 | 115 | 21:00
| Sylhet | 134 | 7:00 | 132 | 1:00 | Joypurhat | 130 | 18:00 | 114 | 21:00
| Chatak | 134 | 7:00 | 129 | 20:00 | Sherpur(Bogura) | 133 | 18:00 | 124 | 21:00
| Sunamganj | 133 | 9:00 | 126 | 20:00 | Mohastangor | 132 | 18:30 | 122 | 21:00
| Biani Bazar | 133 | 5:00 | 128 | 19:00 | Bangura | 136 | 18:00 | 130 | 21:00
| Comilla(s) | 130 | 6:00 | 125 | 10:00 | Rangpur | 127 | 2:00 | 114 | 21:00
| Comilla(n) | 137 | 2:00 | 134 | 6:00 | Lalmonirhat | 126 | 15:00 | 116 | 19:30
| Chandpur | 139 | 11:00 | 131 | 6:00 | Saidpur | 128 | 18:00 | 114 | 21:00
| Feni | 133 | 11:00 | 128 | 20:00 | Purbasadipur | 125 | 18:00 | 106 | 21:00
| Chowmuhani | 134 | 18:00 | 129 | 21:00 | Thakurgaon | 125 | 18:00 | 106 | 21:00
| Ashuganj | 138 | 9:00 | 132 | 23:00 | Palashbari | 128 | 18:30 | 118 | 21:00
| Daudkandi | 137 | 19:30 | 128 | 3:00 | Barapukuria | 134 | 18:00 | 124 | 21:00
| B.Baria | 134 | 13:00 | 126 | 23:00 | Panchagar | 123 | 18:00 | 100 | 21:00
| Ramganj | 134 | 18:30 | 120 | 20:00 | Joldhaka | 125 | 0.75 | 108 | 0.875
| Chaddagram | 136 | 18:00 | 131 | 5:00 | Kurigram | 124 | 0.25 | 110 | 0.8125
| PHP | 133 | 19:30 | 128 | 4:00 | Mithapukur | 130 | 0.58333 | 118 | 0.875
| Kochua | 135 | 10:00 | 131 | 3:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-18
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 350 | 8695 | 3926 | 12621 |  |  |  | QF-LDC-11
0:30 | 352 | 8587.5 | 3767.5 | 12355 | Date: | 2021-07-18
1:00 | 354 | 8480 | 3609 | 12089
1:30 | 339 | 8331 | 3522 | 11853
2:00 | 324 | 8182 | 3435 | 11617
2:30 | 298 | 8056 | 3392 | 11448 | [5 empty] | Gen. at Eve. Peak | 12953 | 12953 MW (21:00 )
3:00 | 272 | 7930 | 3349 | 11279 | [6 empty] | 21:00
3:30 | 263 | 7856.5 | 3292.5 | 11149 | [5 empty] | Gen. at Day Peak | 11210 | 11210 MW (12:00 )
4:00 | 254 | 7783 | 3236 | 11019 | [6 empty] | 12:00
4:30 | 250 | 7710 | 3207 | 10917 | [5 empty] | Highest Generation | 12953
5:00 | 246 | 7637 | 3178 | 10815 | [6 empty] | 21:00
5:30 | 174 | 7269 | 3097.5 | 10366.5
6:00 | 102 | 6901 | 3017 | 9918
6:30 | 93 | 6858 | 2960 | 9818
7:00 | 84 | 6815 | 2903 | 9718
7:30 | 76 | 6803 | 2909.5 | 9712.5
8:00 | 68 | 6791 | 2916 | 9707
8:30 | 38 | 6956 | 2935.5 | 9891.5
9:00 | 8 | 7121 | 2955 | 10076
9:30 | 16 | 7356.5 | 2997 | 10353.5
10:00 | 24 | 7592 | 3039 | 10631
10:30 | 12 | 7666 | 3069.5 | 10735.5
11:00 | 0 | 7740 | 3100 | 10840
11:30 | 49 | 7878.5 | 3146.5 | 11025
12:00 | 98 | 8017 | 3193 | 11210
12:30 | 127 | 8116 | 3205.5 | 11321.5
13:00 | 156 | 8215 | 3218 | 11433
13:30 | 188 | 8229.5 | 3202 | 11431.5
14:00 | 220 | 8244 | 3186 | 11430
14:30 | 225 | 8336 | 3231.5 | 11567.5
15:00 | 230 | 8428 | 3277 | 11705
15:30 | 205 | 8249.5 | 3198 | 11447.5
16:00 | 180 | 8071 | 3119 | 11190
16:30 | 154 | 7901 | 3051 | 10952
17:00 | 128 | 7731 | 2983 | 10714
17:30 | 75 | 7497 | 2985.5 | 10482.5
18:00 | 22 | 7263 | 2988 | 10251
18:30 | 91 | 7702 | 3181.5 | 10883.5
19:00 | 160 | 8141 | 3375 | 11516
19:30 | 460 | 8881 | 3818 | 12699
20:00 | 396 | 8711 | 3866 | 12577 |  |  |  | Executive Engineer
20:30 | 356 | 8768 | 3997 | 12765 |  |  |  | Network Operation Division
21:00 | 316 | 8825 | 4128 | 12953
21:30 | 374 | 8837.5 | 4014 | 12851.5
22:00 | 432 | 8850 | 3900 | 12750 |  |  |  |  | Page 6 of 7
22:30 | 408 | 8782.5 | 3921.5 | 12704
23:00 | 384 | 8715 | 3943 | 12658
23:30 | 367 | 8705 | 3934.5 | 12639.5
24:00 | 350 | 8695 | 3926 | 12621
12953 MW (21:00 )
11210 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-18 |  | Energy | 274611969
[11 empty] | 2021-07-18 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4528 | 808 | 1680 | 4029 | 754 | 120 | 603 | 0 | 132 | 0
0:30 | 4674 | 807.5 | 1769.5 | 3726.5 | 630 | 104 | 534 | 0 | 126 | 0 | Date: | 2021-07-18
1:00 | 4820 | 807 | 1859 | 3424 | 506 | 88 | 465 | 0 | 120 | 0
1:30 | 4818.5 | 807.5 | 1862 | 3234.5 | 504.5 | 88 | 419 | 0 | 119 | 0 | [7 empty] | Total Energy | 274.612 | Total Energy Gen 274.612 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 274.612 MKWHr
2:00 | 4817 | 808 | 1865 | 3045 | 503 | 88 | 373 | 0 | 118 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4813 | 808 | 1885 | 2878.5 | 503 | 88.5 | 355 | 0 | 117 | 0 | [7 empty] | Energy Requirement | 274.612
3:00 | 4809 | 808 | 1905 | 2712 | 503 | 89 | 337 | 0 | 116 | 0
3:30 | 4828.5 | 808.5 | 1894.5 | 2575 | 503 | 89 | 336.5 | 0 | 114 | 0 | [6 empty] | Shortage
4:00 | 4848 | 809 | 1884 | 2438 | 503 | 89 | 336 | 0 | 112 | 0
4:30 | 4848.5 | 808.5 | 1885.5 | 2387.5 | 502.5 | 89 | 285.5 | 0 | 110 | 0
5:00 | 4849 | 808 | 1887 | 2337 | 502 | 89 | 235 | 0 | 108 | 0
5:30 | 4849 | 808 | 1881 | 1961 | 503 | 88.5 | 171.5 | 0 | 103 | 1.5
6:00 | 4849 | 808 | 1875 | 1585 | 504 | 88 | 108 | 0 | 98 | 3
6:30 | 4891 | 808.5 | 1843.5 | 1504.5 | 503.5 | 87.5 | 85 | 0 | 83 | 11.5 |  |  |  |  | Coal
7:00 | 4933 | 809 | 1812 | 1424 | 503 | 87 | 62 | 0 | 68 | 20
7:30 | 4898 | 808 | 1797.5 | 1449.5 | 504 | 87 | 67 | 0 | 72 | 29.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4863 | 807 | 1783 | 1475 | 505 | 87 | 72 | 0 | 76 | 39
8:30 | 4837 | 807 | 1781 | 1642.5 | 504 | 86.5 | 108.5 | 0 | 76 | 49
9:00 | 4811 | 807 | 1779 | 1810 | 503 | 86 | 145 | 0 | 76 | 59
9:30 | 4814.5 | 807 | 1749.5 | 2073 | 502.5 | 86 | 162.5 | 0 | 86 | 72.5
10:00 | 4818 | 807 | 1720 | 2336 | 502 | 86 | 180 | 0 | 96 | 86
10:30 | 4791 | 807 | 1718.5 | 2453 | 503 | 102 | 180 | 0 | 100 | 81
11:00 | 4764 | 807 | 1717 | 2570 | 504 | 118 | 180 | 0 | 104 | 76
11:30 | 4784 | 807 | 1658.5 | 2774.5 | 504.5 | 118 | 180 | 0 | 106 | 92.5
12:00 | 4804 | 807 | 1600 | 2979 | 505 | 118 | 180 | 0 | 108 | 109
12:30 | 4775.5 | 807.5 | 1597 | 3127 | 505 | 118.5 | 172.5 | 0 | 115 | 103.5
13:00 | 4747 | 808 | 1594 | 3275 | 505 | 119 | 165 | 0 | 122 | 98
13:30 | 4747 | 808 | 1594 | 3275 | 505 | 119 | 165 | 0 | 122 | 98
14:00 | 4747 | 808 | 1594 | 3275 | 505 | 119 | 165 | 0 | 122 | 98
14:30 | 4747.5 | 808 | 1602 | 3362.5 | 505 | 121 | 216.5 | 0 | 125 | 81.5
15:00 | 4748 | 808 | 1610 | 3450 | 505 | 123 | 268 | 0 | 128 | 65
15:30 | 4717.5 | 807.5 | 1572 | 3250 | 520 | 123 | 277 | 0 | 123 | 57.5
16:00 | 4687 | 807 | 1534 | 3050 | 535 | 123 | 286 | 0 | 118 | 50
16:30 | 4656 | 807 | 1512 | 2856.5 | 570 | 123 | 285 | 0 | 110 | 32.5
17:00 | 4625 | 807 | 1490 | 2663 | 605 | 123 | 284 | 0 | 102 | 15
17:30 | 4526 | 807.5 | 1427 | 2604.5 | 605.5 | 123 | 280.5 | 0 | 100 | 8.5
18:00 | 4427 | 808 | 1364 | 2546 | 606 | 123 | 277 | 0 | 98 | 2
18:30 | 4548 | 807.5 | 1414.5 | 2885.5 | 611 | 123 | 375 | 0 | 118 | 1
19:00 | 4669 | 807 | 1465 | 3225 | 616 | 123 | 473 | 0 | 138 | 0
19:30 | 4650 | 807 | 1642 | 4147 | 645 | 123 | 547 | 0 | 138 | 0
20:00 | 4574 | 807 | 1664 | 4025 | 654 | 123 | 594 | 0 | 136 | 0
20:30 | 4521 | 807 | 1672.5 | 4204 | 689.5 | 123 | 610 | 0 | 138 | 0
21:00 | 4468 | 807 | 1681 | 4383 | 725 | 123 | 626 | 0 | 140 | 0
21:30 | 4540 | 807 | 1674 | 4227 | 730 | 122 | 611.5 | 0 | 140 | 0
22:00 | 4612 | 807 | 1667 | 4071 | 735 | 121 | 597 | 0 | 140 | 0
22:30 | 4562 | 807.5 | 1674 | 4050 | 754.5 | 120 | 597 | 0 | 139 | 0
23:00 | 4512 | 808 | 1681 | 4029 | 774 | 119 | 597 | 0 | 138 | 0
23:30 | 4520 | 808 | 1680.5 | 4029 | 764 | 119.5 | 600 | 0 | 135 | 0 | Max Temp. in Dhaka |  | 34.8° C
24:00 | 4528 | 808 | 1680 | 4029 | 754 | 120 | 603 | 0 | 132 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 274.612 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 274.612 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-18
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 28 | 28 | 29 | 29 | 29 | 28 | 27 | 27 | 26 | 26 | 58 | 58 | 59 | 61 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 63 | 61 | 59 | 60 | 1062627
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1456000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 618586
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 7 | 11 | 15 | 19 | 10 | 10 | 7 | 6 | 9 | 12 | 4 | 0 | [8 empty] | 106245
6 | Sikalbaha 225MW CCPP (Gas) | 203 | 203 | 203 | 204 | 204 | 204 | 212 | 210 | 204 | 208 | 204 | 217 | 205 | 204 | 204 | 203 | 203 | 203 |  | 215 | 203 | 210 | 203 | 203 | 204 | 204 | 4883284
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2886693
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 36 | [18 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 356267
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2504072
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 45 | 145 | 195 | 200 | 200 | 200 | 150 | 927744
14 | Titas 50 MW Peaking PP | 41 | 41 | [11 empty] | 2 | 41 | 46 | 48 | 48 |  | 49 | 50 | 50 | 50 | 50 | 50 | 50 | 546688
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 334 | 334 | 334 | 334 | 330 | 330 | 328 | 327 | 323 | 326 | 325 | 325 | 339 | 300 | 270 |  | 300 | 333 | 331 | 333 | 335 | 334 | 334 | 7787594
18 | Kodda 300 MW PP Unit-2 (Summit) | 225 | 95 | [7 empty] | 11 | 60 | 201 | 260 | 265 | 268 | 220 | 200 | 190 |  | 215 | 230 | 268 | 268 | 265 | 265 | 268 | 3630653
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT | 189 | 189 | 169 | 189 | 189 | 189 | 189 | 189 | 189 | 189 | 133 | 133 | 134 | 135 | 135 | 134 | 133 | 133 |  | 133 | 133 | 133 | 133 | 133 | 30 | 23 | 3851600
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7265973
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 70 | 70 | 70 | 70 | 1957428
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 594936
33 | Ashuganj 225 MW CCPP | 218 | 217 | 217 | 217 | 218 | 216 | 214 | 214 | 214 | 212 | 212 | 211 | 209 | 215 | 215 | 212 | 189 | 158 |  | 152 | 148 | 132 | 131 | 156 | 168 | 186 | 4745000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 295 | 275 | 265 | 280 | 280 | 285 | 265 | 265 | 270 | 265 | 265 | 265 |  | 295 | 265 | 290 | 260 | 260 | 265 | 260 | 6635000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 295 | 270 | 260 | 275 | 270 | 280 | 260 | 260 | 260 | 260 | 260 | 260 |  | 285 | 260 | 285 | 260 | 260 | 260 | 260 | 6797900
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 52 | 50 | 50 | 52 | 53 | 54 | 54 | 54 | 56 |  | 30 | 30 | 30 | 30 | 20 | 20 | 20 | 1162560
36 | Chandpur 150 MW CCPP | 137 | 130 | 136 | 137 | 132 | 137 | 136 | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 137 | 137 | 138 | 136 |  | 137 | 131 |  |  | 90 | 90 | 87 | 2900670
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 277 | 274 | 276 | 276 | 276 | 275 | 275 | 275 | 275 | 275 |  | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 6754300
40 | Meghnaghat 450 MW CCPP(MPL) | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5519250
41 | Haripur 360MW CCPP(HPL) | 247 | 271 | 277 | 287 | 292 | 272 | 216 | 177 | 155 | 133 | 121 | 106 | 106 | 109 | 122 | 136 | 156 | 162 |  | 160 | 155 | 150 | 145 | 145 | 142 | 175 | 4312000
42 | RPCL 210MW CCPP | 147 | 147 | 153 | 153 | 154 | 153 | 152 | 148 | 131 | 116 | 117 | 114 | 112 | 112 | 115 | 130 | 135 | 138 |  | 132 | 132 | 132 | 132 | 132 | 132 | 147 | 3170960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 8 | 13 | 17 | 26 | 27 | 52 | 42 | 48 | 42 | 30 | 5 | 0 | [8 empty] | 301660
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 |  | 44 | 44 | 43 | 44 | 43 | 43 | 43 | 1023000
45 | Fenchugonj CCPP Phase-2 | [11 empty] | 28 | 28 | 28 | 28 | 28 | 0 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 299400
46 | Shajibazar 330 MW CCPP | 160 | 162 | 162 | 161 | 161 | 162 | 163 | 162 | 161 | 160 | 161 | 160 | 162 | 162 | 160 | 161 | 162 | 163 |  | 161 | 162 | 163 | 163 | 162 | 162 | 162 | 3617000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 61 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 61 | 61 | 61 | 40 |  | 61 | 61 | 61 | 61 | 61 | 56 | 52 | 1427424
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 81 | 81 | 82 | 79 | 80 | 80 | 79 | 79 | 83 | 20 |  | 30 | 84 | 83 | 83 | 84 | 84 | 84 | 1849920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 190 | 190 | 190 |  | 217 | 219 | 219 | 219 | 219 | 218 | 219 | 5205760
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 392000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 256320
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 |  |  | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 204240
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 | 50 | 14 |  | 21 | 53 | 53 | 53 | 53 | 53 | 53 | 1109400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 375264
57 | Bibiana-II 341 MW CCPP (Summit) | 275 | 275 | 285 | 285 | 295 | 280 | 290 | 300 | 310 | 310 | 300 | 300 | 290 | 280 | 290 | 290 | 295 | 290 |  | 280 | 290 | 300 | 310 | 300 | 300 | 280 | 7220500
| Bibiyana South 400 MW | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 400 | 393 | 395 | 400 | 390 | 392 | 400 | 350 |  | 375 | 400 | 392 | 397 | 400 | 398 | 397 | 9405100
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 35 | 35 | 35 | 17 | 17 | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1190534
59 | Tangail Palli Power Gen 22 MW | 19 | 20 | 24 | 24 | 24 | 24 |  |  | 9 | 22 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 517920
60 | Barabkunda 22 MW PP (Regent) | 22 | 20 | 20 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 21 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 468432
61 | Narshingdi 22 MW PP (Doreen) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 |  | 16 | 16 | 18 | 19 | 19 | 19 | 19 | 320976
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 475416
63 | Impoprt (Tripura) | 120 | 118 | 116 | 112 | 108 | 98 | 68 | 76 | 76 | 96 | 104 | 108 | 122 | 120 | 128 | 118 | 102 | 98 |  | 138 | 138 | 136 | 140 | 140 | 138 | 132 | 2737920
64 | Malancha, Ctg. EPZ (United) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 7 | 2 | 2 | 2 | 2 | 10 | 5 | 5 | 5 | 8 | 5 |  | 5 | 11 | 7 | 20 | 29 | 38 | 38 | 423360
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 499824
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 243900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 801300
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 476930
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 27 | 26 | 26 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 |  | 16 | 16 | 21 | 21 | 21 | 21 | 21 | 553860
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  |  |  | 17 | 17 | 17 |  | 33 | 33 | 33 | 656900
73 | Ghorashal 108MW PP (Regent) | 105 | 106 | 106 | 106 | 106 | 106 | 106 | 105 | 102 | 102 | 102 | 0 | [14 empty] | 1174045
| Feni Lanka Power | 105 | 34 | 34 | 34 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 36 | 100 | 100 | 100 | 100 | 100 | 114 | 1055640
| Chowmuhani 113 MW | 106 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 108 | 108 | 108 | 110 | 108 | 110 | 108 | 105 | 105 | 113 |  | 114 | 116 | 114 | 116 | 115 | 104 | 107 | 2619120
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 108 | 17 | 17 | 17 | 39 | 135 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 108 |  | 135 | 162 | 162 | 162 | 162 | 162 | 162 | 3251520
77 | Siddhirganj 100 PP(Dutch Bangla) | 96 | 96 | 96 | 96 | 96 | 24 | 24 | 24 | 60 | 80 | 70 | 80 | 88 | 87 | 87 | 80 | 92 | 95 |  | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 2009558
78 | Gazipur 52 MW PP | 52 | 52 | 52 | 52 | 52 | 16 | 16 | 20 | 42 | 51 | 51 | 42 | 42 | 46 | 51 | 51 | 51 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 1113605
79 | Kodda 150MW PP | 150 | 150 | 150 | 150 | 98 |  |  | 10 | 98 | 133 | 133 | 133 | 118 | 125 | 132 | 132 | 132 | 82 |  | 133 | 133 | 133 | 133 | 133 | 133 | 133 | 2665920
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187200
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 36 | 43 |  | 40 | 43 | 43 | 43 | 43 | 43 | 43 | 1035835
| Gazipur 100 MW PP | 105 | 105 | 105 | 105 | 105 | 70 | 70 | 84 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2516400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 2 | 3 | 4 | 5 | 4 | 2 | 2 | 1 | 0 | [8 empty] | 26039
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 51 | 34 | 34 | 57 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 85 |  | 85 | 85 | 51 | 51 | 51 | 55 | 85 | 2088390
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [11 empty] | 1 | 10 | 23 | 24 | 10 |  |  |  | 8 | 73 | 70 | 75 | 73 | 68 | 69 | 458260
86 | Meghnaghat CCPP ( Summit) | 275 | 300 | 275 | 275 | 275 | 275 | 300 | 290 | 245 | 275 | 275 | 280 | 275 | 240 | 280 | 265 | 255 | 255 |  | 300 | 255 | 285 | 285 | 275 | 250 | 250 | 6652771
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [11 empty] | 17 | 70 | 92 | 94 | 54 | 17 | 17 |  | 53 | 92 | 93 | 92 | 93 | 93 | 92 | 907200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 94 | 94 | 94 | 94 | 94 | 94 | 50 | 80 | 80 | 80 | 70 | 70 | 70 | 82 | 82 | 70 | 70 | 70 |  | 70 | 70 | 82 | 82 | 82 | 82 | 82 | 1902840
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 887384
94 | Gagnagar 102 MW PP (Digital Power) | 7 | [6 empty] | 3 | 24 | 24 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 |  | 84 | 94 | 94 | 100 | 100 | 88 | 102 | 1002672
95 | Patenga 50MW PP (Baraka) | [12 empty] | 13 | 17 | 22 | 19 | 12 | 12 |  | 17 | 40 | 47 | 50 | 50 | 50 | 50 | 377760
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 15 | 15 | [8 empty] | 9 | 18 | 48 | 55 | 55 | 15 | 15 | 15 |  | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 602816
100 | Manikganj 55 MW PP (Northern) | 17 | [8 empty] | 17 | 17 | 55 | 55 | 55 | 55 | 17 | 17 | 17 |  | 17 | 35 | 55 | 17 | 17 | 17 | 55 | 546234
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 1 | 0 | [8 empty] | 14800
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 35 | 35 | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1250640
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 35 | 110 | 102 | 300 | 157 | 108 |  | 814942
105 | Bramhangoan 100 MW PP (Aggreko) | [19 empty] | 36 | 50 | [5 empty] | 54558
106 | Mymensingh 200 MW PP (United) | 196 | 195 | 196 | 195 | 195 | 100 | 60 | 60 | 60 | 60 | 75 | 100 | 100 | 112 | 140 | 100 | 100 | 100 |  | 130 | 192 | 193 | 194 | 195 | 184 | 185 | 3350400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 48 | 100 | 100 | 102 | 102 | 52 | 26 | 433535
114 | Kodda 149 MW PP Unit-1 (Summit) | 50 | 35 | 16 | 16 | 16 | 16 | 16 | 21 | 45 | 45 | 45 | 55 | 100 | 106 | 132 | 100 | 56 | 56 |  | 64 | 100 | 146 | 149 | 149 | 149 | 149 | 1789920
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 10 | [6 empty] | 10 | 10 | 70 | 70 | 100 | 90 | 90 | 90 | 50 | 10 |  | 54 | 90 | 70 | 70 | 70 | 100 | 100 | 1083840
116 | Chandpur 200MW (Desh energy) | 198 | 198 | 198 | 85 | 85 | 17 | 17 | 18 | 55 | 121 | 178 | 180 | 198 | 198 | 197 | 197 | 155 | 155 |  | 160 | 180 |  |  | 45 | 132 | 180 | 3238560
117 | Ashuganj 150MW PP (Midland) | 150 | 145 | 147 | 147 | 100 | 10 | 10 | 13 | 61 | 130 | 142 | 142 | 142 | 145 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3081163
118 | Bibiyana-III 400 MW CCPP | 401 | 402 | 401 | 401 | 403 | 403 | 403 | 403 | 403 | 402 | 402 | 402 | 403 | 403 | 405 | 404 | 405 | 315 |  | 379 | 366 | 382 | 368 | 366 | 368 | 365 | 9411000
| Jamalpur 115 MW PP (United) | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 107 | 97 | 97 | 65 | 115 | 115 | 115 | 115 | 115 | 115 | 107 |  | 105 | 105 | 105 | 106 | 106 | 106 | 106 | 2497200
Anwara 300 MW PP (United)
| Juldah unit-2 (Acorn) | 100 | 100 | 60 |  |  |  |  | 6 | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 10 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 1662720
| Anlima Energy Ltd. | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 |  | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 2703545
| Bhairob 54.5 MW | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 466920
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 12 | 22 | 33 | 28 | 33 | 33 | 4 | 2 | 1 | 1 | 1 | [8 empty] | 160099
120 | Eastern Zone Total | 8480 | 8182 | 7930 | 7783 | 7637 | 6901 | 6815 | 6791 | 7121 | 7592 | 7740 | 8017 | 8215 | 8244 | 8428 | 8071 | 7731 | 7263 |  | 8141 | 8881 | 8711 | 8825 | 8850 | 8715 | 8695 | 193606395
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [13 empty] | 4 | 4 | 8 | 4 | 4 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 132000
| Khulna 225 MW CCPP | 40 | [19 empty] | 60 | 120 | 155 | 155 | 155 | 160 | 786339
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2431200
130
131
132 | United Payra Power Ltd. | 150 | 150 | 150 | 150 | 150 | 100 | 54 | 54 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 35 | 35 |  | 58 | 100 | 81 | 81 | 81 | 81 | 81 | 2191200
133 | Bhola Nutan Biddut BD LTD (GAS) | 215 | 221 | 222 | 223 | 222 | 221 | 221 | 221 | 220 | 218 | 218 | 218 | 218 | 218 | 218 | 218 | 151 | 151 |  | 151 | 200 | 220 | 220 | 220 | 220 | 220 | 5073382
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | 64 | 64 | 64 | 64 | 64 | [14 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 44448
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 81 | 82 | 83 | 71 | 70 | 69 | 70 | 69 | 68 | 68 | 69 | 69 | 67 | 68 | 67 | 66 | 66 | 68 |  | 77 | 77 | 76 | 76 | 76 | 75 | 76 | 1743158
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 33 | 34 | 33 | 31 | 31 | 27 | 26 | 26 | 26 | 26 | 25 | 25 | 26 | 26 | 25 | 25 | 24 | 24 |  | 32 | 34 | 34 | 34 | 34 | 34 | 34 | 687185
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 60 | 10 | 10 | [14 empty] | 5 | 100 | 79 | 100 | 100 | 100 | 100 | 790080
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 15 | 15 | 15 | 15 | 15 | 15 | [20 empty] | 122400
146 | Bheramara HVDC | 807 | 808 | 808 | 809 | 808 | 808 | 809 | 807 | 807 | 807 | 807 | 807 | 808 | 808 | 808 | 807 | 807 | 808 |  | 807 | 807 | 807 | 807 | 807 | 808 | 808 | 19504000
147 | Bheramara 410 MW CCPP | 255 | 260 | 260 | 275 | 275 | 280 | 285 | 285 | 285 | 285 | 275 | 270 | 265 | 260 | 260 | 255 | 260 | 260 |  | 270 | 270 | 270 | 265 | 260 | 260 | 260 | 5851008
148 | Payra 1320 MW | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 310 | 380 | 380 |  | 390 | 420 | 430 | 500 | 510 | 550 | 530 | 9191600
149
150 | Barapukuria TPP Unit-1 | 76 | 73 | 73 | 73 | 72 | 74 | 73 | 75 | 73 | 72 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 76 |  | 76 | 75 | 74 | 75 | 75 | 74 | 74 | 1766400
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3676200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 50 | [10 empty] | 46 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 660928
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 4 | 2 | 3 | 4 | 4 | 4 | 1 | 1 | 0 | [8 empty] | 30540
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 140 |  | 140 | 140 | 140 | 140 | 140 | 140 | 140 | 3713245
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 166 | 168 | 169 | 172 | 177 | 181 | 186 | 186 | 182 | 181 | 181 | 181 | 178 | 178 | 175 | 173 | 173 | 173 |  | 160 | 170 | 170 | 170 | 170 | 170 | 170 | 4448345
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 389 | 362 | 385 | 367 | 357 | 389 | 372 | 400 | 419 | 397 | 408 | 412 | 407 | 380 | 408 | 319 | 310 | 272 |  | 377 | 406 | 409 | 408 | 404 | 413 | 397 | 9222582
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 8 | [14 empty] | 5 | 5 | 18 |  | 18 | 20 | 20 | 20 |  |  |  | 103265
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 12 | 21 | 20 | 19 | 19 | 20 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 481200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  | 11 | 11 | 11 | 5 | 5 |  | 11 | 165240
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 35 | 35 | 24 | 24 | 24 | 24 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 803930
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 22 | 22 | 22 | 22 | 22 | [12 empty] | 21 |  | 21 | 28 | 31 | 28 | 28 | 28 | 29 | 225932
168 | Santahar 50 MW Peaking PP | 28 | 20 | 22 | 21 | 22 | 22 | [11 empty] | 3 |  | 26 | 28 | 29 | 29 | 20 | 20 | 20 | 275948
169 | Natore 52 MW PP (Rajlanka) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 264480
170 | Chapainawabganj 100 MW Peaking PP | 90 | 90 | 93 | 93 | 93 | 86 | 62 | 62 | 47 | 47 | 47 | 47 | 47 | 45 | 45 | 45 | 45 | 51 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1656392
171 | Baghabari 200 MW PP (Paramount) | [20 empty] | 50 | 50 | 200 |  |  |  | 287584
| Bagura 113 MW PP (Confidence)-2 | 35 | [7 empty] | 8 | 35 | 62 | 75 | 90 | 94 | 94 | 50 | 50 | 50 |  | 56 | 90 | 94 | 94 | 94 | 94 | 94 | 1277184
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 90 | 50 | [5 empty] | 25 | 70 | 90 | 113 | 113 | 113 | 113 | 113 | 50 | 50 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1768224
173 | Rangpur 20 MW GTPP | 0 | [18 empty] | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 12000
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 70 | 34 | 34 | 34 |  |  |  |  | 34 | 34 | 90 | 113 | 106 | 113 | 58 | 36 | 34 |  | 100 | 107 | 113 | 113 | 113 | 113 | 113 | 1583289
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 5 | 5 | 4 | 3 | 2 | 1 | [8 empty] | 34666
178
178