## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-22 | Thursday
|  |  | Date (day): | 2021-07-22 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13511.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14542 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-21 | 2021-07-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 |  | 190 | Under maint
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 300 | 300 |  | 65 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 15 | 102 | 108 | 108
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 276 | 278 | 225 | 225 | 187 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 270 | 342 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 270 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 74 | 80 |  | 20 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 15 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 334 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 48 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 31 | 31 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 22 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 12 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 55 | 270 | 270 |  | 30 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 54 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 1726 | 2333 | 3655 | 3897 | 766 | 1010
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 20 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 119 | 122 | 123 | 123 | 107 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 0 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 90 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 10 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 40 | 40
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 30 | 95 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 36 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 108 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 110 | 112 | 112
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 481 | 1100 | 1534 | 1609 | 367 | 415
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 120 | 135
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 193 | 213 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 0 | 188 | 175 | 175 |  |  | ST under maint
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 270 | 0 | 0 |  | 360 | Under shut down
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 26 | 26 | 26 | 26 |  | 19 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 40 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 45 | 8 | 45 | 45 | 150 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 5 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 110 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 25 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 91 | 90 | 90 | 90 |  | 73 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 200 | 170 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 0 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 82 | 140 | 148 | 172
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 13 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 11 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 17 | 17 | 97 |  | Fuel shortage
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 0 | 105 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 923 | 1691 | 1659 | 1828 | 376 | 640
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 200 | 204 | 210 | 210 | -8
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 187 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 45 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 46 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 293 | 559 | 602.6 | 576 | -8 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 161 | 160 | 163 | 163 |  | 167 | GT-1 Under maint
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 5 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 51 | 62 | 63
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 5 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 164 | 219 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 0 | 16 | 16 | 16 |  | 9 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 270 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 315 | 367 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 397 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1405 | 1724 | 1866 | 1867 | 0 | 514
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 615 | 774 | 594 | 788
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 15 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 50 | 0 | 160 |  | 70 | ST not available
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 350 | 350 | 390
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 915 | 1394 | 1199 | 1723 | 0 | 153
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 26 | 33 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 77 | 66 | 76 | 19 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 460 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 152 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 100 | 110 | 110
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 490 | 906 | 1161 | 1171 | 19 | 194
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 70 | 70 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 20 | 20 |  | 51 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 21 | 31 | 31 |  | 19 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 154 | 170 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 172 | 158 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 336 | 401 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 28 | 0 | 30 |  | 20 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 5 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 90 | 95 | 95 |  | 9 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 74 | 90 | 90 |  | 23 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 110 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 746 | 1257 | 1490 | 1514 | 480 | 122
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 74 | 71 | 74 | 74 |  | 15 | Coal Shortage
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 229 | 334 | 345 | 357 | 124 | 120
|  | Total |  |  |  |  | 22031 | 21280 | 7208 | 11298 | 13511.6 | 14542 | 2124 | 3255
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 6902.4033 | 10819 | 12938.7503 | 13925.4645
| A. |  | 2021-07-21 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 11389 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7114 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11298 | MW
| 3 | Day peak Generation : |  |  | 7208 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10819 | MW
| 4 | Evening peak Generation : |  |  | 11298 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 215.5971 | MKWHr | By Solar | 0.70122 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 142.232 | MKWHr |  | By Oil: | 34.8989 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.058 | MKWHr |  | By Hydro: | 2.8588 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2124 | MW | Dhaka | 3010 | 3010 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3255 | MW | Chittagong | 990 | 990 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5379 | MW | Khulna | 1535 | 1535 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1096.78 | MMCFD |  |  | Rajshahi | 1276 | 1276 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 151169358.498 | ii) Oil : | Taka | 225247724.62 | Comilla | 1255 | 1255 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72716301.65 | Total | Taka | 449133384.768 | Mymensingh | 1026 | 1026 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.6855 | MKWHr. | Sylhet | 503 | 503 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -304 | MW (E to W) at | 21:00 | hrs | Barisal | 400 | 400 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -520 | MW at | 20:00 | hrs | Rangpur | 824 | 824 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.5° C |  |  | Total | 10819 | 10819 |  | 0
| B. |  | 2021-07-22 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 35.6° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14542 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3042 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 217.6983 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8278 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2313 | MKWHr. | ii) HVDC Flow at Peak Time |  | 774 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.617 | MKWHr. | iii) Maximum HVDC Flow : |  | 815 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 83.82 |  | (b) Today: | 84.25 |  | (c) Rule Curve: |  | 87.36
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 276 | 301 |  | 0 | 240 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 115 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 22 | 12 | 51 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 94 | 88 | 0 | 21 | 42 | 135 | 0 | 0 | 0 | 310 | 191 | 102 | 91 | 26 | 52 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 21 | 126 | 207 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 162 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 51 | 100 | 372 | 115 | 105 | 105 | 0 | 0 | 35 | 110 | 17 | 99 | 10 | 394 | 0 | 0 | 0 | 111 | 0 | 17 | 0 |  | 815 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 52 | 28 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 160 | 0 | 78 | 0 | 178 | 0 | 362 | 105 | 0 | 0 | 0 | 108 | 0 | 0 | 35 | 370 | 219 | 0 | 126 | 0 |  | 6784 | 3417 | 10201 | 4353 | 815 | 2031 | 1949 | 592 | 120 | 215 | 126 | 0 | 0 | 83.72
2:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 276 | 303 |  | 0 | 240 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 22 | 12 | 51 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 92 | 52 | 0 | 21 | 42 | 135 | 0 | 0 | 0 | 300 | 184 | 102 | 92 | 26 | 52 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 124 | 207 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 51 | 100 | 364 | 115 | 105 | 105 | 0 | 0 | 35 | 110 | 17 | 98 | 0 | 400 | 0 | 0 | 0 | 111 | 0 | 17 | 0 |  | 807 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 70 | 0 | 50 | 0 | 0 | 0 | 0 | 22 | 52 | 28 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 78 | 0 | 183 | 0 | 360 | 105 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 370 | 219 | 0 | 126 | 0 |  | 6611 | 3385 | 9996 | 4345 | 807 | 2040 | 1836 | 592 | 120 | 132 | 124 | 0 | 0 | 83.74
3:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 275 | 302 |  | 0 | 240 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 22 | 12 | 25 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 84 | 52 | 0 | 21 | 42 | 135 | 0 | 0 | 0 | 300 | 183 | 102 | 90 | 26 | 51 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 120 | 208 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 0 | 0 | 0 | 51 | 10 | 367 | 115 | 35 | 105 | 0 | 0 | 17 | 110 | 17 | 105 | 0 | 400 | 0 | 0 | 0 | 111 | 0 | 17 | 0 |  | 807 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 52 | 27 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 78 | 0 | 177 | 0 | 334 | 105 | 0 | 0 | 0 | 107 | 0 | 0 | 0 | 370 | 220 | 0 | 126 | 0 |  | 6376 | 3286 | 9662 | 4332 | 807 | 2004 | 1645 | 592 | 120 | 42 | 120 | 0 | 0 | 83.76
4:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 275 | 302 |  | 0 | 240 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 22 | 12 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 94 | 52 | 0 | 21 | 42 | 135 | 0 | 0 | 0 | 285 | 182 | 102 | 91 | 26 | 52 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 116 | 209 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 51 | 0 | 367 | 115 | 17 | 105 | 0 | 0 | 0 | 51 | 17 | 105 | 0 | 400 | 0 | 0 | 0 | 111 | 0 | 17 | 0 |  | 807 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 27 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 158 | 0 | 76 | 0 | 176 | 0 | 306 | 53 | 0 | 0 | 0 | 70 | 0 | 0 | 0 | 370 | 220 | 0 | 126 | 0 |  | 6193 | 3149 | 9342 | 4316 | 807 | 1975 | 1387 | 591 | 123 | 27 | 116 | 0 | 0 | 83.78
5:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 276 | 302 |  | 0 | 240 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 22 | 12 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 94 | 51 | 0 | 20 | 42 | 135 | 0 | 0 | 0 | 300 | 194 | 102 | 91 | 26 | 52 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 207 | 8 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 162 | 57 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 51 | 0 | 382 | 115 | 17 | 51 | 0 | 0 | 0 | 0 | 17 | 99 | 0 | 396 | 0 | 0 | 0 | 111 | 0 | 17 | 0 |  | 712 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 163 | 0 | 76 | 0 | 181 | 0 | 335 | 53 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 370 | 220 | 0 | 72 | 0 |  | 6125 | 2987 | 9112 | 4359 | 712 | 2014 | 1203 | 591 | 123 | 0 | 110 | 0 | 0 | 83.8
6:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 276 | 302 |  | 0 | 240 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 51 | 0 | 20 | 42 | 135 | 0 | 0 | 0 | 285 | 184 | 102 | 91 | 26 | 51 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 102 | 206 | 8 | 21 | 0 | 43 | 42 | 5 | 0 | 0 | 163 | 56 | 5 | 0 | 219 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 366 | 95 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 106 | 0 | 398 | 0 | 1 | 0 | 35 | 0 | 17 | 0 |  | 711 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 76 | 0 | 177 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 220 | 0 | 0 | 0 |  | 5501 | 2782 | 8283 | 4247 | 711 | 1841 | 636 | 621 | 123 | 0 | 102 | 2 | 0 | 83.82
7:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 276 | 302 |  | 0 | 240 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 51 | 0 | 20 | 42 | 135 | 0 | 0 | 0 | 285 | 185 | 102 | 91 | 26 | 53 | 0 | 5 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 98 | 206 | 8 | 21 | 0 | 43 | 42 | 5 | 0 | 0 | 163 | 20 | 5 | 0 | 219 | 0 | 0 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 95 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 45 | 0 | 398 | 0 | 10 | 0 | 17 | 0 | 17 | 0 |  | 614 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 165 | 0 | 77 | 0 | 183 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 221 | 0 | 0 | 0 |  | 5375 | 2692 | 8067 | 4213 | 614 | 1841 | 545 | 621 | 123 | 0 | 98 | 12 | 0 | 83.84
8:00 | 0 | 0 | 0 | 0 | 300 | 20 | 0 | 276 | 302 |  | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 0 | 0 | 0 | 65 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 12 | 0 | 20 | 42 | 90 | 0 | 0 | 0 | 285 | 181 | 73 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 80 | 206 | 8 | 0 | 1 | 43 | 42 | 5 | 0 | 0 | 162 | 40 | 5 | 0 | 206 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 343 | 75 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 365 | 0 | 29 | 0 | 17 | 0 | 17 | 5 |  | 615 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 157 | 0 | 12 | 0 | 175 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 350 | 186 | 0 | 0 | 0 |  | 4943 | 2498 | 7441 | 4039 | 615 | 1540 | 426 | 571 | 125 | 0 | 80 | 45 | 0 | 83.86
9:00 | 0 | 0 | 0 | 0 | 300 | 15 | 0 | 276 | 301 |  | 0 | 240 | 260 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 0 | 0 | 0 | 65 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 12 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 285 | 168 | 45 | 88 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 11 | 74 | 204 | 8 | 0 | 2 | 43 | 42 | 5 | 0 | 0 | 160 | 40 | 5 | 0 | 164 | 0 | 0 | 0 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 306 | 75 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 340 | 0 | 16 | 0 | 17 | 0 | 17 | 17 |  | 615 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 177 | 0 | 301 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 320 | 182 | 0 | 0 | 2 |  | 4720 | 2394 | 7114 | 3820 | 615 | 1471 | 416 | 541 | 125 | 0 | 74 | 52 | 0 | 83.88
10:00 | 0 | 0 | 0 | 0 | 300 | 14 | 0 | 276 | 270 |  | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 0 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 12 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 285 | 168 | 45 | 90 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 11 | 78 | 204 | 8 | 0 | 1 | 43 | 42 | 5 | 0 | 0 | 162 | 40 | 5 | 0 | 164 | 0 | 0 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 306 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 0 | 17 | 0 | 17 | 0 | 17 | 22 |  | 615 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 12 | 0 | 163 | 0 | 304 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 152 | 0 | 0 | 2 |  | 4652 | 2331 | 6983 | 3785 | 615 | 1403 | 391 | 521 | 123 | 0 | 78 | 67 | 0 | 83.9
11:00 | 0 | 0 | 0 | 0 | 300 | 15 | 0 | 276 | 272 |  | 0 | 240 | 280 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 0 | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 19 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 290 | 172 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 0 | 11 | 78 | 203 | 8 | 0 | 2 | 43 | 42 | 5 | 0 | 0 | 160 | 40 | 5 | 0 | 164 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 308 | 45 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 0 | 18 | 0 | 17 | 0 | 17 | 19 |  | 615 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 12 | 0 | 140 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 152 | 0 | 0 | 3 |  | 4703 | 2330 | 7033 | 3757 | 615 | 1452 | 413 | 523 | 123 | 0 | 78 | 72 | 0 | 83.92
12:00 | 0 | 0 | 0 | 0 | 300 | 15 | 0 | 276 | 270 |  | 0 | 240 | 290 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 8 | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 30 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 305 | 193 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 13 | 11 | 82 | 200 | 0 | 0 | 2 | 43 | 42 | 5 | 0 | 0 | 161 | 40 | 5 | 0 | 164 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 315 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 0 | 46 | 0 | 17 | 0 | 17 | 24 |  | 615 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 12 | 0 | 172 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 152 | 0 | 0 | 4 |  | 4828 | 2380 | 7208 | 3865 | 615 | 1473 | 426 | 523 | 119 | 0 | 82 | 105 | 0 | 83.94
13:00 | 0 | 0 | 0 | 0 | 300 | 15 | 0 | 276 | 270 |  | 0 | 240 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 62 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 295 | 186 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 11 | 86 | 199 | 0 | 0 | 2 | 43 | 42 | 5 | 0 | 0 | 160 | 40 | 5 | 0 | 165 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 313 | 106 | 0 | 0 | 5 | 0 | 0 | 0 | 17 | 34 | 0 | 320 | 0 | 45 | 0 | 40 | 0 | 17 | 21 |  | 712 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 71 | 0 | 149 | 0 | 0 | 0 | 0 | 195 | 0 | 12 | 0 | 196 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 300 | 152 | 0 | 0 | 4 |  | 4964 | 2540 | 7504 | 3934 | 712 | 1463 | 581 | 520 | 119 | 0 | 86 | 89 | 0 | 83.96
14:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 276 | 270 |  | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 87 | 0 | 19 | 42 | 135 | 0 | 0 | 0 | 285 | 180 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 11 | 94 | 203 | 2 | 0 | 1 | 43 | 42 | 5 | 0 | 0 | 159 | 61 | 40 | 0 | 165 | 0 | 0 | 10 | 290 | 16 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 366 | 115 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 45 | 0 | 395 | 0 | 31 | 0 | 72 | 0 | 17 | 20 |  | 805 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 71 | 0 | 149 | 0 | 0 | 0 | 0 | 192 | 0 | 12 | 0 | 191 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 300 | 216 | 0 | 0 | 2 |  | 5263 | 2766 | 8029 | 4134 | 805 | 1638 | 645 | 520 | 119 | 0 | 94 | 74 | 0 | 83.98
15:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 276 | 279 |  | 0 | 240 | 295 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 87 | 0 | 19 | 42 | 135 | 0 | 0 | 0 | 330 | 203 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 11 | 102 | 197 | 8 | 21 | 2 | 44 | 42 | 5 | 0 | 0 | 158 | 55 | 40 | 0 | 165 | 0 | 0 | 10 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 401 | 115 | 0 | 0 | 4 | 0 | 0 | 0 | 17 | 79 | 0 | 385 | 0 | 31 | 0 | 72 | 0 | 17 | 21 |  | 806 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 12 | 0 | 188 | 0 | 403 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 214 | 0 | 0 | 3 |  | 5464 | 2743 | 8207 | 4218 | 806 | 1654 | 710 | 522 | 119 | 0 | 102 | 76 | 0 | 84
16:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 276 | 341 |  | 0 | 240 | 290 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 12 | 0 | 0 | 62 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 87 | 0 | 19 | 42 | 135 | 0 | 0 | 0 | 330 | 203 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 2 | 22 | 11 | 25 | 20 | 106 | 196 | 8 | 21 | 1 | 44 | 42 | 5 | 0 | 0 | 158 | 55 | 40 | 0 | 165 | 0 | 0 | 10 | 315 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 404 | 115 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 105 | 0 | 360 | 0 | 23 | 0 | 72 | 0 | 17 | 7 |  | 806 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 5 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 185 | 0 | 12 | 0 | 196 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 214 | 0 | 0 | 3 |  | 5605 | 2842 | 8447 | 4369 | 806 | 1740 | 733 | 522 | 122 | 0 | 106 | 49 | 0 | 84.02
17:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 276 | 340 |  | 0 | 240 | 290 | 0 | 0 | 0 | 327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 6 | 25 | 12 | 0 | 0 | 61 | 60 | 100 | 0 | 3 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 90 | 0 | 20 | 42 | 135 | 0 | 0 | 0 | 320 | 196 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 35 | 22 | 11 | 33 | 20 | 112 | 199 | 8 | 21 | 0 | 44 | 42 | 5 | 0 | 0 | 160 | 55 | 40 | 0 | 165 | 0 | 0 | 10 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 6 | 0 | 0 | 0 | 384 | 115 | 0 | 0 | 1 | 0 | 0 | 0 | 17 | 105 | 0 | 360 | 0 | 8 | 0 | 72 | 0 | 17 | 10 |  | 787 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 195 | 0 | 12 | 0 | 196 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 300 | 216 | 0 | 0 | 1 |  | 5640 | 2855 | 8495 | 4391 | 787 | 1737 | 796 | 522 | 121 | 0 | 112 | 29 | 0 | 84.04
18:00 | 0 | 0 | 0 | 0 | 300 | 12 | 0 | 276 | 343 |  | 0 | 240 | 265 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 25 | 6 | 25 | 12 | 0 | 0 | 61 | 60 | 100 | 0 | 8 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 93 | 0 | 20 | 42 | 135 | 0 | 0 | 0 | 295 | 182 | 45 | 88 | 26 | 5 | 0 | 5 | 0 | 0 | 43 | 22 | 11 | 33 | 20 | 108 | 202 | 8 | 21 | 0 | 44 | 42 | 5 | 0 | 0 | 162 | 56 | 40 | 0 | 165 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 1 | 0 | 0 | 0 | 366 | 115 | 0 | 3 | 0 | 0 | 1 | 0 | 17 | 105 | 0 | 360 | 0 | 3 | 0 | 72 | 0 | 17 | 1 |  | 787 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 190 | 0 | 12 | 0 | 192 | 0 | 404 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 300 | 215 | 0 | 0 | 0 |  | 5548 | 2841 | 8389 | 4329 | 787 | 1712 | 798 | 522 | 121 | 5 | 108 | 7 | 0 | 84.07
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 14 | 0 | 277 | 300 |  | 0 | 240 | 300 | 0 | 0 | 8 | 327 | 0 | 0 | 0 | 16 | 48 | 19 | 0 | 0 | 0 | 35 | 17 | 40 | 10 | 25 | 6 | 25 | 12 | 22 | 0 | 61 | 60 | 100 | 0 | 19 | 0 | 0 | 120 | 0 |  | 0 | 0 | 51 | 90 | 93 | 5 | 20 | 42 | 100 | 0 | 0 | 0 | 330 | 203 | 16 | 82 | 26 | 5 | 0 | 5 | 0 | 37 | 43 | 22 | 11 | 33 | 20 | 132 | 182 | 8 | 21 | 0 | 44 | 42 | 7 | 0 | 0 | 159 | 50 | 10 | 0 | 205 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 5 | 0 | 0 | 29 | 0 | 16 | 0 | 10 | 58 | 15 | 400 | 115 | 40 | 61 | 0 | 16 | 17 | 29 | 17 | 105 | 36 | 400 | 17 | 0 | 43 | 85 | 0 | 17 | 0 |  | 775 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 90 | 0 | 0 | 21 | 10 | 15 | 21 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 179 | 0 | 30 | 0 | 183 | 0 | 403 | 15 | 0 | 0 | 0 | 60 | 0 | 0 | 10 | 300 | 190 | 0 | 7 | 0 |  | 6333 | 3013 | 9346 | 4339 | 775 | 1593 | 1548 | 522 | 121 | 316 | 132 | 0 | 0 | 84.13
19:30 | 0 | 0 | 0 | 0 | 300 | 52 | 0 | 279 | 350 |  | 0 | 240 | 235 | 0 | 0 | 30 | 332 | 0 | 0 | 0 | 16 | 82 | 70 | 0 | 0 | 0 | 54 | 17 | 55 | 10 | 25 | 6 | 25 | 12 | 43 | 0 | 61 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 15 | 0 | 51 | 90 | 93 | 25 | 20 | 42 | 135 | 0 | 0 | 15 | 295 | 216 | 32 | 81 | 26 | 20 | 0 | 25 | 0 | 42 | 43 | 22 | 11 | 33 | 21 | 130 | 206 | 8 | 21 | 0 | 44 | 42 | 50 | 0 | 0 | 164 | 52 | 84 | 0 | 219 | 0 | 0 | 10 | 250 | 16 | 11 | 0 | 15 | 42 | 0 | 177 | 27 | 18 | 0 | 10 | 160 | 100 | 366 | 115 | 105 | 105 | 0 | 16 | 36 | 108 | 17 | 105 | 50 | 399 | 90 | 0 | 108 | 110 | 0 | 17 | 0 |  | 773 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 90 | 0 | 0 | 29 | 43 | 28 | 21 | 0 | 8 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 197 | 0 | 58 | 100 | 201 | 0 | 289 | 90 | 0 | 15 | 0 | 108 | 0 | 0 | 50 | 380 | 176 | 0 | 100 | 0 |  | 7555 | 3482 | 11037 | 4450 | 773 | 1729 | 2856 | 602 | 121 | 376 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 75 | 0 | 279 | 340 |  | 0 | 240 | 250 | 0 | 0 | 30 | 331 | 0 | 0 | 0 | 0 | 82 | 70 | 0 | 0 | 0 | 54 | 17 | 17 | 15 | 25 | 6 | 25 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 13 | 0 | 51 | 90 | 95 | 0 | 20 | 42 | 100 | 0 | 0 | 85 | 270 | 214 | 8 | 80 | 26 | 20 | 0 | 35 | 0 | 42 | 43 | 22 | 11 | 33 | 21 | 130 | 204 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 0 | 163 | 51 | 84 | 0 | 219 | 0 | 0 | 10 | 260 | 16 | 11 | 0 | 37 | 0 | 0 | 186 | 0 | 35 | 0 | 10 | 135 | 80 | 367 | 115 | 105 | 105 | 0 | 16 | 28 | 99 | 17 | 106 | 50 | 400 | 90 | 0 | 108 | 110 | 0 | 17 | 0 |  | 774 | 0 | 350 | 0 | 0 | 50 | 0 | 0 | 4 | 0 | 0 | 0 | 30 | 16 | 0 | 70 | 0 | 50 | 0 | 90 | 0 | 0 | 33 | 52 | 28 | 22 | 0 | 8 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 72 | 100 | 175 | 0 | 296 | 80 | 0 | 44 | 0 | 108 | 0 | 0 | 90 | 380 | 200 | 0 | 90 | 0 |  | 7438 | 3616 | 11054 | 4418 | 774 | 1787 | 2792 | 601 | 122 | 430 | 130 | 0 | 0 | 84.11
21:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 278 | 342 |  | 0 | 240 | 270 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 15 | 25 | 6 | 25 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 90 | 95 | 0 | 20 | 42 | 80 | 0 | 0 | 188 | 270 | 213 | 8 | 90 | 26 | 40 | 0 | 43 | 0 | 25 | 43 | 22 | 0 | 33 | 21 | 140 | 204 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 0 | 160 | 51 | 84 | 0 | 219 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 55 | 0 | 0 | 187 | 0 | 0 | 0 | 10 | 200 | 110 | 367 | 115 | 105 | 105 | 0 | 16 | 36 | 108 | 17 | 105 | 50 | 397 | 0 | 0 | 54 | 110 | 0 | 17 | 0 |  | 774 | 0 | 350 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 0 | 0 | 33 | 16 | 0 | 70 | 0 | 50 | 0 | 90 | 0 | 0 | 21 | 52 | 28 | 22 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 77 | 100 | 158 | 0 | 401 | 105 | 0 | 74 | 0 | 113 | 0 | 0 | 110 | 460 | 220 | 0 | 100 | 0 |  | 7407 | 3891 | 11298 | 4469 | 774 | 1987 | 2747 | 681 | 122 | 378 | 140 | 0 | 0 | 84.13
22:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 278 | 340 |  | 0 | 240 | 265 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 15 | 25 | 6 | 25 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 90 | 95 | 0 | 20 | 42 | 80 | 0 | 0 | 190 | 270 | 214 | 8 | 89 | 26 | 48 | 0 | 43 | 0 | 25 | 43 | 22 | 0 | 33 | 21 | 142 | 204 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 0 | 162 | 51 | 84 | 0 | 219 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 97 | 0 | 0 | 189 | 0 | 0 | 0 | 10 | 155 | 140 | 366 | 115 | 105 | 105 | 0 | 16 | 36 | 110 | 17 | 106 | 50 | 399 | 0 | 0 | 54 | 110 | 0 | 17 | 0 |  | 774 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 33 | 16 | 0 | 60 | 0 | 50 | 0 | 90 | 0 | 0 | 21 | 52 | 28 | 22 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 183 | 0 | 77 | 100 | 162 | 0 | 392 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 110 | 530 | 219 | 0 | 100 | 0 |  | 7461 | 3928 | 11389 | 4430 | 774 | 1998 | 2790 | 751 | 122 | 382 | 142 | 0 | 0 | 84.15
23:00 | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 280 | 342 |  | 0 | 240 | 275 | 0 | 0 | 0 | 293 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 15 | 25 | 6 | 28 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 90 | 96 | 0 | 20 | 42 | 80 | 0 | 0 | 190 | 270 | 214 | 8 | 90 | 26 | 52 | 0 | 43 | 0 | 25 | 43 | 22 | 11 | 33 | 21 | 148 | 204 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 0 | 163 | 51 | 84 | 0 | 219 | 0 | 0 | 10 | 285 | 16 | 11 | 0 | 114 | 0 | 0 | 193 | 0 | 0 | 0 | 10 | 155 | 150 | 366 | 115 | 105 | 105 | 0 | 16 | 35 | 110 | 17 | 106 | 50 | 397 | 0 | 0 | 54 | 110 | 0 | 17 | 0 |  | 775 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 19 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 50 | 0 | 90 | 0 | 0 | 21 | 52 | 27 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 175 | 0 | 77 | 100 | 179 | 0 | 387 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 110 | 540 | 219 | 0 | 100 | 0 |  | 7490 | 3884 | 11374 | 4354 | 775 | 1999 | 2831 | 764 | 122 | 381 | 148 | 0 | 0 | 84.17
24:00 | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 279 | 342 |  | 0 | 220 | 285 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 15 | 25 | 6 | 28 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 90 | 96 | 0 | 20 | 42 | 80 | 0 | 0 | 192 | 285 | 213 | 8 | 90 | 26 | 51 | 0 | 43 | 0 | 25 | 43 | 22 | 8 | 33 | 21 | 96 | 204 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 0 | 162 | 51 | 81 | 0 | 219 | 0 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 10 | 155 | 150 | 370 | 115 | 105 | 105 | 0 | 16 | 35 | 110 | 17 | 105 | 50 | 393 | 0 | 0 | 54 | 110 | 0 | 17 | 0 |  | 774 | 0 | 235 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 50 | 0 | 45 | 0 | 0 | 21 | 52 | 26 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 150 | 0 | 76 | 100 | 177 | 0 | 379 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 110 | 540 | 220 | 0 | 100 | 0 |  | 7332 | 3718 | 11050 | 4270 | 774 | 1981 | 2727 | 764 | 122 | 316 | 96 | 0 | 0 | 84.19
KWH | 0 | 0 | 0 | 0 | 7239027 | 1381045 | 0 | 6789120 | 7416000 |  | 0 | 5640500 | 6599244 | 0 | 0 | 56174 | 6935130 | 0 | 0 | 0 | 27504 | 480480 | 105332 | 0 | 0 | 0 | 399240 | 38690 | 141766 | 199476 | 600000 | 161100 | 607500 | 288300 | 426720 | 0 | 1402810 | 1456000 | 2300000 | 0 | 184879 | 0 | 0 | 2850343 | 0 |  | 122160 | 0 | 285573 | 1175160 | 1574400 | 22560 | 477600 | 1149600 | 2698878 | 0 | 0 | 794600 | 7116000 | 4641000 | 1338181 | 2128100 | 584784 | 669600 | 0 | 600548 | 0 | 154352 | 445459 | 505440 | 226440 | 675100 | 452950 | 2616960 | 4779120 | 161280 | 349596 | 12000 | 1030000 | 847440 | 614400 | 0 | 0 | 3608000 | 1204608 | 1133760 | 0 | 4737630 | 93000 | 0 | 167580 | 7167000 | 385400 | 158536 | 0 | 371345 | 24865 | 0 | 1483200 | 16355 | 61920 | 126495 | 56640 | 1221120 | 973527 | 8630000 | 2448000 | 937200 | 1133272 | 37199 | 95345 | 311641 | 1041268 | 434340 | 1843800 | 282240 | 8865400 | 116160 | 284870 | 449280 | 1804036 | 0 | 442800 | 156924 |  | 17231273 | 0 | 5695776 | 0 | 0 | 226163 | 0 | 0 | 57230 | 0 | 0 | 0 | 697850 | 69888 | 0 | 1554000 | 0 | 370880 | 0 | 492208 | 0 | 0 | 159814 | 546240 | 258260 | 417600 | 0 | 201384 | 1726255 | 0 | 3670700 | 0 | 0 | 0 | 0 | 4282091 | 0 | 1090668 | 526080 | 4548355 | 0 | 8650100 | 988320 | 0 | 402720 | 0 | 1089945 | 0 | 55527 | 612192 | 9661000 | 4856345 | 0 | 1149600 | 28200 |  | 144280417 | 71316664 | 215597081 | 99241224 | 17231273 | 42990777 | 32413907 | 15057955 | 2858810 | 2484960 | 2616960 | 701215 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8035319.97 | 1822979.4 | 0 | 6857011.2 | 7638480 |  | 0 | 6148145 | 7325160.84 | 0 | 0 | 475232.04 | 7212535.2 | 0 | 0 | 0 | 250836.48 | 4727923.2 | 971161.04 | 0 | 0 | 0 | 2914452 | 299073.7 | 1397812.76 | 149607 | 450000 | 0 | 0 | 0 | 4126382.4 | 0 | 378758.7 | 393120 | 4163000 | 0 | 1717525.91 | 0 | 0 | 4845583.1 | 0 |  | 0 | 0 | 2770058.1 | 11222778 | 13697280 | 178675.2 | 601776 | 3414312 | 3994339.44 | 0 | 0 | 588004 | 7116000 | 4269720 | 1726253.49 | 2447315 | 660805.92 | 937440 | 0 | 1026937.08 | 0 | 1558955.2 | 4254133.45 | 641908.8 | 169830 | 1181425 | 339712.5 | 19627200 | 5065867.2 | 1464422.4 | 443986.92 | 191280 | 1689200 | 1355904 | 1093632 | 0 | 0 | 3752320 | 2373077.76 | 2165481.6 | 0 | 8196099.9 | 203670 | 0 | 341863.2 | 7238670 | 289050 | 120487.36 | 0 | 2807368.2 | 422207.7 | 0 | 7712640 | 273455.6 | 609292.8 | 1478726.55 | 461616 | 13249152 | 6863365.35 | 8025900 | 22325760 | 8856540 | 9870799.12 | 0 | 720808.2 | 2714393.11 | 9152745.72 | 4334713.2 | 15801366 | 1879718.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99252132.48 | 0 | 5980564.8 | 0 | 0 | 3134619.18 | 0 | 0 | 600342.7 | 0 | 0 | 0 | 1081667.5 | 682106.88 | 0 | 3185700 | 0 | 3649459.2 | 0 | 4356040.8 | 0 | 0 | 1548597.66 | 5293065.6 | 2505122 | 801792 | 0 | 152447.688 | 10409317.65 | 0 | 19895194 | 0 | 0 | 0 | 0 | 5652360.12 | 0 | 1636002 | 8948620.8 | 5321575.35 | 0 | 8563599 | 10318060.8 | 0 | 3821812.8 | 0 | 8457973.2 | 0 | 613573.35 | 4524098.88 | 42411790 | 0 | 0 | 0 | 0 |  | 308270539.41 | 262797636.438 | 571068175.848 | 105532104.228 | 99252132.48 | 45637254.27 | 200396606.58 | 72716301.65 | 771878.7 | 24851118.04 | 19627200 | 2283579.9 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 300 | 15 | 0 | 276 | 270 |  | 0 | 240 | 290 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 22 | 8 | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 30 | 0 | 20 | 42 | 80 | 0 | 0 | 0 | 305 | 193 | 45 | 91 | 26 | 5 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 13 | 11 | 82 | 200 | 0 | 0 | 2 | 43 | 42 | 5 | 0 | 0 | 161 | 40 | 5 | 0 | 164 | 0 | 0 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 315 | 45 | 0 | 0 | 3 | 0 | 0 | 0 | 17 | 0 | 0 | 320 | 0 | 46 | 0 | 17 | 0 | 17 | 24 |  | 615 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 5 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 154 | 0 | 12 | 0 | 172 | 0 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 152 | 0 | 0 | 4 |  | 7208 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 102 | 0 | 278 | 342 | 0 | 0 | 240 | 270 | 0 | 0 | 0 | 334 | 0 | 0 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 15 | 25 | 6 | 25 | 12 | 51 | 0 | 62 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 51 | 90 | 95 | 0 | 20 | 42 | 80 | 0 | 0 | 188 | 270 | 213 | 8 | 90 | 26 | 40 | 0 | 43 | 0 | 25 | 43 | 22 | 0 | 33 | 21 | 140 | 204 | 8 | 21 | 0 | 44 | 42 | 53 | 0 | 0 | 160 | 51 | 84 | 0 | 219 | 0 | 0 | 10 | 270 | 16 | 11 | 0 | 55 | 0 | 0 | 187 | 0 | 0 | 0 | 10 | 200 | 110 | 367 | 115 | 105 | 105 | 0 | 16 | 36 | 108 | 17 | 105 | 50 | 397 | 0 | 0 | 54 | 110 | 0 | 17 | 0 |  | 774 | 0 | 350 | 0 | 0 | 50 | 0 | 0 | 15 | 0 | 0 | 0 | 33 | 16 | 0 | 70 | 0 | 50 | 0 | 90 | 0 | 0 | 21 | 52 | 28 | 22 | 0 | 11 | 71 | 0 | 150 | 0 | 0 | 0 | 0 | 170 | 0 | 77 | 100 | 158 | 0 | 401 | 105 | 0 | 74 | 0 | 113 | 0 | 0 | 110 | 460 | 220 | 0 | 100 | 0 |  | 11298 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 108 | 0 | 225 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 63 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 40 | 135 | 0 | 0 | 175 | 0 | 210 | 45 | 90 | 26 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 172 | 210 | 8 | 21 | 0 | 43 | 42 | 51 | 0 | 0 | 163 | 63 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 17 | 113 | 100 | 400 | 104 | 0 | 162 | 112 | 0 | 17 |  |  | 788 | 0 | 390 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 20 | 95 | 0 | 0 | 31 | 52 | 30 | 22 | 0 | 11 | 74 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 76 | 100 | 200 | 0 | 400 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 110
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 108 | 0 | 225 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 100 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 33 | 33 | 52 | 0 | 63 | 60 | 100 | 0 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 40 | 120 | 0 | 0 | 175 | 0 | 210 | 45 | 90 | 26 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 148 | 210 | 8 | 21 | 1.6 | 43 | 42 | 51 | 0 | 0 | 163 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 270 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 17 | 113 | 100 | 400 | 90 | 50 | 162 | 112 | 0 | 17 | 30 |  | 594 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 110 | 0 | 0 | 0 | 50 | 20 | 95 | 0 | 0 | 31 | 52 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 66 | 50 | 200 | 0 | 400 | 105 | 100 | 90 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 110 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 103 | 0 | 225 | 271 | 0 | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 25 | 6 | 22 |  | 0 | 0 | 63 | 60 | 100 | 0 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 40 | 96 | 0 | 18 | 42 | 80 | 0 | 0 | 175 | 0 | 214 | 8 | 90 | 26 | 5 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 98 | 206 | 8 | 21 | 1 | 43 | 42 | 53 | 0 | 0 | 162 | 51 | 81 | 0 | 177 | 0 | 0 | 10 | 300 | 16 | 0 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 6 | 0 | 120 | 0 | 368 | 115 | 17 | 34 | 3 | 0 | 0 | 34 | 17 | 104 | 10 | 350 | 0 | 14 | 0 | 111 | 0 | 17 | 7 | 0 | 582 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 145 | 0 | 66 | 0 | 151 | 0 | 335 | 35 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 400 | 218 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 7114 | 9:00
| Highest Generation |  | 11389 | 22:00
| Day Peak Generation |  | 7208 | 12:00
| Evening Peak Generation |  | 11298 | 21:00
| HVDC Max Flow |  | 815 | 1:00
| HVDC EvPeak Flow |  | 774 | 21:00
| Load factor L.F |  | 78.88%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 7208 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8278 | MW
Evening Peak Generation : |  | 11298 | MW Hour : | 21:00 | Available Max Generation : |  | 14542 | MW
E.P. Demand (at gen end) : |  | 11298 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11389 | MW Hour : | 22:00 | Reserve(Generation end) |  | 3042 | MW
Total Gen. (MKWH) : |  | 215.5971 | System Load Factor : | 78.88% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -520 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-22
Actual : | 84.25 | Ft.(MSL) , | Rule curve : | 87.36 | Ft.( MSL )
Gas Consumed : | Total = | 1096.78 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 151169358.498
: |  | Coal : | 72716301.65 | Oil : | 225247724.62 | Total : | 449133384.768
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4098.0131 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1394.6393 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1249.7444 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1129.3183 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1020.5107 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 823.5188 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 459.0711 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.9969 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 635.1452 |  |  | 0 | 0%
Total | 0 |  | 11021.9577 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-4 & 5
3) Ashuganj-4
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7)Baghabari-100,71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj(N) CCPP GT was synchronized at 19:28.
b) Baghabari 100 MW GT was shut down at 22:15 due to gas shortage.
c) Ashuganj(S) CCPP tripped at 02:29(22/7/2021) due to gas shortage.
d) Sylhet 132/33 kV T-1 transformer tripped at 01:45(22/7/2021) from 33 kV side showing O/C & E/F relay
and was switched on at 02:36.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Under maint.
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7239027 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 102 | 1381045
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 278 | 6789120 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 342 | 7416000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5640500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6599244 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 56174 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 105332 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 15 | 199476 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 334 | 6935130
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 27504 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 399240
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 48 | 480480 | High voltage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 38690 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 141766 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 31 | 761100 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 607500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 12 | 288300 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 426720
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 55 | 371345 | Machine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 24865 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 16355 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 61920 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 937200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 116160 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 54 | 449280 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 156924
| Dhaka area Total |  |  |  | 5819 | 2333 | 47666397
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 184879
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 126495
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 22560 | Reserve.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 122 | 2858810 | Low water level & Unit-2 under maint
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2850343
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1133272
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 285573 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 90 | 1175160 | Engine problem
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 10 | 56640 | Low demand
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 477600
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1149600
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 95 | 1574400 | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 37199
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 95345 | Low demand
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 36 | 311641 | Engine problem
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 108 | 1041268
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 282240 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 110 | 1804036 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1100 | 17767061
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2698878 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4641000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 188 | 794600 | Under maint.
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7116000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 26 | 584784 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 40 | 669600 | Engine problem
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 1338181 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 600548 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 110 | 973527 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 25 | 154352 | Low demand
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 90 | 2128100 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 1221120
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 505440
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 0 | 226440
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2616960
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 675100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 445459 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 452950
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 434340 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1843800 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 442800 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1691 | 30563979
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 204 | 4779120 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 349596
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 161280 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 187 | 1483200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2448000
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 284870
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 122160
| Mymensingh Area Total |  |  |  | 709 | 559 | 9640226
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1030000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 847440 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3608000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 614400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 158536
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 51 | 1204608
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1133760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4737630
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 93000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 385400 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 270 | 7167000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8630000 | FGMO
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 167580
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 397 | 8865400
| Sylhet Area Total |  |  |  | 2377 | 1724 | 38642754
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 774 | 17231273
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 57230 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 50 | 226163 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 350 | 5695776 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 526080
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 988320
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1394 | 24724842
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 69888 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 697850
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 77 | 1090668 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 460 | 9661000 | Low demand
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4856345
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 100 | 1149600 | Low demand
| Barisal Area Total |  |  |  | 2046 | 906 | 17525351
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1554000 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 370880
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Low demand
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 21 | 159814 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 170 | 4282091 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 158 | 4548355 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 401 | 8650100 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 28 | 258260 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 417600
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 201384
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 546240
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 90 | 492208 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 74 | 402720 | Low demand
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 110 | 612192
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 28200
| Rajshahi Area Total |  |  |  | 2179 | 1257 | 22524044
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 71 | 1726255
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3670700 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1089945
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 55527
| Rangpur Area Total |  |  |  | 605 | 334 | 6542427
| Total |  |  |  | 21280 | 11298 | 215597081
| Eastern Grid Total |  |  |  | 14321 | 7407 | 144280417
| Western Grid Total |  |  |  | 6959 | 3891 | 71316664
| National Grid Total |  |  |  | 21280 | 11298 | 215597081
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-21
(a) ENTIRE EASTERN GRID : |  | 6784 | MW | (b) ENTIRE WESTERN GRID : |  | 4035 | MW
i) Dhaka area |  | 3010 | MW | i) Khulna area |  | 1535 | MW
ii) Chittagong area |  | 990 | MW | ii) Rajshahi area |  | 1276 | MW
iii) Comilla area |  | 1255 | MW | iii) Barisal area |  | 400 | MW
iv) Mymensingh area |  | 1026 | MW | iv) Rangpur area |  | 824 | MW
v) Sylhet area |  | 503 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10819 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 80 | 22:00 | Kishoreganj | 158 | 21:00 | Jessore | 117 | 20:00
Munsiganj | 96 | 21:00 | Netrokona | 125 | 19:30 | Benapol | 60 | 19:30
Sonargaon | 45 | 19:30 | Jamalpur | 153 | 21:00 | Jhenida | 114 | 19:00
Shyampur | 70 | 21:00 | Sherpur | 130 | 1:00 | Bottail | 108 | 20:00
Bhulta | 78 | 18:30 | Srimongal | 54 | 19:30 | G.K Project | 59 | 21:00
Madanganj | 30 | 22:00 | Shahjibazar | 94 | 21:00 | Faridpur | 144 | 21:00
Shitalakhya | 54 | 1:00 | Fenchuganj | 46 | 23:00 | Rajbari | 54 | 22:00
Rahim steel | 0 | 0:00 | Kulawara | 49 | 21:00 | Madaripur | 117 | 23:00
Matuail | 28 | 0:00 | Sylhet | 111 | 22:00 | Sariatpur | 82 | 22:00
Ghorasal | 60 | 1:00 | Chatak | 33 | 21:00 | Gopalganj | 98 | 21:00
Narsingdi | 143 | 1:00 | Sunamganj | 52 | 22:00 | Bagerhat | 105 | 19:30
Haripur (SBU) | 36 | 23:00 | Biani Bazar | 74 | 21:00 | Mongla | 16 | 1:00
Sreenagar | 45 | 19:30 | Comilla (S) | 148 | 23:00 | Satkhira | 112 | 21:00
Ullon | 48 | 0:00 | Comilla(N) | 141 | 20:00 | Gallamari | 27 | 23:00
Hasnabad | 67 | 19:30 | Chandpur | 93 | 23:00 | Magura | 56 | 20:00
Magbazar | 64 | 0:00 | Feni | 127 | 20:00 | Norail | 44 | 22:00
Maniknagar | 55 | 0:00 | Chowmuhani | 233 | 21:00 | Chuadanga | 90 | 21:00
Bangabhaban | 4 | 23:00 | Ashuganj | 40 | 22:00 | Borguna | 20 | 22:00
Motijheel | 11 | 23:00 | Daudkandi | 144 | 22:00 | Barisal(N) | 55 | 23:00
Narinda | 38 | 23:00 | B.Baria | 177 | 21:00 | Barisal (S) | 104 | 22:00
Kazla | 46 | 1:00 | Ramganj | 100 | 19:00 | Patuakhali | 129 | 22:00
Dhanmondi | 94 | 19:00 | Chaddagram | 57 | 22:00 | Bhandaria | 60 | 21:00
Lalbag | 42 | 1:00 | PHP | 3 | 9:00 | Borhan Uddin | 47 | 22:00
Madartek | 70 | 23:00 | Kochua | 72 | 20:00 | Ishurdi | 57 | 21:00
Dhaka University | 13 | 20:00 | Madunaghat | 69 | 19:00 | Ruppur Paromanobik | 2 | 18:00
Aftabnagar | 9 | 19:00 | Hathazari | 93 | 21:00 | Natore | 127 | 21:00
Fatullah | 34 | 22:00 | Khulshi | 141 | 1:00 | Bogra | 151 | 22:00
Nawabganj | 54 | 21:00 | Halishahar | 65 | 22:00 | Noagaon | 110 | 21:00
Keraniganj | 54 | 23:00 | Baraulia | 52 | 22:00 | Rajshahi | 154 | 21:00
Mirpur | 98 | 23:00 | Sikalbaha | 27 | 19:30 | Rajshahi New | 15 | 22:00
Kalyanpur | 102 | 19:00 | Dohazari | 94 | 21:00 | C.Nawabganj | 57 | 23:00
Gulshan | 62 | 19:00 | Cox'sbazar | 94 | 1:00 | Amnura | 52 | 21:00
Uttara | 77 | 19:00 | Chandraghona | 34 | 19:30 | Pabna | 97 | 21:00
Uttara New | 12 | 19:00 | Kaptai | 4 | 19:00 | Shahjadpur | 100 | 22:00
Kamrangirchar | 60 | 19:00 | A. Khaer Stl. | 2 | 1:00 | Serajganj | 102 | 22:00
Savar | 102 | 23:00 | Bakulia | 89 | 21:00 | Niyamatpur | 80 | 22:00
Bhasantec | 106 | 23:00 | Julda | 14 | 1:00 | Joypurhat | 59 | 21:00
Agargaon | 61 | 23:00 | TK chemical | 35 | 21:00 | Sherpur(Bogura) | 48 | 21:00
Satmosjid | 87 | 23:00 | Modern Steel | 0 | #N/A | Mohastangor | 72 | 20:00
Tongi | 73 | 23:00 | Shahmirpur | 20 | 19:30 | Bhangura | 34 | 20:00
Kabirpur | 135 | 22:00 | Khagrachhari | 30 | 19:30 | Rangpur | 142 | 19:30
Basundhara | 162 | 19:30 | Matarbari | 42.5 | 21:00 | Lalmonirhat | 45 | 19:30
Manikganj | 78 | 22:00 | Baroiar Hat | 60 | 21:00 | Saidpur | 102 | 22:00
Joydevpur | 103 | 23:00 | Rangamati | 13 | 19:30 | Purbasadipur | 96 | 21:00
New Tongi | 57 | 22:00 | Abul Khair 230 | 79 | 3:00 | Thakurgaon | 89 | 20:00
Kodda | 127 | 2:00 | BSRM | 54 | 2:00 | Palashbari | 120 | 22:00
Dhamrai | 82 | 20:00 | GPH Ispat | 9 | 21:00 | Barapukuria | 54 | 21:00
Rajendrapur | 64 | 21:00 | Agrabad | 68 | 22:00 | Panchagar | 55 | 20:00
Valuka | 92 | 1:00 | Goalpara | 22 | 21:00 | Joldhaka | 68 | 22:00
Tangail | 219 | 21:00 | Central S/S | 90 | 19:30 | Kurigram | 62 | 19:30
Mymensing | 188 | 20:00 | Noapara | 47 | 20:00 | Mithapukur | 33 | 23:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 20:00 | 397 | 22:00 | Kaliakoir | 394 | 0.375 | 385 | 0.79167
| Bheramara | 407 | 19:30 | 396 | 23:00 | Bhulta | 382 | 0.91667 | 371 | 0.66667
| Ashuganj(N) | 385 | 9:00 | 375 | 16:00 | Gopalganj | 409 | 0.625 | 392 | 0.95833
| Payra | 414 | 9:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 223 | 19:30 | 216 | 17:00
| Ishurdi | 235 | 7:00 | 224 | 1:00 | Megnaghat | 234 | 1:00 | 230 | 12:00
| Ashuganj | 236 | 1:00 | 230 | 16:00 | Fenchuganj | 235 | 3:00 | 233 | 5:00
| Serajganj | 230 | 6:00 | 225 | 1:00 | Siddhirganj | 231 | 9:00 | 228 | 15:00
| Baghabari | 232 | 3:00 | 225 | 23:00 | Maniknagar | 230 | 9:00 | 226 | 17:00
| Barapukuria | 235 | 8:00 | 226 | 21:00 | Agargaon | 227 | 9:00 | 222 | 16:00
| Bogra | 224 | 10:00 | 213 | 22:00 | Barisal | 241 | 21:00 | 232 | 19:00
| Rajshahi | 233 | 10:00 | 222 | 2:00 | Bhola 225 MW | 244 | 7:00 | 236 | 16:00
| Khulna South | 229 | 9:00 | 208 | 16:00 | AKSML | 227 | 21:00 | 217 | 15:00
| Rampura | 230 | 4:00 | 227 | 15:00 | BSRM | 226 | 19:30 | 220 | 16:00
| Haripur | 229 | 7:00 | 225 | 16:00 | Bibiyana | 238 | 9:00 | 233 | 12:00
| Hasnabad | 230 | 12:00 | 225 | 14:00 | Bhulta | 231 | 5:00 | 226 | 16:00
| Shyampur | 227 | 9:00 | 220 | 17:00 | Ashuganj (S) | 233 | 1:00 | 229 | 16:00
| Aminbazar | 228 | 1:00 | 223 | 2:00 | Kaliakoir | 228 | 8:00 | 223 | 16:00
| Tongi | 227 | 19:00 | 222 | 15:00 | GPH | 225 | 19:30 | 216 | 16:00
| Comilla (N) | 228 | 9:00 | 223 | 17:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 7:00 | 131 | 17:00 | Madanhat | 135 | 0.79167 | 128 | 0.45833
| Munsiganj | 136 | 20:00 | 130 | 15:00 | Hathazari | 133 | 0.8125 | 129 | 0.25
| Sonargaon | 133 | 19:30 | 130 | 1:00 | Khulshi | 132 | 0.8125 | 125 | 0.45833
| Shyampur | 137 | 8:00 | 134 | 16:00 | Halishahar | 134 | 0.8125 | 125 | 0.5
| Bhulta | 129 | 1:00 | 126 | 15:00 | Baraulia | 131 | 0.77083 | 126 | 0.25
| Madanganj | 136 | 19:30 | 129 | 16:00 | Sikalbaha | 135 | 0.8125 | 126 | 0.25
| Shitalakhya | 141 | 9:00 | 134 | 17:00 | Dohazari | 129 | 0.8125 | 122 | 0.25
| Rahim steal | 134 | 2:00 | 132 | 16:00 | Cox'sbazar | 118 | 0.77083 | 113 | 0.25
| Matuail | 134 | 7:00 | 131 | 17:00 | Chandraghona | 133 | 0.8125 | 128 | 0.66667
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 132 | 0.875 | 130 | 0.041667
| Narsinghdi | 131 | 10:00 | 123 | 21:00 | A. Khaer Stl. | 131 | 0.83333 | 127 | 0.29167
| Haripur (SBU) | 135 | 20:00 | 132 | 15:00 | Bakulia | 133 | 0.83333 | 125 | 0.29167
| Sreenagar | 131 | 19:30 | 126 | 17:00 | Julda | 134 | 0.79167 | 126 | 0.25
| Ullon | 135 | 7:00 | 130 | 16:00 | TK Chemical | 134 | 0.8125 | 126 | 0.33333
| Hasnabad | 140 | 7:00 | 134 | 15:00 | Modern Steel
| Magbazar | 136 | 4:00 | 132 | 15:00 | Shahmirpur | 134 | 0.83333 | 125 | 0.5
| Maniknagar | 135 | 8:00 | 133 | 15:00 | Khagrachhari | 131 | 0.8125 | 126 | 0.66667
| Bangabhaban | 135 | 8:00 | 133 | 15:00 | Matarbari | 120 | 0.41667 | 113 | 0.25
| Motijheel | 135 | 8:00 | 133 | 15:00 | Baroiar Hat | 129 | 0.375 | 123 | 0.91667
| Narinda | 135 | 8:00 | 133 | 15:00 | Rangamati | 132 | 19:30 | 127 | 15:00
| Kazla | 135 | 8:00 | 133 | 15:00 | Agrabad | 133 | 19:30 | 125 | 11:00
| Dhanmondi | 135 | 9:00 | 132 | 16:00 | Goalpara S/S | 138 | 9:00 | 125 | 0.625
| Lalbag | 141 | 9:00 | 134 | 16:00 | Khulna Central S/S | 137 | 9:00 | 123 | 0.625
| Madartek | 135 | 9:00 | 130 | 15:00 | Noapara | 135 | 8:00 | 119 | 0.8125
| Dhaka University | 136 | 9:00 | 130 | 16:00 | Jessore | 132 | 9:00 | 111 | 0.8125
| Aftabnagar | 135 | 4:00 | 130 | 16:00 | Benapol | 132 | 0.375 | 113 | 0.875
| Fatullah | 137 | 8:00 | 134 | 17:00 | Jhenida | 129 | 9:00 | 106 | 0.875
| Nawabganj | 130 | 6:00 | 125 | 16:00 | Bottail | 133 | 0.375 | 119 | 0.79167
| Keraniganj | 131 | 19:30 | 127 | 16:00 | G.K Project | 137 | 0.29167 | 132 | 0.91667
| Mirpur | 137 | 20:00 | 134 | 16:00 | Faridpur | 138 | 0.375 | 128 | 0.875
| Kalyanpur | 138 | 6:00 | 133 | 16:00 | Rajbari | 137 | 0.375 | 125 | 0.875
| Gulshan | 135 | 6:00 | 129 | 16:00 | Madaripur | 141 | 0.375 | 132 | 0.79167
| Uttara | 136 | 6:00 | 131 | 16:00 | Shariyatpur S/S | 140 | 10:00 | 130 | 0.875
| Uttara New | 137 | 6:00 | 131 | 9:00 | Gopalganj | 144 | 0.375 | 132 | 0.875
| Kamrangirchar | 141 | 6:00 | 134 | 9:00 | Bagerhat | 134 | 8:00 | 118 | 0.79167
| Savar | 131 | 19:30 | 131 | 9:00 | Mongla | 135 | 9:00 | 119 | 0.625
| Bhasantec | 137 | 19:30 | 133 | 20:00 | Satkhira | 137 | 9:00 | 118 | 19:30
| Agargaon | 137 | 19:30 | 134 | 20:00 | Gallamari | 139 | 0.375 | 124 | 19:00
| Satmosjid | 137 | 19:30 | 133 | 20:00 | Magura | 128 | 9:00 | 105 | 0.8125
| Tongi | 140 | 19:00 | 136 | 5:00 | Narail | 125 | 0.33333 | 100 | 0.875
| Kabirpur | 141 | 9:00 | 135 | 21:00 | Chuadanga | 124 | 9:00 | 94 | 0.875
| Basundhara | 138 | 19:30 | 130 | 18:00 | Borguna | 136 | 1:00 | 130 | 0.75
| Manikganj | 139 | 19:30 | 134 | 22:00 | Barisal(N) | 141 | 8:00 | 132 | 15:00
| Joydevpur | 138 | 22:00 | 133 | 16:00 | Barisal (S) | 138 | 0.375 | 131 | 0.625
| New Tongi | 139 | 19:30 | 134 | 16:00 | Patuakhali(S) | 140 | 0.125 | 126 | 0.625
| Kodda | 138 | 20:00 | 130 | 16:00 | Bhandaria | 134 | 0.083333 | 125 | 0.79167
| Dhamrai | 133 | 8:00 | 128 | 0:00 | Ishurdi | 136 | 8:00 | 130 | 22:00
| Rajendrapur | 137 | 20:00 | 128 | 18:00 | Ruppur Paromanobik | 136 | 9:00 | 130 | 21:00
| Valuka | 124 | 13:00 | 110 | 20:00 | Natore | 134 | 9:00 | 127 | 21:00
| Tangail | 134 | 6:00 | 125 | 23:00 | Bogra | 132 | 9:00 | 125 | 21:00
| Mymensing | 126 | 13:00 | 114 | 19:00 | Noagaon | 128 | 9:00 | 117 | 22:00
| Kishorganj | 128 | 0:00 | 116 | 20:00 | Rajshahi | 132 | 9:00 | 124 | 22:00
| Netrokona | 125 | 9:00 | 107 | 20:00 | Rajshahi New | 131 | 8:00 | 125 | 14:00
| Jamalpur | 127 | 13:00 | 118 | 19:00 | C.Nawabganj | 130 | 8:00 | 121 | 1:00
| Sherpur | 126 | 2:00 | 116 | 19:00 | Amnura | 130 | 10:00 | 120 | 2:00
| Srimongal | 135 | 4:00 | 130 | 19:00 | Pabna | 136 | 10:00 | 128 | 22:00
| Shahjibazar | 134 | 5:00 | 127 | 19:00 | Shahjadpur | 139 | 7:00 | 130 | 22:00
| Fenchuganj | 135 | 10:00 | 133 | 7:00 | Serajganj | 133 | 8:00 | 126 | 23:00
| Khulawara | 135 | 9:00 | 132 | 18:30 | Niyamatpur | 126 | 10:00 | 111 | 22:00
| Sylhet | 133 | 7:00 | 123 | 8:00 | Joypurhat | 128 | 9:00 | 115 | 22:00
| Chatak | 134 | 7:00 | 128 | 21:00 | Sherpur(Bogura) | 133 | 10:00 | 125 | 21:00
| Sunamganj | 132 | 11:00 | 125 | 21:00 | Mohastangor | 131 | 9:00 | 122 | 21:00
| Biani Bazar | 132 | 8:00 | 126 | 19:30 | Bangura | 136 | 8:00 | 130 | 23:00
| Comilla(s) | 129 | 4:00 | 123 | 23:00 | Rangpur | 127 | 9:00 | 115 | 21:00
| Comilla(n) | 135 | 8:00 | 131 | 22:00 | Lalmonirhat | 127 | 9:00 | 115 | 19:30
| Chandpur | 130 | 19:00 | 124 | 15:00 | Saidpur | 130 | 8:00 | 112 | 21:00
| Feni | 128 | 18:30 | 123 | 16:00 | Purbasadipur | 130 | 9:00 | 109 | 21:00
| Chowmuhani | 132 | 4:00 | 120 | 22:00 | Thakurgaon | 132 | 9:00 | 109 | 23:00
| Ashuganj | 137 | 9:00 | 132 | 19:00 | Palashbari | 130 | 9:00 | 118 | 21:00
| Daudkandi | 131 | 7:00 | 126 | 22:00 | Barapukuria | 135 | 8:00 | 126 | 21:00
| B.Baria | 132 | 9:00 | 125 | 19:00 | Panchagar | 132 | 9:00 | 107 | 21:00
| Ramganj | 126 | 10:00 | 120 | 16:00 | Joldhaka | 127 | 0.375 | 109 | 0.875
| Chaddagram | 131 | 18:30 | 125 | 22:00 | Kurigram | 125 | 0.375 | 110 | 0.91667
| PHP | 128 | 18:30 | 123 | 22:00 | Mithapukur | 130 | 0.375 | 119 | 0.875
| Kochua | 131 | 16:00 | 127 | 19:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 414 | 7332 | 3718 | 11050 |  |  |  | QF-LDC-11
0:30 | 316 | 7058 | 3567.5 | 10625.5 | Date: | 2021-07-21
1:00 | 218 | 6784 | 3417 | 10201
1:30 | 206 | 6697.5 | 3401 | 10098.5
2:00 | 194 | 6611 | 3385 | 9996
2:30 | 197 | 6493.5 | 3335.5 | 9829 | [5 empty] | Gen. at Eve. Peak | 11298 | 11298 MW (21:00 )
3:00 | 200 | 6376 | 3286 | 9662 | [6 empty] | 21:00
3:30 | 193 | 6284.5 | 3217.5 | 9502 | [5 empty] | Gen. at Day Peak | 7208 | 7208 MW (12:00 )
4:00 | 186 | 6193 | 3149 | 9342 | [6 empty] | 12:00
4:30 | 203 | 6159 | 3068 | 9227 | [5 empty] | Highest Generation | 11389
5:00 | 220 | 6125 | 2987 | 9112 | [6 empty] | 22:00
5:30 | 170 | 5813 | 2884.5 | 8697.5
6:00 | 120 | 5501 | 2782 | 8283
6:30 | 131 | 5438 | 2737 | 8175
7:00 | 142 | 5375 | 2692 | 8067
7:30 | 124 | 5159 | 2595 | 7754
8:00 | 106 | 4943 | 2498 | 7441
8:30 | 84 | 4831.5 | 2446 | 7277.5
9:00 | 62 | 4720 | 2394 | 7114
9:30 | 66 | 4686 | 2362.5 | 7048.5
10:00 | 70 | 4652 | 2331 | 6983
10:30 | 70 | 4677.5 | 2330.5 | 7008
11:00 | 70 | 4703 | 2330 | 7033
11:30 | 71 | 4765.5 | 2355 | 7120.5
12:00 | 72 | 4828 | 2380 | 7208
12:30 | 80 | 4896 | 2460 | 7356
13:00 | 88 | 4964 | 2540 | 7504
13:30 | 81 | 5113.5 | 2653 | 7766.5
14:00 | 74 | 5263 | 2766 | 8029
14:30 | 93 | 5363.5 | 2754.5 | 8118
15:00 | 112 | 5464 | 2743 | 8207
15:30 | 93 | 5534.5 | 2792.5 | 8327
16:00 | 74 | 5605 | 2842 | 8447
16:30 | 45 | 5622.5 | 2848.5 | 8471
17:00 | 16 | 5640 | 2855 | 8495
17:30 | 13 | 5594 | 2848 | 8442
18:00 | 10 | 5548 | 2841 | 8389
18:30 | 103 | 5940.5 | 2927 | 8867.5
19:00 | 196 | 6333 | 3013 | 9346
19:30 | 424 | 7555 | 3482 | 11037
20:00 | 520 | 7438 | 3616 | 11054 |  |  |  | Executive Engineer
20:30 | 412 | 7422.5 | 3753.5 | 11176 |  |  |  | Network Operation Division
21:00 | 304 | 7407 | 3891 | 11298
21:30 | 323 | 7434 | 3909.5 | 11343.5
22:00 | 342 | 7461 | 3928 | 11389 |  |  |  |  | Page 6 of 7
22:30 | 342 | 7475.5 | 3906 | 11381.5
23:00 | 342 | 7490 | 3884 | 11374
23:30 | 378 | 7411 | 3801 | 11212
24:00 | 414 | 7332 | 3718 | 11050
11298 MW (21:00 )
7208 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-21 |  | Energy | 215597081
[11 empty] | 2021-07-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4270 | 774 | 1981 | 2831 | 764 | 122 | 316 | 0 | 96 | 0
0:30 | 4311.5 | 794.5 | 2006 | 2390 | 678 | 121 | 265.5 | 0 | 111 | 0 | Date: | 2021-07-21
1:00 | 4353 | 815 | 2031 | 1949 | 592 | 120 | 215 | 0 | 126 | 0
1:30 | 4349 | 811 | 2035.5 | 1892.5 | 592 | 120 | 173.5 | 0 | 125 | 0 | [7 empty] | Total Energy | 215.5971 | Total Energy Gen 215.597 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 215.597 MKWHr
2:00 | 4345 | 807 | 2040 | 1836 | 592 | 120 | 132 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4338.5 | 807 | 2022 | 1740.5 | 592 | 120 | 87 | 0 | 122 | 0 | [7 empty] | Energy Requirement | 215.5971
3:00 | 4332 | 807 | 2004 | 1645 | 592 | 120 | 42 | 0 | 120 | 0
3:30 | 4324 | 807 | 1989.5 | 1516 | 591.5 | 121.5 | 34.5 | 0 | 118 | 0 | [6 empty] | Shortage
4:00 | 4316 | 807 | 1975 | 1387 | 591 | 123 | 27 | 0 | 116 | 0
4:30 | 4337.5 | 759.5 | 1994.5 | 1295 | 591 | 123 | 13.5 | 0 | 113 | 0
5:00 | 4359 | 712 | 2014 | 1203 | 591 | 123 | 0 | 0 | 110 | 0
5:30 | 4303 | 711.5 | 1927.5 | 919.5 | 606 | 123 | 0 | 0 | 106 | 1
6:00 | 4247 | 711 | 1841 | 636 | 621 | 123 | 0 | 0 | 102 | 2
6:30 | 4230 | 662.5 | 1841 | 590.5 | 621 | 123 | 0 | 0 | 100 | 7 |  |  |  |  | Coal
7:00 | 4213 | 614 | 1841 | 545 | 621 | 123 | 0 | 0 | 98 | 12
7:30 | 4126 | 614.5 | 1690.5 | 485.5 | 596 | 124 | 0 | 0 | 89 | 28.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4039 | 615 | 1540 | 426 | 571 | 125 | 0 | 0 | 80 | 45
8:30 | 3929.5 | 615 | 1505.5 | 421 | 556 | 125 | 0 | 0 | 77 | 48.5
9:00 | 3820 | 615 | 1471 | 416 | 541 | 125 | 0 | 0 | 74 | 52
9:30 | 3802.5 | 615 | 1437 | 403.5 | 531 | 124 | 0 | 0 | 76 | 59.5
10:00 | 3785 | 615 | 1403 | 391 | 521 | 123 | 0 | 0 | 78 | 67
10:30 | 3771 | 615 | 1427.5 | 402 | 522 | 123 | 0 | 0 | 78 | 69.5
11:00 | 3757 | 615 | 1452 | 413 | 523 | 123 | 0 | 0 | 78 | 72
11:30 | 3811 | 615 | 1462.5 | 419.5 | 523 | 121 | 0 | 0 | 80 | 88.5
12:00 | 3865 | 615 | 1473 | 426 | 523 | 119 | 0 | 0 | 82 | 105
12:30 | 3899.5 | 663.5 | 1468 | 503.5 | 521.5 | 119 | 0 | 0 | 84 | 97
13:00 | 3934 | 712 | 1463 | 581 | 520 | 119 | 0 | 0 | 86 | 89
13:30 | 3934 | 712 | 1463 | 581 | 520 | 119 | 0 | 0 | 86 | 89
14:00 | 3934 | 712 | 1463 | 581 | 520 | 119 | 0 | 0 | 86 | 89
14:30 | 4076 | 759 | 1558.5 | 645.5 | 521 | 119 | 0 | 0 | 94 | 82.5
15:00 | 4218 | 806 | 1654 | 710 | 522 | 119 | 0 | 0 | 102 | 76
15:30 | 4293.5 | 806 | 1697 | 721.5 | 522 | 120.5 | 0 | 0 | 104 | 62.5
16:00 | 4369 | 806 | 1740 | 733 | 522 | 122 | 0 | 0 | 106 | 49
16:30 | 4380 | 796.5 | 1738.5 | 764.5 | 522 | 121.5 | 0 | 0 | 109 | 39
17:00 | 4391 | 787 | 1737 | 796 | 522 | 121 | 0 | 0 | 112 | 29
17:30 | 4360 | 787 | 1724.5 | 797 | 522 | 121 | 2.5 | 0 | 110 | 18
18:00 | 4329 | 787 | 1712 | 798 | 522 | 121 | 5 | 0 | 108 | 7
18:30 | 4334 | 781 | 1652.5 | 1173 | 522 | 121 | 160.5 | 0 | 120 | 3.5
19:00 | 4339 | 775 | 1593 | 1548 | 522 | 121 | 316 | 0 | 132 | 0
19:30 | 4450 | 773 | 1729 | 2856 | 602 | 121 | 376 | 0 | 130 | 0
20:00 | 4418 | 774 | 1787 | 2792 | 601 | 122 | 430 | 0 | 130 | 0
20:30 | 4443.5 | 774 | 1887 | 2769.5 | 641 | 122 | 404 | 0 | 135 | 0
21:00 | 4469 | 774 | 1987 | 2747 | 681 | 122 | 378 | 0 | 140 | 0
21:30 | 4449.5 | 774 | 1992.5 | 2768.5 | 716 | 122 | 380 | 0 | 141 | 0
22:00 | 4430 | 774 | 1998 | 2790 | 751 | 122 | 382 | 0 | 142 | 0
22:30 | 4392 | 774.5 | 1998.5 | 2810.5 | 757.5 | 122 | 381.5 | 0 | 145 | 0
23:00 | 4354 | 775 | 1999 | 2831 | 764 | 122 | 381 | 0 | 148 | 0
23:30 | 4312 | 774.5 | 1990 | 2831 | 764 | 122 | 348.5 | 0 | 122 | 0 | Max Temp. in Dhaka |  | 32.5° C
24:00 | 4270 | 774 | 1981 | 2831 | 764 | 122 | 316 | 0 | 96 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 215.597 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 215.597 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 60 | 60 | 60 | 63 | 63 | 63 | 63 | 65 | 65 | 63 | 63 | 59 | 59 | 59 | 59 | 62 | 61 | 61 |  | 61 | 61 | 62 | 62 | 62 | 62 | 62 | 1402810
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1456000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [15 empty] | 3 | 8 |  | 19 | 25 | 25 | 25 | 25 | 25 | 25 | 184879
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 |  | 5 | 10 | 17 | 20 | 20 | 5 | 9 | 10 | 7 | 6 | 1 | [8 empty] | 126495
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2850343
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 285573
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 51 | [12 empty] | 3 |  | 61 | 105 | 105 | 105 | 105 | 105 | 105 | 1133272
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 37 | 42 | 42 | 25 | 25 | 25 | 25 | 154352
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 328 | 327 | 328 |  | 327 | 332 | 331 | 334 | 334 | 293 | 290 | 6935130
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 5 | 15 | 37 | 55 | 97 | 114 |  | 371345
19 | Ashuganj 195MW PP (APSCL-United) | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 73 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 45 |  | 16 | 32 | 8 | 8 | 8 | 8 | 8 | 1338181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7239027
26
28 | Ashuganj TPP Unit- 3 | 135 | 135 | 135 | 135 | 135 | 135 | 135 | 90 | 80 | 80 | 80 | 80 | 80 | 135 | 135 | 135 | 135 | 135 |  | 100 | 135 | 100 | 80 | 80 | 80 | 80 | 2698878
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 584784
33 | Ashuganj 225 MW CCPP | 191 | 184 | 183 | 182 | 194 | 184 | 185 | 181 | 168 | 168 | 172 | 193 | 186 | 180 | 203 | 203 | 196 | 182 |  | 203 | 216 | 214 | 213 | 214 | 214 | 213 | 4641000
34 | Ashuganj 450 MW CCPP(South) | 310 | 300 | 300 | 285 | 300 | 285 | 285 | 285 | 285 | 285 | 290 | 305 | 295 | 285 | 330 | 330 | 320 | 295 |  | 330 | 295 | 270 | 270 | 270 | 270 | 285 | 7116000
| Ashuganj 450 MW CCPP(North) | [20 empty] | 15 | 85 | 188 | 190 | 190 | 192 | 794600
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 51 | 52 | 52 | 51 | 53 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 20 | 20 | 40 | 48 | 52 | 51 | 669600
36 | Chandpur 150 MW CCPP | 91 | 92 | 90 | 91 | 91 | 91 | 91 | 91 | 88 | 90 | 91 | 91 | 91 | 91 | 91 | 91 | 91 | 88 |  | 82 | 81 | 80 | 90 | 89 | 90 | 90 | 2128100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 276 | 276 | 275 | 275 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 | 276 |  | 277 | 279 | 279 | 278 | 278 | 280 | 279 | 6789120
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 220 | 5640500
41 | Haripur 360MW CCPP(HPL) | 301 | 303 | 302 | 302 | 302 | 302 | 302 | 302 | 301 | 270 | 272 | 270 | 270 | 270 | 279 | 341 | 340 | 343 |  | 300 | 350 | 340 | 342 | 340 | 342 | 342 | 7416000
42 | RPCL 210MW CCPP | 207 | 207 | 208 | 209 | 207 | 206 | 206 | 206 | 204 | 204 | 203 | 200 | 199 | 203 | 197 | 196 | 199 | 202 |  | 182 | 206 | 204 | 204 | 204 | 204 | 204 | 4779120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 10 | 29 | 16 | 17 | 18 | 46 | 45 | 31 | 31 | 23 | 8 | 3 | [8 empty] | 284870
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 |  | 44 | 44 | 43 | 44 | 43 | 43 | 43 | 1030000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 847440
46 | Shajibazar 330 MW CCPP | 162 | 162 | 162 | 162 | 162 | 163 | 163 | 162 | 160 | 162 | 160 | 161 | 160 | 159 | 158 | 158 | 160 | 162 |  | 159 | 164 | 163 | 160 | 162 | 163 | 162 | 3608000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 57 | 57 | 57 | 57 | 56 | 20 | 40 | 40 | 40 | 40 | 40 | 40 | 61 | 55 | 55 | 55 | 56 |  | 50 | 52 | 51 | 51 | 51 | 51 | 51 | 1204608
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 40 | 40 | 40 | 40 | 40 |  | 10 | 84 | 84 | 84 | 84 | 84 | 81 | 1133760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 206 | 164 | 164 | 164 | 164 | 165 | 165 | 165 | 165 | 165 | 165 |  | 205 | 219 | 219 | 219 | 219 | 219 | 219 | 4737630
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | [21 empty] | 93000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | [8 empty] | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 167580
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | [8 empty] | 2 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 158536
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 7 | 50 | 53 | 53 | 53 | 53 | 53 | 614400
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | [8 empty] | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 385400
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 290 | 290 | 300 | 300 | 305 | 290 | 285 | 275 | 290 | 310 | 300 | 290 | 295 | 315 | 310 | 285 |  | 270 | 250 | 260 | 270 | 285 | 285 | 300 | 7167000
| Bibiyana South 400 MW | 394 | 400 | 400 | 400 | 396 | 398 | 398 | 365 | 340 | 320 | 320 | 320 | 320 | 395 | 385 | 360 | 360 | 360 |  | 400 | 399 | 400 | 397 | 399 | 397 | 393 | 8865400
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 40 | 55 | 17 | 17 | 17 | 17 | 17 | 141766
59 | Tangail Palli Power Gen 22 MW | [19 empty] | 0 | 15 | 13 | 24 | 24 | 24 | 24 | 122160
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 477600
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | [11 empty] | 10 | 10 |  | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 199476
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [7 empty] | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 349596
63 | Impoprt (Tripura) | 126 | 124 | 120 | 116 | 110 | 102 | 98 | 80 | 74 | 78 | 78 | 82 | 86 | 94 | 102 | 106 | 112 | 108 |  | 132 | 130 | 130 | 140 | 142 | 148 | 96 | 2616960
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1149600
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505440
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 |  |  | 11 | 8 | 226440
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  |  |  | 13 | 33 | 33 | 33 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 675100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 17 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 452950
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 8 | 8 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 161100
71 | Maona 33 MW PP(Summit) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 28 | 28 | 607500
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  |  |  |  | 8 | 12 | 12 | 12 | 12 | 12 | 12 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 288300
73 | Ghorashal 108MW PP (Regent) | 102 | 102 | 102 | 102 | 102 | 103 | 102 | 20 | 15 | 14 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 |  | 14 | 52 | 75 | 102 | 102 | 103 | 102 | 1381045
| Feni Lanka Power | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 434340
| Chowmuhani 113 MW | 99 | 98 | 105 | 105 | 99 | 106 | 45 | [5 empty] | 34 | 45 | 79 | 105 | 105 | 105 |  | 105 | 105 | 106 | 105 | 106 | 106 | 105 | 1843800
| Manikgonj 162MW PP(MPGL) | [19 empty] | 43 | 108 | 108 | 54 | 54 | 54 | 54 | 449280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 51 | 51 | 25 | [16 empty] | 22 | 43 | 51 | 51 | 51 | 51 | 51 | 426720
79 | Kodda 150MW PP | 115 | 32 | [15 empty] | 5 |  | 48 | 82 | 82 | 48 | 48 | 48 | 48 | 480480
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  | 2 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 161280
81 | Jangalia 52 MW PP (Lakdanavi) | 25 | 16 | 16 | 16 | [11 empty] | 2 | 35 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 445459
| Gazipur 100 MW PP | 105 | 105 | 35 | 17 | 17 | [14 empty] | 40 | 105 | 105 | 105 | 105 | 105 | 105 | 937200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 3 | 4 | 4 | 3 | 5 | 4 | 4 | 3 | 1 | 0 | [8 empty] | 37199
| Jodiac Power | 35 | 35 | 17 | [14 empty] | 1 |  | 17 | 36 | 28 | 36 | 36 | 35 | 35 | 311641
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 51 | [15 empty] | 29 | 108 | 99 | 108 | 110 | 110 | 110 | 1041268
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 19 | 70 | 70 |  |  |  |  | 105332
86 | Meghnaghat CCPP ( Summit) | 260 | 260 | 280 | 260 | 280 | 280 | 285 | 270 | 260 | 265 | 280 | 290 | 285 | 270 | 295 | 290 | 290 | 265 |  | 300 | 235 | 250 | 270 | 265 | 275 | 285 | 6599244
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 17 | 90 | 90 |  |  |  |  | 116160
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 94 | 92 | 84 | 94 | 94 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 20 | 20 | 20 | 20 | 20 |  | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 1175160
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 25 | 35 | 43 | 43 | 43 | 43 | 600548
94 | Gagnagar 102 MW PP (Digital Power) | [17 empty] | 7 |  | 16 | 16 | [5 empty] | 27504
95 | Patenga 50MW PP (Baraka) | [19 empty] | 5 | 25 | [5 empty] | 22560
96 | Chattogram 108 MW PP (ECPV) | 88 | 52 | 52 | 52 | 51 | 51 | 51 | 12 | 12 | 12 | 19 | 30 | 62 | 87 | 87 | 87 | 90 | 93 |  | 93 | 93 | 95 | 95 | 95 | 96 | 96 | 1574400
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 8 | 30 | 30 |  |  |  |  | 56174
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 17 | 17 |  |  |  |  | 38690
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 2 | 1 | 0 | 0 | [8 empty] | 12000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | [13 empty] | 35 | 54 | 54 | 54 | 54 | 54 | 54 | 399240
104 | Keranigonj 300 MW PP (APR) | [20 empty] | 42 | [5 empty] | 24865
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 80 | 80 | 80 | 50 | 50 | [11 empty] | 24 | 24 |  | 29 | 177 | 186 | 187 | 189 | 193 | 194 | 1483200
112 | Aurahati 100MW PP (Aggreko) | [20 empty] | 27 | [5 empty] | 16355
114 | Kodda 149 MW PP Unit-1 (Summit) | [17 empty] | 0 |  | 16 | 18 | 35 |  |  |  |  | 61920
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 56640
116 | Chandpur 200MW (Desh energy) | 51 | 51 | 51 | 51 | 51 | [14 empty] | 58 | 160 | 135 | 200 | 155 | 155 | 155 | 1221120
117 | Ashuganj 150MW PP (Midland) | 100 | 100 | 10 | [16 empty] | 15 | 100 | 80 | 110 | 140 | 150 | 150 | 973527
118 | Bibiyana-III 400 MW CCPP | 372 | 364 | 367 | 367 | 382 | 366 | 366 | 343 | 306 | 306 | 308 | 315 | 313 | 366 | 401 | 404 | 384 | 366 |  | 400 | 366 | 367 | 367 | 366 | 366 | 370 | 8630000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 95 | 95 | 75 | 75 | 45 | 45 | 45 | 106 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2448000
| Anwara 300 MW PP (United) | [19 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 95345
| Juldah unit-2 (Acorn) | 10 | [18 empty] | 36 | 50 | 50 | 50 | 50 | 50 | 50 | 282240
| Anlima Energy Ltd. | 111 | 111 | 111 | 111 | 111 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 40 | 72 | 72 | 72 | 72 | 72 |  | 85 | 110 | 110 | 110 | 110 | 110 | 110 | 1804036
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 442800
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 0 | 5 | 17 | 22 | 19 | 24 | 21 | 20 | 21 | 7 | 10 | 1 | [8 empty] | 156924
120 | Eastern Zone Total | 6784 | 6611 | 6376 | 6193 | 6125 | 5501 | 5375 | 4943 | 4720 | 4652 | 4703 | 4828 | 4964 | 5263 | 5464 | 5605 | 5640 | 5548 |  | 6333 | 7555 | 7438 | 7407 | 7461 | 7490 | 7332 | 144280417
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [19 empty] | 4 | 4 | 4 | 15 | 19 | 19 |  | 57230
| Khulna 225 MW CCPP | [21 empty] | 50 | 50 | 50 | 50 | 50 | 226163
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 53 | 53 | [14 empty] | 15 | 90 | 80 | 105 | 105 | 105 | 105 | 988320
130
131
132 | United Payra Power Ltd. | 126 | 126 | 126 | 126 | 72 | [14 empty] | 7 | 100 | 90 | 100 | 100 | 100 | 100 | 1149600
133 | Bhola Nutan Biddut BD LTD (GAS) | 219 | 219 | 220 | 220 | 220 | 220 | 221 | 186 | 182 | 152 | 152 | 152 | 152 | 216 | 214 | 214 | 216 | 215 |  | 190 | 176 | 200 | 220 | 219 | 219 | 220 | 4856345
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [21 empty] | 16 | 16 | 16 | 16 | 16 | 69888
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 78 | 78 | 78 | 76 | 76 | 76 | 77 | 12 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 |  | 30 | 58 | 72 | 77 | 77 | 77 | 76 | 1090668
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 34 | 34 | 34 | 32 | 25 | 25 | 24 | 24 | 24 | 26 | 26 | 25 | 26 | 29 | 29 | 28 |  | 30 | 30 | 30 | 33 | 33 | 32 | 32 | 697850
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 100 | 100 | 100 | 100 | 100 | 100 | 526080
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 815 | 807 | 807 | 807 | 712 | 711 | 614 | 615 | 615 | 615 | 615 | 615 | 712 | 805 | 806 | 806 | 787 | 787 |  | 775 | 773 | 774 | 774 | 774 | 775 | 774 | 17231273
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 370 | 390 | 390 |  | 320 | 350 | 350 | 350 | 300 | 300 | 235 | 5695776
148 | Payra 1320 MW | 370 | 370 | 370 | 370 | 370 | 400 | 400 | 350 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 380 | 380 | 460 | 530 | 540 | 540 | 9661000
149
150 | Barapukuria TPP Unit-1 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 74 | 74 | 71 | 71 | 72 | 73 | 72 | 72 |  | 72 | 72 | 71 | 71 | 71 | 74 | 74 | 1726255
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 150 | 149 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3670700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 60 |  |  | 1554000
| Baghabari 50 MW Peaking PP | 50 | 50 | [17 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 370880
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 2 | 2 | 3 | 4 | 4 | 2 | 3 | 3 | 1 | 0 | [8 empty] | 28200
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 160 | 164 | 159 | 158 | 163 | 159 | 165 | 157 | 159 | 154 | 140 | 154 | 195 | 192 | 168 | 185 | 195 | 190 |  | 179 | 197 | 183 | 170 | 183 | 175 | 150 | 4282091
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 183 | 177 | 176 | 181 | 177 | 183 | 175 | 177 | 163 | 140 | 172 | 196 | 191 | 188 | 196 | 196 | 192 |  | 183 | 201 | 175 | 158 | 162 | 179 | 177 | 4548355
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 362 | 360 | 334 | 306 | 335 | 336 | 335 | 325 | 301 | 304 | 335 | 336 | 336 | 400 | 403 | 404 | 405 | 404 |  | 403 | 289 | 296 | 401 | 392 | 387 | 379 | 8650100
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 5 | 5 | 5 | 5 | 5 | 5 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 417600
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 201384
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 22 | 22 | 15 | [16 empty] | 21 | 29 | 33 | 21 | 21 | 21 | 21 | 159814
168 | Santahar 50 MW Peaking PP | 28 | 28 | 27 | 27 | [15 empty] | 15 | 28 | 28 | 28 | 28 | 27 | 26 | 258260
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | [14 empty] | 10 | 43 | 52 | 52 | 52 | 52 | 52 | 546240
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 90 | 90 | 90 | 90 | 90 | 90 | 45 | 492208
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [20 empty] | 15 | 44 | 74 | 90 | 90 | 90 | 402720
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [18 empty] | 10 | 50 | 90 | 110 | 110 | 110 | 110 | 612192
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 |  |  |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 108 | 113 | 107 | 70 | 48 | [14 empty] | 60 | 108 | 108 | 113 | 113 | 113 | 113 | 1089945
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 2 | 4 | 6 | 6 | 7 | 7 | 5 | 5 | 3 | 2 | [8 empty] | 55527
178
178