## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-26 | Monday
|  |  | Date (day): | 2021-07-26 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14289.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15180 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-25 | 2021-07-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 145 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 78 | 90 | 90 | 90 |  | 18 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 374 | 356 | 330 | 360 | 52 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 300 | 345 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 280 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 80 |  | 20 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 19 | 18 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 40 | 60 | 150 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 300 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 0 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 35 | 34 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 20 | 20 | 20 | 21 |  | 12 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 32 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 270 | 270 |  | 30 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 34 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 35 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 72 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 1923 | 2133 | 3555 | 3844 | 651 | 1178
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 95 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 8 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 125 | 121 | 120 | 121 | 109 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 10 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 60 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 30 | 40
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 62 | 97 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 0 | 108 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 116 | 112 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 642 | 1119 | 1641 | 1731 | 249 | 415
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 100 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 203 | 212 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 285 | 270 | 270 |  | 90 | ST under maint
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 295 | 360 | 360
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 20 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 16 | 16 | 179 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 42 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 123 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 136 | 130 | 136 |  | 27 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 85 | 170 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 106 | 140 | 138 | 162
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 16 | 40 | 40 |  | 12 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 17 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 104 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1304 | 1783 | 2161 | 2325 | 363 | 330
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 198 | 202 | 202 | 202
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 8 | 193 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 75 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 22 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 334 | 563 | 594.6 | 568 | 0 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 43 | 43 |  | 47 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 183 | 180 | 180 | 150 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 14 | 47 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 59 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 218 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 310 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 401 | 386 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 9 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 390 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1637 | 1818 | 1882 | 1883 | 150 | 345
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 786 | 786 | 801 | 801
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 85 | 25 | 160 |  | 75 | ST not available
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 396 | 360 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 20 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1161 | 1472 | 1441 | 1746 | 0 | 158
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 86 | 80 | 86 | 9 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 500 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 160 | 219 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 90 | 90 |  | 60 | Engine problem
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 497 | 927 | 1155 | 1161 | 9 | 254
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 80 | 70 | 80 | 20 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 20 | 20 |  | 51 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 39 | 30 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 174 | 177 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 176 | 172 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 340 | 346 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 40 | 95 | 95 |  | 9 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 90 | 90 | 90 |  | 23 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 95 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 725 | 1140 | 1532 | 1580 | 400 | 136
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 73 | 72 | 75 | 75
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 149 | 161 | 150 | 150 | 124 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 97 | 95 | 97 |  | 16 | Engine problem
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 228 | 330 | 328 | 342 | 124 | 121
|  | Total |  |  |  |  | 22031 | 21280 | 8451 | 11285 | 14289.6 | 15180 | 1946 | 3024
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7974.7186 | 10649 | 13484.2668 | 14324.4856
| A. |  | 2021-07-25 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 11332 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7807 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11285 | MW
| 3 | Day peak Generation : |  |  | 8451 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10649 | MW
| 4 | Evening peak Generation : |  |  | 11285 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 225.4998 | MKWHr | By Solar | 0.65625 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 155.2898 | MKWHr |  | By Oil: | 29.6584 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.2679 | MKWHr |  | By Hydro: | 2.8457 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1946 | MW | Dhaka | 2926 | 2926 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3024 | MW | Chittagong | 971 | 971 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4970 | MW | Khulna | 1535 | 1535 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1210.91 | MMCFD |  |  | Rajshahi | 1304 | 1304 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 166854236.942 | ii) Oil : | Taka | 187334844.14 | Comilla | 1196 | 1196 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 73749056.16 | Total | Taka | 427938137.242 | Mymensingh | 1003 | 1003 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 5.4335 | MKWHr. | Sylhet | 501 | 501 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -414 | MW (E to W) at | 21:00 | hrs | Barisal | 393 | 393 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -506 | MW at | 23:00 | hrs | Rangpur | 820 | 820 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34° C |  |  | Total | 10649 | 10649 |  | 0
| B. |  | 2021-07-26 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15180 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9100 | MW
| 4 | Reserve(Generation end) |  |  |  | 2980 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 242.7724 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8322 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.0131 | MKWHr. | ii) HVDC Flow at Peak Time |  | 786 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7686 | MKWHr. | iii) Maximum HVDC Flow : |  | 796 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.52 |  | (b) Today: | 84.58 |  | (c) Rule Curve: |  | 88
.

## YesterdayGen
2021-07-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 300 | 99 | 0 | 363 | 347 |  | 0 | 240 | 255 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 18 | 25 | 6 | 28 | 12 | 8 | 0 | 62 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 97 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 275 | 181 | 8 | 133 | 26 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 205 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 107 | 0 | 51 | 0 | 0 | 0 | 0 | 105 | 65 | 0 | 360 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 796 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 52 | 25 | 22 | 0 | 11 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 83 | 0 | 195 | 0 | 337 | 105 | 0 | 0 | 0 | 113 | 0 | 0 | 35 | 440 | 221 | 0 | 0 | 0 |  | 6602 | 3358 | 9960 | 4916 | 796 | 1930 | 1364 | 663 | 122 | 49 | 120 | 0 | 0 | 84.51
2:00 | 0 | 0 | 0 | 110 | 300 | 99 | 0 | 363 | 347 |  | 0 | 240 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 28 | 12 | 0 | 0 | 59 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 77 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 275 | 181 | 8 | 133 | 26 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 207 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 275 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 107 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 65 | 0 | 360 | 0 | 0 | 0 | 53 | 0 | 17 | 0 |  | 796 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 72 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 82 | 0 | 194 | 0 | 311 | 105 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 410 | 221 | 0 | 0 | 0 |  | 6431 | 3215 | 9646 | 4917 | 796 | 1893 | 1173 | 632 | 119 | 0 | 116 | 0 | 0 | 84.51
3:00 | 0 | 0 | 0 | 110 | 300 | 99 | 0 | 362 | 347 |  | 0 | 240 | 255 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 6 | 28 | 12 | 0 | 0 | 57 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 181 | 8 | 134 | 26 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 207 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 107 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 65 | 0 | 360 | 0 | 0 | 0 | 53 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 81 | 0 | 178 | 0 | 310 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 350 | 222 | 0 | 0 | 0 |  | 6385 | 3039 | 9424 | 4861 | 786 | 1902 | 1069 | 575 | 117 | 0 | 114 | 0 | 0 | 84.52
4:00 | 0 | 0 | 0 | 110 | 300 | 99 | 0 | 334 | 307 |  | 0 | 240 | 250 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 28 | 12 | 0 | 0 | 57 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 181 | 8 | 133 | 26 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 207 | 8 | 21 | 0 | 43 | 42 | 47 | 0 | 0 | 162 | 62 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 108 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 65 | 0 | 360 | 0 | 0 | 0 | 53 | 0 | 17 | 0 |  | 787 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 81 | 0 | 176 | 0 | 305 | 70 | 0 | 0 | 0 | 113 | 0 | 0 | 0 | 330 | 222 | 0 | 0 | 0 |  | 6193 | 3016 | 9209 | 4835 | 787 | 1851 | 955 | 554 | 117 | 0 | 110 | 0 | 0 | 84.52
5:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 326 | 307 |  | 0 | 240 | 265 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 0 | 12 | 0 | 0 | 59 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 20 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 181 | 8 | 134 | 26 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 207 | 8 | 21 | 0 | 43 | 42 | 11 | 0 | 0 | 161 | 62 | 10 | 0 | 192 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 366 | 115 | 0 | 17 | 0 | 0 | 0 | 0 | 70 | 65 | 0 | 360 | 0 | 0 | 0 | 53 | 0 | 17 | 0 |  | 786 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 43 | 0 | 178 | 0 | 334 | 70 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 350 | 221 | 0 | 0 | 0 |  | 5965 | 2962 | 8927 | 4774 | 786 | 1652 | 914 | 574 | 119 | 0 | 108 | 0 | 0 | 84.52
6:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 324 | 284 |  | 0 | 240 | 245 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 0 | 12 | 0 | 0 | 60 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 182 | 8 | 131 | 26 | 30 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 100 | 207 | 8 | 21 | 0 | 43 | 42 | 11 | 0 | 0 | 162 | 62 | 10 | 0 | 178 | 18 | 0 | 10 | 265 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 115 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 26 | 0 | 320 | 0 | 2 | 0 | 53 | 0 | 17 | 1 |  | 787 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 169 | 0 | 32 | 0 | 178 | 0 | 299 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 330 | 171 | 0 | 0 | 0 |  | 5560 | 2654 | 8214 | 4532 | 787 | 1484 | 633 | 555 | 120 | 0 | 100 | 3 | 0 | 84.52
7:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 282 | 278 |  | 0 | 240 | 225 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 28 | 12 | 0 | 0 | 61 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 65 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 182 | 8 | 131 | 26 | 30 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 94 | 208 | 8 | 21 | 0 | 43 | 42 | 11 | 0 | 0 | 160 | 40 | 10 | 0 | 179 | 18 | 0 | 10 | 255 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 115 | 0 | 17 | 0 | 0 | 0 | 0 | 35 | 8 | 0 | 327 | 0 | 8 | 0 | 17 | 0 | 17 | 4 |  | 786 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 32 | 0 | 140 | 0 | 260 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 171 | 0 | 0 | 0 |  | 5427 | 2476 | 7903 | 4387 | 786 | 1428 | 560 | 515 | 121 | 0 | 94 | 12 | 0 | 84.53
8:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 281 | 255 |  | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 6 | 28 | 12 | 0 | 0 | 63 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 255 | 183 | 8 | 137 | 26 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 92 | 204 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 162 | 40 | 10 | 0 | 178 | 18 | 0 | 10 | 230 | 16 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 320 | 75 | 0 | 17 | 1 | 0 | 0 | 0 | 17 | 8 | 0 | 320 | 0 | 14 | 0 | 17 | 0 | 17 | 10 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 15 | 140 | 0 | 263 | 90 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 290 | 140 | 0 | 0 | 0 |  | 5343 | 2464 | 7807 | 4358 | 786 | 1292 | 611 | 515 | 123 | 0 | 92 | 30 | 0 | 84.53
9:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 304 | 255 |  | 0 | 240 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 28 | 12 | 0 | 0 | 63 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 270 | 193 | 8 | 138 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 11 | 33 | 20 | 96 | 203 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 161 | 40 | 10 | 0 | 178 | 18 | 0 | 10 | 230 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 327 | 75 | 0 | 17 | 1 | 0 | 0 | 0 | 17 | 8 | 0 | 320 | 0 | 12 | 0 | 17 | 0 | 17 | 27 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 20 | 140 | 0 | 263 | 90 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 300 | 140 | 0 | 0 | 3 |  | 5474 | 2483 | 7957 | 4446 | 786 | 1291 | 636 | 524 | 123 | 0 | 96 | 55 | 0 | 84.53
10:00 | 0 | 0 | 0 | 110 | 300 | 22 | 0 | 325 | 255 |  | 0 | 240 | 280 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 28 | 12 | 0 | 0 | 63 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 64 | 0 | 21 | 42 | 80 | 0 | 0 | 265 | 255 | 187 | 8 | 138 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 102 | 203 | 0 | 21 | 1 | 43 | 43 | 11 | 0 | 0 | 161 | 40 | 10 | 0 | 178 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 12 | 0 | 0 | 0 | 317 | 75 | 0 | 17 | 1 | 0 | 0 | 0 | 17 | 8 | 0 | 320 | 0 | 30 | 0 | 17 | 0 | 17 | 24 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 74 | 0 | 150 | 0 | 0 | 0 | 0 | 143 | 0 | 12 | 20 | 155 | 0 | 340 | 90 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 300 | 161 | 0 | 0 | 3 |  | 5539 | 2612 | 8151 | 4441 | 786 | 1476 | 623 | 524 | 123 | 0 | 102 | 76 | 0 | 84.53
11:00 | 0 | 0 | 0 | 110 | 300 | 25 | 0 | 326 | 265 |  | 0 | 240 | 280 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 6 | 28 | 20 | 0 | 0 | 65 | 60 | 95 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 60 | 0 | 21 | 42 | 80 | 0 | 0 | 265 | 260 | 189 | 8 | 138 | 23 | 5 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 102 | 201 | 8 | 21 | 1 | 43 | 43 | 11 | 0 | 0 | 159 | 40 | 10 | 0 | 178 | 18 | 0 | 10 | 305 | 16 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 16 | 0 | 0 | 0 | 344 | 75 | 0 | 17 | 5 | 0 | 0 | 0 | 17 | 8 | 0 | 340 | 0 | 27 | 0 | 17 | 0 | 17 | 31 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 164 | 0 | 12 | 20 | 179 | 0 | 342 | 105 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 161 | 0 | 0 | 3 |  | 5633 | 2674 | 8307 | 4549 | 786 | 1491 | 642 | 523 | 125 | 0 | 102 | 89 | 0 | 84.54
12:00 | 0 | 0 | 0 | 110 | 145 | 78 | 0 | 374 | 300 |  | 0 | 240 | 295 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 25 | 20 | 0 | 0 | 65 | 60 | 95 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 62 | 0 | 21 | 42 | 80 | 0 | 0 | 295 | 290 | 203 | 8 | 137 | 23 | 30 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 106 | 198 | 8 | 21 | 2 | 43 | 42 | 14 | 0 | 0 | 158 | 40 | 10 | 0 | 219 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 401 | 75 | 0 | 17 | 5 | 0 | 0 | 0 | 17 | 8 | 0 | 350 | 0 | 22 | 0 | 17 | 0 | 17 | 32 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 12 | 20 | 176 | 0 | 340 | 105 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 160 | 0 | 0 | 5 |  | 5840 | 2611 | 8451 | 4567 | 786 | 1606 | 659 | 522 | 125 | 0 | 106 | 80 | 0 | 84.54
13:00 | 0 | 0 | 0 | 110 | 90 | 91 | 0 | 396 | 344 |  | 0 | 240 | 295 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 19 | 25 | 10 | 25 | 20 | 0 | 0 | 64 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 78 | 0 | 21 | 42 | 80 | 0 | 0 | 265 | 260 | 187 | 8 | 138 | 23 | 40 | 0 | 20 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 108 | 198 | 8 | 21 | 2 | 43 | 43 | 47 | 0 | 0 | 158 | 55 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 17 | 0 | 0 | 0 | 370 | 75 | 0 | 0 | 6 | 0 | 0 | 0 | 17 | 8 | 0 | 385 | 0 | 49 | 0 | 17 | 0 | 17 | 24 |  | 786 | 0 | 390 | 0 | 0 | 5 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 76 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 61 | 0 | 198 | 0 | 405 | 53 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 320 | 218 | 0 | 0 | 5 |  | 5995 | 2925 | 8920 | 4695 | 786 | 1947 | 596 | 545 | 124 | 9 | 108 | 110 | 0 | 84.54
14:00 | 0 | 0 | 0 | 110 | 60 | 94 | 0 | 395 | 344 |  | 0 | 240 | 270 | 0 | 0 | 0 | 332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 20 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 40 | 90 | 0 | 21 | 40 | 80 | 0 | 0 | 260 | 270 | 183 | 8 | 137 | 23 | 50 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 118 | 197 | 8 | 21 | 2 | 43 | 43 | 47 | 0 | 0 | 158 | 60 | 83 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 7 | 0 | 0 | 1 | 367 | 82 | 1 | 0 | 2 | 0 | 0 | 0 | 52 | 21 | 0 | 390 | 0 | 28 | 0 | 28 | 0 | 17 | 30 |  | 786 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 21 | 0 | 8 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 193 | 0 | 77 | 0 | 192 | 0 | 405 | 53 | 0 | 0 | 0 | 0 | 0 | 6 | 15 | 360 | 216 | 0 | 0 | 5 |  | 6133 | 2992 | 9125 | 4719 | 786 | 1997 | 709 | 582 | 120 | 14 | 118 | 80 | 0 | 84.54
15:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 394 | 344 |  | 0 | 240 | 270 | 0 | 0 | 0 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 20 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 40 | 90 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 182 | 8 | 137 | 23 | 50 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 116 | 199 | 8 | 21 | 2 | 44 | 43 | 47 | 0 | 0 | 160 | 60 | 81 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 14 | 0 | 0 | 8 | 367 | 86 | 17 | 0 | 1 | 0 | 0 | 0 | 98 | 36 | 0 | 390 | 0 | 15 | 0 | 76 | 0 | 17 | 25 |  | 786 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 20 | 0 | 11 | 77 | 0 | 149 | 0 | 0 | 0 | 0 | 186 | 0 | 78 | 0 | 188 | 0 | 394 | 53 | 0 | 0 | 0 | 50 | 0 | 5 | 35 | 410 | 216 | 0 | 0 | 2 |  | 6213 | 3126 | 9339 | 4651 | 786 | 1975 | 977 | 636 | 120 | 14 | 116 | 64 | 0 | 84.55
16:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 394 | 332 |  | 0 | 240 | 255 | 0 | 0 | 0 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 20 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 90 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 182 | 45 | 136 | 23 | 50 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 112 | 200 | 8 | 21 | 1 | 44 | 43 | 49 | 0 | 0 | 161 | 60 | 82 | 0 | 191 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 2 | 0 | 0 | 10 | 367 | 86 | 17 | 0 | 1 | 0 | 0 | 0 | 52 | 36 | 0 | 389 | 0 | 10 | 0 | 72 | 0 | 17 | 19 |  | 786 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 71 | 0 | 149 | 0 | 0 | 0 | 0 | 182 | 0 | 80 | 0 | 184 | 0 | 370 | 53 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 400 | 216 | 0 | 0 | 1 |  | 6054 | 3020 | 9074 | 4578 | 786 | 1982 | 805 | 620 | 119 | 34 | 112 | 38 | 0 | 84.55
17:00 | 0 | 0 | 0 | 110 | 0 | 94 | 0 | 361 | 299 |  | 0 | 240 | 255 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 20 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 81 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 182 | 45 | 138 | 23 | 50 | 0 | 35 | 0 | 0 | 0 | 21 | 11 | 33 | 20 | 106 | 202 | 8 | 21 | 0 | 44 | 43 | 13 | 0 | 0 | 162 | 61 | 10 | 0 | 191 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 3 | 0 | 0 | 10 | 307 | 86 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 36 | 0 | 360 | 0 | 7 | 0 | 35 | 0 | 17 | 4 |  | 786 | 0 | 330 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 50 | 0 | 0 | 0 | 90 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 166 | 0 | 74 | 0 | 178 | 0 | 370 | 17 | 0 | 0 | 0 | 5 | 0 | 3 | 0 | 370 | 216 | 0 | 0 | 1 |  | 5596 | 2958 | 8554 | 4409 | 786 | 1825 | 593 | 592 | 119 | 104 | 106 | 20 | 0 | 84.55
18:00 | 0 | 0 | 0 | 110 | 0 | 25 | 0 | 335 | 270 |  | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 20 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 80 | 0 |  | 0 | 0 | 0 | 10 | 38 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 183 | 45 | 137 | 23 | 35 | 0 | 8 | 0 | 0 | 0 | 22 | 11 | 8 | 20 | 100 | 201 | 8 | 21 | 0 | 44 | 43 | 14 | 0 | 0 | 162 | 40 | 10 | 0 | 191 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 306 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 311 | 0 | 1 | 0 | 17 | 0 | 17 | 3 |  | 786 | 0 | 300 | 0 | 0 | 10 | 0 | 0 | 4 | 0 | 0 | 0 | 25 | 0 | 0 | 50 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 74 | 0 | 149 | 0 | 0 | 0 | 0 | 167 | 0 | 34 | 0 | 174 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 300 | 178 | 0 | 0 | 0 |  | 5200 | 2775 | 7975 | 4174 | 786 | 1638 | 524 | 523 | 119 | 106 | 100 | 5 | 0 | 84.55
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 0 | 35 | 0 | 325 | 285 |  | 0 | 240 | 300 | 0 | 0 | 0 | 290 | 0 | 0 | 0 | 5 | 48 | 0 | 0 | 0 | 0 | 17 | 17 | 10 | 19 | 25 | 7 | 25 | 20 | 24 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 30 | 10 | 50 | 0 | 21 | 42 | 80 | 0 | 0 | 305 | 315 | 209 | 45 | 137 | 23 | 35 | 0 | 8 | 0 | 0 | 2 | 22 | 11 | 22 | 20 | 132 | 200 | 8 | 21 | 0 | 44 | 43 | 16 | 0 | 0 | 162 | 58 | 10 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 2 | 0 | 0 | 26 | 0 | 0 | 0 | 22 | 4 | 16 | 390 | 90 | 0 | 11 | 0 | 0 | 0 | 8 | 52 | 46 | 35 | 346 | 0 | 0 | 35 | 20 | 0 | 17 | 0 |  | 786 | 0 | 350 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 80 | 0 | 50 | 0 | 92 | 0 | 0 | 18 | 8 | 0 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 47 | 0 | 184 | 0 | 380 | 10 | 0 | 9 | 0 | 85 | 0 | 0 | 25 | 320 | 217 | 0 | 23 | 0 |  | 6036 | 3191 | 9227 | 4657 | 786 | 1722 | 987 | 541 | 119 | 283 | 132 | 0 | 0 | 84.56
19:30 | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 337 | 320 |  | 0 | 240 | 270 | 0 | 0 | 15 | 270 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 45 | 35 | 19 | 25 | 7 | 25 | 20 | 42 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 10 | 0 | 51 | 30 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 260 | 270 | 214 | 45 | 136 | 23 | 55 | 0 | 25 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 130 | 206 | 8 | 21 | 0 | 43 | 43 | 43 | 0 | 0 | 162 | 59 | 80 | 0 | 218 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 30 | 0 | 0 | 194 | 0 | 0 | 0 | 60 | 85 | 100 | 317 | 115 | 34 | 68 | 0 | 0 | 0 | 70 | 88 | 105 | 50 | 396 | 36 | 0 | 162 | 53 | 0 | 17 | 0 |  | 786 | 0 | 350 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 80 | 0 | 50 | 0 | 78 | 0 | 0 | 24 | 11 | 7 | 22 | 0 | 11 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 178 | 0 | 66 | 100 | 187 | 0 | 308 | 53 | 0 | 72 | 0 | 92 | 0 | 0 | 60 | 430 | 217 | 0 | 90 | 0 |  | 7223 | 3595 | 10818 | 4579 | 786 | 1864 | 2392 | 652 | 119 | 296 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 0 | 86 | 0 | 344 | 300 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 7 | 25 | 20 | 16 | 0 | 59 | 60 | 100 | 120 | 3 | 0 | 0 | 120 | 0 |  | 8 | 0 | 51 | 0 | 97 | 0 | 20 | 36 | 100 | 0 | 0 | 285 | 295 | 212 | 45 | 136 | 23 | 56 | 0 | 37 | 0 | 0 | 16 | 22 | 11 | 33 | 20 | 132 | 203 | 8 | 21 | 0 | 43 | 43 | 49 | 0 | 0 | 184 | 61 | 84 | 0 | 218 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 175 | 0 | 0 | 0 | 60 | 70 | 93 | 327 | 115 | 25 | 76 | 0 | 0 | 0 | 91 | 17 | 103 | 50 | 390 | 53 | 0 | 72 | 103 | 0 | 17 | 0 |  | 786 | 0 | 350 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 80 | 0 | 50 | 0 | 40 | 0 | 0 | 28 | 32 | 16 | 22 | 0 | 11 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 171 | 0 | 76 | 90 | 175 | 0 | 347 | 100 | 0 | 68 | 0 | 98 | 0 | 0 | 80 | 440 | 218 | 0 | 90 | 0 |  | 7076 | 3706 | 10782 | 4639 | 786 | 1928 | 2247 | 661 | 119 | 270 | 132 | 0 | 0 | 84.56
21:00 | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 356 | 345 |  | 0 | 240 | 280 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 9 | 25 | 20 | 32 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 285 | 295 | 212 | 45 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 140 | 202 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 183 | 59 | 84 | 0 | 218 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 193 | 0 | 0 | 0 | 60 | 85 | 123 | 386 | 115 | 34 | 105 | 0 | 0 | 0 | 108 | 17 | 104 | 50 | 390 | 35 | 0 | 72 | 116 | 0 | 17 | 0 |  | 786 | 0 | 396 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 80 | 0 | 0 | 0 | 40 | 0 | 0 | 39 | 43 | 25 | 22 | 0 | 11 | 72 | 0 | 161 | 0 | 0 | 0 | 0 | 177 | 0 | 86 | 100 | 172 | 0 | 346 | 105 | 0 | 90 | 0 | 97 | 0 | 0 | 95 | 500 | 219 | 0 | 90 | 0 |  | 7416 | 3869 | 11285 | 4790 | 786 | 2015 | 2460 | 733 | 121 | 240 | 140 | 0 | 0 | 84.56
22:00 | 0 | 0 | 0 | 110 | 0 | 91 | 0 | 398 | 347 |  | 0 | 240 | 275 | 0 | 0 | 0 | 332 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 9 | 25 | 20 | 34 | 0 | 63 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 23 | 0 | 51 | 0 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 265 | 280 | 213 | 45 | 137 | 20 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 144 | 202 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 203 | 59 | 84 | 0 | 218 | 18 | 0 | 9 | 300 | 16 | 11 | 0 | 15 | 0 | 0 | 198 | 0 | 5 | 0 | 60 | 99 | 150 | 370 | 115 | 34 | 105 | 0 | 0 | 0 | 108 | 17 | 106 | 50 | 393 | 35 | 0 | 72 | 116 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 22 | 43 | 33 | 21 | 0 | 11 | 75 | 0 | 152 | 0 | 0 | 0 | 0 | 169 | 0 | 85 | 100 | 160 | 0 | 346 | 105 | 0 | 90 | 0 | 97 | 0 | 0 | 95 | 500 | 219 | 0 | 90 | 0 |  | 7551 | 3781 | 11332 | 4848 | 786 | 2009 | 2509 | 727 | 123 | 186 | 144 | 0 | 0 | 84.56
23:00 | 0 | 0 | 0 | 110 | 0 | 91 | 0 | 398 | 347 |  | 0 | 240 | 265 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 9 | 25 | 24 | 34 | 0 | 64 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 270 | 214 | 45 | 137 | 20 | 55 | 0 | 43 | 0 | 0 | 15 | 22 | 11 | 33 | 21 | 144 | 204 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 200 | 61 | 84 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 189 | 0 | 15 | 0 | 60 | 100 | 150 | 367 | 115 | 34 | 105 | 0 | 0 | 0 | 108 | 17 | 107 | 50 | 397 | 35 | 0 | 72 | 116 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 22 | 43 | 34 | 22 | 0 | 11 | 76 | 0 | 151 | 0 | 0 | 0 | 0 | 159 | 0 | 85 | 100 | 147 | 0 | 335 | 105 | 0 | 90 | 0 | 97 | 0 | 0 | 95 | 500 | 219 | 0 | 90 | 0 |  | 7529 | 3724 | 11253 | 4816 | 786 | 1989 | 2505 | 727 | 124 | 162 | 144 | 0 | 0 | 84.57
24:00 | 0 | 0 | 0 | 110 | 0 | 91 | 0 | 398 | 347 |  | 0 | 240 | 270 | 0 | 0 | 0 | 332 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 9 | 25 | 24 | 32 | 0 | 64 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 275 | 214 | 45 | 137 | 20 | 54 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 140 | 204 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 190 | 61 | 84 | 0 | 218 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 184 | 0 | 35 | 0 | 20 | 100 | 100 | 366 | 115 | 34 | 105 | 0 | 0 | 0 | 110 | 17 | 106 | 10 | 396 | 0 | 0 | 35 | 116 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 40 | 0 | 0 | 22 | 43 | 34 | 22 | 0 | 11 | 70 | 0 | 154 | 0 | 0 | 0 | 0 | 161 | 0 | 85 | 100 | 148 | 0 | 346 | 105 | 0 | 94 | 0 | 97 | 0 | 0 | 95 | 470 | 220 | 0 | 90 | 0 |  | 7244 | 3710 | 10954 | 4809 | 786 | 1995 | 2244 | 694 | 124 | 162 | 140 | 0 | 0 | 84.57
KWH | 0 | 0 | 0 | 2677500 | 3784473 | 1625681 | 0 | 8577030 | 7484000 |  | 0 | 5640750 | 6391825 | 0 | 0 | 15678 | 6846058 | 0 | 114000 | 0 | 18576 | 37440 | 0 | 0 | 0 | 0 | 442800 | 269138 | 128473 | 318960 | 600000 | 188460 | 659800 | 486900 | 168000 | 0 | 1397673 | 1448000 | 2400000 | 2800000 | 29964 | 0 | 0 | 2850342 | 0 |  | 104640 | 0 | 252981 | 347520 | 1824000 | 0 | 492672 | 1074720 | 2145262 | 0 | 0 | 6769500 | 6606000 | 4649000 | 518545 | 3240840 | 540360 | 886560 | 0 | 768504 | 0 | 0 | 108720 | 495216 | 246600 | 776000 | 501700 | 2768640 | 4774720 | 171840 | 484596 | 12000 | 1027000 | 994200 | 756600 | 0 | 0 | 3803000 | 1300224 | 1218240 | 0 | 4899630 | 392000 | 0 | 238320 | 7002500 | 369840 | 202032 | 0 | 87818 | 0 | 0 | 2083200 | 0 | 57600 | 62235 | 278400 | 471360 | 714254 | 8446000 | 2335200 | 210000 | 814614 | 22439 | 0 | 0 | 545306 | 972420 | 1252440 | 247680 | 8584900 | 178560 | 243090 | 411840 | 1381255 | 0 | 439920 | 239671 |  | 19013091 | 0 | 8447517 | 0 | 0 | 347090 | 0 | 0 | 19200 | 0 | 0 | 0 | 661374 | 0 | 0 | 1266000 | 0 | 85680 | 0 | 515920 | 0 | 0 | 108569 | 420000 | 170751 | 507840 | 0 | 231516 | 1786472 | 0 | 3682800 | 0 | 0 | 0 | 0 | 4264145 | 0 | 1311811 | 632640 | 4416055 | 0 | 8154545 | 1842720 | 0 | 457536 | 0 | 1161523 | 0 | 46212 | 616128 | 9798600 | 4769782 | 0 | 487200 | 30600 |  | 150246445 | 75253317 | 225499762 | 112670048 | 19013091 | 42619772 | 28120788 | 15267872 | 2845673 | 1537631 | 2768640 | 656247 | 0
Fuel Cost | 0 | 0 | 0 | 3935925 | 4200765.03 | 2145898.92 | 0 | 8662800.3 | 7708520 |  | 0 | 6148417.5 | 7094925.75 | 0 | 0 | 132635.88 | 7119900.32 | 0 | 197220 | 0 | 169413.12 | 368409.6 | 0 | 0 | 0 | 0 | 3232440 | 2080436.74 | 1266743.78 | 239220 | 450000 | 0 | 0 | 0 | 1624560 | 0 | 377371.71 | 390960 | 4344000 | 5068000 | 278365.56 | 0 | 0 | 4845581.4 | 0 |  | 0 | 0 | 2453915.7 | 3318816 | 15868800 | 0 | 620766.72 | 3191918.4 | 3174987.76 | 0 | 0 | 5009430 | 6606000 | 4277080 | 668923.05 | 3726966 | 610606.8 | 1241184 | 0 | 1314141.84 | 0 | 0 | 1038276 | 628924.32 | 184950 | 1358000 | 376275 | 20764800 | 5061203.2 | 1560307.2 | 615436.92 | 191280 | 1684280 | 1590720 | 1346748 | 0 | 0 | 3955120 | 2561441.28 | 2326838.4 | 0 | 8476359.9 | 858480 | 0 | 486172.8 | 7072525 | 277380 | 153544.32 | 0 | 663904.08 | 0 | 0 | 10832640 | 0 | 566784 | 727527.15 | 2268960 | 5114256 | 5035490.7 | 7854780 | 21297024 | 1984500 | 7095287.94 | 0 | 0 | 0 | 4793239.74 | 9704751.6 | 10733410.8 | 1649548.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 109515404.16 | 0 | 8869892.85 | 0 | 0 | 4810667.4 | 0 | 0 | 201408 | 0 | 0 | 0 | 1025129.7 | 0 | 0 | 2595300 | 0 | 843091.2 | 0 | 4565892 | 0 | 0 | 1052033.61 | 4069800 | 1656284.7 | 975052.8 | 0 | 175257.612 | 10772426.16 | 0 | 19960776 | 0 | 0 | 0 | 0 | 5628671.4 | 0 | 1967716.5 | 10761206.4 | 5166784.35 | 0 | 8072999.55 | 19237996.8 | 0 | 4342016.64 | 0 | 9013418.48 | 0 | 510642.6 | 4553185.92 | 43015854 | 0 | 0 | 0 | 0 |  | 277057214.03 | 283358908.832 | 560416122.862 | 121162050.482 | 109515404.16 | 45692186.46 | 171383141.93 | 73749056.16 | 768331.71 | 15951702.21 | 20764800 | 1429449.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 145 | 78 | 0 | 374 | 300 |  | 0 | 240 | 295 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 25 | 10 | 25 | 20 | 0 | 0 | 65 | 60 | 95 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 10 | 62 | 0 | 21 | 42 | 80 | 0 | 0 | 295 | 290 | 203 | 8 | 137 | 23 | 30 | 0 | 10 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 106 | 198 | 8 | 21 | 2 | 43 | 42 | 14 | 0 | 0 | 158 | 40 | 10 | 0 | 219 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 8 | 0 | 0 | 0 | 401 | 75 | 0 | 17 | 5 | 0 | 0 | 0 | 17 | 8 | 0 | 350 | 0 | 22 | 0 | 17 | 0 | 17 | 32 |  | 786 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 73 | 0 | 149 | 0 | 0 | 0 | 0 | 174 | 0 | 12 | 20 | 176 | 0 | 340 | 105 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 300 | 160 | 0 | 0 | 5 |  | 8451 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 356 | 345 | 0 | 0 | 240 | 280 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 9 | 25 | 20 | 32 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 51 | 0 | 97 | 0 | 21 | 42 | 100 | 0 | 0 | 285 | 295 | 212 | 45 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 140 | 202 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 183 | 59 | 84 | 0 | 218 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 193 | 0 | 0 | 0 | 60 | 85 | 123 | 386 | 115 | 34 | 105 | 0 | 0 | 0 | 108 | 17 | 104 | 50 | 390 | 35 | 0 | 72 | 116 | 0 | 17 | 0 |  | 786 | 0 | 396 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 80 | 0 | 0 | 0 | 40 | 0 | 0 | 39 | 43 | 25 | 22 | 0 | 11 | 72 | 0 | 161 | 0 | 0 | 0 | 0 | 177 | 0 | 86 | 100 | 172 | 0 | 346 | 105 | 0 | 90 | 0 | 97 | 0 | 0 | 95 | 500 | 219 | 0 | 90 | 0 |  | 11285 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 360 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 60 | 0 | 102 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 10 | 25 | 21 | 52 | 0 | 61 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 40 | 80 | 0 | 0 | 270 | 360 | 210 | 16 | 136 | 23 | 55 | 0 | 43 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 162 | 202 | 8 | 21 | 0 | 44 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 801 | 0 | 400 | 0 | 0 | 160 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 80 | 0 | 50 | 20 | 95 | 0 | 0 | 40 | 43 | 34 | 22 | 0 | 11 | 75 | 0 | 150 | 10 | 10 | 0 | 0 | 200 | 0 | 86 | 100 | 200 | 0 | 400 | 105 | 200 | 90 | 100 | 97 | 0 | 0 | 95 | 622 | 220 |  | 90
Forecast for Day | 0 | 0 | 0 | 110 | 0 | 90 | 0 | 330 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 40 | 0 | 100 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 25 | 20 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 30 | 80 | 0 | 0 | 270 | 360 | 210 | 16 | 130 | 20 | 55 | 0 | 42 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 138 | 202 | 8 | 21 | 1.6 | 43 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 270 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 400 | 90 | 50 | 162 | 112 | 0 | 17 | 30 |  | 801 | 0 | 360 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 0 | 0 | 30 | 43 | 0 | 22 | 0 | 11 | 75 | 0 | 150 | 0 | 0 | 0 | 0 | 200 | 0 | 80 | 50 | 200 | 0 | 400 | 105 | 100 | 90 | 100 | 95 | 0 | 8 | 95 | 622 | 220 |  | 90 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 352 | 308 | 0 | 0 | 240 | 262 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 25 |  | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 215 | 16 | 136 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 0 | 0 | 102 | 207 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 180 | 61 | 10 | 0 | 164 | 18 | 0 | 9 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 3 | 0 | 17 | 0 | 342 | 115 | 0 | 17 | 1 | 0 | 0 | 51 | 0 | 65 | 0 | 380 | 0 | 9 | 0 | 90 | 0 | 17 | 9 | 0 | 794 | 0 | 340 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 76 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 145 | 0 | 324 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 320 | 220 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 7807 | 8:00
| Highest Generation |  | 11332 | 22:00
| Day Peak Generation |  | 8451 | 12:00
| Evening Peak Generation |  | 11285 | 21:00
| HVDC Max Flow |  | 796 | 1:00
| HVDC EvPeak Flow |  | 786 | 21:00
| Load factor L.F |  | 82.91%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-26
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8451 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8322 | MW
Evening Peak Generation : |  | 11285 | MW Hour : | 21:00 | Available Max Generation : |  | 15180 | MW
E.P. Demand (at gen end) : |  | 11285 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12200 | MW
Maximum Generation : |  | 11332 | MW Hour : | 22:00 | Reserve(Generation end) |  | 2980 | MW
Total Gen. (MKWH) : |  | 225.4998 | System Load Factor : | 82.91% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -506 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-26
Actual : | 84.58 | Ft.(MSL) , | Rule curve : | 88 | Ft.( MSL )
Gas Consumed : | Total = | 1210.91 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 166854236.942
: |  | Coal : | 73749056.16 | Oil : | 187334844.14 | Total : | 427938137.242
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4282.9942 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1458.8842 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1307.5447 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1181.6306 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1067.7378 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 861.6327 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 478.6567 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 221.7645 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 664.5489 |  |  | 0 | 0%
Total | 0 |  | 11525.3943 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2
2) Ghorasal-3,4 & 7
3) Ashuganj-4 & 5
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Ashuganj #4 was synchronized at 08:30 and was shut down at 08:53 due to gas shortage.
b) Aminbazar-Kallyanpur 132 kV Ckt-2 was under shut down from 10:44 to 15:03 for C/M.
c) Bheramara-GK 132 kV Ckt-1 was under shut down from 11:21 to 12:57 for C/M.
d) Khulna-225 MW CCPP GT & ST were synchronized at 12:10 & 18:34 due to DCT preparation.
e) Ghorasal #7 CCPP ST & GT were shut down at 14:10 & 14:13 respectively for minor inspection.
f) Shajibazar-330 MW CCPP GT-1 was synchronized at 19:31.
g) Baghabari-100 MW GT was synchronized at 16:50.
h) Siddirganj peaking GT-1 was synchronized at 21:19.
i) Bagethat 132/33 kV T-1 transformer in under shut down since 07:05(26/7/21) for C/M.
j) Cumilla(N) 132/33 kV T-3 transformer in under shut down since 07:47(26/7/21) for C/M. |  |  |  |  | About 50 MW power interruption occurred under Cumilla(N) S/S area
k) Khulna-225 MW CCPP ST was shut down since 05:08(26/7/21). |  |  |  |  | since 07:47(26/7/21).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2677500 | Machine problem
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 3784473 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 90 | 1625681 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 356 | 8577030 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7484000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5640750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6391825 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 15678 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 318960 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 114000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 300 | 6846058
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 18576 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 442800
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 0 | 37440 | Reserve.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 269138
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 128473 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 788460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 659800 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 20 | 486900 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 32 | 168000 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 87818 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 57600 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 34 | 210000 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 35 | 178560 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 72 | 411840 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 239671
| Dhaka area Total |  |  |  | 5819 | 2133 | 47661031
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 29964 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 62235
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 121 | 2845673 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2850342 | Machine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 814614
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 252981 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 347520 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 60 | 278400 | Low demand
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 492672
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1074720
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 97 | 1824000 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22439
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 108 | 545306
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 247680 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1381255
| Chattogram area Total |  |  |  | 2382 | 1119 | 18269801
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 100 | 2145262 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 212 | 4649000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 6769500 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 6606000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 540360 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 886560
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 518545 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 768504 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 714254 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3240840 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 85 | 471360 | Low demand
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 495216
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246600
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2768640
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 776000
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 108720 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 501700 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 972420 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 1252440 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 439920 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1783 | 34871841
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 202 | 4774720
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 484596
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 171840 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 12000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 193 | 2083200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2335200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 243090
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 104640
| Mymensingh Area Total |  |  |  | 709 | 563 | 10209286
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1027000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 994200 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 183 | 3803000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 756600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 202032
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1300224 | Engine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1218240
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 218 | 4899630
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 392000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 369840 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 310 | 7002500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 386 | 8446000 | FGMO
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 9 | 238320
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 390 | 8584900
| Sylhet Area Total |  |  |  | 2377 | 1818 | 39234486
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 786 | 19013091
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 19200 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 85 | 347090 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 396 | 8447517
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 632640
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1842720
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1472 | 30302258
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 661374
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 86 | 1311811 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 9798600
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 219 | 4769782
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 487200 | Low demand
| Barisal Area Total |  |  |  | 2046 | 927 | 17028767
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 80 | 1266000 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 85680 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 39 | 108569 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 177 | 4264145 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 172 | 4416055 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 346 | 8154545 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 170751 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 507840
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 231516
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 420000
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 40 | 515920 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 457536 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 616128 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30600
| Rajshahi Area Total |  |  |  | 2179 | 1140 | 21245285
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1786472 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 161 | 3682800 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 97 | 1161523 | Engine problem
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46212
| Rangpur Area Total |  |  |  | 605 | 330 | 6677007
| Total |  |  |  | 21280 | 11285 | 225499762
| Eastern Grid Total |  |  |  | 14321 | 7416 | 150246445
| Western Grid Total |  |  |  | 6959 | 3869 | 75253317
| National Grid Total |  |  |  | 21280 | 11285 | 225499762
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-25
(a) ENTIRE EASTERN GRID : |  | 6597 | MW | (b) ENTIRE WESTERN GRID : |  | 4052 | MW
i) Dhaka area |  | 2926 | MW | i) Khulna area |  | 1535 | MW
ii) Chittagong area |  | 971 | MW | ii) Rajshahi area |  | 1304 | MW
iii) Comilla area |  | 1196 | MW | iii) Barisal area |  | 393 | MW
iv) Mymensingh area |  | 1003 | MW | iv) Rangpur area |  | 820 | MW
v) Sylhet area |  | 501 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10649 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 80 | 22:00 | Kishoreganj | 142 | 0:00 | Jessore | 119 | 21:00
Munsiganj | 92 | 22:00 | Netrokona | 132 | 21:00 | Benapol | 58 | 21:00
Sonargaon | 46 | 20:00 | Jamalpur | 152 | 21:00 | Jhenida | 114 | 21:00
Shyampur | 68 | 23:00 | Sherpur | 130 | 22:00 | Bottail | 114 | 19:30
Bhulta | 85 | 21:00 | Srimongal | 62 | 23:00 | G.K Project | 60 | 21:00
Madanganj | 28 | 20:00 | Shahjibazar | 88 | 22:00 | Faridpur | 143 | 23:00
Shitalakhya | 54 | 15:00 | Fenchuganj | 47 | 20:00 | Rajbari | 50 | 19:30
Rahim steel | 0 | 0:00 | Kulawara | 48 | 19:30 | Madaripur | 112 | 23:00
Matuail | 27 | 21:00 | Sylhet | 110 | 19:00 | Sariatpur | 76 | 22:00
Ghorasal | 70 | 22:00 | Chatak | 31 | 21:00 | Gopalganj | 98 | 21:00
Narsingdi | 141 | 22:00 | Sunamganj | 51 | 21:00 | Bagerhat | 101 | 21:00
Haripur (SBU) | 38 | 2:00 | Biani Bazar | 70 | 21:00 | Mongla | 24 | 12:00
Sreenagar | 42 | 21:00 | Comilla (S) | 144 | 22:00 | Satkhira | 112 | 21:00
Ullon | 47 | 23:00 | Comilla(N) | 107 | 21:00 | Gallamari | 30 | 19:00
Hasnabad | 71 | 20:00 | Chandpur | 86 | 23:00 | Magura | 60 | 20:00
Magbazar | 71 | 14:00 | Feni | 119 | 23:00 | Norail | 42 | 19:30
Maniknagar | 58 | 11:00 | Chowmuhani | 217 | 22:00 | Chuadanga | 92 | 19:30
Bangabhaban | 11 | 10:00 | Ashuganj | 40 | 22:00 | Borguna | 20 | 22:00
Motijheel | 19 | 11:00 | Daudkandi | 136 | 21:00 | Barisal(N) | 50 | 23:00
Narinda | 36 | 12:00 | B.Baria | 174 | 21:00 | Barisal (S) | 106 | 22:00
Kazla | 54 | 21:00 | Ramganj | 92 | 23:00 | Patuakhali | 123 | 22:00
Dhanmondi | 114 | 13:00 | Chaddagram | 44 | 23:00 | Bhandaria | 59 | 22:00
Lalbag | 44 | 0:00 | PHP | 8 | 14:00 | Borhan Uddin | 48 | 22:00
Madartek | 68 | 23:00 | Kochua | 66 | 21:00 | Ishurdi | 60 | 21:00
Dhaka University | 17 | 13:00 | Madunaghat | 53 | 20:00 | Ruppur Paromanobik | 3 | 21:00
Aftabnagar | 9 | 13:00 | Hathazari | 82 | 20:00 | Natore | 133 | 21:00
Fatullah | 32 | 22:00 | Khulshi | 96 | 21:00 | Bogra | 154 | 21:00
Nawabganj | 52 | 21:00 | Halishahar | 66 | 20:00 | Noagaon | 112 | 21:00
Keraniganj | 51 | 23:00 | Baraulia | 73 | 19:30 | Rajshahi | 155 | 21:00
Mirpur | 97 | 23:00 | Sikalbaha | 23 | 20:00 | Rajshahi New | 15 | 21:00
Kalyanpur | 96 | 14:00 | Dohazari | 88 | 21:00 | C.Nawabganj | 57 | 20:00
Gulshan | 76 | 14:00 | Cox'sbazar | 92 | 19:00 | Amnura | 52 | 21:00
Uttara | 66 | 23:00 | Chandraghona | 28 | 19:00 | Pabna | 101 | 21:00
Uttara New | 12 | 13:00 | Kaptai | 4 | 19:00 | Shahjadpur | 90 | 20:00
Kamrangirchar | 58 | 23:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 96 | 21:00
Savar | 104 | 20:00 | Bakulia | 80 | 19:30 | Niyamatpur | 80 | 21:00
Bhasantec | 104 | 14:00 | Julda | 14 | 19:00 | Joypurhat | 60 | 21:00
Agargaon | 64 | 13:00 | TK chemical | 28 | 19:00 | Sherpur(Bogura) | 50 | 21:00
Satmosjid | 85 | 24:00 | Modern Steel | 0 | #N/A | Mohastangor | 68 | 21:00
Tongi | 68 | 21:00 | Shahmirpur | 17 | 19:00 | Bhangura | 34 | 21:00
Kabirpur | 126 | 22:00 | Khagrachhari | 26 | 19:30 | Rangpur | 140 | 20:00
Basundhara | 178 | 14:00 | Matarbari | 36 | 20:00 | Lalmonirhat | 47 | 19:30
Manikganj | 76 | 21:00 | Baroiar Hat | 42 | 19:30 | Saidpur | 104 | 21:00
Joydevpur | 91 | 21:00 | Rangamati | 12 | 19:30 | Purbasadipur | 104 | 20:00
New Tongi | 58 | 15:00 | Abul Khair 230 | 2 | 10:00 | Thakurgaon | 92 | 20:00
Kodda | 117 | 21:00 | BSRM | 2 | 18:30 | Palashbari | 115 | 1:00
Dhamrai | 82 | 19:30 | GPH Ispat | 83 | 20:00 | Barapukuria | 56 | 20:00
Rajendrapur | 78 | 22:00 | Agrabad | 60 | 20:00 | Panchagar | 57 | 19:30
Valuka | 86 | 20:00 | Goalpara | 25 | 22:00 | Joldhaka | 63 | 2:00
Tangail | 210 | 22:00 | Central S/S | 87 | 20:00 | Kurigram | 61 | 1:00
Mymensing | 199 | 0:00 | Noapara | 45 | 19:30 | Mithapukur | 35 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 403 | 6:00 | 399 | 1:00 | Kaliakoir | 394 | 0.75 | 385 | 0.95833
| Bheramara | 404 | 4:00 | 396 | 1:00 | Bhulta | 385 | 0.29167 | 377 | 0.625
| Ashuganj(N) | 391 | 1:00 | 385 | 13:00 | Gopalganj | 413 | 0.625 | 387 | 0.875
| Payra | 413 | 6:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 224 | 1:00 | 218 | 18:00
| Ishurdi | 235 | 18:00 | 224 | 21:00 | Megnaghat | 236 | 7:00 | 231 | 11:00
| Ashuganj | 239 | 19:30 | 231 | 18:30 | Fenchuganj | 237 | 5:00 | 233 | 24:00
| Serajganj | 229 | 18:30 | 224 | 19:30 | Siddhirganj | 232 | 19:30 | 229 | 13:00
| Baghabari | 232 | 5:00 | 225 | 19:00 | Maniknagar | 231 | 19:30 | 227 | 13:00
| Barapukuria | 234 | 18:30 | 225 | 21:00 | Agargaon | 228 | 18:30 | 222 | 15:00
| Bogra | 222 | 19:00 | 213 | 14:00 | Barisal | 241 | 6:00 | 232 | 1:00
| Rajshahi | 234 | 18:30 | 220 | 13:00 | Bhola 225 MW | 244 | 15:00 | 238 | 1:00
| Khulna South | 228 | 8:00 | 213 | 1:00 | AKSML | 225 | 6:00 | 221 | 12:00
| Rampura | 230 | 5:00 | 227 | 13:00 | BSRM | 229 | 19:30 | 221 | 18:30
| Haripur | 230 | 3:00 | 226 | 12:00 | Bibiyana | 239 | 7:00 | 235 | 2:00
| Hasnabad | 230 | 8:00 | 225 | 14:00 | Bhulta | 232 | 4:00 | 227 | 15:00
| Shyampur | 228 | 6:00 | 220 | 15:00 | Ashuganj (S) | 235 | 20:00 | 231 | 1:00
| Aminbazar | 229 | 1:00 | 224 | 2:00 | Kaliakoir | 228 | 6:00 | 222 | 23:00
| Tongi | 227 | 5:00 | 222 | 21:00 | GPH | 225 | 7:00 | 219 | 18:00
| Comilla (N) | 229 | 19:30 | 224 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 6:00 | 132 | 13:00 | Madanhat | 134 | 0.83333 | 129 | 0.45833
| Munsiganj | 136 | 19:30 | 131 | 8:00 | Hathazari | 133 | 0.041667 | 130 | 0.54167
| Sonargaon | 133 | 19:30 | 128 | 9:00 | Khulshi | 133 | 0.8125 | 125 | 0.54167
| Shyampur | 138 | 7:00 | 135 | 11:00 | Halishahar | 134 | 0.8125 | 124 | 0.77083
| Bhulta | 130 | 5:00 | 126 | 1:00 | Baraulia | 134 | 0.8125 | 126 | 0.75
| Madanganj | 134 | 19:00 | 131 | 1:00 | Sikalbaha | 135 | 0.875 | 125 | 0.77083
| Shitalakhya | 138 | 6:00 | 134 | 13:00 | Dohazari | 130 | 0.8125 | 122 | 0.75
| Rahim steal | 135 | 7:00 | 133 | 1:00 | Cox'sbazar | 124 | 0.54167 | 114 | 0.20833
| Matuail | 134 | 6:00 | 132 | 13:00 | Chandraghona | 135 | 0.8125 | 129 | 0.75
| Ghorasal | 137 | 1:00 | 136 | 8:00 | Kaptai | 132 | 0.041667 | 132 | 0.041667
| Narsinghdi | 131 | 7:00 | 124 | 22:00 | A. Khaer Stl. | 130 | 0.041667 | 127 | 0.5
| Haripur (SBU) | 134 | 1:00 | 132 | 14:00 | Bakulia | 132 | 0.83333 | 125 | 0.77083
| Sreenagar | 130 | 7:00 | 127 | 1:00 | Julda | 131 | 0.041667 | 127 | 0.45833
| Ullon | 136 | 7:00 | 131 | 14:00 | TK Chemical | 134 | 0.8125 | 125 | 0.75
| Hasnabad | 137 | 1:00 | 134 | 15:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 136 | 6:00 | 131 | 15:00 | Shahmirpur | 135 | 0.8125 | 125 | 0.75
| Maniknagar | 135 | 3:00 | 132 | 15:00 | Khagrachhari | 132 | 0.8125 | 119 | 0.58333
| Bangabhaban | 135 | 3:00 | 132 | 15:00 | Matarbari | 121 | 0.8125 | 114 | 0.77083
| Motijheel | 135 | 3:00 | 132 | 15:00 | Baroiar Hat | 131 | 0.8125 | 125 | 0.54167
| Narinda | 135 | 3:00 | 132 | 15:00 | Rangamati | 133 | 19:30 | 128 | 18:00
| Kazla | 135 | 3:00 | 132 | 15:00 | Agrabad | 133 | 19:30 | 125 | 18:00
| Dhanmondi | 136 | 7:00 | 131 | 14:00 | Goalpara S/S | 137 | 8:00 | 128 | 0.041667
| Lalbag | 139 | 6:00 | 134 | 13:00 | Khulna Central S/S | 137 | 8:00 | 127 | 0.041667
| Madartek | 136 | 7:00 | 131 | 15:00 | Noapara | 134 | 8:00 | 124 | 0.041667
| Dhaka University | 136 | 6:00 | 132 | 13:00 | Jessore | 129 | 10:00 | 116 | 0.91667
| Aftabnagar | 136 | 5:00 | 132 | 14:00 | Benapol | 129 | 0.75 | 117 | 0.041667
| Fatullah | 138 | 6:00 | 135 | 13:00 | Jhenida | 125 | 18:00 | 108 | 0.875
| Nawabganj | 131 | 7:00 | 127 | 13:00 | Bottail | 131 | 0.41667 | 120 | 0.875
| Keraniganj | 131 | 7:00 | 127 | 15:00 | G.K Project | 139 | 0.33333 | 131 | 0.875
| Mirpur | 136 | 3:00 | 133 | 13:00 | Faridpur | 136 | 0.25 | 127 | 0.875
| Kalyanpur | 138 | 19:30 | 133 | 13:00 | Rajbari | 136 | 0.29167 | 126 | 0.83333
| Gulshan | 135 | 5:00 | 131 | 13:00 | Madaripur | 140 | 0.45833 | 131 | 0.875
| Uttara | 138 | 19:00 | 132 | 13:00 | Shariyatpur S/S | 139 | 18:00 | 130 | 0.041667
| Uttara New | 138 | 13:00 | 132 | 13:00 | Gopalganj | 142 | 0.29167 | 131 | 0.83333
| Kamrangirchar | 139 | 19:00 | 133 | 13:00 | Bagerhat | 136 | 10:00 | 125 | 0.041667
| Savar | 132 | 19:30 | 132 | 15:00 | Mongla | 135 | 9:00 | 124 | 0.041667
| Bhasantec | 138 | 6:00 | 133 | 15:00 | Satkhira | 135 | 7:00 | 124 | 1:00
| Agargaon | 140 | 6:00 | 134 | 13:00 | Gallamari | 137 | 0.33333 | 127 | 1:00
| Satmosjid | 138 | 6:00 | 134 | 12:00 | Magura | 125 | 10:00 | 105 | 0.83333
| Tongi | 139 | 5.00 | 136 | 22:00 | Narail | 123 | 0.75 | 104 | 0.875
| Kabirpur | 141 | 4.00 | 136 | 22:00 | Chuadanga | 119 | 18:30 | 96 | 0.875
| Basundhara | 138 | 7:00 | 133 | 15:00 | Borguna | 136 | 18:00 | 129 | 0.041667
| Manikganj | 139 | 6.00 | 133 | 20:00 | Barisal(N) | 139 | 7:00 | 132 | 1:00
| Joydevpur | 139 | 19:00 | 134 | 1:00 | Barisal (S) | 136 | 0.29167 | 130 | 0.041667
| New Tongi | 138 | 8:00 | 134 | 13:00 | Patuakhali(S) | 138 | 0.77083 | 127 | 0.041667
| Kodda | 134 | 19:30 | 130 | 1:00 | Bhandaria | 134 | 0.70833 | 125 | 0.875
| Dhamrai | 134 | 6.00 | 130 | 22:00 | Ishurdi | 136 | 18:00 | 129 | 21:00
| Rajendrapur | 133 | 8:00 | 127 | 1:00 | Ruppur Paromanobik | 135 | 9:00 | 130 | 21:00
| Valuka | 123 | 18:00 | 114 | 1:00 | Natore | 133 | 7:00 | 126 | 21:00
| Tangail | 133 | 7:00 | 127 | 1:00 | Bogra | 132 | 18:30 | 124 | 13:00
| Mymensing | 125 | 7:00 | 115 | 0:00 | Noagaon | 127 | 18:00 | 118 | 21:00
| Kishorganj | 128 | 7:00 | 120 | 1:00 | Rajshahi | 132 | 18:00 | 123 | 14:00
| Netrokona | 122 | 18:00 | 110 | 21:00 | Rajshahi New | 132 | 18:00 | 124 | 19:30
| Jamalpur | 130 | 19:30 | 120 | 10:00 | C.Nawabganj | 131 | 18:00 | 120 | 14:00
| Sherpur | 128 | 19:30 | 116 | 13:00 | Amnura | 132 | 18:00 | 120 | 13:00
| Srimongal | 135 | 7:00 | 132 | 4:00 | Pabna | 134 | 18:00 | 127 | 21:00
| Shahjibazar | 135 | 16:00 | 131 | 1:00 | Shahjadpur | 139 | 18:00 | 135 | 21:00
| Fenchuganj | 136 | 14:00 | 133 | 9:00 | Serajganj | 130 | 3:00 | 125 | 21:00
| Khulawara | 133 | 7:00 | 132 | 1:00 | Niyamatpur | 122 | 5:00 | 113 | 14:00
| Sylhet | 132 | 5:00 | 130 | 1:00 | Joypurhat | 128 | 18:00 | 115 | 21:00
| Chatak | 132 | 14:00 | 128 | 1:00 | Sherpur(Bogura) | 132 | 18:00 | 125 | 21:00
| Sunamganj | 130 | 18:00 | 125 | 1:00 | Mohastangor | 130 | 18:30 | 122 | 14:00
| Biani Bazar | 132 | 18:00 | 126 | 1:00 | Bangura | 136 | 18:30 | 130 | 21:00
| Comilla(s) | 127 | 4:00 | 123 | 21:00 | Rangpur | 125 | 18:30 | 114 | 21:00
| Comilla(n) | 134 | 4:00 | 132 | 1:00 | Lalmonirhat | 126 | 18:30 | 115 | 21:00
| Chandpur | 130 | 20:00 | 125 | 12:00 | Saidpur | 128 | 18:00 | 113 | 14:00
| Feni | 129 | 20:00 | 125 | 12:00 | Purbasadipur | 125 | 18:00 | 109 | 21:00
| Chowmuhani | 126 | 21:00 | 123 | 6:00 | Thakurgaon | 128 | 18:30 | 108 | 21:00
| Ashuganj | 137 | 18:00 | 134 | 1:00 | Palashbari | 125 | 18:00 | 116 | 13:00
| Daudkandi | 132 | 7:00 | 128 | 1:00 | Barapukuria | 134 | 18:30 | 125 | 21:00
| B.Baria | 132 | 15:00 | 127 | 21:00 | Panchagar | 128 | 18:00 | 107 | 19:30
| Ramganj | 128 | 19:30 | 122 | 13:00 | Joldhaka | 124 | 0.75 | 109 | 0.875
| Chaddagram | 134 | 19:30 | 127 | 13:00 | Kurigram | 126 | 0.75 | 112 | 0.875
| PHP | 132 | 19:30 | 125 | 12:00 | Mithapukur | 129 | 0.79167 | 117 | 0.58333
| Kochua | 129 | 19:00 | 126 | 1:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 452 | 7244 | 3710 | 10954 |  |  |  | QF-LDC-11
0:30 | 394 | 6923 | 3534 | 10457 | Date: | 2021-07-25
1:00 | 336 | 6602 | 3358 | 9960
1:30 | 368 | 6516.5 | 3286.5 | 9803
2:00 | 400 | 6431 | 3215 | 9646
2:30 | 415 | 6408 | 3127 | 9535 | [5 empty] | Gen. at Eve. Peak | 11285 | 11285 MW (21:00 )
3:00 | 430 | 6385 | 3039 | 9424 | [6 empty] | 21:00
3:30 | 409 | 6289 | 3027.5 | 9316.5 | [5 empty] | Gen. at Day Peak | 8451 | 8451 MW (12:00 )
4:00 | 388 | 6193 | 3016 | 9209 | [6 empty] | 12:00
4:30 | 359 | 6079 | 2989 | 9068 | [5 empty] | Highest Generation | 11332
5:00 | 330 | 5965 | 2962 | 8927 | [6 empty] | 22:00
5:30 | 313 | 5762.5 | 2808 | 8570.5
6:00 | 296 | 5560 | 2654 | 8214
6:30 | 321 | 5493.5 | 2565 | 8058.5
7:00 | 346 | 5427 | 2476 | 7903
7:30 | 333 | 5385 | 2470 | 7855
8:00 | 320 | 5343 | 2464 | 7807
8:30 | 344 | 5408.5 | 2473.5 | 7882
9:00 | 368 | 5474 | 2483 | 7957
9:30 | 283 | 5506.5 | 2547.5 | 8054
10:00 | 198 | 5539 | 2612 | 8151
10:30 | 201 | 5586 | 2643 | 8229
11:00 | 204 | 5633 | 2674 | 8307
11:30 | 287 | 5736.5 | 2642.5 | 8379
12:00 | 370 | 5840 | 2611 | 8451
12:30 | 325 | 5917.5 | 2768 | 8685.5
13:00 | 280 | 5995 | 2925 | 8920
13:30 | 272 | 6064 | 2958.5 | 9022.5
14:00 | 264 | 6133 | 2992 | 9125
14:30 | 226 | 6173 | 3059 | 9232
15:00 | 188 | 6213 | 3126 | 9339
15:30 | 189 | 6133.5 | 3073 | 9206.5
16:00 | 190 | 6054 | 3020 | 9074
16:30 | 104 | 5825 | 2989 | 8814
17:00 | 18 | 5596 | 2958 | 8554
17:30 | 28 | 5398 | 2866.5 | 8264.5
18:00 | 38 | 5200 | 2775 | 7975
18:30 | 48 | 5618 | 2983 | 8601
19:00 | 58 | 6036 | 3191 | 9227
19:30 | 484 | 7223 | 3595 | 10818
20:00 | 380 | 7076 | 3706 | 10782 |  |  |  | Executive Engineer
20:30 | 397 | 7246 | 3787.5 | 11033.5 |  |  |  | Network Operation Division
21:00 | 414 | 7416 | 3869 | 11285
21:30 | 451 | 7483.5 | 3825 | 11308.5
22:00 | 488 | 7551 | 3781 | 11332 |  |  |  |  | Page 6 of 7
22:30 | 497 | 7540 | 3752.5 | 11292.5
23:00 | 506 | 7529 | 3724 | 11253
23:30 | 479 | 7386.5 | 3717 | 11103.5
24:00 | 452 | 7244 | 3710 | 10954
11285 MW (21:00 )
8451 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-25 |  | Energy | 225499762
[11 empty] | 2021-07-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4809 | 786 | 1995 | 2505 | 694 | 124 | 162 | 0 | 140 | 0
0:30 | 4862.5 | 791 | 1962.5 | 1934.5 | 678.5 | 123 | 105.5 | 0 | 130 | 0 | Date: | 2021-07-25
1:00 | 4916 | 796 | 1930 | 1364 | 663 | 122 | 49 | 0 | 120 | 0
1:30 | 4916.5 | 796 | 1911.5 | 1268.5 | 647.5 | 120.5 | 24.5 | 0 | 118 | 0 | [7 empty] | Total Energy | 225.4998 | Total Energy Gen 225.500 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 225.500 MKWHr
2:00 | 4917 | 796 | 1893 | 1173 | 632 | 119 | 0 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4889 | 791 | 1897.5 | 1121 | 603.5 | 118 | 0 | 0 | 115 | 0 | [7 empty] | Energy Requirement | 225.4998
3:00 | 4861 | 786 | 1902 | 1069 | 575 | 117 | 0 | 0 | 114 | 0
3:30 | 4848 | 786.5 | 1876.5 | 1012 | 564.5 | 117 | 0 | 0 | 112 | 0 | [6 empty] | Shortage
4:00 | 4835 | 787 | 1851 | 955 | 554 | 117 | 0 | 0 | 110 | 0
4:30 | 4804.5 | 786.5 | 1751.5 | 934.5 | 564 | 118 | 0 | 0 | 109 | 0
5:00 | 4774 | 786 | 1652 | 914 | 574 | 119 | 0 | 0 | 108 | 0
5:30 | 4653 | 786.5 | 1568 | 773.5 | 564.5 | 119.5 | 0 | 0 | 104 | 1.5
6:00 | 4532 | 787 | 1484 | 633 | 555 | 120 | 0 | 0 | 100 | 3
6:30 | 4459.5 | 786.5 | 1456 | 596.5 | 535 | 120.5 | 0 | 0 | 97 | 7.5 |  |  |  |  | Coal
7:00 | 4387 | 786 | 1428 | 560 | 515 | 121 | 0 | 0 | 94 | 12
7:30 | 4372.5 | 786 | 1360 | 585.5 | 515 | 122 | 0 | 0 | 93 | 21 |  |  |  | Oil |  |  |  | ,
8:00 | 4358 | 786 | 1292 | 611 | 515 | 123 | 0 | 0 | 92 | 30
8:30 | 4402 | 786 | 1291.5 | 623.5 | 519.5 | 123 | 0 | 0 | 94 | 42.5
9:00 | 4446 | 786 | 1291 | 636 | 524 | 123 | 0 | 0 | 96 | 55
9:30 | 4443.5 | 786 | 1383.5 | 629.5 | 524 | 123 | 0 | 0 | 99 | 65.5
10:00 | 4441 | 786 | 1476 | 623 | 524 | 123 | 0 | 0 | 102 | 76
10:30 | 4495 | 786 | 1483.5 | 632.5 | 523.5 | 124 | 0 | 0 | 102 | 82.5
11:00 | 4549 | 786 | 1491 | 642 | 523 | 125 | 0 | 0 | 102 | 89
11:30 | 4558 | 786 | 1548.5 | 650.5 | 522.5 | 125 | 0 | 0 | 104 | 84.5
12:00 | 4567 | 786 | 1606 | 659 | 522 | 125 | 0 | 0 | 106 | 80
12:30 | 4631 | 786 | 1776.5 | 627.5 | 533.5 | 124.5 | 4.5 | 0 | 107 | 95
13:00 | 4695 | 786 | 1947 | 596 | 545 | 124 | 9 | 0 | 108 | 110
13:30 | 4695 | 786 | 1947 | 596 | 545 | 124 | 9 | 0 | 108 | 110
14:00 | 4695 | 786 | 1947 | 596 | 545 | 124 | 9 | 0 | 108 | 110
14:30 | 4673 | 786 | 1961 | 786.5 | 590.5 | 122 | 11.5 | 0 | 112 | 87
15:00 | 4651 | 786 | 1975 | 977 | 636 | 120 | 14 | 0 | 116 | 64
15:30 | 4614.5 | 786 | 1978.5 | 891 | 628 | 119.5 | 24 | 0 | 114 | 51
16:00 | 4578 | 786 | 1982 | 805 | 620 | 119 | 34 | 0 | 112 | 38
16:30 | 4493.5 | 786 | 1903.5 | 699 | 606 | 119 | 69 | 0 | 109 | 29
17:00 | 4409 | 786 | 1825 | 593 | 592 | 119 | 104 | 0 | 106 | 20
17:30 | 4291.5 | 786 | 1731.5 | 558.5 | 557.5 | 119 | 105 | 0 | 103 | 12.5
18:00 | 4174 | 786 | 1638 | 524 | 523 | 119 | 106 | 0 | 100 | 5
18:30 | 4415.5 | 786 | 1680 | 755.5 | 532 | 119 | 194.5 | 0 | 116 | 2.5
19:00 | 4657 | 786 | 1722 | 987 | 541 | 119 | 283 | 0 | 132 | 0
19:30 | 4579 | 786 | 1864 | 2392 | 652 | 119 | 296 | 0 | 130 | 0
20:00 | 4639 | 786 | 1928 | 2247 | 661 | 119 | 270 | 0 | 132 | 0
20:30 | 4714.5 | 786 | 1971.5 | 2353.5 | 697 | 120 | 255 | 0 | 136 | 0
21:00 | 4790 | 786 | 2015 | 2460 | 733 | 121 | 240 | 0 | 140 | 0
21:30 | 4819 | 786 | 2012 | 2484.5 | 730 | 122 | 213 | 0 | 142 | 0
22:00 | 4848 | 786 | 2009 | 2509 | 727 | 123 | 186 | 0 | 144 | 0
22:30 | 4832 | 786 | 1999 | 2507 | 727 | 123.5 | 174 | 0 | 144 | 0
23:00 | 4816 | 786 | 1989 | 2505 | 727 | 124 | 162 | 0 | 144 | 0
23:30 | 4812.5 | 786 | 1992 | 2505 | 710.5 | 124 | 162 | 0 | 142 | 0 | Max Temp. in Dhaka |  | 34° C
24:00 | 4809 | 786 | 1995 | 2505 | 694 | 124 | 162 | 0 | 140 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 225.500 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 225.500 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 62 | 59 | 57 | 57 | 59 | 60 | 61 | 63 | 63 | 63 | 65 | 65 | 64 | 60 | 60 | 59 | 59 | 59 |  | 59 | 59 | 59 | 61 | 63 | 64 | 64 | 1397673
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1448000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 95 | 95 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
5 | Raozan 25 MW PP | [21 empty] | 3 | 8 | 8 | 8 | 0 | 29964
| Teknaf 20MW PP (Solartech) | [6 empty] | 0 | 4 | 8 | 12 | 16 | 8 | 17 | 7 | 14 | 2 | 3 | 0 | [8 empty] | 62235
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 80 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2850342
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 30 | 51 | 51 | 51 | 51 | 51 | 51 | 252981
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 0 | [6 empty] | 11 | 68 | 76 | 105 | 105 | 105 | 105 | 814614
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | [23 empty] | 40 | 40 | 40 | 114000
17 | Siddhirganj 335 MW CCPP | 280 | 280 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 280 | 332 | 328 | 292 | 290 | 250 |  | 290 | 270 | 270 | 300 | 332 | 335 | 332 | 6846058
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 2 | 30 | 15 | 15 | 15 |  | 0 | 87818
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 45 |  | 45 | 45 | 45 | 45 | 45 | 45 | 45 | 518545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2677500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 145 | 90 | 60 | [11 empty] | 0 | 3784473
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 100 | 100 | 100 | 100 | 100 | 100 | 2145262
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 540360
33 | Ashuganj 225 MW CCPP | 181 | 181 | 181 | 181 | 181 | 182 | 182 | 183 | 193 | 187 | 189 | 203 | 187 | 183 | 182 | 182 | 182 | 183 |  | 209 | 214 | 212 | 212 | 213 | 214 | 214 | 4649000
34 | Ashuganj 450 MW CCPP(South) | 275 | 275 | 255 | 255 | 255 | 255 | 255 | 255 | 270 | 255 | 260 | 290 | 260 | 270 | 270 | 270 | 270 | 270 |  | 315 | 270 | 295 | 295 | 280 | 270 | 275 | 6606000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 265 | 265 | 295 | 265 | 260 | 260 | 260 | 260 | 260 |  | 305 | 260 | 285 | 285 | 265 | 275 | 275 | 6769500
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 5 | 5 | 5 | 5 | 30 | 40 | 50 | 50 | 50 | 50 | 35 |  | 35 | 55 | 56 | 55 | 55 | 55 | 54 | 886560
36 | Chandpur 150 MW CCPP | 133 | 133 | 134 | 133 | 134 | 131 | 131 | 137 | 138 | 138 | 138 | 137 | 138 | 137 | 137 | 136 | 138 | 137 |  | 137 | 136 | 136 | 136 | 137 | 137 | 137 | 3240840
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 363 | 363 | 362 | 334 | 326 | 324 | 282 | 281 | 304 | 325 | 326 | 374 | 396 | 395 | 394 | 394 | 361 | 335 |  | 325 | 337 | 344 | 356 | 398 | 398 | 398 | 8577030
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5640750
41 | Haripur 360MW CCPP(HPL) | 347 | 347 | 347 | 307 | 307 | 284 | 278 | 255 | 255 | 255 | 265 | 300 | 344 | 344 | 344 | 332 | 299 | 270 |  | 285 | 320 | 300 | 345 | 347 | 347 | 347 | 7484000
42 | RPCL 210MW CCPP | 205 | 207 | 207 | 207 | 207 | 207 | 208 | 204 | 203 | 203 | 201 | 198 | 198 | 197 | 199 | 200 | 202 | 201 |  | 200 | 206 | 203 | 202 | 202 | 204 | 204 | 4774720
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 8 | 14 | 12 | 30 | 27 | 22 | 49 | 28 | 15 | 10 | 7 | 1 | [8 empty] | 243090
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 |  | 44 | 43 | 43 | 44 | 43 | 43 | 43 | 1027000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 42 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 994200
46 | Shajibazar 330 MW CCPP | 162 | 162 | 162 | 162 | 161 | 162 | 160 | 162 | 161 | 161 | 159 | 158 | 158 | 158 | 160 | 161 | 162 | 162 |  | 162 | 162 | 184 | 183 | 203 | 200 | 190 | 3803000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 62 | 62 | 62 | 62 | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 60 | 60 | 60 | 61 | 40 |  | 58 | 59 | 61 | 59 | 59 | 61 | 61 | 1300224
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 84 | 83 | 81 | 82 | 10 | 10 |  | 10 | 80 | 84 | 84 | 84 | 84 | 84 | 1218240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 192 | 178 | 179 | 178 | 178 | 178 | 178 | 219 | 219 | 219 | 219 | 191 | 191 | 191 |  | 219 | 218 | 218 | 218 | 218 | 218 | 218 | 4899630
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 392000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 238320
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 202032
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 47 | 47 | 47 | 49 | 13 | 14 |  | 16 | 43 | 49 | 47 | 50 | 50 | 50 | 756600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 369840
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 275 | 285 | 280 | 280 | 265 | 255 | 230 | 230 | 305 | 305 | 305 | 290 | 300 | 290 | 290 | 280 | 290 |  | 300 | 270 | 290 | 310 | 300 | 290 | 285 | 7002500
| Bibiyana South 400 MW | 360 | 360 | 360 | 360 | 360 | 320 | 327 | 320 | 320 | 320 | 340 | 350 | 385 | 390 | 390 | 389 | 360 | 311 |  | 346 | 396 | 390 | 390 | 393 | 397 | 396 | 8584900
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 10 | 35 | 17 | 17 | 17 | 35 | 17 | 128473
59 | Tangail Palli Power Gen 22 MW | [20 empty] | 10 | 8 | 24 | 23 | 24 | 24 | 104640
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 20 | 21 | 21 | 21 | 21 | 492672
61 | Narshingdi 22 MW PP (Doreen) | 18 | 19 | 19 | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  |  |  | 19 | 19 | 19 | 19 | 19 |  | 0 | 318960
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 484596
63 | Impoprt (Tripura) | 120 | 116 | 114 | 110 | 108 | 100 | 94 | 92 | 96 | 102 | 102 | 106 | 108 | 118 | 116 | 112 | 106 | 100 |  | 132 | 130 | 132 | 140 | 144 | 144 | 140 | 2768640
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 40 | 42 | 42 | 42 | 42 |  | 42 | 42 | 36 | 42 | 42 | 42 | 42 | 1074720
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495216
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 246600
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 8 |  | 22 | 33 | 33 | 33 | 33 | 33 | 33 | 776000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 20 | 20 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 501700
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 10 | 10 | 8 | 8 | 8 | 8 | 8 |  | 7 | 7 | 7 | 9 | 9 | 9 | 9 | 188460
71 | Maona 33 MW PP(Summit) | 28 | 28 | 28 | 28 |  |  | 28 | 28 | 28 | 28 | 28 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 659800
72 | Rupganj 33 MW PP(Summit) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 24 | 24 | 486900
73 | Ghorashal 108MW PP (Regent) | 99 | 99 | 99 | 99 | 22 | 22 | 22 | 22 | 22 | 22 | 25 | 78 | 91 | 94 | 94 | 94 | 94 | 25 |  | 35 | 90 | 86 | 90 | 91 | 91 | 91 | 1625681
| Feni Lanka Power | 105 | 70 | 70 | 70 | 70 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 52 | 98 | 52 |  |  |  | 52 | 88 | 17 | 17 | 17 | 17 | 17 | 972420
| Chowmuhani 113 MW | 65 | 65 | 65 | 65 | 65 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 21 | 36 | 36 | 36 | 36 |  | 46 | 105 | 103 | 104 | 106 | 107 | 106 | 1252440
| Manikgonj 162MW PP(MPGL) | [19 empty] | 35 | 162 | 72 | 72 | 72 | 72 | 35 | 411840
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 | [18 empty] | 24 | 42 | 16 | 32 | 34 | 34 | 32 | 168000
79 | Kodda 150MW PP | [19 empty] | 48 | 16 |  |  |  |  | 0 | 37440
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 171840
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 2 | 25 | 16 | 16 | 16 | 15 | 16 | 108720
| Gazipur 100 MW PP | [13 empty] | 1 | 17 | 17 |  |  |  |  | 34 | 25 | 34 | 34 | 34 | 34 | 210000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 1 | 1 | 5 | 5 | 6 | 2 | 1 | 1 | 2 | [9 empty] | 22439
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | [19 empty] | 8 | 70 | 91 | 108 | 108 | 108 | 110 | 545306
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 255 | 260 | 255 | 250 | 265 | 245 | 225 | 265 | 285 | 280 | 280 | 295 | 295 | 270 | 270 | 255 | 255 | 270 |  | 300 | 270 | 280 | 280 | 275 | 265 | 270 | 6391825
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [20 empty] | 36 | 53 | 35 | 35 | 35 | 0 | 178560
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 40 | 40 | 10 | 10 | 10 |  | 10 | 30 |  |  |  |  | 0 | 347520
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 35 | 35 | 35 | 35 | 8 |  | 8 | 25 | 37 | 43 | 43 | 43 | 43 | 768504
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 5 | 16 |  |  |  |  | 0 | 18576
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) | 97 | 77 | 64 | 64 | 64 | 64 | 65 | 64 | 64 | 64 | 60 | 62 | 78 | 90 | 90 | 90 | 81 | 38 |  | 50 | 97 | 97 | 97 | 97 | 97 | 97 | 1824000
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [20 empty] | 15 | [5 empty] | 15678
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 17 | 45 | 55 | 55 | 55 | 55 | 17 | 269138
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 1 | 1 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | [8 empty] | 12000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | [9 empty] | 10 | 17 | 17 | 17 | 17 | 17 |  | 17 | 54 | 54 | 54 | 54 | 54 | 35 | 442800
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 192 | 193 | 100 | 100 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 12 | 40 | 40 | 8 | 8 |  | 26 | 194 | 175 | 193 | 198 | 189 | 184 | 2083200
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [23 empty] | 5 | 15 | 35 | 57600
115 | Juldah 100 MW PP Unit-3 (Acorn) | [19 empty] | 22 | 60 | 60 | 60 | 60 | 60 | 20 | 278400
116 | Chandpur 200MW (Desh energy) | [19 empty] | 4 | 85 | 70 | 85 | 99 | 100 | 100 | 471360
117 | Ashuganj 150MW PP (Midland) | [13 empty] | 1 | 8 | 10 | 10 | 10 |  | 16 | 100 | 93 | 123 | 150 | 150 | 100 | 714254
118 | Bibiyana-III 400 MW CCPP | 367 | 366 | 366 | 366 | 366 | 319 | 319 | 320 | 327 | 317 | 344 | 401 | 370 | 367 | 367 | 367 | 307 | 306 |  | 390 | 317 | 327 | 386 | 370 | 367 | 366 | 8446000
| Jamalpur 115 MW PP (United) | 107 | 107 | 107 | 108 | 115 | 115 | 115 | 75 | 75 | 75 | 75 | 75 | 75 | 82 | 86 | 86 | 86 | 85 |  | 90 | 115 | 115 | 115 | 115 | 115 | 115 | 2335200
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | [19 empty] | 35 | 50 | 50 | 50 | 50 | 50 | 10 | 247680
| Anlima Energy Ltd. | 116 | 53 | 53 | 53 | 53 | 53 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 28 | 76 | 72 | 35 | 17 |  | 20 | 53 | 103 | 116 | 116 | 116 | 116 | 1381255
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 439920
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 4 | 10 | 27 | 24 | 31 | 32 | 24 | 30 | 25 | 19 | 4 | 3 | [8 empty] | 239671
120 | Eastern Zone Total | 6602 | 6431 | 6385 | 6193 | 5965 | 5560 | 5427 | 5343 | 5474 | 5539 | 5633 | 5840 | 5995 | 6133 | 6213 | 6054 | 5596 | 5200 |  | 6036 | 7223 | 7076 | 7416 | 7551 | 7529 | 7244 | 150246445
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [12 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [8 empty] | 19200
| Khulna 225 MW CCPP | [12 empty] | 5 | 10 | 10 | 10 | 10 | 10 |  | 45 | 70 | 85 | 85 | 40 | 15 | 15 | 347090
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 70 | 70 | 70 | 35 | 35 | 90 | 90 | 90 | 105 | 105 | 53 | 53 | 53 | 53 | 17 |  |  | 10 | 53 | 100 | 105 | 105 | 105 | 105 | 1842720
130
131
132 | United Payra Power Ltd. | [19 empty] | 23 | 90 | 90 | 90 | 90 | 90 | 90 | 487200
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 222 | 222 | 221 | 171 | 171 | 140 | 140 | 161 | 161 | 160 | 218 | 216 | 216 | 216 | 216 | 178 |  | 217 | 217 | 218 | 219 | 219 | 219 | 220 | 4769782
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 83 | 82 | 81 | 81 | 43 | 32 | 32 |  |  | 12 | 12 | 12 | 61 | 77 | 78 | 80 | 74 | 34 |  | 47 | 66 | 76 | 86 | 85 | 85 | 85 | 1311811
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 32 | 31 | 29 | 28 | 27 | 24 | 23 | 23 | 23 | 25 | 26 | 27 | 26 | 25 | 25 | 25 |  | 30 | 31 | 32 | 32 | 32 | 32 | 32 | 661374
141 | Noapara 100 MW PP (Bangla Trac) | [7 empty] | 15 | 20 | 20 | 20 | 20 | [8 empty] | 100 | 90 | 100 | 100 | 100 | 100 | 632640
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 796 | 796 | 786 | 787 | 786 | 787 | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 786 |  | 786 | 786 | 786 | 786 | 786 | 786 | 786 | 19013091
147 | Bheramara 410 MW CCPP | 405 | 405 | 400 | 405 | 405 | 300 | 270 | 250 | 250 | 250 | 250 | 250 | 390 | 390 | 390 | 390 | 330 | 300 |  | 350 | 350 | 350 | 396 | 400 | 400 | 400 | 8447517
148 | Payra 1320 MW | 440 | 410 | 350 | 330 | 350 | 330 | 290 | 290 | 300 | 300 | 300 | 300 | 320 | 360 | 410 | 400 | 370 | 300 |  | 320 | 430 | 440 | 500 | 500 | 500 | 470 | 9798600
149
150 | Barapukuria TPP Unit-1 | 73 | 72 | 75 | 74 | 74 | 75 | 75 | 75 | 74 | 74 | 73 | 73 | 76 | 73 | 77 | 71 | 73 | 74 |  | 72 | 73 | 72 | 72 | 75 | 76 | 70 | 1786472
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 161 | 152 | 151 | 154 | 3682800
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | [5 empty] | 50 | 50 |  | 80 | 80 | 80 | 80 | 70 | 70 | 70 | 1266000
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 |  |  |  | 0 | 85680
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 0 | 3 | 3 | 3 | 5 | 5 | 5 | 2 | 1 | 1 | 0 | [8 empty] | 30600
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 169 | 169 | 169 | 169 | 169 | 169 | 140 | 140 | 140 | 143 | 164 | 174 | 193 | 193 | 186 | 182 | 166 | 167 |  | 178 | 178 | 171 | 177 | 169 | 159 | 161 | 4264145
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 195 | 194 | 178 | 176 | 178 | 178 | 140 | 140 | 140 | 155 | 179 | 176 | 198 | 192 | 188 | 184 | 178 | 174 |  | 184 | 187 | 175 | 172 | 160 | 147 | 148 | 4416055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 337 | 311 | 310 | 305 | 334 | 299 | 260 | 263 | 263 | 340 | 342 | 340 | 405 | 405 | 394 | 370 | 370 | 390 |  | 380 | 308 | 347 | 346 | 346 | 335 | 346 | 8154545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 507840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 231516
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 18 | 24 | 28 | 39 | 22 | 22 | 22 | 108569
168 | Santahar 50 MW Peaking PP | 25 | [19 empty] | 7 | 16 | 25 | 33 | 34 | 34 | 170751
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | [11 empty] | 2 | 36 | 8 | 8 | 8 |  | 8 | 11 | 32 | 43 | 43 | 43 | 43 | 420000
170 | Chapainawabganj 100 MW Peaking PP | 24 | [14 empty] | 20 | 90 | 92 |  | 92 | 78 | 40 | 40 | 40 | 40 | 40 | 515920
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | [19 empty] | 9 | 72 | 68 | 90 | 90 | 90 | 94 | 457536
172 | Confidence Power Bogura Unit-1 113 MW | 35 | [12 empty] | 15 | 35 |  |  |  |  | 25 | 60 | 80 | 95 | 95 | 95 | 95 | 616128
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 50 | [9 empty] | 50 | 34 | 5 |  |  | 85 | 92 | 98 | 97 | 97 | 97 | 97 | 1161523
177 | Sympa Solar Power 8MW | [5 empty] | 0 |  | 1 | 4 | 5 | 6 | 6 | 7 | 6 | 5 | 4 | 3 | 1 | [8 empty] | 46212
178
178