## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-27 | Tuesday
|  |  | Date (day): | 2021-07-27 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14609.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15430 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-26 | 2021-07-27 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 22 | 95 | 90 | 95 |  | 13 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 354 | 392 | 360 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 340 | 343 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Gas shortage
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 280 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 80 |  | 20 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 18 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 39 | 91 | 60 | 90 | 120 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 270 | 326 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 17 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 32 | 34 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 20 | 24 |  | 9 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 42 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 270 | 270 |  | 30 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 70 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 17 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 17 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 30 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 1859 | 2305 | 3665 | 3994 | 489 | 1170
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 5 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 121 | 120 | 121 | 109 |  | Low water lavel
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 |  | 51 | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 42 | 30 | 42
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 2 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 51 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 50 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 92 | 116 | 112 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 692 | 1064 | 1641 | 1733 | 249 | 415
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 |  | 134 | Under maint
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 209 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 285 | 270 | 270 |  | 90 | ST under maint
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 310 | 360 | 360
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 20 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 42 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 65 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 136 | 130 | 136 |  | 27 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 100 | 170 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 108 | 138 | 138 | 162
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 40 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 22
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 17 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 65 | 110 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1441 | 1718 | 2153 | 2321 | 371 | 327
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 199 | 199 | 202 | 202
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 24 | 197 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 106 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 39 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 406 | 555 | 594.6 | 568 | 0 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 44 | 43 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 43 | 43 | 43 | 43 |  | 47 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 179 | 177 | 180 | 180 | 150 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 14 | 47 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 60 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 219 | 219 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 8 | 16 | 16 | 16 |  | 9 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 305 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 373 | 382 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 350 | 386 | 400 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1644 | 1787 | 1882 | 1883 | 150 | 345
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 794 | 791 | 801 | 801
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 10 | 20 | 200 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 390 | 400 | 360 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1194 | 1416 | 1616 | 1811 | 0 | 83
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 54 | 82 | 80 | 82 | 13 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 320 | 480 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 90 | 90 | 90 |  | 60 | Engine problem
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 615 | 904 | 1155 | 1157 | 13 | 254
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 70 | 70 | 70 | 70 | 30 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 5 | 20 | 20 |  | 51 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 116 | 100 | 120 | 90 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 200 | 192 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 199 | 159 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 388 | 405 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 32 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 0 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 43 | 43 | 43 |  | 9 | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 90 | 90 | 90 |  | 23 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 70 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 891 | 1337 | 1632 | 1680 | 290 | 137
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 147 | 155 | 150 | 150 | 124 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 260 | 268 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 9002 | 11354 | 14609.6 | 15430 | 1686 | 3008
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8608.7472 | 10858 | 13971.379 | 14755.9398
| A. |  | 2021-07-26 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 11419 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8322 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 11354 | MW
| 3 | Day peak Generation : |  |  | 9002 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10858 | MW
| 4 | Evening peak Generation : |  |  | 11354 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 235.4615 | MKWHr | By Solar | 0.55225 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 159.197 | MKWHr |  | By Oil: | 35.6349 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.1997 | MKWHr |  | By Hydro: | 2.8506 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1686 | MW | Dhaka | 3149 | 3149 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3008 | MW | Chittagong | 921 | 921 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4694 | MW | Khulna | 1494 | 1494 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1266.14 | MMCFD |  |  | Rajshahi | 1295 | 1295 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 170884318.616 | ii) Oil : | Taka | 226758563.18 | Comilla | 1235 | 1235 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72544598.81 | Total | Taka | 470187480.606 | Mymensingh | 1035 | 1035 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 5.299 | MKWHr. | Sylhet | 533 | 533 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -206 | MW (E to W) at | 21:00 | hrs | Barisal | 384 | 384 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -462 | MW at | 3:00 | hrs | Rangpur | 812 | 812 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.2° C |  |  | Total | 10858 | 10858 |  | 0
| B. |  | 2021-07-27 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 35.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15430 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8500 | MW
| 4 | Reserve(Generation end) |  |  |  | 3930 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 237.1317 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8171 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.192 | MKWHr. | ii) HVDC Flow at Peak Time |  | 791 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8349 | MKWHr. | iii) Maximum HVDC Flow : |  | 801 | MW at | 16:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.58 |  | (b) Today: | 84.6 |  | (c) Rule Curve: |  | 88.16
.

## YesterdayGen
2021-07-26
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 0 | 92 | 0 | 398 | 348 |  | 0 | 240 | 263 | 0 | 0 | 0 | 333 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 14 | 25 | 9 | 25 | 24 | 16 | 0 | 65 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 23 | 0 | 0 | 0 | 94 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 270 | 215 | 45 | 137 | 20 | 56 | 0 | 43 | 0 | 0 | 16 | 22 | 0 | 33 | 21 | 136 | 204 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 183 | 62 | 84 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 46 | 0 | 20 | 100 | 100 | 366 | 107 | 0 | 105 | 0 | 0 | 0 | 110 | 0 | 107 | 10 | 398 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 43 | 33 | 22 | 0 | 11 | 72 | 0 | 152 | 0 | 0 | 0 | 0 | 159 | 0 | 85 | 60 | 146 | 0 | 319 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 470 | 219 | 0 | 90 | 0 |  | 7060 | 3607 | 10667 | 4800 | 786 | 1975 | 2086 | 694 | 125 | 65 | 136 | 0 | 0 | 84.57
2:00 | 0 | 0 | 0 | 110 | 0 | 92 | 0 | 398 | 345 |  | 0 | 240 | 254 | 0 | 0 | 0 | 334 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 14 | 25 | 9 | 25 | 24 | 0 | 0 | 63 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 96 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 270 | 215 | 45 | 137 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 0 | 33 | 21 | 134 | 204 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 182 | 62 | 84 | 0 | 218 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 25 | 0 | 0 | 100 | 50 | 367 | 107 | 0 | 105 | 0 | 0 | 0 | 110 | 0 | 106 | 0 | 398 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 786 | 0 | 400 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 33 | 22 | 0 | 11 | 77 | 0 | 151 | 0 | 0 | 0 | 0 | 158 | 0 | 86 | 10 | 145 | 0 | 332 | 105 | 0 | 94 | 0 | 97 | 0 | 0 | 70 | 470 | 219 | 0 | 54 | 0 |  | 6867 | 3479 | 10346 | 4799 | 786 | 1981 | 1777 | 698 | 123 | 48 | 134 | 0 | 0 | 84.57
3:00 | 0 | 0 | 0 | 110 | 0 | 92 | 0 | 398 | 341 |  | 0 | 240 | 267 | 0 | 0 | 0 | 335 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 9 | 25 | 24 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 81 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 270 | 215 | 45 | 138 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 130 | 204 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 181 | 61 | 84 | 0 | 218 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 17 | 0 | 0 | 68 | 50 | 366 | 107 | 0 | 85 | 0 | 0 | 0 | 110 | 0 | 65 | 0 | 395 | 0 | 0 | 0 | 90 | 0 | 17 | 0 |  | 794 | 0 | 400 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 77 | 0 | 150 | 0 | 0 | 0 | 0 | 159 | 0 | 86 | 0 | 146 | 0 | 341 | 105 | 0 | 94 | 0 | 97 | 0 | 0 | 0 | 420 | 219 | 0 | 35 | 0 |  | 6735 | 3352 | 10087 | 4810 | 794 | 1986 | 1557 | 647 | 120 | 43 | 130 | 0 | 0 | 84.57
4:00 | 0 | 0 | 0 | 110 | 0 | 92 | 0 | 398 | 341 |  | 0 | 240 | 272 | 0 | 0 | 0 | 335 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 9 | 25 | 24 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 50 | 0 | 21 | 42 | 100 | 0 | 0 | 275 | 270 | 216 | 45 | 135 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 128 | 205 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 182 | 61 | 84 | 0 | 218 | 18 | 0 | 9 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 15 | 0 | 0 | 68 | 50 | 366 | 107 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 65 | 0 | 401 | 0 | 0 | 0 | 90 | 0 | 17 | 0 |  | 794 | 0 | 400 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 33 | 22 | 0 | 11 | 77 | 0 | 151 | 0 | 0 | 0 | 0 | 160 | 0 | 85 | 0 | 147 | 0 | 315 | 70 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 420 | 218 | 0 | 35 | 0 |  | 6684 | 3261 | 9945 | 4819 | 794 | 1958 | 1418 | 648 | 117 | 63 | 128 | 0 | 0 | 84.57
5:00 | 0 | 0 | 0 | 110 | 0 | 92 | 0 | 398 | 342 |  | 0 | 240 | 260 | 0 | 0 | 0 | 333 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 25 | 24 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 31 | 0 | 21 | 42 | 100 | 0 | 0 | 290 | 285 | 214 | 45 | 136 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 205 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 182 | 61 | 10 | 0 | 218 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 15 | 0 | 0 | 68 | 0 | 377 | 107 | 0 | 17 | 0 | 0 | 0 | 85 | 0 | 65 | 0 | 396 | 0 | 0 | 0 | 90 | 0 | 17 | 0 |  | 794 | 0 | 400 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 26 | 22 | 0 | 11 | 77 | 0 | 150 | 0 | 0 | 0 | 0 | 171 | 0 | 85 | 0 | 158 | 0 | 347 | 70 | 0 | 70 | 0 | 70 | 0 | 0 | 0 | 370 | 219 | 0 | 0 | 0 |  | 6481 | 3196 | 9677 | 4857 | 794 | 1923 | 1207 | 597 | 117 | 56 | 126 | 0 | 0 | 84.58
6:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 398 | 341 |  | 0 | 240 | 254 | 0 | 0 | 0 | 336 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 25 | 24 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 7 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 270 | 216 | 16 | 136 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 206 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 183 | 61 | 10 | 0 | 218 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 15 | 0 | 0 | 51 | 0 | 366 | 107 | 0 | 17 | 0 | 0 | 0 | 51 | 0 | 65 | 0 | 400 | 0 | 2 | 0 | 90 | 0 | 17 | 2 |  | 794 | 0 | 370 | 0 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 26 | 22 | 0 | 11 | 77 | 0 | 150 | 0 | 0 | 0 | 0 | 158 | 0 | 52 | 0 | 146 | 0 | 316 | 17 | 0 | 35 | 0 | 52 | 0 | 0 | 0 | 320 | 219 | 0 | 0 | 0 |  | 5995 | 2889 | 8884 | 4746 | 794 | 1631 | 891 | 547 | 118 | 41 | 112 | 4 | 0 | 84.58
7:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 369 | 308 |  | 0 | 240 | 263 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 25 | 24 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 35 | 80 | 0 | 0 | 260 | 270 | 215 | 16 | 137 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 205 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 183 | 61 | 10 | 0 | 164 | 18 | 0 | 9 | 280 | 16 | 5 | 0 | 0 | 0 | 0 | 50 | 0 | 15 | 1 | 0 | 17 | 0 | 366 | 115 | 0 | 17 | 0 | 0 | 0 | 51 | 0 | 65 | 0 | 398 | 0 | 3 | 0 | 90 | 0 | 17 | 5 |  | 794 | 0 | 340 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 77 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 52 | 0 | 147 | 0 | 339 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 320 | 220 | 0 | 0 | 0 |  | 5742 | 2781 | 8523 | 4532 | 794 | 1609 | 774 | 547 | 119 | 30 | 108 | 10 | 0 | 84.58
8:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 352 | 308 |  | 0 | 240 | 262 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 9 | 25 | 24 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 270 | 215 | 16 | 136 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 0 | 0 | 102 | 207 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 180 | 61 | 10 | 0 | 164 | 18 | 0 | 9 | 285 | 16 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 3 | 0 | 17 | 0 | 342 | 115 | 0 | 17 | 1 | 0 | 0 | 51 | 0 | 65 | 0 | 380 | 0 | 9 | 0 | 90 | 0 | 17 | 9 |  | 794 | 0 | 340 | 0 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 76 | 0 | 149 | 0 | 0 | 0 | 0 | 140 | 0 | 0 | 0 | 145 | 0 | 324 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 320 | 220 | 0 | 0 | 1 |  | 5620 | 2702 | 8322 | 4412 | 794 | 1553 | 748 | 545 | 119 | 25 | 102 | 24 | 0 | 84.58
9:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 352 | 307 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 42 | 80 | 0 | 0 | 290 | 300 | 210 | 16 | 137 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 20 | 0 | 104 | 204 | 8 | 21 | 1 | 44 | 43 | 11 | 0 | 0 | 182 | 60 | 10 | 0 | 164 | 18 | 0 | 0 | 300 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 15 | 8 | 0 | 17 | 0 | 348 | 115 | 0 | 17 | 2 | 0 | 0 | 51 | 0 | 65 | 0 | 350 | 0 | 17 | 0 | 90 | 0 | 17 | 11 |  | 794 | 0 | 340 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 73 | 0 | 150 | 0 | 0 | 0 | 0 | 147 | 0 | 48 | 0 | 149 | 0 | 347 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 0 | 320 | 218 | 0 | 0 | 1 |  | 5725 | 2810 | 8535 | 4484 | 794 | 1626 | 765 | 543 | 122 | 55 | 104 | 42 | 0 | 84.58
10:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 353 | 306 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 6 | 0 | 21 | 42 | 80 | 0 | 0 | 280 | 290 | 211 | 16 | 138 | 20 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 201 | 8 | 21 | 1 | 44 | 43 | 11 | 0 | 0 | 180 | 60 | 10 | 0 | 165 | 18 | 0 | 9 | 310 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 5 | 0 | 17 | 0 | 330 | 115 | 0 | 17 | 4 | 0 | 0 | 51 | 0 | 65 | 0 | 350 | 0 | 37 | 0 | 90 | 0 | 17 | 21 |  | 794 | 0 | 340 | 0 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 72 | 0 | 149 | 0 | 0 | 0 | 0 | 179 | 0 | 52 | 0 | 176 | 0 | 347 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 320 | 218 | 0 | 0 | 5 |  | 5771 | 2874 | 8645 | 4529 | 794 | 1644 | 766 | 541 | 122 | 65 | 108 | 76 | 0 | 84.58
11:00 | 0 | 0 | 0 | 110 | 0 | 22 | 0 | 354 | 306 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 36 | 80 | 0 | 0 | 280 | 290 | 210 | 16 | 137 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 200 | 8 | 19 | 1 | 44 | 43 | 14 | 0 | 0 | 177 | 60 | 10 | 0 | 165 | 18 | 0 | 8 | 315 | 8 | 8 | 0 | 0 | 0 | 0 | 24 | 0 | 16 | 6 | 0 | 17 | 0 | 390 | 115 | 0 | 17 | 5 | 0 | 0 | 51 | 0 | 65 | 0 | 350 | 0 | 32 | 0 | 90 | 0 | 17 | 7 |  | 794 | 0 | 340 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 0 | 79 | 0 | 145 | 0 | 0 | 0 | 0 | 182 | 0 | 52 | 0 | 179 | 0 | 347 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 320 | 219 | 0 | 0 | 3 |  | 5801 | 2837 | 8638 | 4591 | 794 | 1646 | 760 | 544 | 122 | 20 | 104 | 57 | 0 | 84.58
12:00 | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 354 | 340 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 305 | 335 | 210 | 36 | 138 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 199 | 8 | 19 | 2 | 44 | 43 | 14 | 0 | 0 | 179 | 60 | 10 | 0 | 219 | 18 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 5 | 0 | 17 | 0 | 373 | 115 | 0 | 17 | 2 | 0 | 0 | 51 | 0 | 65 | 0 | 350 | 0 | 39 | 0 | 92 | 0 | 17 | 30 |  | 794 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 0 | 75 | 0 | 147 | 0 | 0 | 0 | 0 | 200 | 0 | 54 | 0 | 199 | 0 | 388 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 320 | 218 | 0 | 0 | 5 |  | 6042 | 2960 | 9002 | 4851 | 794 | 1743 | 746 | 542 | 122 | 10 | 108 | 86 | 0 | 84.58
13:00 | 0 | 0 | 0 | 170 | 0 | 75 | 0 | 371 | 340 |  | 0 | 240 | 275 | 0 | 0 | 0 | 300 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 5 | 3 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 64 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 300 | 305 | 209 | 36 | 137 | 23 | 10 | 0 | 20 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 118 | 199 | 8 | 19 | 2 | 44 | 43 | 31 | 0 | 0 | 178 | 60 | 84 | 0 | 192 | 18 | 0 | 10 | 305 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 6 | 10 | 17 | 1 | 367 | 115 | 0 | 17 | 5 | 0 | 0 | 34 | 0 | 65 | 10 | 350 | 0 | 43 | 10 | 97 | 0 | 17 | 18 |  | 800 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 0 | 74 | 0 | 155 | 0 | 0 | 0 | 0 | 200 | 0 | 78 | 0 | 196 | 0 | 400 | 5 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 340 | 217 | 0 | 0 | 5 |  | 6259 | 3030 | 9289 | 4881 | 800 | 1932 | 773 | 569 | 124 | 10 | 118 | 82 | 0 | 84.59
14:00 | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 399 | 342 |  | 0 | 240 | 245 | 0 | 0 | 0 | 300 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 100 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 100 | 0 | 0 | 300 | 305 | 211 | 36 | 130 | 23 | 30 | 0 | 32 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 126 | 199 | 8 | 21 | 2 | 44 | 43 | 47 | 0 | 0 | 179 | 60 | 82 | 0 | 191 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 2 | 50 | 17 | 26 | 367 | 115 | 0 | 19 | 4 | 0 | 0 | 41 | 0 | 65 | 30 | 350 | 0 | 21 | 35 | 97 | 0 | 17 | 22 |  | 792 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 21 | 0 | 0 | 73 | 0 | 155 | 0 | 0 | 21 | 0 | 199 | 0 | 81 | 0 | 190 | 0 | 347 | 35 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 370 | 216 | 0 | 0 | 5 |  | 6423 | 3068 | 9491 | 4916 | 792 | 1921 | 947 | 598 | 122 | 10 | 126 | 59 | 0 | 84.59
15:00 | 0 | 0 | 0 | 170 | 0 | 86 | 0 | 396 | 338 |  | 0 | 240 | 275 | 0 | 0 | 0 | 300 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 3 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 100 | 0 | 0 | 260 | 295 | 186 | 36 | 139 | 23 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 108 | 196 | 8 | 21 | 1 | 43 | 43 | 47 | 0 | 0 | 174 | 60 | 82 | 0 | 191 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 8 | 2 | 50 | 17 | 60 | 332 | 115 | 0 | 45 | 2 | 0 | 0 | 68 | 0 | 65 | 10 | 350 | 16 | 26 | 17 | 97 | 0 | 17 | 10 |  | 800 | 0 | 385 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 0 | 73 | 0 | 157 | 0 | 0 | 92 | 0 | 176 | 0 | 82 | 0 | 180 | 0 | 376 | 35 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 390 | 216 | 0 | 0 | 2 |  | 6482 | 3173 | 9655 | 4860 | 800 | 1956 | 1133 | 620 | 122 | 10 | 108 | 46 | 0 | 84.59
16:00 | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 397 | 332 |  | 0 | 240 | 260 | 0 | 0 | 0 | 300 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 14 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 100 | 0 | 0 | 260 | 290 | 182 | 36 | 135 | 23 | 30 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 106 | 199 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 178 | 60 | 82 | 0 | 191 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 34 | 0 | 10 | 17 | 10 | 330 | 115 | 0 | 17 | 0 | 0 | 0 | 68 | 0 | 81 | 10 | 350 | 0 | 18 | 0 | 97 | 0 | 17 | 8 |  | 801 | 0 | 385 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 0 | 0 | 156 | 0 | 0 | 90 | 0 | 167 | 0 | 83 | 0 | 175 | 0 | 347 | 0 | 0 | 0 | 0 | 33 | 0 | 3 | 0 | 400 | 216 | 0 | 0 | 1 |  | 6339 | 3019 | 9358 | 4837 | 801 | 1937 | 939 | 556 | 122 | 30 | 106 | 30 | 0 | 84.59
17:00 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 391 | 302 |  | 0 | 240 | 275 | 0 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 20 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 290 | 182 | 8 | 137 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 100 | 197 | 0 | 21 | 0 | 43 | 43 | 14 | 0 | 0 | 178 | 40 | 10 | 0 | 191 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 40 | 0 | 34 | 0 | 10 | 17 | 0 | 305 | 115 | 0 | 17 | 1 | 16 | 0 | 51 | 0 | 104 | 10 | 320 | 0 | 7 | 0 | 106 | 0 | 17 | 4 |  | 800 | 0 | 350 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 70 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 16 | 0 | 21 | 0 | 0 | 0 | 0 | 151 | 0 | 0 | 88 | 0 | 166 | 0 | 34 | 0 | 174 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 340 | 184 | 0 | 0 | 0 |  | 5853 | 2790 | 8643 | 4643 | 800 | 1558 | 883 | 491 | 120 | 34 | 100 | 14 | 0 | 84.59
18:00 | 0 | 0 | 0 | 170 | 0 | 33 | 0 | 318 | 242 |  | 0 | 240 | 275 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 25 | 7 | 25 | 24 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 270 | 300 | 190 | 8 | 136 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 86 | 198 | 0 | 21 | 0 | 43 | 43 | 14 | 0 | 0 | 177 | 40 | 10 | 0 | 164 | 18 | 0 | 10 | 280 | 16 | 0 | 0 | 4 | 0 | 0 | 40 | 0 | 34 | 0 | 10 | 17 | 0 | 314 | 115 | 0 | 17 | 0 | 16 | 0 | 51 | 0 | 104 | 10 | 320 | 0 | 3 | 0 | 116 | 0 | 17 | 1 |  | 800 | 0 | 300 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 0 | 0 | 70 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 0 | 0 | 0 | 155 | 0 | 0 | 70 | 0 | 160 | 0 | 34 | 0 | 159 | 0 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 142 | 0 | 0 | 0 |  | 5650 | 2515 | 8165 | 4415 | 800 | 1378 | 901 | 425 | 120 | 35 | 86 | 5 | 0 | 84.59
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 50 | 0 | 310 | 288 |  | 0 | 240 | 260 | 0 | 0 | 8 | 280 | 0 | 36 | 0 | 16 | 48 | 10 | 0 | 0 | 0 | 54 | 17 | 20 | 19 | 25 | 7 | 25 | 24 | 40 | 0 | 60 | 60 | 100 | 120 | 6 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 8 | 21 | 42 | 80 | 0 | 0 | 280 | 310 | 196 | 8 | 137 | 20 | 10 | 0 | 20 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 120 | 198 | 5 | 21 | 0 | 44 | 43 | 32 | 0 | 0 | 179 | 60 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 0 | 0 | 17 | 0 | 0 | 79 | 0 | 34 | 0 | 50 | 24 | 30 | 398 | 106 | 13 | 36 | 0 | 16 | 0 | 56 | 17 | 105 | 50 | 335 | 11 | 0 | 14 | 116 | 0 | 0 | 0 |  | 791 | 0 | 350 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 75 | 0 | 0 | 17 | 16 | 40 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 81 | 0 | 148 | 0 | 75 | 1 | 147 | 0 | 336 | 26 | 0 | 20 | 0 | 85 | 0 | 0 | 50 | 300 | 216 | 0 | 19 | 0 |  | 6569 | 3115 | 9684 | 4705 | 791 | 1755 | 1475 | 452 | 120 | 266 | 120 | 0 | 0 | 84.6
19:30 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 391 | 343 |  | 0 | 240 | 245 | 0 | 0 | 15 | 280 | 0 | 32 | 0 | 16 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 7 | 25 | 24 | 51 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 14 | 21 | 42 | 80 | 0 | 0 | 260 | 290 | 181 | 8 | 136 | 23 | 54 | 0 | 43 | 0 | 0 | 37 | 22 | 11 | 25 | 21 | 120 | 202 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 181 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 270 | 16 | 5 | 0 | 75 | 0 | 0 | 195 | 0 | 70 | 0 | 100 | 100 | 65 | 367 | 106 | 0 | 105 | 0 | 16 | 0 | 85 | 17 | 108 | 50 | 385 | 20 | 0 | 54 | 116 | 0 | 17 | 0 |  | 791 | 0 | 370 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 27 | 16 | 34 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 105 | 0 | 183 | 0 | 77 | 100 | 150 | 0 | 381 | 105 | 0 | 91 | 0 | 113 | 0 | 0 | 70 | 420 | 217 | 0 | 90 | 0 |  | 7362 | 3758 | 11120 | 4834 | 791 | 1965 | 2426 | 576 | 121 | 287 | 120 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 389 | 345 |  | 0 | 240 | 254 | 0 | 0 | 15 | 300 | 0 | 57 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 25 | 9 | 25 | 24 | 51 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 9 | 21 | 42 | 80 | 0 | 0 | 260 | 290 | 212 | 8 | 130 | 23 | 45 | 0 | 43 | 0 | 0 | 32 | 22 | 11 | 25 | 21 | 134 | 202 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 181 | 61 | 84 | 0 | 219 | 18 | 0 | 10 | 280 | 16 | 5 | 0 | 15 | 0 | 0 | 187 | 0 | 60 | 0 | 100 | 84 | 65 | 367 | 106 | 0 | 102 | 0 | 0 | 0 | 105 | 17 | 107 | 50 | 396 | 29 | 0 | 35 | 116 | 0 | 14 | 0 |  | 792 | 0 | 370 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 39 | 43 | 33 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 108 | 0 | 184 | 0 | 84 | 80 | 152 | 0 | 387 | 105 | 0 | 87 | 0 | 113 | 0 | 0 | 70 | 440 | 219 | 0 | 90 | 0 |  | 7333 | 3793 | 11126 | 4918 | 792 | 1983 | 2305 | 595 | 121 | 278 | 134 | 0 | 0 | 84.6
21:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 392 | 343 |  | 0 | 240 | 280 | 0 | 0 | 0 | 326 | 0 | 91 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 9 | 25 | 24 | 42 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 285 | 310 | 209 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 138 | 199 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 177 | 60 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 197 | 0 | 70 | 0 | 100 | 100 | 65 | 382 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 110 | 50 | 386 | 17 | 0 | 17 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 30 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 116 | 0 | 192 | 0 | 82 | 100 | 159 | 0 | 405 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 70 | 480 | 220 | 0 | 90 | 0 |  | 7429 | 3925 | 11354 | 5088 | 791 | 2018 | 2301 | 635 | 121 | 262 | 138 | 0 | 0 | 84.6
22:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 398 | 344 |  | 0 | 240 | 275 | 0 | 0 | 0 | 327 | 0 | 92 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 9 | 25 | 24 | 43 | 0 | 62 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 51 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 275 | 295 | 210 | 8 | 137 | 23 | 54 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 128 | 199 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 179 | 60 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 70 | 0 | 100 | 100 | 65 | 380 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 111 | 50 | 388 | 17 | 0 | 17 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 30 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 124 | 0 | 196 | 0 | 82 | 100 | 174 | 0 | 414 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 500 | 220 | 0 | 90 | 0 |  | 7419 | 4000 | 11419 | 5101 | 791 | 2040 | 2310 | 655 | 122 | 272 | 128 | 0 | 0 | 84.6
23:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 400 | 345 |  | 0 | 240 | 267 | 0 | 0 | 0 | 331 | 0 | 92 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 9 | 25 | 24 | 51 | 0 | 63 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 2 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 211 | 8 | 136 | 23 | 54 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 25 | 21 | 126 | 201 | 8 | 21 | 0 | 44 | 43 | 50 | 0 | 0 | 178 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 190 | 0 | 58 | 0 | 100 | 100 | 65 | 365 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 109 | 50 | 391 | 17 | 0 | 17 | 116 | 0 | 17 | 0 |  | 792 | 0 | 400 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 30 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 120 | 0 | 189 | 0 | 85 | 40 | 177 | 0 | 411 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 500 | 220 | 0 | 90 | 0 |  | 7265 | 3989 | 11254 | 5055 | 792 | 2041 | 2199 | 656 | 123 | 262 | 126 | 0 | 0 | 84.6
24:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 400 | 346 |  | 0 | 240 | 260 | 0 | 0 | 0 | 334 | 0 | 92 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 0 | 0 | 19 | 25 | 9 | 25 | 24 | 51 | 0 | 64 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 212 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 124 | 203 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 181 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 36 | 0 | 100 | 100 | 65 | 366 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 115 | 50 | 400 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 792 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 30 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 119 | 0 | 189 | 0 | 84 | 0 | 178 | 0 | 405 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 500 | 220 | 0 | 90 | 0 |  | 7184 | 3980 | 11164 | 5088 | 792 | 2026 | 2061 | 654 | 124 | 295 | 124 | 0 | 0 | 84.6
KWH | 0 | 0 | 0 | 3433500 | 0 | 1522181 | 0 | 9216000 | 7840000 |  | 0 | 5640500 | 6474124 | 0 | 0 | 29677 | 7333240 | 0 | 1436000 | 0 | 23904 | 180960 | 13493 | 0 | 0 | 0 | 741960 | 203076 | 204116 | 278136 | 600000 | 226440 | 730100 | 706500 | 291840 | 0 | 1398638 | 1452000 | 2300000 | 2900000 | 40096 | 0 | 0 | 2900018 | 0 |  | 237840 | 0 | 242300 | 0 | 387840 | 22560 | 482544 | 1087200 | 2184806 | 0 | 0 | 6977100 | 6977000 | 4994000 | 602181 | 3240100 | 490320 | 828000 | 0 | 766068 | 0 | 0 | 214930 | 499140 | 251100 | 732200 | 472450 | 2834880 | 4754160 | 163200 | 461124 | 11650 | 103000 | 1005480 | 805200 | 0 | 0 | 3981000 | 1424832 | 1225920 | 0 | 4777460 | 388000 | 0 | 210780 | 7169000 | 341256 | 210144 | 0 | 82799 | 0 | 0 | 2736000 | 0 | 692640 | 36855 | 689280 | 1251360 | 821309 | 8627000 | 2647200 | 27600 | 1282145 | 27480 | 55200 | 0 | 1939525 | 116280 | 2084040 | 379200 | 8917100 | 137280 | 245490 | 239040 | 2470200 | 0 | 433440 | 171760 |  | 19192000 | 0 | 9209376 | 0 | 0 | 738240 | 0 | 0 | 0 | 0 | 0 | 0 | 648350 | 0 | 0 | 1688000 | 0 | 0 | 36390 | 505224 | 0 | 0 | 145925 | 680160 | 392000 | 499440 | 0 | 161928 | 1194327 | 0 | 3746700 | 0 | 0 | 1108000 | 0 | 4356118 | 0 | 1626794 | 523200 | 4214236 | 0 | 8497873 | 1196160 | 0 | 1020288 | 0 | 1527436 | 0 | 28774 | 612672 | 10258700 | 5138618 | 0 | 700800 | 30240 |  | 155783487 | 79677969 | 235461456 | 115088908 | 19192000 | 44108105 | 33393910 | 15199727 | 2850638 | 2241039 | 2834880 | 552249 | 0
Fuel Cost | 0 | 0 | 0 | 5047245 | 0 | 2009278.92 | 0 | 9308160 | 8075200 |  | 0 | 6148145 | 7186277.64 | 0 | 0 | 251067.42 | 7626569.6 | 0 | 2484280 | 0 | 218004.48 | 1780646.4 | 124405.46 | 0 | 0 | 0 | 5416308 | 1569777.48 | 2012583.76 | 208602 | 450000 | 0 | 0 | 0 | 2822092.8 | 0 | 377632.26 | 392040 | 4163000 | 5249000 | 372491.84 | 0 | 0 | 4930030.6 | 0 |  | 0 | 0 | 2350310 | 0 | 3374208 | 178675.2 | 608005.44 | 3228984 | 3233512.88 | 0 | 0 | 5163054 | 6977000 | 4594480 | 776813.49 | 3726115 | 554061.6 | 1159200 | 0 | 1309976.28 | 0 | 0 | 2052581.5 | 633907.8 | 188325 | 1281350 | 354337.5 | 21261600 | 5039409.6 | 1481856 | 585627.48 | 185701 | 168920 | 1608768 | 1433256 | 0 | 0 | 4140240 | 2806919.04 | 2341507.2 | 0 | 8265005.8 | 849720 | 0 | 429991.2 | 7240690 | 255942 | 159709.44 | 0 | 625960.44 | 0 | 0 | 14227200 | 0 | 6815577.6 | 430834.95 | 5617632 | 13577256 | 5790228.45 | 8023110 | 24142464 | 260820 | 11167482.95 | 0 | 417312 | 0 | 17048424.75 | 1160474.4 | 17860222.8 | 2525472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110545920 | 0 | 9669844.8 | 0 | 0 | 10232006.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1004942.5 | 0 | 0 | 3460400 | 0 | 0 | 369722.4 | 4471232.4 | 0 | 0 | 1414013.25 | 6590750.4 | 3802400 | 958924.8 | 0 | 122579.496 | 7201791.81 | 0 | 20307114 | 0 | 0 | 1296360 | 0 | 5750075.76 | 0 | 2440191 | 8899632 | 4930656.12 | 0 | 8412894.27 | 12487910.4 | 0 | 9682533.12 | 0 | 11852903.36 | 0 | 317952.7 | 4527646.08 | 45035693 | 0 | 0 | 0 | 0 |  | 307913071.45 | 295786090.066 | 603699161.516 | 123914323.956 | 110545920 | 46969994.66 | 202338232.33 | 72544598.81 | 769672.26 | 24420330.85 | 21261600 | 934488.65 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 354 | 340 |  | 0 | 240 | 280 | 0 | 0 | 0 | 270 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 7 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 305 | 335 | 210 | 36 | 138 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 199 | 8 | 19 | 2 | 44 | 43 | 14 | 0 | 0 | 179 | 60 | 10 | 0 | 219 | 18 | 0 | 10 | 305 | 8 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 5 | 0 | 17 | 0 | 373 | 115 | 0 | 17 | 2 | 0 | 0 | 51 | 0 | 65 | 0 | 350 | 0 | 39 | 0 | 92 | 0 | 17 | 30 |  | 794 | 0 | 390 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 0 | 75 | 0 | 147 | 0 | 0 | 0 | 0 | 200 | 0 | 54 | 0 | 199 | 0 | 388 | 0 | 0 | 0 | 0 | 35 | 0 | 3 | 0 | 320 | 218 | 0 | 0 | 5 |  | 9002 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 392 | 343 | 0 | 0 | 240 | 280 | 0 | 0 | 0 | 326 | 0 | 91 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 9 | 25 | 24 | 42 | 0 | 61 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 51 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 285 | 310 | 209 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 138 | 199 | 8 | 21 | 0 | 44 | 43 | 47 | 0 | 0 | 177 | 60 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 197 | 0 | 70 | 0 | 100 | 100 | 65 | 382 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 110 | 50 | 386 | 17 | 0 | 17 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 30 | 43 | 32 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 116 | 0 | 192 | 0 | 82 | 100 | 159 | 0 | 405 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 70 | 480 | 220 | 0 | 90 | 0 |  | 11354 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 412 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 90 | 0 | 102 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 10 | 25 | 24 | 52 | 0 | 61 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 42 | 80 | 0 | 0 | 270 | 360 | 210 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 22 | 162 | 202 | 8 | 21 | 0 | 44 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 400 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 801 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 0 | 0 | 30 | 43 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 120 | 0 | 200 | 0 | 82 | 100 | 200 | 0 | 400 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 90
Forecast for Day | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 360 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 60 | 0 | 100 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 25 | 20 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 30 | 80 | 0 | 0 | 270 | 360 | 210 | 8 | 130 | 20 | 55 | 0 | 42 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 138 | 202 | 8 | 21 | 1.6 | 43 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 16 | 11 | 100 | 270 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 400 | 90 | 50 | 162 | 112 | 0 | 17 | 30 |  | 801 | 0 | 360 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 0 | 0 | 30 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 200 | 0 | 80 | 50 | 200 | 0 | 400 | 105 | 100 | 90 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 90 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 0 | 54 | 0 | 306 | 278 | 0 | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 |  | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 180 | 8 | 134 | 23 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 84 | 203 | 0 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 183 | 40 | 10 | 0 | 151 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 319 | 115 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 8 | 10 | 200 | 0 | 15 | 0 | 35 | 0 | 17 | 11 | 0 | 801 | 0 | 320 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 70 | 0 | 130 | 0 | 22 | 0 | 180 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 8322 | 8:00
| Highest Generation |  | 11419 | 22:00
| Day Peak Generation |  | 9002 | 12:00
| Evening Peak Generation |  | 11354 | 21:00
| HVDC Max Flow |  | 801 | 16:00
| HVDC EvPeak Flow |  | 791 | 21:00
| Load factor L.F |  | 85.92%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-27
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-26 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9002 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8171 | MW
Evening Peak Generation : |  | 11354 | MW Hour : | 21:00 | Available Max Generation : |  | 15430 | MW
E.P. Demand (at gen end) : |  | 11354 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11500 | MW
Maximum Generation : |  | 11419 | MW Hour : | 22:00 | Reserve(Generation end) |  | 3930 | MW
Total Gen. (MKWH) : |  | 235.4615 | System Load Factor : | 85.92% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -462 | MW at | 3:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-27
Actual : | 84.6 | Ft.(MSL) , | Rule curve : | 88.16 | Ft.( MSL )
Gas Consumed : | Total = | 1266.14 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 170884318.616
: |  | Coal : | 72544598.81 | Oil : | 226758563.18 | Total : | 470187480.606
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4092.6888 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1392.7901 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1248.0808 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1127.8126 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1019.1514 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 822.4217 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 458.5073 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 211.7157 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 634.2989 |  |  | 0 | 0%
Total | 0 |  | 11007.4674 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4 & 7
3) Ashuganj-4 & 5
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Khulna©-Khulna-225 MW P/S 132 kV Ckt-2 was under shut down from 09:18 to 10:37 due to red hot
maintenance work.
b) Siddirganj GT-1 synchronized at 13:28.
c) Aminbazar-Kallyanpur 132 kV Ckt-1 was under shut down from 13:40 to 17:08 for C/M.
d) Kabirpur 132/33 kV T-3 transformer was under shut down from 11:49 to 13:33 for C/M.
e) Barapukuria #1 was shut down at 15:50 due to boiler tube leakage.
f) Fenchuganj-Kulaura 132 kV Ckt-2 was under shut down from 14:18 to 15:13 due to red hot maintenance
at line DS R-phase at Kulaura end.
g) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 19:45 showing dist.Z2 at Dohazari end & dist.Z1,3-phase
at Cox'sbazar end and was switched on at 20:34.
h) Barishal(N) 132/33 kV T-4 & T-5 transformers tripped at 16:09 due to LT bus PT Y-phase burst and |  |  |  |  | About 32 MW power interruption occurred under Barishal S/S area
were switched on at 17:30. |  |  |  |  | from 16:09 to 17:30.
i) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 21:40 showing dist.Z2 at Dohazari end & dist.Z1,3-phase
at Cox'sbazar end and was switched on at 22:35.Again tripped at 03:01(27/7/21) showing same reason.
j) Khulna-225 MW CCPP ST was synchronized at 22:13.
k) Bibiyana(S)-400 MW CCPP ST was shut down at 01:15(27/7/21) for minor inspection.
l) Kishorganj 132/33 kV T-3 transformer & 33 kV bus were shut down from 07:08 to 09:53 for C/M. |  |  |  |  | About 30 MW power interruption occurred under Kishorganj S/S area
from 07:08 to 09:53.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-26 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 3433500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 95 | 1522181 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 392 | 9216000 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 343 | 7840000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5640500 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6474124 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 29677 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 13493 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 278136 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 91 | 1436000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7333240
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 23904 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 741960
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 180960 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 17 | 203076 | Low demand
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 17 | 204116 | Low demand
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 34 | 826440 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 730100 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 706500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 291840 | Engine problem
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 82799 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 70 | 692640 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 27600 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 17 | 137280 | Low demand
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 17 | 239040 | Low demand
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 171760
| Dhaka area Total |  |  |  | 5819 | 2305 | 48476866
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 40096 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 36855
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 22560 | Reserve.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 121 | 2850638 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2900018 | Machine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 1282145
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 242300 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 689280
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 482544
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 1087200
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 387840 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 27480
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 55200 | Reserve.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1939525
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 379200 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2470200
| Chattogram area Total |  |  |  | 2382 | 1064 | 20093081
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 2184806 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Under maint.
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 209 | 4994000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 285 | 6977100 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 6977000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 490320 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 828000
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 602181 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 766068 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 65 | 821309 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 136 | 3240100 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 100 | 1251360 | Low demand
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 499140
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 251100
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 138 | 2834880
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 732200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 214930 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 472450 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 17 | 116280 | Low demand
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 110 | 2084040 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 433440 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1718 | 36770704
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 199 | 4754160
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 461124
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 163200 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11650
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 197 | 2736000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 2647200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 245490
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 237840
| Mymensingh Area Total |  |  |  | 709 | 555 | 11256664
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 103000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1005480 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 177 | 3981000 | GT-1 under maint
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 805200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210144
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 60 | 1424832 | Engine problem
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1225920
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4777460
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 388000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 341256 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7169000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 382 | 8627000 | FGMO
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 210780
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 386 | 8917100
| Sylhet Area Total |  |  |  | 2377 | 1787 | 39186172
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 791 | 19192000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 20 | 738240 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 9209376
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 523200
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1196160
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1416 | 30858976
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 648350
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 82 | 1626794 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 10258700
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 5138618
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 90 | 700800 | Low demand
| Barisal Area Total |  |  |  | 2046 | 904 | 18373262
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1688000 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 5 | 36390 | Low demand
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 145925 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 116 | 1108000 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 192 | 4356118 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 159 | 4214236 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 405 | 8497873 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 32 | 392000 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 499440
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 161928
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 680160 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 505224 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 1020288 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 70 | 612672 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 30240
| Rajshahi Area Total |  |  |  | 2179 | 1337 | 23948494
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 1194327 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3746700 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1527436
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28774
| Rangpur Area Total |  |  |  | 605 | 268 | 6497237
| Total |  |  |  | 21280 | 11354 | 235461456
| Eastern Grid Total |  |  |  | 14321 | 7429 | 155783487
| Western Grid Total |  |  |  | 6959 | 3925 | 79677969
| National Grid Total |  |  |  | 21280 | 11354 | 235461456
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-26
(a) ENTIRE EASTERN GRID : |  | 6873 | MW | (b) ENTIRE WESTERN GRID : |  | 3985 | MW
i) Dhaka area |  | 3149 | MW | i) Khulna area |  | 1494 | MW
ii) Chittagong area |  | 921 | MW | ii) Rajshahi area |  | 1295 | MW
iii) Comilla area |  | 1235 | MW | iii) Barisal area |  | 384 | MW
iv) Mymensingh area |  | 1035 | MW | iv) Rangpur area |  | 812 | MW
v) Sylhet area |  | 533 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10858 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 82 | 21:00 | Kishoreganj | 144 | 22:00 | Jessore | 114 | 19:30
Munsiganj | 94 | 22:00 | Netrokona | 130 | 23:00 | Benapol | 56 | 20:00
Sonargaon | 48 | 21:00 | Jamalpur | 157 | 21:00 | Jhenida | 108 | 19:30
Shyampur | 70 | 21:00 | Sherpur | 138 | 22:00 | Bottail | 116 | 20:00
Bhulta | 89 | 21:00 | Srimongal | 64 | 22:00 | G.K Project | 57 | 21:00
Madanganj | 28 | 1:00 | Shahjibazar | 103 | 22:00 | Faridpur | 147 | 22:00
Shitalakhya | 58 | 14:00 | Fenchuganj | 49 | 21:00 | Rajbari | 51 | 20:00
Rahim steel | 0 | 1:00 | Kulawara | 49 | 19:00 | Madaripur | 107 | 21:00
Matuail | 30 | 21:00 | Sylhet | 120 | 19:00 | Sariatpur | 74 | 21:00
Ghorasal | 70 | 21:00 | Chatak | 33 | 21:00 | Gopalganj | 96 | 22:00
Narsingdi | 145 | 23:00 | Sunamganj | 54 | 22:00 | Bagerhat | 95 | 22:00
Haripur (SBU) | 31 | 12:00 | Biani Bazar | 74 | 21:00 | Mongla | 22 | 1:00
Sreenagar | 44 | 21:00 | Comilla (S) | 138 | 21:00 | Satkhira | 104 | 1:00
Ullon | 49 | 21:00 | Comilla(N) | 137 | 22:00 | Gallamari | 29 | 1:00
Hasnabad | 72 | 14:00 | Chandpur | 83 | 21:00 | Magura | 56 | 19:30
Magbazar | 73 | 13:00 | Feni | 129 | 22:00 | Norail | 43 | 21:00
Maniknagar | 64 | 13:00 | Chowmuhani | 142 | 24:00 | Chuadanga | 92 | 21:00
Bangabhaban | 12 | 10:00 | Ashuganj | 42 | 21:00 | Borguna | 18 | 21:00
Motijheel | 20 | 10:00 | Daudkandi | 146 | 22:00 | Barisal(N) | 49 | 22:00
Narinda | 40 | 15:00 | B.Baria | 172 | 23:00 | Barisal (S) | 104 | 21:00
Kazla | 62 | 21:00 | Ramganj | 96 | 23:00 | Patuakhali | 117 | 23:00
Dhanmondi | 126 | 13:00 | Chaddagram | 63 | 23:00 | Bhandaria | 56 | 22:00
Lalbag | 47 | 14:00 | PHP | 9 | 9:00 | Borhan Uddin | 48 | 22:00
Madartek | 72 | 23:00 | Kochua | 66 | 20:00 | Ishurdi | 58 | 21:00
Dhaka University | 18 | 11:00 | Madunaghat | 55 | 20:00 | Ruppur Paromanobik | 3 | 7:00
Aftabnagar | 10 | 21:00 | Hathazari | 88 | 19:00 | Natore | 134 | 21:00
Fatullah | 34 | 23:00 | Khulshi | 105 | 19:00 | Bogra | 143 | 1:00
Nawabganj | 54 | 21:00 | Halishahar | 61 | 18:30 | Noagaon | 116 | 23:00
Keraniganj | 52 | 21:00 | Baraulia | 63 | 23:00 | Rajshahi | 152 | 21:00
Mirpur | 102 | 23:00 | Sikalbaha | 24 | 18:00 | Rajshahi New | 15 | 22:00
Kalyanpur | 105 | 13:00 | Dohazari | 96 | 21:00 | C.Nawabganj | 61 | 20:00
Gulshan | 78 | 13:00 | Cox'sbazar | 81 | 7:00 | Amnura | 54 | 21:00
Uttara | 73 | 19:00 | Chandraghona | 30 | 20:00 | Pabna | 101 | 19:30
Uttara New | 13 | 23:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 95 | 20:00
Kamrangirchar | 61 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 96 | 22:00
Savar | 112 | 14:00 | Bakulia | 87 | 22:00 | Niyamatpur | 83 | 22:00
Bhasantec | 109 | 23:00 | Julda | 14 | 19:00 | Joypurhat | 59 | 21:00
Agargaon | 68 | 23:00 | TK chemical | 29.5 | 22:00 | Sherpur(Bogura) | 52 | 21:00
Satmosjid | 89 | 23:00 | Modern Steel | 0 | #N/A | Mohastangor | 70 | 22:00
Tongi | 76 | 21:00 | Shahmirpur | 18 | 19:30 | Bhangura | 34 | 20:00
Kabirpur | 131 | 21:00 | Khagrachhari | 24 | 21:00 | Rangpur | 128 | 24:00
Basundhara | 190 | 14:00 | Matarbari | 33.5 | 18:30 | Lalmonirhat | 47 | 1:00
Manikganj | 72 | 19:30 | Baroiar Hat | 44 | 19:30 | Saidpur | 99 | 1:00
Joydevpur | 98 | 22:00 | Rangamati | 12 | 18:30 | Purbasadipur | 105 | 21:00
New Tongi | 60 | 13:00 | Abul Khair 230 | 10 | 18:00 | Thakurgaon | 91 | 21:00
Kodda | 131 | 21:00 | BSRM | 5 | 21:00 | Palashbari | 126 | 20:00
Dhamrai | 78 | 21:00 | GPH Ispat | 88 | 16:00 | Barapukuria | 56 | 22:00
Rajendrapur | 80 | 21:00 | Agrabad | 62 | 19:00 | Panchagar | 57 | 20:00
Valuka | 80 | 21:00 | Goalpara | 31 | 13:00 | Joldhaka | 62 | 20:00
Tangail | 218 | 21:00 | Central S/S | 87 | 19:30 | Kurigram | 63 | 19:30
Mymensing | 206 | 19:30 | Noapara | 46 | 19:30 | Mithapukur | 36 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-26 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 404 | 18:30 | 397 | 20:00 | Kaliakoir | 395 | 0.33333 | 385 | 0.54167
| Bheramara | 403 | 19:30 | 394 | 23:00 | Bhulta | 384 | 0.79167 | 378 | 0.91667
| Ashuganj(N) | 390 | 13:00 | 385 | 12:00 | Gopalganj | 410 | 0.625 | 386 | 0.875
| Payra | 414 | 9:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 224 | 19:00 | 220 | 13:00
| Ishurdi | 235 | 18:30 | 226 | 13:00 | Megnaghat | 232 | 8:00 | 230 | 11:00
| Ashuganj | 238 | 18:00 | 235 | 4:00 | Fenchuganj | 237 | 6:00 | 233 | 19:30
| Serajganj | 229 | 18:30 | 225 | 1:00 | Siddhirganj | 233 | 18:30 | 229 | 11:00
| Baghabari | 232 | 18:00 | 225 | 22:00 | Maniknagar | 231 | 18:30 | 227 | 13:00
| Barapukuria | 233 | 18:00 | 223 | 22:00 | Agargaon | 228 | 18:30 | 222 | 13:00
| Bogra | 222 | 18:30 | 212 | 21:00 | Barisal | 242 | 19:00 | 235 | 21:00
| Rajshahi | 233 | 18:00 | 220 | 13:00 | Bhola 225 MW | 244 | 10:00 | 241 | 3:00
| Khulna South | 229 | 18:30 | 213 | 13:00 | AKSML | 225 | 19:00 | 219 | 13:00
| Rampura | 228 | 18:30 | 226 | 13:00 | BSRM | 227 | 18:30 | 223 | 13:00
| Haripur | 230 | 18:30 | 226 | 10:00 | Bibiyana | 238 | 8:00 | 235 | 1:00
| Hasnabad | 228 | 1:00 | 225 | 13:00 | Bhulta | 232 | 18:30 | 227 | 14:00
| Shyampur | 225 | 9:00 | 220 | 13:00 | Ashuganj (S) | 235 | 18:30 | 232 | 6:00
| Aminbazar | 228 | 1:00 | 224 | 2:00 | Kaliakoir | 227 | 6:00 | 215 | 14:00
| Tongi | 228 | 18:00 | 221 | 13:00 | GPH | 225 | 19:00 | 220 | 15:00
| Comilla (N) | 228 | 5:00 | 224 | 24:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 3:00 | 132 | 13:00 | Madanhat | 134 | 0.77083 | 129 | 0.5
| Munsiganj | 136 | 18:30 | 131 | 13:00 | Hathazari | 133 | 0.041667 | 130 | 0.54167
| Sonargaon | 133 | 13:00 | 128 | 3:00 | Khulshi | 131 | 0.083333 | 126 | 0.54167
| Shyampur | 138 | 18:30 | 135 | 12:00 | Halishahar | 133 | 0.8125 | 127 | 0.45833
| Bhulta | 130 | 4:00 | 126 | 23:00 | Baraulia | 132 | 0.083333 | 128 | 0.29167
| Madanganj | 133 | 7:00 | 130 | 14:00 | Sikalbaha | 134 | 0.75 | 127 | 0.54167
| Shitalakhya | 138 | 19:00 | 133 | 13:00 | Dohazari | 132 | 0.8125 | 124 | 0.54167
| Rahim steal | 135 | 18:30 | 133 | 1:00 | Cox'sbazar | 126 | 0.79167 | 115 | 0.54167
| Matuail | 134 | 3:00 | 132 | 13:00 | Chandraghona | 134 | 0.83333 | 129 | 0.54167
| Ghorasal | 137 | 1:00 | 136 | 8:00 | Kaptai | 132 | 0.041667 | 131 | 0.54167
| Narsinghdi | 129 | 7:00 | 123 | 23:00 | A. Khaer Stl. | 132 | 0.8125 | 129 | 0.33333
| Haripur (SBU) | 135 | 8:00 | 133 | 1:00 | Bakulia | 134 | 0.8125 | 127 | 0.54167
| Sreenagar | 130 | 19:00 | 127 | 13:00 | Julda | 135 | 0.79167 | 128 | 0.29167
| Ullon | 135 | 6:00 | 131 | 13:00 | TK Chemical | 133 | 0.79167 | 127 | 0.54167
| Hasnabad | 136 | 18:30 | 134 | 0:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 134 | 5:00 | 130 | 12:00 | Shahmirpur | 135 | 0.8125 | 127 | 0.54167
| Maniknagar | 135 | 7:00 | 132 | 15:00 | Khagrachhari | 132 | 0.875 | 129 | 0.41667
| Bangabhaban | 135 | 7:00 | 132 | 15:00 | Matarbari | 129 | 0.77083 | 118 | 0.20833
| Motijheel | 135 | 7:00 | 132 | 15:00 | Baroiar Hat | 130 | 0.75 | 126 | 0.041667
| Narinda | 135 | 7:00 | 132 | 15:00 | Rangamati | 133 | 19:30 | 129 | 4:00
| Kazla | 135 | 7:00 | 132 | 15:00 | Agrabad | 132 | 19:00 | 126 | 12:00
| Dhanmondi | 135 | 6:00 | 132 | 12:00 | Goalpara S/S | 138 | 18:30 | 130 | 0.5
| Lalbag | 138 | 18:30 | 133 | 14:00 | Khulna Central S/S | 138 | 18:30 | 128 | 0.54167
| Madartek | 135 | 18:30 | 131 | 13:00 | Noapara | 135 | 18:30 | 123 | 0.54167
| Dhaka University | 135 | 6:00 | 132 | 11:00 | Jessore | 131 | 18:30 | 115 | 0.54167
| Aftabnagar | 135 | 5:00 | 131 | 13:00 | Benapol | 132 | 0.77083 | 116 | 0.54167
| Fatullah | 138 | 19:30 | 135 | 12:00 | Jhenida | 127 | 18:30 | 111 | 0.54167
| Nawabganj | 131 | 18:30 | 126 | 0:00 | Bottail | 132 | 0.77083 | 121 | 0.875
| Keraniganj | 131 | 18:30 | 126 | 12:00 | G.K Project | 139 | 0.77083 | 132 | 0.041667
| Mirpur | 136 | 18:00 | 131 | 14:00 | Faridpur | 137 | 0.33333 | 127 | 0.875
| Kalyanpur | 137 | 18:00 | 134 | 11:00 | Rajbari | 136 | 0.33333 | 128 | 0.041667
| Gulshan | 134 | 6;00 | 131 | 12:00 | Madaripur | 139 | 0.41667 | 131 | 0.875
| Uttara | 135 | 8:00 | 131 | 12:00 | Shariyatpur S/S | 140 | 18:30 | 129 | 0.875
| Uttara New | 138 | 11:00 | 132 | 12:00 | Gopalganj | 144 | 0.75 | 131 | 0.875
| Kamrangirchar | 137 | 19:00 | 132 | 16:00 | Bagerhat | 134 | 18:00 | 125 | 0.5
| Savar | 132 | 6:00 | 133 | 12:00 | Mongla | 132 | 17:00 | 124 | 0.54167
| Bhasantec | 137 | 6:00 | 132 | 15:00 | Satkhira | 138 | 18:30 | 125 | 14:00
| Agargaon | 136 | 7:00 | 132 | 21:00 | Gallamari | 139 | 0.77083 | 129 | 13:00
| Satmosjid | 137 | 6:00 | 132 | 15:00 | Magura | 127 | 18:00 | 108 | 0.875
| Tongi | 140 | 18:00 | 135 | 21:00 | Narail | 126 | 0.75 | 107 | 0.041667
| Kabirpur | 141 | 18:30 | 135 | 13:00 | Chuadanga | 123 | 18:30 | 100 | 0.54167
| Basundhara | 139 | 18:30 | 132 | 13:00 | Borguna | 138 | 18:30 | 130 | 0.16667
| Manikganj | 140 | 6.00 | 134 | 24:00 | Barisal(N) | 140 | 18:30 | 134 | 21:00
| Joydevpur | 139 | 18:30 | 133 | 3:00 | Barisal (S) | 137 | 0.70833 | 133 | 0.041667
| New Tongi | 139 | 18:30 | 133 | 13:00 | Patuakhali(S) | 138 | 0.8125 | 127 | 0.20833
| Kodda | 136 | 18:30 | 127 | 14:00 | Bhandaria | 135 | 0.625 | 125 | 0.875
| Dhamrai | 133 | 18:00 | 129 | 21:00 | Ishurdi | 136 | 18:00 | 130 | 13:00
| Rajendrapur | 135 | 18:30 | 126 | 14:00 | Ruppur Paromanobik | 136 | 18:00 | 130 | 21:00
| Valuka | 125 | 18:30 | 110 | 23:00 | Natore | 133 | 18:30 | 126 | 21:00
| Tangail | 134 | 16:00 | 126 | 21:00 | Bogra | 131 | 18:30 | 123 | 13:00
| Mymensing | 127 | 18:30 | 115 | 22:00 | Noagaon | 129 | 18:30 | 117 | 13:00
| Kishorganj | 128 | 10:00 | 117 | 23:00 | Rajshahi | 132 | 18:00 | 124 | 13:00
| Netrokona | 124 | 7:00 | 108 | 23:00 | Rajshahi New | 131 | 18:00 | 123 | 13:00
| Jamalpur | 130 | 6:00 | 121 | 23:00 | C.Nawabganj | 130 | 18:30 | 120 | 12:00
| Sherpur | 129 | 6:00 | 118 | 23:00 | Amnura | 129 | 18:30 | 118 | 2:00
| Srimongal | 135 | 9:00 | 132 | 19:30 | Pabna | 134 | 18:00 | 128 | 21:00
| Shahjibazar | 134 | 14:00 | 130 | 22:00 | Shahjadpur | 137 | 18:00 | 132 | 21:00
| Fenchuganj | 135 | 7:00 | 132 | 20:00 | Serajganj | 132 | 18:00 | 126 | 21:00
| Khulawara | 134 | 16:00 | 131 | 22:00 | Niyamatpur | 123 | 19:00 | 113 | 13:00
| Sylhet | 132 | 16:00 | 130 | 1:00 | Joypurhat | 128 | 18:30 | 116 | 13:00
| Chatak | 132 | 6:00 | 126 | 23:00 | Sherpur(Bogura) | 132 | 18:30 | 125 | 22:00
| Sunamganj | 130 | 8:00 | 124 | 20:00 | Mohastangor | 129 | 18:00 | 122 | 22:00
| Biani Bazar | 130 | 6:00 | 125 | 22:00 | Bangura | 135 | 18:30 | 131 | 23:00
| Comilla(s) | 128 | 18:00 | 123 | 20:00 | Rangpur | 124 | 18:30 | 114 | 22:00
| Comilla(n) | 136 | 18:30 | 131 | 24:00 | Lalmonirhat | 124 | 18:30 | 115 | 1:00
| Chandpur | 130 | 9:00 | 126 | 15:00 | Saidpur | 126 | 18:00 | 111 | 24:00
| Feni | 130 | 18:30 | 124 | 24:00 | Purbasadipur | 124 | 18:30 | 106 | 22:00
| Chowmuhani | 129 | 18:00 | 124 | 15:00 | Thakurgaon | 126 | 18:30 | 105 | 22:00
| Ashuganj | 136 | 16:00 | 132 | 23:00 | Palashbari | 125 | 18:30 | 115 | 22:00
| Daudkandi | 132 | 18:30 | 126 | 24:00 | Barapukuria | 133 | 18:00 | 123 | 22:00
| B.Baria | 131 | 18:00 | 126 | 23:00 | Panchagar | 128 | 18:30 | 104 | 22:00
| Ramganj | 129 | 18:30 | 121 | 15:00 | Joldhaka | 122 | 0.77083 | 107 | 0.91667
| Chaddagram | 132 | 21:00 | 127 | 23:00 | Kurigram | 121 | 0.77083 | 110 | 0.875
| PHP | 130 | 18:30 | 124 | 15:00 | Mithapukur | 126 | 0.77083 | 117 | 0.875
| Kochua | 130 | 19:30 | 126 | 15:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-26
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 112 | 7184 | 3980 | 11164 |  |  |  | QF-LDC-11
0:30 | 272 | 7122 | 3793.5 | 10915.5 | Date: | 2021-07-26
1:00 | 432 | 7060 | 3607 | 10667
1:30 | 427 | 6963.5 | 3543 | 10506.5
2:00 | 422 | 6867 | 3479 | 10346
2:30 | 442 | 6801 | 3415.5 | 10216.5 | [5 empty] | Gen. at Eve. Peak | 11354 | 11354 MW (21:00 )
3:00 | 462 | 6735 | 3352 | 10087 | [6 empty] | 21:00
3:30 | 452 | 6709.5 | 3306.5 | 10016 | [5 empty] | Gen. at Day Peak | 9002 | 9002 MW (12:00 )
4:00 | 442 | 6684 | 3261 | 9945 | [6 empty] | 12:00
4:30 | 429 | 6582.5 | 3228.5 | 9811 | [5 empty] | Highest Generation | 11419
5:00 | 416 | 6481 | 3196 | 9677 | [6 empty] | 22:00
5:30 | 409 | 6238 | 3042.5 | 9280.5
6:00 | 402 | 5995 | 2889 | 8884
6:30 | 406 | 5868.5 | 2835 | 8703.5
7:00 | 410 | 5742 | 2781 | 8523
7:30 | 377 | 5681 | 2741.5 | 8422.5
8:00 | 344 | 5620 | 2702 | 8322
8:30 | 292 | 5672.5 | 2756 | 8428.5
9:00 | 240 | 5725 | 2810 | 8535
9:30 | 212 | 5748 | 2842 | 8590
10:00 | 184 | 5771 | 2874 | 8645
10:30 | 210 | 5786 | 2855.5 | 8641.5
11:00 | 236 | 5801 | 2837 | 8638
11:30 | 232 | 5921.5 | 2898.5 | 8820
12:00 | 228 | 6042 | 2960 | 9002
12:30 | 254 | 6150.5 | 2995 | 9145.5
13:00 | 280 | 6259 | 3030 | 9289
13:30 | 265 | 6341 | 3049 | 9390
14:00 | 250 | 6423 | 3068 | 9491
14:30 | 218 | 6452.5 | 3120.5 | 9573
15:00 | 186 | 6482 | 3173 | 9655
15:30 | 177 | 6410.5 | 3096 | 9506.5
16:00 | 168 | 6339 | 3019 | 9358
16:30 | 127 | 6096 | 2904.5 | 9000.5
17:00 | 86 | 5853 | 2790 | 8643
17:30 | 139 | 5751.5 | 2652.5 | 8404
18:00 | 192 | 5650 | 2515 | 8165
18:30 | 221 | 6109.5 | 2815 | 8924.5
19:00 | 250 | 6569 | 3115 | 9684
19:30 | 292 | 7362 | 3758 | 11120
20:00 | 290 | 7333 | 3793 | 11126 |  |  |  | Executive Engineer
20:30 | 248 | 7381 | 3859 | 11240 |  |  |  | Network Operation Division
21:00 | 206 | 7429 | 3925 | 11354
21:30 | 207 | 7424 | 3962.5 | 11386.5
22:00 | 208 | 7419 | 4000 | 11419 |  |  |  |  | Page 6 of 7
22:30 | 182 | 7342 | 3994.5 | 11336.5
23:00 | 156 | 7265 | 3989 | 11254
23:30 | 134 | 7224.5 | 3984.5 | 11209
24:00 | 112 | 7184 | 3980 | 11164
11354 MW (21:00 )
9002 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-26 |  | Energy | 235461456
[11 empty] | 2021-07-26 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 5088 | 792 | 2026 | 2199 | 654 | 124 | 295 | 0 | 124 | 0
0:30 | 4944 | 789 | 2000.5 | 2142.5 | 674 | 124.5 | 180 | 0 | 130 | 0 | Date: | 2021-07-26
1:00 | 4800 | 786 | 1975 | 2086 | 694 | 125 | 65 | 0 | 136 | 0
1:30 | 4799.5 | 786 | 1978 | 1931.5 | 696 | 124 | 56.5 | 0 | 135 | 0 | [7 empty] | Total Energy | 235.4615 | Total Energy Gen 235.461 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.461 MKWHr
2:00 | 4799 | 786 | 1981 | 1777 | 698 | 123 | 48 | 0 | 134 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4804.5 | 790 | 1983.5 | 1667 | 672.5 | 121.5 | 45.5 | 0 | 132 | 0 | [7 empty] | Energy Requirement | 235.4615
3:00 | 4810 | 794 | 1986 | 1557 | 647 | 120 | 43 | 0 | 130 | 0
3:30 | 4814.5 | 794 | 1972 | 1487.5 | 647.5 | 118.5 | 53 | 0 | 129 | 0 | [6 empty] | Shortage
4:00 | 4819 | 794 | 1958 | 1418 | 648 | 117 | 63 | 0 | 128 | 0
4:30 | 4838 | 794 | 1940.5 | 1312.5 | 622.5 | 117 | 59.5 | 0 | 127 | 0
5:00 | 4857 | 794 | 1923 | 1207 | 597 | 117 | 56 | 0 | 126 | 0
5:30 | 4801.5 | 794 | 1777 | 1049 | 572 | 117.5 | 48.5 | 0 | 119 | 2
6:00 | 4746 | 794 | 1631 | 891 | 547 | 118 | 41 | 0 | 112 | 4
6:30 | 4639 | 794 | 1620 | 832.5 | 547 | 118.5 | 35.5 | 0 | 110 | 7 |  |  |  |  | Coal
7:00 | 4532 | 794 | 1609 | 774 | 547 | 119 | 30 | 0 | 108 | 10
7:30 | 4472 | 794 | 1581 | 761 | 546 | 119 | 27.5 | 0 | 105 | 17 |  |  |  | Oil |  |  |  | ,
8:00 | 4412 | 794 | 1553 | 748 | 545 | 119 | 25 | 0 | 102 | 24
8:30 | 4448 | 794 | 1589.5 | 756.5 | 544 | 120.5 | 40 | 0 | 103 | 33
9:00 | 4484 | 794 | 1626 | 765 | 543 | 122 | 55 | 0 | 104 | 42
9:30 | 4506.5 | 794 | 1635 | 765.5 | 542 | 122 | 60 | 0 | 106 | 59
10:00 | 4529 | 794 | 1644 | 766 | 541 | 122 | 65 | 0 | 108 | 76
10:30 | 4560 | 794 | 1645 | 763 | 542.5 | 122 | 42.5 | 0 | 106 | 66.5
11:00 | 4591 | 794 | 1646 | 760 | 544 | 122 | 20 | 0 | 104 | 57
11:30 | 4721 | 794 | 1694.5 | 753 | 543 | 122 | 15 | 0 | 106 | 71.5
12:00 | 4851 | 794 | 1743 | 746 | 542 | 122 | 10 | 0 | 108 | 86
12:30 | 4866 | 797 | 1837.5 | 759.5 | 555.5 | 123 | 10 | 0 | 113 | 84
13:00 | 4881 | 800 | 1932 | 773 | 569 | 124 | 10 | 0 | 118 | 82
13:30 | 4881 | 800 | 1932 | 773 | 569 | 124 | 10 | 0 | 118 | 82
14:00 | 4881 | 800 | 1932 | 773 | 569 | 124 | 10 | 0 | 118 | 82
14:30 | 4870.5 | 800 | 1944 | 953 | 594.5 | 123 | 10 | 0 | 113 | 64
15:00 | 4860 | 800 | 1956 | 1133 | 620 | 122 | 10 | 0 | 108 | 46
15:30 | 4848.5 | 800.5 | 1946.5 | 1036 | 588 | 122 | 20 | 0 | 107 | 38
16:00 | 4837 | 801 | 1937 | 939 | 556 | 122 | 30 | 0 | 106 | 30
16:30 | 4740 | 800.5 | 1747.5 | 911 | 523.5 | 121 | 32 | 0 | 103 | 22
17:00 | 4643 | 800 | 1558 | 883 | 491 | 120 | 34 | 0 | 100 | 14
17:30 | 4529 | 800 | 1468 | 892 | 458 | 120 | 34.5 | 0 | 93 | 9.5
18:00 | 4415 | 800 | 1378 | 901 | 425 | 120 | 35 | 0 | 86 | 5
18:30 | 4560 | 795.5 | 1566.5 | 1188 | 438.5 | 120 | 150.5 | 0 | 103 | 2.5
19:00 | 4705 | 791 | 1755 | 1475 | 452 | 120 | 266 | 0 | 120 | 0
19:30 | 4834 | 791 | 1965 | 2426 | 576 | 121 | 287 | 0 | 120 | 0
20:00 | 4918 | 792 | 1983 | 2305 | 595 | 121 | 278 | 0 | 134 | 0
20:30 | 5003 | 791.5 | 2000.5 | 2303 | 615 | 121 | 270 | 0 | 136 | 0
21:00 | 5088 | 791 | 2018 | 2301 | 635 | 121 | 262 | 0 | 138 | 0
21:30 | 5094.5 | 791 | 2029 | 2305.5 | 645 | 121.5 | 267 | 0 | 133 | 0
22:00 | 5101 | 791 | 2040 | 2310 | 655 | 122 | 272 | 0 | 128 | 0
22:30 | 5078 | 791.5 | 2040.5 | 2254.5 | 655.5 | 122.5 | 267 | 0 | 127 | 0
23:00 | 5055 | 792 | 2041 | 2199 | 656 | 123 | 262 | 0 | 126 | 0
23:30 | 5071.5 | 792 | 2033.5 | 2199 | 655 | 123.5 | 278.5 | 0 | 125 | 0 | Max Temp. in Dhaka |  | 35.2° C
24:00 | 5088 | 792 | 2026 | 2199 | 654 | 124 | 295 | 0 | 124 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 235.461 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 235.461 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-26
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 65 | 63 | 60 | 57 | 57 | 58 | 59 | 59 | 62 | 62 | 62 | 62 | 64 | 62 | 62 | 62 | 60 | 60 |  | 60 | 61 | 61 | 61 | 62 | 63 | 64 | 1398638
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1452000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [19 empty] | 6 | 8 | 8 | 8 | 8 | 8 |  | 40096
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | 3 | 8 | 5 | 6 | 5 | 6 | 2 | 2 | 0 | [10 empty] | 36855
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900018
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 2 |  | 242300
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 85 | 85 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 19 | 45 | 17 | 17 | 17 |  | 36 | 105 | 102 | 105 | 105 | 105 | 105 | 1282145
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 39 | 39 | 39 | 40 | 39 | 39 | 39 | 39 | 40 | 39 | 39 | 39 | 91 | 87 | 91 | 91 | 35 | 37 |  | 36 | 32 | 57 | 91 | 92 | 92 | 92 | 1436000
17 | Siddhirganj 335 MW CCPP | 333 | 334 | 335 | 335 | 333 | 336 | 270 | 270 | 270 | 270 | 270 | 270 | 300 | 300 | 300 | 300 | 300 | 250 |  | 280 | 280 | 300 | 326 | 327 | 331 | 334 | 7333240
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 4 |  | 17 | 75 | 15 |  |  |  |  | 82799
19 | Ashuganj 195MW PP (APSCL-United) | 45 | 45 | 45 | 45 | 45 | 16 | 16 | 16 | 16 | 16 | 16 | 36 | 36 | 36 | 36 | 36 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 602181
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 3433500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 100 | 100 | 100 | 100 | 100 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 | 100 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 2184806
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 490320
33 | Ashuganj 225 MW CCPP | 215 | 215 | 215 | 216 | 214 | 216 | 215 | 215 | 210 | 211 | 210 | 210 | 209 | 211 | 186 | 182 | 182 | 190 |  | 196 | 181 | 212 | 209 | 210 | 211 | 212 | 4994000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 270 | 270 | 285 | 270 | 270 | 270 | 300 | 290 | 290 | 335 | 305 | 305 | 295 | 290 | 290 | 300 |  | 310 | 290 | 290 | 310 | 295 | 280 | 280 | 6977000
| Ashuganj 450 MW CCPP(North) | 275 | 275 | 275 | 275 | 290 | 275 | 260 | 260 | 290 | 280 | 280 | 305 | 300 | 300 | 260 | 260 | 260 | 270 |  | 280 | 260 | 260 | 285 | 275 | 260 | 260 | 6977100
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 30 | 30 | 30 | 10 | 10 |  | 10 | 54 | 45 | 55 | 54 | 54 | 55 | 828000
36 | Chandpur 150 MW CCPP | 137 | 137 | 138 | 135 | 136 | 136 | 137 | 136 | 137 | 138 | 137 | 138 | 137 | 130 | 139 | 135 | 137 | 136 |  | 137 | 136 | 130 | 136 | 137 | 136 | 138 | 3240100
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 398 | 398 | 398 | 398 | 398 | 398 | 369 | 352 | 352 | 353 | 354 | 354 | 371 | 399 | 396 | 397 | 391 | 318 |  | 310 | 391 | 389 | 392 | 398 | 400 | 400 | 9216000
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5640500
41 | Haripur 360MW CCPP(HPL) | 348 | 345 | 341 | 341 | 342 | 341 | 308 | 308 | 307 | 306 | 306 | 340 | 340 | 342 | 338 | 332 | 302 | 242 |  | 288 | 343 | 345 | 343 | 344 | 345 | 346 | 7840000
42 | RPCL 210MW CCPP | 204 | 204 | 204 | 205 | 205 | 206 | 205 | 207 | 204 | 201 | 200 | 199 | 199 | 199 | 196 | 199 | 197 | 198 |  | 198 | 202 | 202 | 199 | 199 | 201 | 203 | 4754160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 3 | 9 | 17 | 37 | 32 | 39 | 43 | 21 | 26 | 18 | 7 | 3 | [8 empty] | 245490
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 43 | 43 |  | 44 | 44 | 44 | 44 | 43 | 44 | 43 | 103000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1005480
46 | Shajibazar 330 MW CCPP | 183 | 182 | 181 | 182 | 182 | 183 | 183 | 180 | 182 | 180 | 177 | 179 | 178 | 179 | 174 | 178 | 178 | 177 |  | 179 | 181 | 181 | 177 | 179 | 178 | 181 | 3981000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 62 | 61 | 61 | 61 | 61 | 61 | 61 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 40 | 40 |  | 60 | 61 | 61 | 60 | 60 | 56 | 56 | 1424832
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 84 | 82 | 82 | 82 | 10 | 10 |  | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 1225920
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 218 | 218 | 218 | 218 | 218 | 218 | 164 | 164 | 164 | 165 | 165 | 219 | 192 | 191 | 191 | 191 | 191 | 164 |  | 219 | 219 | 219 | 219 | 219 | 219 | 219 | 4777460
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 388000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 210780
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 5 | 5 | 5 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  | 5 | 5 | 11 | 11 | 11 | 11 | 210144
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 31 | 47 | 47 | 50 | 14 | 14 |  | 32 | 47 | 47 | 47 | 50 | 50 | 50 | 805200
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 341256
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 285 | 285 | 285 | 290 | 280 | 280 | 285 | 300 | 310 | 315 | 305 | 305 | 280 | 280 | 290 | 280 | 280 |  | 290 | 270 | 280 | 290 | 300 | 300 | 290 | 7169000
| Bibiyana South 400 MW | 398 | 398 | 395 | 401 | 396 | 400 | 398 | 380 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 350 | 320 | 320 |  | 335 | 385 | 396 | 386 | 388 | 391 | 400 | 8917100
58 | Nababganj 55 MW PP (Southern power ) | [12 empty] | 3 | 17 | 17 |  |  |  |  | 20 | 35 | 35 | 17 | 17 | 17 |  | 204116
59 | Tangail Palli Power Gen 22 MW | 23 | [13 empty] | 3 | 14 | 20 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 237840
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482544
61 | Narshingdi 22 MW PP (Doreen) | 14 | 14 | 16 | 16 |  |  |  |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  |  | 19 | 19 | 16 | 19 | 19 | 19 | 19 | 278136
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 461124
63 | Impoprt (Tripura) | 136 | 134 | 130 | 128 | 126 | 112 | 108 | 102 | 104 | 108 | 104 | 108 | 118 | 126 | 108 | 106 | 100 | 86 |  | 120 | 120 | 134 | 138 | 128 | 126 | 124 | 2834880
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 35 | 42 | 42 | 42 | 36 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1087200
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 21 | 21 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499140
66 | Feni 11 MW PP (Doreen) |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 251100
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 20 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 25 | 25 | 25 | 25 | 25 | 33 | 732200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 0 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 472450
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 | 7 |  | 7 | 7 | 9 | 9 | 9 | 9 | 9 | 226440
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 730100
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 706500
73 | Ghorashal 108MW PP (Regent) | 92 | 92 | 92 | 92 | 92 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 75 | 90 | 86 | 90 | 33 | 33 |  | 50 | 95 | 95 | 95 | 95 | 95 | 95 | 1522181
| Feni Lanka Power | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 116280
| Chowmuhani 113 MW | 107 | 106 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 81 | 104 | 104 |  | 105 | 108 | 107 | 110 | 111 | 109 | 115 | 2084040
| Manikgonj 162MW PP(MPGL) | [12 empty] | 10 | 35 | 17 |  |  |  |  | 14 | 54 | 35 | 17 | 17 | 17 | 0 | 239040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 16 | [18 empty] | 40 | 51 | 51 | 42 | 43 | 51 | 51 | 291840
79 | Kodda 150MW PP | [19 empty] | 48 | 48 | 48 | 32 | 32 | 16 | 16 | 180960
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 |  | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 163200
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | [18 empty] | 16 | 37 | 32 | 43 | 43 | 16 | 16 | 214930
| Gazipur 100 MW PP | [19 empty] | 13 | [6 empty] | 27600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 4 | 5 | 2 | 5 | 4 | 2 | 0 | 1 | [9 empty] | 27480
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 85 | 85 | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 34 | 41 | 68 | 68 | 51 | 51 |  | 56 | 85 | 105 | 110 | 110 | 110 | 110 | 1939525
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 10 | [6 empty] | 13493
86 | Meghnaghat CCPP ( Summit) | 263 | 254 | 267 | 272 | 260 | 254 | 263 | 262 | 280 | 280 | 280 | 280 | 275 | 245 | 275 | 260 | 275 | 275 |  | 260 | 245 | 254 | 280 | 275 | 267 | 260 | 6474124
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [14 empty] | 16 |  |  |  |  | 11 | 20 | 29 | 17 | 17 | 17 |  | 137280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [26 empty] | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 20 | 32 | 43 | 43 | 10 | 10 |  | 20 | 43 | 43 | 43 | 43 | 43 | 43 | 766068
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 16 | 16 | [5 empty] | 23904
95 | Patenga 50MW PP (Baraka) | [19 empty] | 8 | 14 | 9 |  |  |  |  | 22560
96 | Chattogram 108 MW PP (ECPV) | 94 | 96 | 81 | 50 | 31 | 7 | 6 | 6 | 6 | 6 | [10 empty] | 0 | [5 empty] | 387840
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [19 empty] | 8 | 15 | 15 |  |  |  |  | 29677
100 | Manikganj 55 MW PP (Northern) | [12 empty] | 5 | 17 | 17 | 17 |  |  |  | 17 | 35 | 35 | 17 | 17 | 17 | 0 | 203076
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 11650
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 741960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 192 | 192 | 192 | 80 | 50 | 24 | 24 | 24 | 24 | 24 | 24 | 31 | 80 | 80 | 40 | 40 |  | 79 | 195 | 187 | 197 | 200 | 190 | 191 | 2736000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 46 | 25 | 17 | 15 | 15 | 15 | 15 | 16 | 15 | 16 | 16 |  |  |  | 8 | 34 | 34 | 34 |  | 34 | 70 | 60 | 70 | 70 | 58 | 36 | 692640
115 | Juldah 100 MW PP Unit-3 (Acorn) | 20 | [11 empty] | 10 | 50 | 50 | 10 | 10 | 10 |  | 50 | 100 | 100 | 100 | 100 | 100 | 100 | 689280
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 68 | 68 | 68 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 24 | 100 | 84 | 100 | 100 | 100 | 100 | 1251360
117 | Ashuganj 150MW PP (Midland) | 100 | 50 | 50 | 50 | [8 empty] | 1 | 26 | 60 | 10 |  |  |  | 30 | 65 | 65 | 65 | 65 | 65 | 65 | 821309
118 | Bibiyana-III 400 MW CCPP | 366 | 367 | 366 | 366 | 377 | 366 | 366 | 342 | 348 | 330 | 390 | 373 | 367 | 367 | 332 | 330 | 305 | 314 |  | 398 | 367 | 367 | 382 | 380 | 365 | 366 | 8627000
| Jamalpur 115 MW PP (United) | 107 | 107 | 107 | 107 | 107 | 107 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 2647200
| Anwara 300 MW PP (United) | [16 empty] | 16 | 16 |  | 16 | 16 | [5 empty] | 55200
| Juldah unit-2 (Acorn) | 10 | [11 empty] | 10 | 30 | 10 | 10 | 10 | 10 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 379200
| Anlima Energy Ltd. | 116 | 116 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 92 | 97 | 97 | 97 | 97 | 106 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2470200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 14 | 17 | 17 | 17 | 17 | 433440
| Spectra Solar Plant Ltd. | [5 empty] | 2 | 5 | 9 | 11 | 21 | 7 | 30 | 18 | 22 | 10 | 8 | 4 | 1 | [8 empty] | 171760
120 | Eastern Zone Total | 7060 | 6867 | 6735 | 6684 | 6481 | 5995 | 5742 | 5620 | 5725 | 5771 | 5801 | 6042 | 6259 | 6423 | 6482 | 6339 | 5853 | 5650 |  | 6569 | 7362 | 7333 | 7429 | 7419 | 7265 | 7184 | 155783487
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 15 | 15 | 10 | 30 | 30 | 15 | 30 | 25 | 55 | 65 | 20 | 10 | 10 | 10 | 10 | 30 | 30 | 30 |  | 30 | 30 | 10 | 20 | 30 | 85 | 120 | 738240
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 70 | 70 | 17 | [6 empty] | 5 | 35 | 35 |  |  |  |  | 26 | 105 | 105 | 105 | 105 | 105 | 105 | 1196160
130
131
132 | United Payra Power Ltd. | 90 | 54 | 35 | 35 | [15 empty] | 19 | 90 | 90 | 90 | 90 | 90 | 90 | 700800
133 | Bhola Nutan Biddut BD LTD (GAS) | 219 | 219 | 219 | 218 | 219 | 219 | 220 | 220 | 218 | 218 | 219 | 218 | 217 | 216 | 216 | 216 | 184 | 142 |  | 216 | 217 | 219 | 220 | 220 | 220 | 220 | 5138618
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 85 | 86 | 86 | 85 | 85 | 52 | 52 |  | 48 | 52 | 52 | 54 | 78 | 81 | 82 | 83 | 34 | 34 |  | 75 | 77 | 84 | 82 | 82 | 85 | 84 | 1626794
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 31 | 31 | 31 | 31 | 31 | 31 | 25 | 24 | 23 | 23 | 23 | 23 | 23 | 25 | 27 | 25 | 25 | 28 |  | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 648350
141 | Noapara 100 MW PP (Bangla Trac) | 60 | 10 | [17 empty] | 1 | 100 | 80 | 100 | 100 | 40 |  | 523200
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 786 | 786 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 794 | 800 | 792 | 800 | 801 | 800 | 800 |  | 791 | 791 | 792 | 791 | 791 | 792 | 792 | 19192000
147 | Bheramara 410 MW CCPP | 400 | 400 | 400 | 400 | 400 | 370 | 340 | 340 | 340 | 340 | 340 | 390 | 390 | 390 | 385 | 385 | 350 | 300 |  | 350 | 370 | 370 | 400 | 400 | 400 | 405 | 9209376
148 | Payra 1320 MW | 470 | 470 | 420 | 420 | 370 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 340 | 370 | 390 | 400 | 340 | 270 |  | 300 | 420 | 440 | 480 | 500 | 500 | 500 | 10258700
149
150 | Barapukuria TPP Unit-1 | 72 | 77 | 77 | 77 | 77 | 77 | 77 | 76 | 73 | 72 | 79 | 75 | 74 | 73 | 73 | [11 empty] | 1194327
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 152 | 151 | 150 | 151 | 150 | 150 | 150 | 149 | 150 | 149 | 145 | 147 | 155 | 155 | 157 | 156 | 151 | 155 |  | 152 | 156 | 155 | 155 | 155 | 156 | 154 | 3746700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1688000
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 1 | 5 | 3 | 5 | 5 | 5 | 2 | 1 | 0 | 0 | [8 empty] | 30240
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | [13 empty] | 21 | 92 | 90 | 88 | 70 |  | 81 | 105 | 108 | 116 | 124 | 120 | 119 | 1108000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 159 | 158 | 159 | 160 | 171 | 158 | 140 | 140 | 147 | 179 | 182 | 200 | 200 | 199 | 176 | 167 | 166 | 160 |  | 148 | 183 | 184 | 192 | 196 | 189 | 189 | 4356118
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 146 | 145 | 146 | 147 | 158 | 146 | 147 | 145 | 149 | 176 | 179 | 199 | 196 | 190 | 180 | 175 | 174 | 159 |  | 147 | 150 | 152 | 159 | 174 | 177 | 178 | 4214236
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 319 | 332 | 341 | 315 | 347 | 316 | 339 | 324 | 347 | 347 | 347 | 388 | 400 | 347 | 376 | 347 | 335 | 253 |  | 336 | 381 | 387 | 405 | 414 | 411 | 405 | 8497873
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 4 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 36390
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 499440
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | [10 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 161928
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 17 | [18 empty] | 17 | 27 | 39 | 30 | 30 | 30 | 30 | 145925
168 | Santahar 50 MW Peaking PP | 33 | 33 | 33 | 33 | 26 | 26 | [13 empty] | 40 | 34 | 33 | 32 | 32 | 32 | 32 | 392000
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 52 | 52 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 30 | 43 | 16 | 16 | 16 |  | 16 | 16 | 43 | 43 | 43 | 43 | 43 | 680160
170 | Chapainawabganj 100 MW Peaking PP | [19 empty] | 75 | 92 | 92 | 92 | 92 | 92 | 92 | 505224
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 70 | 70 | 35 | [13 empty] | 20 | 91 | 87 | 90 | 94 | 94 | 94 | 1020288
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 70 | [17 empty] | 50 | 70 | 70 | 70 | 75 | 75 | 75 | 612672
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 97 | 97 | 70 | 70 | 52 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 33 |  |  |  | 85 | 113 | 113 | 113 | 113 | 113 | 113 | 1527436
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 2 | 1 | [8 empty] | 28774
178
178