## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-28 | Wednesday
|  |  | Date (day): | 2021-07-28 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14146.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14994 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-27 | 2021-07-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 13 | 93 | 90 | 95 |  | 13 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 333 | 395 | 360 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 302 | 345 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 285 | 272 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 80 |  | 20 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 13 | 18 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 90 | 60 | 90 | 120 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 280 | 330 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 0 | 35 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 32 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 33 | 33 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 24 | 24 | 20 | 24 |  | 9 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 0 | 270 | 270 |  | 30 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 1 | 0 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 52 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 33 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 1791 | 2200 | 3665 | 3994 | 489 | 1170
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 1 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 122 | 94 | 60 | 60 | 170 |  | Unit 1,2,3 Under S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 17 | 54 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 17 | 51 | 51 |  | 51 | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 10 | 80 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 42 | 25 | 30 | 42
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 108 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 70 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 17 | 116 | 112 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 591 | 933 | 1581 | 1672 | 310 | 415
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 80 | 70 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 60 | 60 | 60 |  | 74 | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 199 | 193 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 295 | 330 | 330
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 295 | 360 | 360
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 13 | 23 | 20 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 10 | 10 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 26 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 10 | 43 | 42 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 0 | 30 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 85 | 130 | 136 |  | 27 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 17 | 81 | 170 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 110 | 126 | 121 | 149
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 21 | 22
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 115 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1338 | 1537 | 2256 | 2428 | 371 | 177
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 194 | 199 | 202 | 202
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 32 | 200 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 105 | 105 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 57 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 410 | 557 | 594.6 | 568 | 0 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 43 | 43 |  | 47 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 225 | 192 | 180 | 180 | 150 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 40 | 63 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 152 | 219 | 150 | 150 |  | 81 | ST Under maint. |  | 2021-07-08
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 16 | 16 |  | 9 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 0 | 0 | 0 |  | 341 | Under maint
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 315 | 403 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 200 | 260 | 260 | 260 |  | 123 | ST Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1382 | 1412 | 1326 | 1327 | 150 | 890
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 801 | 791 | 807 | 807
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 243 | 0 | 200 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 400 | 360 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1344 | 1396 | 1622 | 1817 | 0 | 83
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 0 | 0 | 0 | 0 |  | 194 | Under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 23 | 84 | 80 | 82 | 13 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 500 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 152 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 90 | 90 |  | 60 | Engine problem
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 495 | 853 | 1155 | 1157 | 13 | 254
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 60 | 70 | 70 | 70 | 30 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 0 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 20 | 20 |  | 51 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 30 | 30 |  | 20 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 130 | 144 | 100 | 144 | 66 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 194 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 193 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 350 | 411 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 47 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 90 | 90 | 90 |  | 23 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 75 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 1 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 933 | 1400 | 1676 | 1748 | 216 | 143
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 150 | 150 | 150 | 124 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 189 | 263 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 8473 | 10551 | 14146.6 | 14994 | 1673 | 3409
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 8073.0802 | 10053 | 13478.8901 | 14286.2934
| A. |  | 2021-07-27 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 10752 | MW at | 1:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8120 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10551 | MW
| 3 | Day peak Generation : |  |  | 8473 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 10053 | MW
| 4 | Evening peak Generation : |  |  | 10551 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 226.3802 | MKWHr | By Solar | 0.60465 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 154.357 | MKWHr |  | By Oil: | 33.7828 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.8079 | MKWHr |  | By Hydro: | 1.8625 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1673 | MW | Dhaka | 2883 | 2883 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3409 | MW | Chittagong | 787 | 787 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5082 | MW | Khulna | 1381 | 1381 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1219.25 | MMCFD |  |  | Rajshahi | 1245 | 1245 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 171292805.932 | ii) Oil : | Taka | 237438427.44 | Comilla | 1093 | 1093 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 64493704 | Total | Taka | 473224937.372 | Mymensingh | 1025 | 1025 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.004 | MKWHr. | Sylhet | 532 | 532 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -36 | MW (E to W) at | 21:00 | hrs | Barisal | 285 | 285 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -184 | MW at | 4:00 | hrs | Rangpur | 822 | 822 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34° C |  |  | Total | 10053 | 10053 |  | 0
| B. |  | 2021-07-28 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 11000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14994 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 8000 | MW
| 4 | Reserve(Generation end) |  |  |  | 3994 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 231.6018 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 7385 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.216 | MKWHr. | ii) HVDC Flow at Peak Time |  | 791 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7494 | MKWHr. | iii) Maximum HVDC Flow : |  | 801 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.6 |  | (b) Today: | 84.58 |  | (c) Rule Curve: |  | 88.32
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 0 | 94 | 0 | 400 | 342 |  | 0 | 240 | 270 | 0 | 0 | 0 | 332 | 0 | 92 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 19 | 25 | 9 | 25 | 24 | 24 | 0 | 65 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 23 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 212 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 122 | 203 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 182 | 56 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 17 | 0 | 50 | 100 | 10 | 366 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 17 | 115 | 20 | 204 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 800 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 5 | 92 | 0 | 0 | 23 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 118 | 0 | 188 | 0 | 84 | 0 | 178 | 0 | 413 | 70 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 500 | 221 | 0 | 90 | 0 |  | 6789 | 3963 | 10752 | 4887 | 800 | 2030 | 1845 | 655 | 125 | 288 | 122 | 0 | 0 | 84.6
2:00 | 0 | 0 | 0 | 170 | 0 | 91 | 0 | 400 | 342 |  | 0 | 240 | 270 | 0 | 0 | 0 | 333 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 0 | 0 | 19 | 25 | 9 | 25 | 24 | 24 | 0 | 64 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 211 | 8 | 136 | 23 | 56 | 0 | 43 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 116 | 203 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 182 | 51 | 84 | 0 | 219 | 18 | 0 | 10 | 300 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 17 | 0 | 20 | 100 | 10 | 365 | 106 | 0 | 105 | 0 | 0 | 0 | 110 | 0 | 110 | 20 | 170 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 801 | 0 | 405 | 0 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 55 | 0 | 0 | 0 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 119 | 0 | 188 | 0 | 84 | 0 | 178 | 0 | 413 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 500 | 221 | 0 | 54 | 0 |  | 6682 | 3813 | 10495 | 4849 | 801 | 2038 | 1686 | 654 | 124 | 227 | 116 | 0 | 0 | 84.6
3:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 400 | 342 |  | 0 | 240 | 267 | 0 | 0 | 0 | 304 | 0 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 8 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 265 | 280 | 212 | 8 | 137 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 203 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 183 | 51 | 84 | 0 | 219 | 18 | 0 | 10 | 285 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 20 | 100 | 10 | 366 | 106 | 0 | 34 | 0 | 0 | 0 | 68 | 0 | 109 | 20 | 266 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 800 | 0 | 405 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 119 | 0 | 188 | 0 | 86 | 0 | 178 | 0 | 413 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 450 | 221 | 0 | 17 | 0 |  | 6533 | 3672 | 10205 | 4923 | 800 | 2030 | 1442 | 605 | 121 | 170 | 114 | 0 | 0 | 84.6
4:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 399 | 343 |  | 0 | 240 | 266 | 0 | 0 | 0 | 300 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 212 | 8 | 135 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 203 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 184 | 51 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 192 | 0 | 0 | 0 | 20 | 85 | 0 | 366 | 106 | 0 | 34 | 0 | 0 | 0 | 68 | 0 | 110 | 20 | 270 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 801 | 0 | 350 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 117 | 0 | 187 | 0 | 86 | 0 | 184 | 0 | 404 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 400 | 221 | 0 | 0 | 0 |  | 6467 | 3475 | 9942 | 4835 | 801 | 2027 | 1318 | 550 | 121 | 180 | 110 | 0 | 0 | 84.6
5:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 399 | 343 |  | 0 | 240 | 260 | 0 | 0 | 0 | 300 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 22 | 80 | 0 | 0 | 260 | 280 | 212 | 8 | 132 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 106 | 202 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 183 | 51 | 84 | 0 | 219 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 191 | 0 | 0 | 0 | 20 | 51 | 0 | 366 | 106 | 0 | 17 | 0 | 0 | 0 | 34 | 0 | 110 | 20 | 270 | 0 | 0 | 0 | 90 | 0 | 17 | 0 |  | 801 | 0 | 350 | 0 | 0 | 190 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 121 | 0 | 189 | 0 | 85 | 0 | 186 | 0 | 410 | 0 | 0 | 94 | 0 | 113 | 0 | 0 | 0 | 370 | 221 | 0 | 0 | 0 |  | 6317 | 3446 | 9763 | 4838 | 801 | 2012 | 1173 | 525 | 118 | 190 | 106 | 0 | 0 | 84.6
6:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 367 | 308 |  | 0 | 240 | 253 | 0 | 0 | 0 | 250 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 213 | 8 | 136 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 98 | 203 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 182 | 51 | 50 | 0 | 178 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 318 | 106 | 0 | 17 | 0 | 0 | 0 | 34 | 0 | 110 | 10 | 270 | 0 | 1 | 0 | 72 | 0 | 17 | 1 |  | 800 | 0 | 320 | 0 | 0 | 205 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 118 | 0 | 187 | 0 | 52 | 0 | 184 | 0 | 324 | 0 | 0 | 0 | 0 | 57 | 0 | 0 | 0 | 340 | 180 | 0 | 0 | 0 |  | 5829 | 3064 | 8893 | 4636 | 800 | 1751 | 786 | 496 | 119 | 205 | 98 | 2 | 0 | 84.6
7:00 | 0 | 0 | 0 | 170 | 0 | 54 | 0 | 316 | 279 |  | 0 | 240 | 274 | 0 | 0 | 0 | 250 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 285 | 212 | 8 | 136 | 23 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 80 | 201 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 182 | 40 | 10 | 0 | 151 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 318 | 115 | 0 | 17 | 0 | 0 | 0 | 34 | 0 | 46 | 10 | 200 | 0 | 9 | 0 | 35 | 0 | 17 | 3 |  | 800 | 0 | 320 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 70 | 0 | 157 | 0 | 22 | 0 | 188 | 0 | 351 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 180 | 0 | 0 | 0 |  | 5433 | 2935 | 8368 | 4381 | 800 | 1599 | 692 | 455 | 119 | 230 | 80 | 12 | 0 | 84.6
8:00 | 0 | 0 | 0 | 170 | 0 | 54 | 0 | 306 | 278 |  | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 59 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 280 | 180 | 8 | 134 | 23 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 84 | 203 | 0 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 183 | 40 | 10 | 0 | 151 | 18 | 0 | 10 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 319 | 115 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 8 | 10 | 200 | 0 | 15 | 0 | 35 | 0 | 17 | 11 |  | 801 | 0 | 320 | 0 | 0 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 154 | 0 | 0 | 70 | 0 | 130 | 0 | 22 | 0 | 180 | 0 | 320 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 150 | 0 | 0 | 1 |  | 5333 | 2838 | 8171 | 4290 | 801 | 1537 | 620 | 454 | 119 | 239 | 84 | 27 | 0 | 84.6
9:00 | 0 | 0 | 0 | 170 | 0 | 54 | 0 | 301 | 276 |  | 0 | 240 | 240 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 19 | 25 | 8 | 25 | 24 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 260 | 285 | 180 | 8 | 137 | 23 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 22 | 86 | 203 | 0 | 21 | 1 | 43 | 43 | 11 | 0 | 0 | 182 | 40 | 10 | 0 | 152 | 18 | 0 | 10 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 10 | 17 | 0 | 318 | 115 | 0 | 17 | 1 | 0 | 0 | 17 | 0 | 8 | 10 | 200 | 0 | 17 | 0 | 35 | 0 | 17 | 5 |  | 801 | 0 | 300 | 0 | 0 | 249 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 70 | 0 | 130 | 0 | 22 | 0 | 173 | 0 | 314 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 290 | 151 | 0 | 0 | 2 |  | 5298 | 2822 | 8120 | 4274 | 801 | 1523 | 595 | 445 | 121 | 249 | 86 | 26 | 0 | 84.6
10:00 | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 303 | 277 |  | 0 | 240 | 280 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 8 | 25 | 24 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 278 | 320 | 192 | 8 | 136 | 10 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 118 | 198 | 0 | 21 | 2 | 43 | 42 | 11 | 0 | 0 | 178 | 40 | 10 | 0 | 152 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 10 | 17 | 0 | 327 | 106 | 0 | 17 | 2 | 0 | 0 | 17 | 0 | 5 | 0 | 200 | 0 | 44 | 0 | 17 | 0 | 17 | 1 |  | 800 | 0 | 300 | 0 | 0 | 247 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 70 | 0 | 130 | 0 | 22 | 0 | 161 | 0 | 351 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 300 | 152 | 0 | 0 | 2 |  | 5278 | 2834 | 8112 | 4290 | 800 | 1486 | 544 | 451 | 121 | 247 | 118 | 55 | 0 | 84.6
11:00 | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 330 | 303 |  | 0 | 240 | 275 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 8 | 25 | 24 | 0 | 0 | 61 | 60 | 100 | 150 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 80 | 0 | 0 | 260 | 270 | 181 | 26 | 138 | 10 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 0 | 15 | 104 | 196 | 0 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 228 | 40 | 10 | 0 | 152 | 18 | 0 | 9 | 295 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 0 | 315 | 106 | 0 | 17 | 3 | 0 | 0 | 17 | 0 | 1 | 0 | 200 | 0 | 57 | 0 | 17 | 0 | 17 | 3 |  | 800 | 0 | 300 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 106 | 0 | 151 | 0 | 23 | 0 | 181 | 0 | 328 | 0 | 0 | 0 | 0 | 34 | 0 | 4 | 0 | 300 | 152 | 0 | 0 | 0 |  | 5320 | 2886 | 8206 | 4353 | 800 | 1513 | 551 | 452 | 121 | 245 | 104 | 67 | 0 | 84.59
12:00 | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 333 | 302 |  | 0 | 240 | 285 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 8 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 335 | 295 | 199 | 26 | 136 | 13 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 110 | 194 | 0 | 21 | 1 | 43 | 42 | 11 | 0 | 0 | 225 | 40 | 10 | 0 | 152 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 1 | 1 | 10 | 17 | 0 | 315 | 105 | 0 | 17 | 4 | 0 | 0 | 17 | 0 | 8 | 0 | 200 | 0 | 57 | 0 | 17 | 0 | 17 | 33 |  | 801 | 0 | 300 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 164 | 0 | 23 | 0 | 188 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 300 | 152 | 0 | 0 | 1 |  | 5512 | 2961 | 8473 | 4548 | 801 | 1529 | 568 | 450 | 122 | 243 | 110 | 102 | 0 | 84.59
13:00 | 0 | 0 | 0 | 170 | 0 | 58 | 0 | 361 | 345 |  | 0 | 240 | 290 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 345 | 300 | 206 | 26 | 50 | 13 | 30 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 112 | 194 | 0 | 21 | 3 | 43 | 42 | 11 | 0 | 0 | 220 | 40 | 10 | 0 | 151 | 18 | 0 | 9 | 310 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 15 | 0 | 10 | 17 | 0 | 365 | 105 | 0 | 17 | 3 | 0 | 0 | 17 | 0 | 19 | 0 | 200 | 0 | 55 | 0 | 17 | 0 | 17 | 33 |  | 800 | 0 | 360 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 130 | 0 | 203 | 0 | 23 | 0 | 195 | 0 | 408 | 1 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 300 | 151 | 0 | 0 | 3 |  | 5699 | 3140 | 8839 | 4676 | 800 | 1716 | 616 | 451 | 122 | 244 | 112 | 102 | 0 | 84.59
14:00 | 0 | 0 | 0 | 170 | 0 | 81 | 0 | 380 | 347 |  | 0 | 240 | 245 | 0 | 0 | 0 | 330 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 24 | 0 | 0 | 63 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 310 | 270 | 180 | 26 | 79 | 0 | 30 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 118 | 196 | 6 | 21 | 2 | 43 | 42 | 50 | 0 | 0 | 230 | 40 | 10 | 0 | 151 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 17 | 0 | 10 | 17 | 0 | 365 | 115 | 0 | 17 | 3 | 0 | 0 | 17 | 0 | 36 | 0 | 240 | 0 | 42 | 0 | 17 | 0 | 17 | 35 |  | 791 | 0 | 400 | 0 | 0 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 141 | 0 | 206 | 0 | 23 | 0 | 184 | 0 | 363 | 23 | 0 | 0 | 0 | 105 | 0 | 7 | 0 | 330 | 210 | 0 | 0 | 4 |  | 5850 | 3321 | 9171 | 4813 | 791 | 1793 | 712 | 484 | 123 | 244 | 118 | 93 | 0 | 84.59
15:00 | 0 | 0 | 0 | 170 | 0 | 84 | 0 | 383 | 344 |  | 0 | 240 | 260 | 0 | 0 | 0 | 329 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 35 | 310 | 295 | 212 | 26 | 85 | 20 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 120 | 193 | 6 | 21 | 0 | 43 | 42 | 50 | 0 | 0 | 206 | 65 | 70 | 0 | 173 | 18 | 0 | 9 | 280 | 16 | 11 | 0 | 0 | 0 | 0 | 50 | 0 | 17 | 0 | 10 | 17 | 0 | 365 | 105 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 46 | 0 | 17 | 0 | 17 | 20 |  | 788 | 0 | 395 | 0 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 142 | 0 | 194 | 0 | 22 | 0 | 163 | 0 | 390 | 35 | 0 | 0 | 0 | 52 | 0 | 6 | 0 | 350 | 220 | 0 | 0 | 3 |  | 5802 | 3288 | 9090 | 4680 | 788 | 1892 | 664 | 502 | 122 | 245 | 120 | 77 | 0 | 84.59
16:00 | 0 | 0 | 0 | 170 | 0 | 25 | 0 | 387 | 306 |  | 0 | 240 | 265 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 60 | 285 | 280 | 183 | 8 | 84 | 20 | 30 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 116 | 193 | 8 | 21 | 0 | 43 | 42 | 11 | 0 | 0 | 233 | 64 | 84 | 0 | 219 | 18 | 0 | 9 | 260 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 0 | 365 | 75 | 0 | 4 | 1 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 33 | 0 | 47 | 0 | 17 | 2 |  | 788 | 0 | 320 | 0 | 0 | 185 | 0 | 0 | 0 | 2 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 181 | 0 | 22 | 0 | 196 | 0 | 390 | 17 | 0 | 0 | 0 | 55 | 0 | 5 | 0 | 380 | 154 | 0 | 0 | 2 |  | 5478 | 3106 | 8584 | 4512 | 788 | 1636 | 650 | 530 | 122 | 187 | 116 | 43 | 0 | 84.59
17:00 | 0 | 0 | 0 | 170 | 0 | 25 | 0 | 332 | 307 |  | 0 | 240 | 265 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 12 | 0 | 0 | 32 | 60 | 100 | 120 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 60 | 285 | 280 | 175 | 8 | 85 | 23 | 30 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 112 | 193 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 231 | 40 | 30 | 0 | 178 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 2 | 327 | 75 | 0 | 17 | 1 | 0 | 0 | 17 | 0 | 36 | 0 | 0 | 0 | 15 | 0 | 53 | 0 | 17 | 2 |  | 788 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 0 | 5 | 0 | 0 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 167 | 0 | 22 | 0 | 178 | 0 | 307 | 17 | 0 | 0 | 0 | 55 | 0 | 3 | 0 | 400 | 151 | 0 | 0 | 0 |  | 5181 | 2950 | 8131 | 4237 | 788 | 1525 | 681 | 550 | 92 | 125 | 112 | 21 | 0 | 84.58
18:00 | 0 | 0 | 0 | 170 | 0 | 25 | 0 | 297 | 267 |  | 0 | 240 | 250 | 0 | 0 | 2 | 250 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 12 | 0 | 0 | 32 | 60 | 100 | 120 | 0 | 0 | 0 | 70 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 36 | 70 | 0 | 60 | 275 | 280 | 201 | 8 | 85 | 23 | 10 | 0 | 10 | 0 | 0 | 10 | 22 | 11 | 33 | 20 | 104 | 199 | 8 | 21 | 0 | 43 | 43 | 11 | 0 | 0 | 230 | 40 | 30 | 0 | 178 | 18 | 0 | 10 | 270 | 16 | 11 | 0 | 20 | 0 | 0 | 32 | 0 | 0 | 0 | 10 | 17 | 28 | 327 | 55 | 0 | 17 | 0 | 16 | 0 | 17 | 0 | 36 | 0 | 60 | 0 | 3 | 0 | 53 | 0 | 17 | 1 |  | 788 | 0 | 280 | 0 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 70 | 0 | 160 | 0 | 23 | 0 | 130 | 0 | 288 | 17 | 0 | 0 | 0 | 34 | 0 | 2 | 0 | 350 | 131 | 0 | 0 | 0 |  | 5137 | 2602 | 7739 | 4125 | 788 | 1405 | 664 | 500 | 92 | 55 | 104 | 6 | 0 | 84.58
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 58 | 0 | 274 | 322 |  | 0 | 240 | 285 | 0 | 0 | 15 | 250 | 0 | 35 | 0 | 16 | 25 | 0 | 0 | 0 | 0 | 54 | 35 | 15 | 16 | 25 | 8 | 25 | 24 | 12 | 0 | 33 | 60 | 100 | 120 | 4 | 0 | 0 | 120 | 0 |  | 2 | 0 | 51 | 10 | 0 | 8 | 21 | 42 | 70 | 0 | 60 | 300 | 305 | 197 | 8 | 86 | 23 | 10 | 0 | 24 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 134 | 197 | 8 | 21 | 0 | 44 | 43 | 11 | 0 | 0 | 232 | 63 | 30 | 0 | 197 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 32 | 0 | 0 | 84 | 0 | 0 | 0 | 50 | 47 | 48 | 348 | 60 | 8 | 25 | 0 | 16 | 0 | 56 | 34 | 78 | 50 | 260 | 5 | 0 | 22 | 84 | 0 | 17 | 0 |  | 788 | 0 | 300 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 60 | 0 | 0 | 11 | 8 | 15 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 77 | 0 | 150 | 0 | 45 | 0 | 144 | 0 | 384 | 55 | 0 | 40 | 0 | 80 | 0 | 0 | 50 | 360 | 151 | 0 | 4 | 0 |  | 6028 | 3045 | 9073 | 4506 | 788 | 1388 | 1442 | 510 | 93 | 212 | 134 | 0 | 0 | 84.58
19:30 | 0 | 0 | 0 | 170 | 0 | 85 | 0 | 392 | 322 |  | 0 | 240 | 260 | 0 | 0 | 0 | 300 | 0 | 31 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 17 | 16 | 25 | 8 | 25 | 0 | 30 | 0 | 33 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 10 | 0 | 34 | 10 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 275 | 280 | 202 | 8 | 84 | 23 | 10 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 134 | 200 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 232 | 64 | 84 | 0 | 225 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 45 | 0 | 0 | 195 | 0 | 0 | 0 | 10 | 100 | 148 | 388 | 96 | 40 | 51 | 0 | 16 | 0 | 108 | 0 | 115 | 10 | 260 | 17 | 0 | 0 | 116 | 0 | 17 | 0 |  | 788 | 0 | 300 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 70 | 0 | 0 | 0 | 87 | 0 | 0 | 20 | 8 | 34 | 22 | 0 | 0 | 0 | 0 | 150 | 0 | 0 | 135 | 0 | 183 | 0 | 52 | 50 | 183 | 0 | 396 | 105 | 0 | 88 | 0 | 113 | 0 | 0 | 70 | 400 | 222 | 0 | 17 | 0 |  | 6640 | 3564 | 10204 | 4800 | 788 | 1617 | 1975 | 550 | 93 | 247 | 134 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 372 | 347 |  | 0 | 240 | 228 | 0 | 0 | 0 | 333 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 16 | 25 | 8 | 25 | 24 | 34 | 0 | 33 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 19 | 0 | 34 | 10 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 275 | 280 | 202 | 8 | 85 | 23 | 10 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 120 | 200 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 220 | 65 | 84 | 0 | 225 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 177 | 0 | 0 | 0 | 10 | 100 | 80 | 400 | 105 | 50 | 51 | 0 | 16 | 0 | 108 | 0 | 115 | 10 | 260 | 0 | 0 | 0 | 115 | 0 | 17 | 0 |  | 791 | 0 | 385 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 92 | 6 | 0 | 33 | 25 | 35 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 140 | 0 | 184 | 0 | 68 | 57 | 186 | 0 | 380 | 105 | 0 | 86 | 0 | 113 | 0 | 0 | 70 | 420 | 221 | 0 | 17 | 0 |  | 6549 | 3739 | 10288 | 5003 | 791 | 1647 | 1798 | 570 | 93 | 266 | 120 | 0 | 0 | 84.58
21:00 | 0 | 0 | 0 | 170 | 0 | 93 | 0 | 395 | 345 |  | 0 | 240 | 272 | 0 | 0 | 0 | 330 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 13 | 25 | 8 | 25 | 24 | 51 | 0 | 34 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 0 | 21 | 25 | 70 | 0 | 60 | 295 | 295 | 193 | 8 | 85 | 23 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 126 | 199 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 192 | 63 | 84 | 0 | 219 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 80 | 81 | 30 | 403 | 105 | 52 | 54 | 0 | 0 | 0 | 108 | 0 | 115 | 70 | 260 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 22 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 194 | 0 | 84 | 100 | 193 | 0 | 411 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 75 | 500 | 220 | 0 | 17 | 0 |  | 6639 | 3912 | 10551 | 5048 | 791 | 1677 | 2013 | 650 | 94 | 152 | 126 | 0 | 0 | 84.58
22:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 391 | 346 |  | 0 | 240 | 277 | 0 | 0 | 0 | 332 | 0 | 57 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 15 | 25 | 8 | 25 | 24 | 51 | 0 | 0 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 0 | 21 | 31 | 70 | 0 | 60 | 270 | 290 | 205 | 8 | 86 | 23 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 130 | 199 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 226 | 63 | 84 | 0 | 219 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 100 | 118 | 30 | 401 | 107 | 52 | 54 | 0 | 0 | 0 | 110 | 0 | 117 | 100 | 262 | 31 | 0 | 0 | 116 | 0 | 17 | 0 |  | 791 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 22 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 144 | 0 | 181 | 0 | 81 | 100 | 181 | 0 | 337 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 480 | 221 | 0 | 0 | 0 |  | 6769 | 3775 | 10544 | 5002 | 791 | 1609 | 2165 | 635 | 60 | 152 | 130 | 0 | 0 | 84.58
23:00 | 0 | 0 | 0 | 170 | 0 | 92 | 0 | 393 | 346 |  | 0 | 240 | 278 | 0 | 0 | 0 | 331 | 0 | 57 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 17 | 25 | 8 | 25 | 21 | 51 | 0 | 0 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 17 | 0 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 280 | 295 | 207 | 8 | 86 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 128 | 199 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 182 | 59 | 84 | 0 | 219 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 100 | 120 | 30 | 402 | 107 | 52 | 54 | 0 | 0 | 0 | 110 | 0 | 108 | 100 | 263 | 35 | 0 | 0 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 22 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 144 | 0 | 181 | 0 | 84 | 100 | 171 | 0 | 335 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 220 | 0 | 0 | 0 |  | 6734 | 3712 | 10446 | 4965 | 791 | 1609 | 2156 | 585 | 60 | 152 | 128 | 0 | 0 | 84.57
24:00 | 0 | 0 | 0 | 170 | 0 | 93 | 0 | 393 | 347 |  | 0 | 240 | 272 | 0 | 0 | 0 | 330 | 0 | 87 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 17 | 0 | 17 | 25 | 8 | 25 | 21 | 51 | 0 | 0 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 295 | 334 | 210 | 8 | 86 | 20 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 199 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 182 | 59 | 84 | 0 | 212 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 100 | 120 | 33 | 403 | 97 | 52 | 54 | 0 | 0 | 0 | 110 | 0 | 109 | 100 | 0 | 35 | 0 | 0 | 116 | 0 | 17 | 0 |  | 791 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 22 | 52 | 25 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 144 | 0 | 187 | 0 | 83 | 100 | 173 | 0 | 366 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 380 | 220 | 0 | 0 | 0 |  | 6521 | 3678 | 10199 | 4781 | 791 | 1638 | 2142 | 535 | 60 | 126 | 126 | 0 | 0 | 84.57
KWH | 0 | 0 | 0 | 4221000 | 0 | 1557727 | 0 | 8761340 | 7662000 |  | 0 | 5640250 | 6373760 | 0 | 0 | 24278 | 7149030 | 0 | 1536000 | 0 | 22464 | 187680 | 0 | 0 | 0 | 0 | 606960 | 101702 | 24465 | 376596 | 600000 | 219960 | 764600 | 660200 | 346080 | 0 | 414480 | 1448000 | 2400000 | 3000000 | 47430 | 0 | 0 | 2779774 | 0 |  | 176880 | 0 | 125484 | 17520 | 0 | 15840 | 482352 | 1017120 | 1858568 | 0 | 540972 | 7018500 | 6938000 | 4821000 | 317818 | 2597210 | 459432 | 694080 | 0 | 839172 | 0 | 0 | 97800 | 507744 | 257580 | 788000 | 486440 | 2749440 | 4679120 | 138240 | 489816 | 10750 | 1026000 | 995160 | 759600 | 0 | 0 | 4595000 | 1172736 | 1248000 | 0 | 4518110 | 388000 | 0 | 230580 | 5269800 | 352608 | 264000 | 0 | 110399 | 0 | 0 | 2700000 | 0 | 109440 | 2159 | 709440 | 1324320 | 413163 | 8515000 | 2427600 | 272400 | 836363 | 24961 | 45164 | 0 | 1372471 | 50160 | 1667400 | 549120 | 4772100 | 128640 | 359920 | 33120 | 1712455 | 0 | 443160 | 140912 |  | 19216000 | 0 | 8759520 | 0 | 0 | 3671040 | 0 | 0 | 0 | 5760 | 0 | 0 | 579845 | 0 | 0 | 1637000 | 0 | 0 | 5939 | 497952 | 129110 | 0 | 122981 | 686400 | 255536 | 505200 | 0 | 214326 | 0 | 0 | 3764100 | 0 | 0 | 2906100 | 0 | 4430991 | 0 | 1188941 | 464640 | 4551491 | 0 | 8793945 | 876480 | 0 | 1040256 | 0 | 1851628 | 0 | 42609 | 714048 | 10043800 | 4561527 | 0 | 249600 | 23340 |  | 144590115 | 81790105 | 226380220 | 113491376 | 19216000 | 40865605 | 28910396 | 13807900 | 1862480 | 4872372 | 2749440 | 604651 | 0
Fuel Cost | 0 | 0 | 0 | 6204870 | 0 | 2056199.64 | 0 | 8848953.4 | 7891860 |  | 0 | 6147872.5 | 7074873.6 | 0 | 0 | 205391.88 | 7434991.2 | 0 | 2657280 | 0 | 204871.68 | 1846771.2 | 0 | 0 | 0 | 0 | 4430808 | 786156.46 | 241224.9 | 282447 | 450000 | 0 | 0 | 0 | 3346593.6 | 0 | 111909.6 | 390960 | 4344000 | 5430000 | 440624.7 | 0 | 0 | 4725615.8 | 0 |  | 0 | 0 | 1217194.8 | 167316 | 0 | 125452.8 | 607763.52 | 3020846.4 | 2750680.64 | 0 | 795228.84 | 5193690 | 6938000 | 4435320 | 409985.22 | 2986791.5 | 519158.16 | 971712 | 0 | 1434984.12 | 0 | 0 | 933990 | 644834.88 | 193185 | 1379000 | 364830 | 20620800 | 4959867.2 | 1255219.2 | 622066.32 | 171355 | 1682640 | 1592256 | 1352088 | 0 | 0 | 4778800 | 2310289.92 | 2383680 | 0 | 7816330.3 | 849720 | 0 | 470383.2 | 5322498 | 264456 | 200640 | 0 | 834616.44 | 0 | 0 | 14040000 | 0 | 1076889.6 | 25238.71 | 5781936 | 14368872 | 2912799.15 | 7918950 | 22139712 | 2574180 | 7284721.73 | 0 | 341439.84 | 0 | 12064020.09 | 500596.8 | 14289618 | 3657139.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110684160 | 0 | 9197496 | 0 | 0 | 50880614.4 | 0 | 0 | 0 | 60364.8 | 0 | 0 | 898759.75 | 0 | 0 | 3355850 | 0 | 0 | 60340.24 | 4406875.2 | 994147 | 0 | 1191685.89 | 6651216 | 2478699.2 | 969984 | 0 | 162244.782 | 0 | 0 | 20401422 | 0 | 0 | 3400137 | 0 | 5848908.12 | 0 | 1783411.5 | 7903526.4 | 5325244.47 | 0 | 8706005.55 | 9150451.2 | 0 | 9872029.44 | 0 | 14368633.28 | 0 | 470829.45 | 5276814.72 | 44092282 | 0 | 0 | 0 | 0 |  | 277108057.74 | 328592132.392 | 605700190.132 | 127472536.052 | 110684160 | 43820269.88 | 175295881.71 | 64493704 | 502869.6 | 62142545.73 | 20620800 | 667423.16 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 0 | 13 | 0 | 333 | 302 |  | 0 | 240 | 285 | 0 | 0 | 0 | 280 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 8 | 25 | 24 | 0 | 0 | 62 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 80 | 0 | 0 | 335 | 295 | 199 | 26 | 136 | 13 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 33 | 16 | 110 | 194 | 0 | 21 | 1 | 43 | 42 | 11 | 0 | 0 | 225 | 40 | 10 | 0 | 152 | 18 | 0 | 9 | 290 | 16 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 1 | 1 | 10 | 17 | 0 | 315 | 105 | 0 | 17 | 4 | 0 | 0 | 17 | 0 | 8 | 0 | 200 | 0 | 57 | 0 | 17 | 0 | 17 | 33 |  | 801 | 0 | 300 | 0 | 0 | 243 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 130 | 0 | 164 | 0 | 23 | 0 | 188 | 0 | 350 | 0 | 0 | 0 | 0 | 34 | 0 | 5 | 0 | 300 | 152 | 0 | 0 | 1 |  | 8473 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 0 | 93 | 0 | 395 | 345 | 0 | 0 | 240 | 272 | 0 | 0 | 0 | 330 | 0 | 90 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 13 | 25 | 8 | 25 | 24 | 51 | 0 | 34 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 17 | 0 | 0 | 0 | 21 | 25 | 70 | 0 | 60 | 295 | 295 | 193 | 8 | 85 | 23 | 10 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 126 | 199 | 8 | 21 | 0 | 43 | 43 | 50 | 0 | 0 | 192 | 63 | 84 | 0 | 219 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 0 | 80 | 81 | 30 | 403 | 105 | 52 | 54 | 0 | 0 | 0 | 108 | 0 | 115 | 70 | 260 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 791 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 22 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 194 | 0 | 84 | 100 | 193 | 0 | 411 | 105 | 0 | 90 | 0 | 113 | 0 | 0 | 75 | 500 | 220 | 0 | 17 | 0 |  | 10551 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 412 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 90 | 0 | 102 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 10 | 25 | 24 | 52 | 0 | 0 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 42 | 80 | 0 | 60 | 330 | 360 | 210 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 22 | 149 | 202 | 8 | 21 | 0 | 44 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 150 | 18 | 0 | 10 | 0 | 16 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 260 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 807 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 20 | 60 | 0 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 35 | 0 | 30 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 144 | 0 | 200 | 0 | 82 | 100 | 200 | 0 | 400 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 90
Forecast for Day | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 360 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 60 | 0 | 100 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 25 | 20 | 52 | 0 | 0 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 30 | 80 | 0 | 60 | 330 | 360 | 210 | 8 | 130 | 20 | 55 | 0 | 42 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 121 | 202 | 8 | 21 | 1.6 | 43 | 43 | 51 | 0 | 0 | 180 | 60 | 84 | 0 | 150 | 18 | 0 | 10 | 0 | 16 | 11 | 100 | 270 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 260 | 90 | 50 | 162 | 112 | 0 | 17 | 30 |  | 807 | 0 | 360 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 35 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 200 | 0 | 80 | 50 | 200 | 0 | 400 | 105 | 100 | 90 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 90 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 307 | 308 | 0 | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 |  | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 20 | 70 | 0 | 60 | 265 | 290 | 187 | 8 | 85 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 82 | 200 | 8 | 21 | 1 | 43 | 43 | 14 | 0 | 0 | 183 | 60 | 10 | 0 | 158 | 18 | 0 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 352 | 85 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 26 | 0 | 230 | 0 | 31 | 0 | 53 | 0 | 17 | 21 | 0 | 793 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 94 | 0 | 165 | 0 | 11 | 0 | 167 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 181 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 8120 | 9:00
| Highest Generation |  | 10752 | 1:00
| Day Peak Generation |  | 8473 | 12:00
| Evening Peak Generation |  | 10551 | 21:00
| HVDC Max Flow |  | 801 | 2:00
| HVDC EvPeak Flow |  | 791 | 21:00
| Load factor L.F |  | 87.73%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-28
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8473 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 7385 | MW
Evening Peak Generation : |  | 10551 | MW Hour : | 21:00 | Available Max Generation : |  | 14994 | MW
E.P. Demand (at gen end) : |  | 10551 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 11000 | MW
Maximum Generation : |  | 10752 | MW Hour : | 1:00 | Reserve(Generation end) |  | 3994 | MW
Total Gen. (MKWH) : |  | 226.3802 | System Load Factor : | 87.73% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -184 | MW at | 4:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-28
Actual : | 84.58 | Ft.(MSL) , | Rule curve : | 88.32 | Ft.( MSL )
Gas Consumed : | Total = | 1219.25 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 171292805.932
: |  | Coal : | 64493704 | Oil : | 237438427.44 | Total : | 473224937.372
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3903.1339 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1326.9567 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1188.8513 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1074.2069 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 970.7566 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 783.3654 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 438.4374 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 201.7066 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 604.1683 |  |  | 0 | 0%
Total | 0 |  | 10491.5831 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4 & 7
3) Ashuganj-4 & 5
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7) Baghabari-71 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tongi-Bashundhara 132 kV Ckt-1 tripped at 08:50 from both ends showing Dist.Z1, A,C at Tongi end
& Dist.Z1 at Bashundhara end and was switched on at 09:11.
b) Ishwardi 230/132 kV T03 transformer tripped at 08:15 showing OLTC trip and was switched on at 11:12.
c) Jamalpur 132/33 kV T4 transformer was under shut down from 08:54 to 16:24 for C/M.
d) Kabirpur 132/33 kV T2 transformer was under shut down from 10:58 to 14:15 for C/M.
e) Madunaghat 132/33 kV T1 & T2 transformers tripped at 10:56 due to heavy flashing at 33 kV Bus and
were switched on at 11:22.
f) Bibiyana South tripped at 14:40 due to GBC problem and GT was synchronized at 17:39 and again tripped
23:53 and was synchronized at 00:28(28/07/2021).
g) Ashuganj Unit-5 was synchronized at 14:16.
h) Summit Bibiyana tripped at 18:04 due to problem with control system.
i) Sirajganj-Baghabari 132 kV Ckt tripped at 17:29 showing Dist. & SOTF and was switched on at 19:20.
j) Bakulia 132/33 kV T3 transformer was under shut down from 20:40 to 21:38 due to R/H maintenance by PDB. |  |  |  |  | About 29 MW power interruption occurred under Bakulia S/S area
from 20:40 to 21:38.
k) Khulna 225 MW CCPP ST & GT were shutdown at 18:17 and 20:12 respectively.
l) Barishal South 132/33 kV T1 & T2 (33 kV side) transformers tripped at 00:15(28/07/2021) due to 33 kV |  |  |  |  | About 32 MW power interruption occurred under Barishal South S/S
WZPDCL feeder fault and were switched on at 00:36(28/07/2021). |  |  |  |  | area from 00:15(28/07/2021) to 00:36(28/07/2021).
m) Barishal South-(Barguna)-Patuakhali 132 kV Ckt tripped at 01:32(28/07/2021) from Barishal South end
showing Dist. Z1, E/F and was switched on at 09:07(28/07/2021).
n) HVDC-Khulna(S) 230 kV Ckt-1 is under shutdown since 07:15(28/07/2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4221000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 93 | 1557727 | Engine problem
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 8761340 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7662000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5640250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 272 | 6373760 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 24278 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 13 | 376596 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 90 | 1536000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7149030
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 22464 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 606960 | Low demand
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 32 | 187680 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 0 | 101702 | Reserve.
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 24465 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 819960 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 764600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 24 | 660200 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 346080
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 0 | 110399 | Reserve.
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 0 | 109440 | Reserve.
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 52 | 272400 | Low demand
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 128640 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 33120 | Reserve.
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 140912
| Dhaka area Total |  |  |  | 5819 | 2200 | 47631003
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 47430 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 2159
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 15840 | Reserve.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 94 | 1862480 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2779774 | Machine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 54 | 836363 | Low demand
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 17 | 125484 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 17520 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 80 | 709440 | Low demand
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 482352
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 25 | 1017120
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Reserve.
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 24961
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 45164 | Reserve.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 108 | 1372471
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 549120 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 1712455
| Chattogram area Total |  |  |  | 2382 | 933 | 17000133
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 70 | 1858568 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 60 | 540972 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 193 | 4821000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 295 | 7018500 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 6938000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 459432 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 10 | 694080 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 317818 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 839172 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 30 | 413163 | Low demand
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 85 | 2597210 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 81 | 1324320 | Low demand
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 507744
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 257580
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 126 | 2749440
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 788000
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 97800 | Reserve.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 486440 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 50160 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 115 | 1667400
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443160 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1537 | 34869959
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 199 | 4679120
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 489816
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 138240 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10750
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 200 | 2700000
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 105 | 2427600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 359920
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 176880
| Mymensingh Area Total |  |  |  | 709 | 557 | 10982326
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1026000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 995160 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 192 | 4595000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 759600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 63 | 1172736
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1248000
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 219 | 4518110
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 388000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 352608 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 5269800 | Tripped at 18:04.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 403 | 8515000 | FGMO
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 230580
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 4772100
| Sylhet Area Total |  |  |  | 2377 | 1412 | 34106694
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 791 | 19216000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 3671040 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 5760 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 8759520
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 464640
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 876480
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1396 | 32993440
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 579845
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 0 | 0 | Under maint.
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 84 | 1188941 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 10043800
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4561527
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 249600 | Low demand
| Barisal Area Total |  |  |  | 2046 | 853 | 16623713
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1637000 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 0 | 0 | Reserve.
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 5939 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 129110 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 122981 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 144 | 2906100 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 194 | 4430991 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 193 | 4551491 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 411 | 8793945 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 255536 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 505200
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 214326
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 686400
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 47 | 497952 | Low demand
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 90 | 1040256 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 75 | 714048 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 23340
| Rajshahi Area Total |  |  |  | 2179 | 1400 | 26514615
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Coal shortage
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3764100 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1851628
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 42609
| Rangpur Area Total |  |  |  | 605 | 263 | 5658337
| Total |  |  |  | 21280 | 10551 | 226380220
| Eastern Grid Total |  |  |  | 14321 | 6639 | 144590115
| Western Grid Total |  |  |  | 6959 | 3912 | 81790105
| National Grid Total |  |  |  | 21280 | 10551 | 226380220
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-27
(a) ENTIRE EASTERN GRID : |  | 6320 | MW | (b) ENTIRE WESTERN GRID : |  | 3733 | MW
i) Dhaka area |  | 2883 | MW | i) Khulna area |  | 1381 | MW
ii) Chittagong area |  | 787 | MW | ii) Rajshahi area |  | 1245 | MW
iii) Comilla area |  | 1093 | MW | iii) Barisal area |  | 285 | MW
iv) Mymensingh area |  | 1025 | MW | iv) Rangpur area |  | 822 | MW
v) Sylhet area |  | 532 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 10053 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 78 | 21:00 | Kishoreganj | 144 | 1:00 | Jessore | 108 | 22:00
Munsiganj | 85 | 1:00 | Netrokona | 136 | 20:00 | Benapol | 56 | 19:30
Sonargaon | 44 | 1:00 | Jamalpur | 158 | 0:00 | Jhenida | 107 | 19:30
Shyampur | 64 | 1:00 | Sherpur | 134 | 21:00 | Bottail | 110 | 20:00
Bhulta | 89 | 1:00 | Srimongal | 62 | 21:00 | G.K Project | 59 | 21:00
Madanganj | 25 | 12:00 | Shahjibazar | 101 | 21:00 | Faridpur | 137 | 1:00
Shitalakhya | 57 | 13:00 | Fenchuganj | 47 | 19:30 | Rajbari | 49 | 21:00
Rahim steel | 0 | 1:00 | Kulawara | 50 | 19:00 | Madaripur | 104 | 21:00
Matuail | 29 | 20:00 | Sylhet | 127 | 19:00 | Sariatpur | 72 | 1:00
Ghorasal | 61 | 23:00 | Chatak | 33 | 21:00 | Gopalganj | 94 | 21:00
Narsingdi | 137 | 1:00 | Sunamganj | 55 | 21:00 | Bagerhat | 82 | 22:00
Haripur (SBU) | 46 | 23:00 | Biani Bazar | 71 | 22:00 | Mongla | 26 | 12:00
Sreenagar | 40 | 1:00 | Comilla (S) | 134 | 19:00 | Satkhira | 92 | 1:00
Ullon | 47 | 1:00 | Comilla(N) | 127 | 21:00 | Gallamari | 30 | 13:00
Hasnabad | 69 | 1:00 | Chandpur | 82 | 1:00 | Magura | 54 | 19:30
Magbazar | 72 | 12:00 | Feni | 115 | 1:00 | Norail | 42 | 20:00
Maniknagar | 62 | 14:00 | Chowmuhani | 206 | 1:00 | Chuadanga | 92 | 21:00
Bangabhaban | 12 | 13:00 | Ashuganj | 45 | 23:00 | Borguna | 16 | 1:00
Motijheel | 20 | 12:00 | Daudkandi | 134 | 1:00 | Barisal(N) | 48 | 1:00
Narinda | 36 | 1:00 | B.Baria | 166 | 22:00 | Barisal (S) | 94 | 1:00
Kazla | 57 | 0:00 | Ramganj | 92 | 1:00 | Patuakhali | 112 | 1:00
Dhanmondi | 126 | 13:00 | Chaddagram | 60 | 1:00 | Bhandaria | 40 | 21:00
Lalbag | 48 | 13:00 | PHP | 9 | 18:30 | Borhan Uddin | 45 | 1:00
Madartek | 66 | 1:00 | Kochua | 68 | 22:00 | Ishurdi | 58 | 20:00
Dhaka University | 19 | 12:00 | Madunaghat | 51 | 1:00 | Ruppur Paromanobik | 3 | 7:00
Aftabnagar | 9 | 13:00 | Hathazari | 80 | 1:00 | Natore | 125 | 20:00
Fatullah | 30 | 1:00 | Khulshi | 96 | 20:00 | Bogra | 142 | 21:00
Nawabganj | 49 | 21:00 | Halishahar | 60 | 20:00 | Noagaon | 110 | 21:00
Keraniganj | 49 | 23:00 | Baraulia | 53 | 2:00 | Rajshahi | 144 | 21:00
Mirpur | 94 | 19:00 | Sikalbaha | 23 | 1:00 | Rajshahi New | 13 | 19:30
Kalyanpur | 96 | 13:00 | Dohazari | 92 | 1:00 | C.Nawabganj | 60 | 20:00
Gulshan | 78 | 13:00 | Cox'sbazar | 67 | 21:00 | Amnura | 50 | 1:00
Uttara | 70 | 1:00 | Chandraghona | 30 | 19:00 | Pabna | 100 | 21:00
Uttara New | 12 | 13:00 | Kaptai | 4.4 | 18:30 | Shahjadpur | 94 | 21:00
Kamrangirchar | 57 | 1:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 91 | 20:00
Savar | 104 | 18:30 | Bakulia | 78 | 12:00 | Niyamatpur | 77 | 1:00
Bhasantec | 109 | 13:00 | Julda | 13 | 1:00 | Joypurhat | 59 | 21:00
Agargaon | 69 | 1:00 | TK chemical | 26 | 1:00 | Sherpur(Bogura) | 50 | 1:00
Satmosjid | 84 | 1:00 | Modern Steel | 0 | #N/A | Mohastangor | 68 | 1:00
Tongi | 72 | 1:00 | Shahmirpur | 17 | 1:00 | Bhangura | 32 | 21:00
Kabirpur | 125 | 20:00 | Khagrachhari | 28 | 9:00 | Rangpur | 131 | 21:00
Basundhara | 189 | 13:00 | Matarbari | 20.5 | 1:00 | Lalmonirhat | 48 | 20:00
Manikganj | 74 | 21:00 | Baroiar Hat | 40 | 1:00 | Saidpur | 100 | 21:00
Joydevpur | 93 | 22:00 | Rangamati | 12 | 19:00 | Purbasadipur | 112 | 21:00
New Tongi | 62 | 13:00 | Abul Khair 230 | 8 | 19:00 | Thakurgaon | 90 | 20:00
Kodda | 121 | 22:00 | BSRM | 2 | 1:00 | Palashbari | 124 | 19:30
Dhamrai | 80 | 22:00 | GPH Ispat | 89 | 11:00 | Barapukuria | 57 | 20:00
Rajendrapur | 80 | 22:00 | Agrabad | 57 | 12:00 | Panchagar | 54 | 19:30
Valuka | 76 | 22:00 | Goalpara | 28 | 20:00 | Joldhaka | 66 | 20:00
Tangail | 208 | 22:00 | Central S/S | 84 | 20:00 | Kurigram | 60 | 2:00
Mymensing | 202 | 23:00 | Noapara | 51 | 20:00 | Mithapukur | 36 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 9:00 | 397 | 21:00 | Kaliakoir | 393 | 0.33333 | 385 | 0.95833
| Bheramara | 403 | 18:30 | 396 | 1:00 | Bhulta | 386 | 0.125 | 378 | 0.041667
| Ashuganj(N) | 3856 | 9:00 | 380 | 12:00 | Gopalganj | 409 | 0.625 | 392 | 0.041667
| Payra | 414 | 9:00 | 404 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 227 | 19:00 | 221 | 4:00
| Ishurdi | 235 | 18:30 | 225 | 13:00 | Megnaghat | 233 | 9:00 | 228 | 14:00
| Ashuganj | 238 | 9:00 | 235 | 1:00 | Fenchuganj | 236 | 9:00 | 232 | 19:30
| Serajganj | 230 | 7:00 | 225 | 1:00 | Siddhirganj | 233 | 9:00 | 228 | 13:00
| Baghabari | 233 | 18:30 | 225 | 22:00 | Maniknagar | 231 | 9:00 | 225 | 2:00
| Barapukuria | 234 | 18:30 | 222 | 23:00 | Agargaon | 229 | 8:00 | 222 | 13:00
| Bogra | 222 | 18:30 | 212 | 13:00 | Barisal | 244 | 19:00 | 236 | 2:00
| Rajshahi | 234 | 18:30 | 220 | 13:00 | Bhola 225 MW | 247 | 9:00 | 241 | 4:00
| Khulna South | 240 | 9:00 | 215 | 22:00 | AKSML | 227 | 19:00 | 221 | 16:00
| Rampura | 230 | 7:00 | 227 | 11:00 | BSRM | 230 | 18:30 | 224 | 13:00
| Haripur | 229 | 5:00 | 226 | 11:00 | Bibiyana | 238 | 9:00 | 234 | 20:00
| Hasnabad | 229 | 7:00 | 225 | 12:00 | Bhulta | 232 | 9:00 | 228 | 13:00
| Shyampur | 228 | 9:00 | 220 | 1:00 | Ashuganj (S) | 235 | 9:00 | 231 | 1:00
| Aminbazar | 230 | 1:00 | 224 | 2:00 | Kaliakoir | 224 | 6:00 | 216 | 1:00
| Tongi | 227 | 18:00 | 217 | 13:00 | GPH | 227 | 18:30 | 222 | 14:00
| Comilla (N) | 231 | 18:30 | 225 | 13:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 18:30 | 132 | 1:00 | Madanhat | 135 | 0.79167 | 131 | 0.375
| Munsiganj | 137 | 18:30 | 131 | 12:00 | Hathazari | 134 | 0.77083 | 131 | 0.16667
| Sonargaon | 134 | 19:00 | 129 | 1:00 | Khulshi | 133 | 0.79167 | 127 | 0.58333
| Shyampur | 138 | 9:00 | 135 | 1:00 | Halishahar | 134 | 0.79167 | 127 | 0.625
| Bhulta | 130 | 8:00 | 127 | 11:00 | Baraulia | 134 | 0.77083 | 129 | 0.5
| Madanganj | 133 | 16:00 | 130 | 11:00 | Sikalbaha | 135 | 0.79167 | 129 | 0.5
| Shitalakhya | 138 | 19:00 | 133 | 13:00 | Dohazari | 132 | 0.79167 | 126 | 0.041667
| Rahim steal | 135 | 18:00 | 133 | 1:00 | Cox'sbazar | 127 | 0.29167 | 117 | 0.5
| Matuail | 135 | 18:30 | 132 | 1:00 | Chandraghona | 135 | 0.77083 | 131 | 0.58333
| Ghorasal | 137 | 1:00 | 135 | 13:00 | Kaptai | 134 | 0.75 | 132 | 0.041667
| Narsinghdi | 132 | 13:00 | 123 | 1:00 | A. Khaer Stl. | 133 | 0.875 | 130 | 0.041667
| Haripur (SBU) | 135 | 18:00 | 133 | 1:00 | Bakulia | 134 | 0.8125 | 127 | 0.625
| Sreenagar | 131 | 19:00 | 127 | 1:00 | Julda | 136 | 0.77083 | 128 | 0.5
| Ullon | 134 | 3:00 | 132 | 11:00 | TK Chemical | 135 | 0.77083 | 129 | 0.20833
| Hasnabad | 138 | 18:30 | 133 | 14:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 134 | 9:00 | 130 | 11:00 | Shahmirpur | 135 | 0.875 | 127 | 0.625
| Maniknagar | 136 | 18:30 | 133 | 1:00 | Khagrachhari | 133 | 0.375 | 130 | 0.625
| Bangabhaban | 136 | 18:30 | 133 | 1:00 | Matarbari | 130 | 0.29167 | 120 | 0.5
| Motijheel | 136 | 18:30 | 133 | 1:00 | Baroiar Hat | 132 | 0.77083 | 126 | 0.041667
| Narinda | 136 | 18:30 | 133 | 1:00 | Rangamati | 134 | 18:30 | 130 | 15:00
| Kazla | 136 | 18:30 | 133 | 1:00 | Agrabad | 134 | 19:00 | 128 | 12:00
| Dhanmondi | 135 | 18:00 | 132 | 11:00 | Goalpara S/S | 138 | 8:00 | 128 | 0.91667
| Lalbag | 139 | 18:30 | 133 | 13:00 | Khulna Central S/S | 138 | 8:00 | 127 | 0.91667
| Madartek | 135 | 6:00 | 131 | 13:00 | Noapara | 133 | 7:00 | 124 | 0.91667
| Dhaka University | 135 | 5:00 | 132 | 11:00 | Jessore | 130 | 7:00 | 117 | 0.91667
| Aftabnagar | 135 | 5:00 | 131 | 13:00 | Benapol | 128 | 0.25 | 116 | 0.875
| Fatullah | 138 | 18:30 | 134 | 13:00 | Jhenida | 126 | 8:00 | 110 | 0.91667
| Nawabganj | 130 | 9:00 | 126 | 1:00 | Bottail | 131 | 0.33333 | 122 | 0.875
| Keraniganj | 131 | 18:30 | 127 | 1:00 | G.K Project | 137 | 0.77083 | 132 | 0.875
| Mirpur | 137 | 18:00 | 132 | 13:00 | Faridpur | 137 | 0.75 | 129 | 0.91667
| Kalyanpur | 138 | 18:30 | 134 | 11:00 | Rajbari | 136 | 0.33333 | 127 | 0.875
| Gulshan | 135 | 18:30 | 131 | 12:00 | Madaripur | 141 | 0.29167 | 133 | 0.83333
| Uttara | 136 | 18:00 | 132 | 1:00 | Shariyatpur S/S | 141 | 9:00 | 133 | 0.91667
| Uttara New | 137 | 12:00 | 131 | 13:00 | Gopalganj | 145 | 0.375 | 135 | 0.875
| Kamrangirchar | 137 | 18:00 | 133 | 13:00 | Bagerhat | 134 | 8:00 | 125 | 0.91667
| Savar | 131 | 9:00 | 131 | 13:00 | Mongla | 134 | 8:00 | 124 | 0.5
| Bhasantec | 136 | 9:00 | 131 | 13:00 | Satkhira | 137 | 8:00 | 124 | 22:00
| Agargaon | 138 | 9:00 | 132 | 13:00 | Gallamari | 139 | 0.33333 | 128 | 12:00
| Satmosjid | 137 | 18:30 | 132 | 1:00 | Magura | 125 | 6:00 | 106 | 0.875
| Tongi | 139 | 7:00 | 134 | 20:00 | Narail | 125 | 0.33333 | 108 | 0.875
| Kabirpur | 140 | 7:00 | 135 | 22:00 | Chuadanga | 118 | 6:00 | 99 | 0.875
| Basundhara | 137 | 18:30 | 133 | 9:00 | Borguna | 141 | 9:00 | 134 | 0.16667
| Manikganj | 139 | 18:00 | 135 | 1:00 | Barisal(N) | 143 | 8:00 | 135 | 2:00
| Joydevpur | 137 | 19:30 | 133 | 11:00 | Barisal (S) | 140 | 0.29167 | 134 | 0.041667
| New Tongi | 138 | 17:00 | 134 | 1:00 | Patuakhali(S) | 138 | 0.33333 | 132 | 0.20833
| Kodda | 134 | 19:00 | 130 | 1:00 | Bhandaria | 140 | 0.33333 | 126 | 0.33333
| Dhamrai | 134 | 18:30 | 129 | 22:00 | Ishurdi | 136 | 18:30 | 130 | 21:00
| Rajendrapur | 132 | 19:30 | 126 | 1:00 | Ruppur Paromanobik | 135 | 18:00 | 130 | 21:00
| Valuka | 126 | 18:00 | 111 | 1:00 | Natore | 133 | 18:30 | 125 | 13:00
| Tangail | 134 | 7:00 | 124 | 23:00 | Bogra | 134 | 18:30 | 123 | 12:00
| Mymensing | 127 | 9:00 | 114 | 1:00 | Noagaon | 129 | 18:30 | 117 | 13:00
| Kishorganj | 129 | 18:00 | 117 | 23:00 | Rajshahi | 132 | 18:30 | 123 | 13:00
| Netrokona | 124 | 9:00 | 108 | 23:00 | Rajshahi New | 132 | 18:30 | 122 | 13:00
| Jamalpur | 131 | 18:30 | 119 | 23:00 | C.Nawabganj | 130 | 18:30 | 121 | 13:00
| Sherpur | 128 | 18:30 | 116 | 23:00 | Amnura | 132 | 20:00 | 120 | 4:00
| Srimongal | 135 | 17:00 | 132 | 21:00 | Pabna | 134 | 18:30 | 128 | 21:00
| Shahjibazar | 135 | 6:00 | 129 | 23:00 | Shahjadpur | 137 | 18:30 | 132 | 21:00
| Fenchuganj | 135 | 9:00 | 132 | 19:00 | Serajganj | 130 | 5:00 | 127 | 19:30
| Khulawara | 134 | 5:00 | 131 | 19:00 | Niyamatpur | 125 | 18:30 | 114 | 13:00
| Sylhet | 132 | 4:00 | 129 | 18:30 | Joypurhat | 130 | 18:30 | 115 | 13:00
| Chatak | 131 | 15:00 | 126 | 19:00 | Sherpur(Bogura) | 133 | 18:30 | 124 | 13:00
| Sunamganj | 128 | 3:00 | 123 | 21:00 | Mohastangor | 132 | 18:30 | 122 | 13:00
| Biani Bazar | 129 | 6:00 | 125 | 22:00 | Bangura | 134 | 6:00 | 130 | 21:00
| Comilla(s) | 130 | 6:00 | 125 | 19:00 | Rangpur | 125 | 18:30 | 114 | 1:00
| Comilla(n) | 139 | 18:30 | 132 | 1:00 | Lalmonirhat | 125 | 18:30 | 116 | 1:00
| Chandpur | 136 | 18:30 | 125 | 13:00 | Saidpur | 127 | 18:00 | 112 | 1:00
| Feni | 134 | 18:30 | 124 | 1:00 | Purbasadipur | 125 | 18:00 | 108 | 21:00
| Chowmuhani | 132 | 18:30 | 124 | 12:00 | Thakurgaon | 125 | 18:30 | 108 | 19:30
| Ashuganj | 137 | 18:00 | 132 | 1:00 | Palashbari | 127 | 18:30 | 116 | 1:00
| Daudkandi | 134 | 18:30 | 127 | 1:00 | Barapukuria | 134 | 18:30 | 124 | 21:00
| B.Baria | 133 | 18:30 | 126 | 23:00 | Panchagar | 128 | 18:30 | 106 | 19:30
| Ramganj | 133 | 19:00 | 123 | 2:00 | Joldhaka | 124 | 0.77083 | 108 | 0.875
| Chaddagram | 136 | 18:30 | 127 | 1:00 | Kurigram | 121 | 0.77083 | 110 | 0.041667
| PHP | 133 | 18:30 | 125 | 1:00 | Mithapukur | 128 | 0.77083 | 117 | 0.041667
| Kochua | 135 | 20:00 | 127 | 1:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 20 | 6521 | 3678 | 10199 |  |  |  | QF-LDC-11
0:30 | 31 | 6655 | 3820.5 | 10475.5 | Date: | 2021-07-27
1:00 | 42 | 6789 | 3963 | 10752
1:30 | 56 | 6735.5 | 3888 | 10623.5
2:00 | 70 | 6682 | 3813 | 10495
2:30 | 92 | 6607.5 | 3742.5 | 10350 | [5 empty] | Gen. at Eve. Peak | 10551 | 10551 MW (21:00 )
3:00 | 114 | 6533 | 3672 | 10205 | [6 empty] | 21:00
3:30 | 149 | 6500 | 3573.5 | 10073.5 | [5 empty] | Gen. at Day Peak | 8473 | 8473 MW (12:00 )
4:00 | 184 | 6467 | 3475 | 9942 | [6 empty] | 12:00
4:30 | 154 | 6392 | 3460.5 | 9852.5 | [5 empty] | Highest Generation | 10752
5:00 | 124 | 6317 | 3446 | 9763 | [6 empty] | 1:00
5:30 | 121 | 6073 | 3255 | 9328
6:00 | 118 | 5829 | 3064 | 8893
6:30 | 106 | 5631 | 2999.5 | 8630.5
7:00 | 94 | 5433 | 2935 | 8368
7:30 | 83 | 5383 | 2886.5 | 8269.5
8:00 | 72 | 5333 | 2838 | 8171
8:30 | 62 | 5315.5 | 2830 | 8145.5
9:00 | 52 | 5298 | 2822 | 8120
9:30 | 28 | 5288 | 2828 | 8116
10:00 | 4 | 5278 | 2834 | 8112
10:30 | 10 | 5299 | 2860 | 8159
11:00 | 16 | 5320 | 2886 | 8206
11:30 | 20 | 5416 | 2923.5 | 8339.5
12:00 | 24 | 5512 | 2961 | 8473
12:30 | 37 | 5605.5 | 3050.5 | 8656
13:00 | 50 | 5699 | 3140 | 8839
13:30 | 30 | 5774.5 | 3230.5 | 9005
14:00 | 10 | 5850 | 3321 | 9171
14:30 | 13 | 5826 | 3304.5 | 9130.5
15:00 | 16 | 5802 | 3288 | 9090
15:30 | 33 | 5640 | 3197 | 8837
16:00 | 50 | 5478 | 3106 | 8584
16:30 | 85 | 5329.5 | 3028 | 8357.5
17:00 | 120 | 5181 | 2950 | 8131
17:30 | 75 | 5159 | 2776 | 7935
18:00 | 30 | 5137 | 2602 | 7739
18:30 | 85 | 5582.5 | 2823.5 | 8406
19:00 | 140 | 6028 | 3045 | 9073
19:30 | 154 | 6640 | 3564 | 10204
20:00 | 0 | 6549 | 3739 | 10288 |  |  |  | Executive Engineer
20:30 | 18 | 6594 | 3825.5 | 10419.5 |  |  |  | Network Operation Division
21:00 | 36 | 6639 | 3912 | 10551
21:30 | 88 | 6704 | 3843.5 | 10547.5
22:00 | 140 | 6769 | 3775 | 10544 |  |  |  |  | Page 6 of 7
22:30 | 132 | 6751.5 | 3743.5 | 10495
23:00 | 124 | 6734 | 3712 | 10446
23:30 | 72 | 6627.5 | 3695 | 10322.5
24:00 | 20 | 6521 | 3678 | 10199
10551 MW (21:00 )
8473 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-27 |  | Energy | 226380220
[11 empty] | 2021-07-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4781 | 791 | 1638 | 2156 | 535 | 60 | 126 | 0 | 126 | 0
0:30 | 4834 | 795.5 | 1834 | 2000.5 | 595 | 92.5 | 207 | 0 | 124 | 0 | Date: | 2021-07-27
1:00 | 4887 | 800 | 2030 | 1845 | 655 | 125 | 288 | 0 | 122 | 0
1:30 | 4868 | 800.5 | 2034 | 1765.5 | 654.5 | 124.5 | 257.5 | 0 | 119 | 0 | [7 empty] | Total Energy | 226.3802 | Total Energy Gen 226.380 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.380 MKWHr
2:00 | 4849 | 801 | 2038 | 1686 | 654 | 124 | 227 | 0 | 116 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4886 | 800.5 | 2034 | 1564 | 629.5 | 122.5 | 198.5 | 0 | 115 | 0 | [7 empty] | Energy Requirement | 226.3802
3:00 | 4923 | 800 | 2030 | 1442 | 605 | 121 | 170 | 0 | 114 | 0
3:30 | 4879 | 800.5 | 2028.5 | 1380 | 577.5 | 121 | 175 | 0 | 112 | 0 | [6 empty] | Shortage
4:00 | 4835 | 801 | 2027 | 1318 | 550 | 121 | 180 | 0 | 110 | 0
4:30 | 4836.5 | 801 | 2019.5 | 1245.5 | 537.5 | 119.5 | 185 | 0 | 108 | 0
5:00 | 4838 | 801 | 2012 | 1173 | 525 | 118 | 190 | 0 | 106 | 0
5:30 | 4737 | 800.5 | 1881.5 | 979.5 | 510.5 | 118.5 | 197.5 | 0 | 102 | 1
6:00 | 4636 | 800 | 1751 | 786 | 496 | 119 | 205 | 0 | 98 | 2
6:30 | 4508.5 | 800 | 1675 | 739 | 475.5 | 119 | 217.5 | 0 | 89 | 7 |  |  |  |  | Coal
7:00 | 4381 | 800 | 1599 | 692 | 455 | 119 | 230 | 0 | 80 | 12
7:30 | 4335.5 | 800.5 | 1568 | 656 | 454.5 | 119 | 234.5 | 0 | 82 | 19.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4290 | 801 | 1537 | 620 | 454 | 119 | 239 | 0 | 84 | 27
8:30 | 4282 | 801 | 1530 | 607.5 | 449.5 | 120 | 244 | 0 | 85 | 26.5
9:00 | 4274 | 801 | 1523 | 595 | 445 | 121 | 249 | 0 | 86 | 26
9:30 | 4282 | 800.5 | 1504.5 | 569.5 | 448 | 121 | 248 | 0 | 102 | 40.5
10:00 | 4290 | 800 | 1486 | 544 | 451 | 121 | 247 | 0 | 118 | 55
10:30 | 4321.5 | 800 | 1499.5 | 547.5 | 451.5 | 121 | 246 | 0 | 111 | 61
11:00 | 4353 | 800 | 1513 | 551 | 452 | 121 | 245 | 0 | 104 | 67
11:30 | 4450.5 | 800.5 | 1521 | 559.5 | 451 | 121.5 | 244 | 0 | 107 | 84.5
12:00 | 4548 | 801 | 1529 | 568 | 450 | 122 | 243 | 0 | 110 | 102
12:30 | 4612 | 800.5 | 1622.5 | 592 | 450.5 | 122 | 243.5 | 0 | 111 | 102
13:00 | 4676 | 800 | 1716 | 616 | 451 | 122 | 244 | 0 | 112 | 102
13:30 | 4676 | 800 | 1716 | 616 | 451 | 122 | 244 | 0 | 112 | 102
14:00 | 4676 | 800 | 1716 | 616 | 451 | 122 | 244 | 0 | 112 | 102
14:30 | 4678 | 794 | 1804 | 640 | 476.5 | 122 | 244.5 | 0 | 116 | 89.5
15:00 | 4680 | 788 | 1892 | 664 | 502 | 122 | 245 | 0 | 120 | 77
15:30 | 4596 | 788 | 1764 | 657 | 516 | 122 | 216 | 0 | 118 | 60
16:00 | 4512 | 788 | 1636 | 650 | 530 | 122 | 187 | 0 | 116 | 43
16:30 | 4374.5 | 788 | 1580.5 | 665.5 | 540 | 107 | 156 | 0 | 114 | 32
17:00 | 4237 | 788 | 1525 | 681 | 550 | 92 | 125 | 0 | 112 | 21
17:30 | 4181 | 788 | 1465 | 672.5 | 525 | 92 | 90 | 0 | 108 | 13.5
18:00 | 4125 | 788 | 1405 | 664 | 500 | 92 | 55 | 0 | 104 | 6
18:30 | 4315.5 | 788 | 1396.5 | 1053 | 505 | 92.5 | 133.5 | 0 | 119 | 3
19:00 | 4506 | 788 | 1388 | 1442 | 510 | 93 | 212 | 0 | 134 | 0
19:30 | 4800 | 788 | 1617 | 1975 | 550 | 93 | 247 | 0 | 134 | 0
20:00 | 5003 | 791 | 1647 | 1798 | 570 | 93 | 266 | 0 | 120 | 0
20:30 | 5025.5 | 791 | 1662 | 1905.5 | 610 | 93.5 | 209 | 0 | 123 | 0
21:00 | 5048 | 791 | 1677 | 2013 | 650 | 94 | 152 | 0 | 126 | 0
21:30 | 5025 | 791 | 1643 | 2089 | 642.5 | 77 | 152 | 0 | 128 | 0
22:00 | 5002 | 791 | 1609 | 2165 | 635 | 60 | 152 | 0 | 130 | 0
22:30 | 4983.5 | 791 | 1609 | 2160.5 | 610 | 60 | 152 | 0 | 129 | 0
23:00 | 4965 | 791 | 1609 | 2156 | 585 | 60 | 152 | 0 | 128 | 0
23:30 | 4873 | 791 | 1623.5 | 2156 | 560 | 60 | 139 | 0 | 127 | 0 | Max Temp. in Dhaka |  | 34° C
24:00 | 4781 | 791 | 1638 | 2156 | 535 | 60 | 126 | 0 | 126 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 226.380 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 226.380 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 65 | 64 | 61 | 61 | 58 | 59 | 59 | 59 | 61 | 61 | 61 | 62 | 62 | 63 | 62 | 62 | 32 | 32 |  | 33 | 33 | 33 | 34 |  |  |  | 414480
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1448000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 150 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | [10 empty] | 0 | [8 empty] | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 47430
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | [5 empty] | 1 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 2159
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 70 | 70 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2779774
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 34 | 34 | 17 | 17 | 17 | 0 | 125484
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 4 | 17 | 17 |  | 25 | 51 | 51 | 54 | 54 | 54 | 54 | 836363
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 92 | 93 | 92 | 63 | 63 | 63 | 39 | 39 | 37 | 37 | 35 | 35 | 35 | 88 | 88 | 35 | 35 | 35 |  | 35 | 31 | 90 | 90 | 57 | 57 | 87 | 1536000
17 | Siddhirganj 335 MW CCPP | 332 | 333 | 304 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 330 | 329 | 280 | 280 | 250 |  | 250 | 300 | 333 | 330 | 332 | 331 | 330 | 7149030
18 | Kodda 300 MW PP Unit-2 (Summit) | [17 empty] | 20 |  | 32 | 45 | 15 |  |  |  |  | 110399
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 26 | 26 | 26 | 26 | 26 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 317818
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4221000
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1858568
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | [14 empty] | 35 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 540972
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 10 | 10 | 13 | 13 |  | 20 | 20 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 459432
33 | Ashuganj 225 MW CCPP | 212 | 211 | 212 | 212 | 212 | 213 | 212 | 180 | 180 | 192 | 181 | 199 | 206 | 180 | 212 | 183 | 175 | 201 |  | 197 | 202 | 202 | 193 | 205 | 207 | 210 | 4821000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 280 | 285 | 280 | 285 | 320 | 270 | 295 | 300 | 270 | 295 | 280 | 280 | 280 |  | 305 | 280 | 280 | 295 | 290 | 295 | 334 | 6938000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 265 | 260 | 260 | 260 | 260 | 260 | 260 | 278 | 260 | 335 | 345 | 310 | 310 | 285 | 285 | 275 |  | 300 | 275 | 275 | 295 | 270 | 280 | 295 | 7018500
35 | Ashuganj 55 MW PP (Precision) | 55 | 56 | 56 | 56 | 56 | 56 | 20 | 20 | 20 | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 30 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 694080
36 | Chandpur 150 MW CCPP | 136 | 136 | 137 | 135 | 132 | 136 | 136 | 134 | 137 | 136 | 138 | 136 | 50 | 79 | 85 | 84 | 85 | 85 |  | 86 | 84 | 85 | 85 | 86 | 86 | 86 | 2597210
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 400 | 400 | 400 | 399 | 399 | 367 | 316 | 306 | 301 | 303 | 330 | 333 | 361 | 380 | 383 | 387 | 332 | 297 |  | 274 | 392 | 372 | 395 | 391 | 393 | 393 | 8761340
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5640250
41 | Haripur 360MW CCPP(HPL) | 342 | 342 | 342 | 343 | 343 | 308 | 279 | 278 | 276 | 277 | 303 | 302 | 345 | 347 | 344 | 306 | 307 | 267 |  | 322 | 322 | 347 | 345 | 346 | 346 | 347 | 7662000
42 | RPCL 210MW CCPP | 203 | 203 | 203 | 203 | 202 | 203 | 201 | 203 | 203 | 198 | 196 | 194 | 194 | 196 | 193 | 193 | 193 | 199 |  | 197 | 200 | 200 | 199 | 199 | 199 | 199 | 4679120
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 9 | 15 | 17 | 44 | 57 | 57 | 55 | 42 | 46 | 33 | 15 | 3 | [8 empty] | 359920
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1026000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 42 | 42 | 42 | 42 | 42 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 995160
46 | Shajibazar 330 MW CCPP | 182 | 182 | 183 | 184 | 183 | 182 | 182 | 183 | 182 | 178 | 228 | 225 | 220 | 230 | 206 | 233 | 231 | 230 |  | 232 | 232 | 220 | 192 | 226 | 182 | 182 | 4595000
47 | Shahjibazar GTPP Unit- 8 & 9 | 56 | 51 | 51 | 51 | 51 | 51 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 65 | 64 | 40 | 40 |  | 63 | 64 | 65 | 63 | 63 | 59 | 59 | 1172736
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 50 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 70 | 84 | 30 | 30 |  | 30 | 84 | 84 | 84 | 84 | 84 | 84 | 1248000
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 219 | 219 | 219 | 219 | 219 | 178 | 151 | 151 | 152 | 152 | 152 | 152 | 151 | 151 | 173 | 219 | 178 | 178 |  | 197 | 225 | 225 | 219 | 219 | 219 | 212 | 4518110
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 388000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 230580
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 50 | 50 | 11 | 11 | 11 |  | 11 | 50 | 50 | 50 | 52 | 52 | 52 | 759600
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 352608
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 300 | 285 | 290 | 290 | 280 | 290 | 290 | 280 | 290 | 295 | 290 | 310 | 290 | 280 | 260 | 290 | 270 | [8 empty] | 5269800
| Bibiyana South 400 MW | 204 | 170 | 266 | 270 | 270 | 270 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 240 | 0 |  |  | 60 |  | 260 | 260 | 260 | 260 | 262 | 263 |  | 4772100
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 15 | 17 | [5 empty] | 24465
59 | Tangail Palli Power Gen 22 MW | 23 | 22 | [17 empty] | 2 | 10 | 19 | 24 | 24 | 24 | 22 | 176880
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482352
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 17 | 16 | 16 | 16 | 16 |  | 16 |  | 16 | 16 | 16 | 13 | 15 | 17 | 17 | 376596
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 489816
63 | Impoprt (Tripura) | 122 | 116 | 114 | 110 | 106 | 98 | 80 | 84 | 86 | 118 | 104 | 110 | 112 | 118 | 120 | 116 | 112 | 104 |  | 134 | 134 | 120 | 126 | 130 | 128 | 126 | 2749440
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 22 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 36 |  | 42 | 42 | 42 | 25 | 31 | 42 | 42 | 1017120
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 507744
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 257580
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 788000
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 20 | 15 | 16 | 21 | 16 | 20 | 20 | 18 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 21 | 486440
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 219960
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 764600
72 | Rupganj 33 MW PP(Summit) | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 12 | 12 |  | 24 |  | 24 | 24 | 24 | 21 | 21 | 660200
73 | Ghorashal 108MW PP (Regent) | 94 | 91 | 95 | 95 | 95 | 95 | 54 | 54 | 54 | 13 | 13 | 13 | 58 | 81 | 84 | 25 | 25 | 25 |  | 58 | 85 | 90 | 93 | 95 | 92 | 93 | 1557727
| Feni Lanka Power | 17 | [18 empty] | 34 | [6 empty] | 50160
| Chowmuhani 113 MW | 115 | 110 | 109 | 110 | 110 | 110 | 46 | 8 | 8 | 5 | 1 | 8 | 19 | 36 | 36 | 36 | 36 | 36 |  | 78 | 115 | 115 | 115 | 117 | 108 | 109 | 1667400
| Manikgonj 162MW PP(MPGL) | [19 empty] | 22 | [6 empty] | 33120
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 24 | 24 | 8 | [16 empty] | 12 | 30 | 34 | 51 | 51 | 51 | 51 | 346080
79 | Kodda 150MW PP | 16 | [18 empty] | 25 | 32 | 32 | 32 | 32 | 32 | 32 | 187680
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 138240
81 | Jangalia 52 MW PP (Lakdanavi) | 16 | 16 | [15 empty] | 10 |  | 25 | 8 | 8 |  |  |  |  | 97800
| Gazipur 100 MW PP | [19 empty] | 8 | 40 | 50 | 52 | 52 | 52 | 52 | 272400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 3 | 3 | 2 | 1 | 1 | 0 | [8 empty] | 24961
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 110 | 110 | 68 | 68 | 34 | 34 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 56 | 108 | 108 | 108 | 110 | 110 | 110 | 1372471
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [26 empty] | 0
86 | Meghnaghat CCPP ( Summit) | 270 | 270 | 267 | 266 | 260 | 253 | 274 | 265 | 240 | 280 | 275 | 285 | 290 | 245 | 260 | 265 | 265 | 250 |  | 285 | 260 | 228 | 272 | 277 | 278 | 272 | 6373760
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | [19 empty] | 5 | 17 |  |  | 31 | 35 | 35 | 128640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [19 empty] | 10 | 10 | 10 |  |  |  |  | 17520
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 25 | 43 | 10 | 10 | 10 |  | 24 | 43 | 43 | 43 | 43 | 43 | 43 | 839172
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 16 | [6 empty] | 22464
95 | Patenga 50MW PP (Baraka) | [19 empty] | 8 | [6 empty] | 15840
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [17 empty] | 2 |  | 15 | [6 empty] | 24278
100 | Manikganj 55 MW PP (Northern) | [19 empty] | 35 | 35 |  |  | 17 | 17 | 17 | 101702
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 2 | 0 | 1 | 3 | 2 | 0 | 0 | 0 | 0 | [8 empty] | 10750
103 | Kamalaghat 54 MW PP(Banco Energy) | 36 | 36 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 35 | 35 | 54 | 54 | 54 | 606960
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 191 | 192 | 191 | 50 | 50 | 50 | 50 | 16 | 32 | 32 | 32 | 45 | 50 | 32 | 32 | 32 |  | 84 | 195 | 177 | 200 | 200 | 193 | 193 | 2700000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 17 | 17 | [9 empty] | 1 | 15 | 17 | 17 | [11 empty] | 109440
115 | Juldah 100 MW PP Unit-3 (Acorn) | 50 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 50 | 10 | 10 | 80 | 100 | 100 | 100 | 709440
116 | Chandpur 200MW (Desh energy) | 100 | 100 | 100 | 85 | 51 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 47 | 100 | 100 | 81 | 118 | 120 | 120 | 1324320
117 | Ashuganj 150MW PP (Midland) | 10 | 10 | 10 | [13 empty] | 2 | 28 |  | 48 | 148 | 80 | 30 | 30 | 30 | 33 | 413163
118 | Bibiyana-III 400 MW CCPP | 366 | 365 | 366 | 366 | 366 | 318 | 318 | 319 | 318 | 327 | 315 | 315 | 365 | 365 | 365 | 365 | 327 | 327 |  | 348 | 388 | 400 | 403 | 401 | 402 | 403 | 8515000
| Jamalpur 115 MW PP (United) | 106 | 106 | 106 | 106 | 106 | 106 | 115 | 115 | 115 | 106 | 106 | 105 | 105 | 115 | 105 | 75 | 75 | 55 |  | 60 | 96 | 105 | 105 | 107 | 107 | 97 | 2427600
| Anwara 300 MW PP (United) | [17 empty] | 16 |  | 16 | 16 | 16 |  |  |  |  | 45164
| Juldah unit-2 (Acorn) | 20 | 20 | 20 | 20 | 20 | 10 | 10 | 10 | 10 | [10 empty] | 50 | 10 | 10 | 70 | 100 | 100 | 100 | 549120
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 90 | 72 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 47 | 53 | 53 |  | 84 | 116 | 115 | 116 | 116 | 116 | 116 | 1712455
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443160
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 11 | 5 | 1 | 3 | 33 | 33 | 35 | 20 | 2 | 2 | 1 | [8 empty] | 140912
120 | Eastern Zone Total | 6789 | 6682 | 6533 | 6467 | 6317 | 5829 | 5433 | 5333 | 5298 | 5278 | 5320 | 5512 | 5699 | 5850 | 5802 | 5478 | 5181 | 5137 |  | 6028 | 6640 | 6549 | 6639 | 6769 | 6734 | 6521 | 144590115
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | 120 | 140 | 170 | 180 | 190 | 205 | 230 | 239 | 249 | 247 | 245 | 243 | 244 | 244 | 245 | 185 | 120 | 55 |  | 50 | 40 | 40 |  |  |  |  | 3671040
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | [11 empty] | 1 | 23 | 35 | 17 | 17 | 17 |  | 55 | 105 | 105 | 105 | 105 | 105 | 105 | 876480
130
131
132 | United Payra Power Ltd. | 90 | 54 | 17 | [16 empty] | 4 | 17 | 17 | 17 |  |  |  | 249600
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 221 | 221 | 221 | 221 | 180 | 180 | 150 | 151 | 152 | 152 | 152 | 151 | 210 | 220 | 154 | 151 | 131 |  | 151 | 222 | 221 | 220 | 221 | 220 | 220 | 4561527
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 84 | 84 | 86 | 86 | 85 | 52 | 22 | 22 | 22 | 22 | 23 | 23 | 23 | 23 | 22 | 22 | 22 | 23 |  | 45 | 52 | 68 | 84 | 81 | 84 | 83 | 1188941
Bhola 225 MW CCPP
140 | Bhola 33 MW PP (Venture) | 32 | 32 | 33 | 33 | 33 | 30 | 17 | 17 | 20 | 19 | 20 | 20 | 22 | 26 | 21 | 24 | 22 | 24 |  | 31 | 31 | 32 | 32 | 29 | 21 | 18 | 579845
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 50 | 57 | 100 | 100 | 100 | 100 | 464640
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 2 | 5 | [9 empty] | 5760
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 800 | 801 | 800 | 801 | 801 | 800 | 800 | 801 | 801 | 800 | 800 | 801 | 800 | 791 | 788 | 788 | 788 | 788 |  | 788 | 788 | 791 | 791 | 791 | 791 | 791 | 19216000
147 | Bheramara 410 MW CCPP | 405 | 405 | 405 | 350 | 350 | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 360 | 400 | 395 | 320 | 320 | 280 |  | 300 | 300 | 385 | 400 | 395 | 400 | 390 | 8759520
148 | Payra 1320 MW | 500 | 500 | 450 | 400 | 370 | 340 | 300 | 300 | 290 | 300 | 300 | 300 | 300 | 330 | 350 | 380 | 400 | 350 |  | 360 | 400 | 420 | 500 | 480 | 430 | 380 | 10043800
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 155 | 154 | 155 | 150 | 155 | 156 | 155 | 154 | 155 | 151 | 152 | 150 | 151 | 154 | 152 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 155 | 155 | 155 | 3764100
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 60 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1637000
Baghabari 50 MW Peaking PP
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 2 | 0 | 1 | 3 | 4 | 3 | 2 | 0 | 0 | [8 empty] | 23340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 118 | 119 | 119 | 117 | 121 | 118 | 70 | 70 | 70 | 70 | 106 | 130 | 130 | 141 | 142 | 100 | 100 | 70 |  | 77 | 135 | 140 | 144 | 144 | 144 | 144 | 2906100
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 188 | 188 | 187 | 189 | 187 | 157 | 130 | 130 | 130 | 151 | 164 | 203 | 206 | 194 | 181 | 167 | 160 |  | 150 | 183 | 184 | 194 | 181 | 181 | 187 | 4430991
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 178 | 178 | 184 | 186 | 184 | 188 | 180 | 173 | 161 | 181 | 188 | 195 | 184 | 163 | 196 | 178 | 130 |  | 144 | 183 | 186 | 193 | 181 | 171 | 173 | 4551491
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 413 | 413 | 413 | 404 | 410 | 324 | 351 | 320 | 314 | 351 | 328 | 350 | 408 | 363 | 390 | 390 | 307 | 288 |  | 384 | 396 | 380 | 411 | 337 | 335 | 366 | 8793945
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 5 | [25 empty] | 5939
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 505200
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 11 | 11 | 11 | 11 | 11 | 214326
165 | Amnura 50 MW PP(Sinha) | [21 empty] | 6 | 35 | 35 | 35 | 35 | 129110
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | 23 | [18 empty] | 11 | 20 | 33 | 22 | 22 | 22 | 22 | 122981
168 | Santahar 50 MW Peaking PP | 32 | 32 | [17 empty] | 15 | 34 | 35 | 34 | 34 | 34 | 25 | 255536
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 25 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 33 | 43 | 8 |  | 8 | 8 | 25 | 52 | 52 | 52 | 52 | 686400
170 | Chapainawabganj 100 MW Peaking PP | 92 | 55 | [17 empty] | 60 | 87 | 92 | 47 | 47 | 47 | 47 | 497952
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | [14 empty] | 40 | 88 | 86 | 90 | 94 | 94 | 94 | 1040256
172 | Confidence Power Bogura Unit-1 113 MW | 75 | 75 | 75 | [16 empty] | 50 | 70 | 70 | 75 | 75 | 75 | 75 | 714048
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 57 | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 105 | 52 | 55 | 55 | 34 |  | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 1851628
177 | Sympa Solar Power 8MW | [6 empty] | 0 | 0 |  | 4 | 4 | 5 | 5 | 7 | 6 | 5 | 3 | 2 | [8 empty] | 42609
178
178