## Forecast
1 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-07-29 | Thursday
|  |  | Date (day): | 2021-07-29 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13961.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14733 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-07-28 | 2021-07-29 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 170 | 170 | 170 | 170
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 0 | 0 | 0 |  | 365 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 85 | 99 | 90 | 100 |  | 8 | Engine problem
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 352 | 370 | 360 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 345 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 275 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 0 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 80 | 80 |  | 20 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 16 | 19 | 18 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 35 | 90 | 60 | 90 | 120 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 214 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 0 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel Shortage.
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 16 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 0 | 0 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 34 | 33 | 35 | 35 |  | 45 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 8 | 17 | 20 | 24 |  | 9 | Engine problem
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 15 | 270 | 270 |  | 30 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 0 | 16 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 0 | 0 | 90 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 0 | 0 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 12 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 1900 | 2104 | 3665 | 3999 | 489 | 1165
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 0 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 60 | 119 | 118 | 119 | 111 |  | Unit 1,2,3 Under S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 120 | 120 | 120 | 120 |  | 30 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 9 | 17 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 34 | 51 | 51 |  | 51 | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 0 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 33 | 42 | 30 | 42
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 12 | 93 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 0 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 17 | 108 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 0 | 30 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 65 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 560 | 1028 | 1643 | 1731 | 251 | 415
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 70 | 80 | 80 | 80 | 55 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  | 54 | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 213 | 210 | 210 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 310 | 330 | 330
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 270 | 305 | 360 | 360
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 30 | 30 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 19 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 3 | 50 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 83 | 137 | 135 | 137 |  | 26 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 0 | 18 | 170 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 88 | 120 | 121 | 148
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 0 | 40 | 40 |  | 12 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 6 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 0 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 8 | 105 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1205 | 1618 | 2285 | 2444 | 371 | 159
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 196 | 205 | 205 | 205
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 0 | 194 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 85 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 50 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 360 | 565 | 597.6 | 571 | 0 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 42 | 43 | 43 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 43 | 43 | 43 |  | 47 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 0 | 0 | 0 | 0 |  | 163 | Under maint
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 180 | 274 | 275 | 275 | 55 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 11 | 50 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 61 | 60 | 60
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 10 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 140 | 140 | 150 | 150 |  | 81 | ST Under maint. |  | 2021-07-08
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 16 | 19 | 19 |  | 6 | Engine problem
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 0 | 0 | 0 | 0 |  | 341 | Under maint
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 402 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 9 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 264 | 269 | 260 | 260 |  | 123 | ST Under maint.
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1171 | 1418 | 1424 | 1425 | 55 | 887
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 795 | 781 | 699 | 699
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 0 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 376 | 360 | 0 | 0 |  |  | under maintenance.
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 0 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1171 | 1346 | 1179 | 1309 | 0 | 83
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 30 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 60 | 66 | 66 | 66 |  | 128 | Under maint
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 14 | 12 | 80 | 82 | 13 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 290 | 480 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 134 | 201 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 0 | 90 | 90 |  | 60 | Engine problem
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 520 | 789 | 1221 | 1223 | 13 | 188
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 70 | 70 | 70 | 70 | 30 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 20 | 20 |  | 51 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 22 | 30 | 30 |  | 20 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 95 | 142 | 100 | 144 | 66 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 191 | 188 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 202 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 379 | 385 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 9 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 8 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 47 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 23 | 39 | 90 | 90 |  | 23 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 25 | 45 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1022 | 1266 | 1676 | 1748 | 216 | 143
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 153 | 153 | 150 | 150 | 124 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 0 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 6 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 159 | 266 | 271 | 283 | 124 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 8068 | 10400 | 13961.6 | 14733 | 1519 | 3317
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 7711.1462 | 9940 | 13344.0677 | 14081.3481
| A. |  | 2021-07-28 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 10487 | MW at | 22:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 7385 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 10400 | MW
| 3 | Day peak Generation : |  |  | 8068 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 9940 | MW
| 4 | Evening peak Generation : |  |  | 10400 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 212.074 | MKWHr | By Solar | 0.59367 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 146.3987 | MKWHr |  | By Oil: | 28.6721 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.2776 | MKWHr |  | By Hydro: | 2.594 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 1519 | MW | Dhaka | 2831 | 2831 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 3317 | MW | Chittagong | 869 | 869 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4836 | MW | Khulna | 1362 | 1362 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1231.58 | MMCFD |  |  | Rajshahi | 1273 | 1273 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 160513154.158 | ii) Oil : | Taka | 174276695.42 | Comilla | 1070 | 1070 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 57806072 | Total | Taka | 392595921.578 | Mymensingh | 1000 | 1000 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.9695 | MKWHr. | Sylhet | 489 | 489 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -140 | MW (E to W) at | 21:00 | hrs | Barisal | 252 | 252 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -216 | MW at | 24:00 | hrs | Rangpur | 794 | 794 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 31.0° C |  |  | Total | 9940 | 9940 |  | 0
| B. |  | 2021-07-29 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 34.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 10000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14733 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 7200 | MW
| 4 | Reserve(Generation end) |  |  |  | 4733 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 202.2256 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 6927 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 19.1149 | MKWHr. | ii) HVDC Flow at Peak Time |  | 781 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.423 | MKWHr. | iii) Maximum HVDC Flow : |  | 812 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 84.58 |  | (b) Today: | 84.69 |  | (c) Rule Curve: |  | 88.49
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-07-28
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 170 | 0 | 98 | 0 | 380 | 308 |  | 0 | 240 | 237 | 0 | 0 | 0 | 335 | 0 | 57 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 35 | 0 | 17 | 25 | 8 | 25 | 21 | 51 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 260 | 270 | 205 | 8 | 83 | 20 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 122 | 203 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 182 | 61 | 84 | 0 | 212 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 90 | 135 | 45 | 401 | 98 | 35 | 55 | 0 | 0 | 0 | 110 | 0 | 108 | 80 | 240 | 35 | 0 | 0 | 116 | 0 | 17 | 0 |  | 812 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 144 | 0 | 167 | 0 | 85 | 0 | 185 | 0 | 335 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 300 | 220 | 0 | 0 | 0 |  | 6548 | 3474 | 10022 | 4887 | 812 | 1583 | 1998 | 455 | 60 | 105 | 122 | 0 | 0 | 84.57
2:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 359 | 308 |  | 0 | 240 | 243 | 0 | 0 | 0 | 335 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 35 | 0 | 16 | 25 | 8 | 25 | 21 | 51 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 70 | 0 | 60 | 260 | 270 | 213 | 8 | 83 | 20 | 20 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 204 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 182 | 61 | 84 | 0 | 212 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 10 | 140 | 50 | 400 | 107 | 17 | 54 | 0 | 0 | 0 | 110 | 0 | 108 | 0 | 270 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 805 | 0 | 405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 144 | 0 | 171 | 0 | 85 | 0 | 183 | 0 | 335 | 53 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 290 | 205 | 0 | 0 | 0 |  | 6326 | 3335 | 9661 | 4908 | 805 | 1569 | 1703 | 446 | 60 | 50 | 120 | 0 | 0 | 84.57
3:00 | 0 | 0 | 0 | 170 | 0 | 14 | 0 | 361 | 309 |  | 0 | 240 | 270 | 0 | 0 | 0 | 332 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 16 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 1 | 0 | 21 | 42 | 70 | 0 | 60 | 275 | 285 | 208 | 8 | 86 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 116 | 201 | 8 | 21 | 0 | 43 | 43 | 52 | 0 | 0 | 182 | 61 | 84 | 0 | 191 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 34 | 0 | 402 | 107 | 17 | 0 | 0 | 0 | 0 | 68 | 0 | 108 | 0 | 269 | 0 | 0 | 0 | 115 | 0 | 17 | 0 |  | 790 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 121 | 0 | 174 | 0 | 83 | 0 | 179 | 0 | 387 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 270 | 221 | 0 | 0 | 0 |  | 5843 | 3292 | 9135 | 4839 | 790 | 1510 | 1345 | 425 | 60 | 50 | 116 | 0 | 0 | 84.57
4:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 362 | 308 |  | 0 | 240 | 274 | 0 | 0 | 0 | 330 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 16 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 5 | 0 | 21 | 4 | 70 | 0 | 60 | 285 | 290 | 210 | 8 | 86 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 201 | 8 | 21 | 0 | 43 | 43 | 53 | 0 | 0 | 182 | 61 | 84 | 0 | 191 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 0 | 0 | 0 | 34 | 0 | 400 | 107 | 17 | 0 | 0 | 0 | 0 | 68 | 0 | 108 | 0 | 267 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 793 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 110 | 0 | 175 | 0 | 84 | 0 | 174 | 0 | 388 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 270 | 220 | 0 | 0 | 0 |  | 5816 | 3136 | 8952 | 4691 | 793 | 1471 | 1354 | 425 | 60 | 50 | 108 | 0 | 0 | 84.57
5:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 362 | 308 |  | 0 | 240 | 256 | 0 | 0 | 0 | 334 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 16 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 22 | 0 | 0 | 0 | 7 | 0 | 21 | 26 | 70 | 0 | 60 | 260 | 270 | 204 | 8 | 85 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 104 | 203 | 8 | 21 | 0 | 43 | 43 | 53 | 0 | 0 | 182 | 61 | 84 | 0 | 191 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 193 | 0 | 0 | 0 | 0 | 34 | 0 | 398 | 107 | 17 | 0 | 0 | 0 | 0 | 68 | 0 | 110 | 0 | 220 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 793 | 0 | 150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 70 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 115 | 0 | 183 | 0 | 62 | 0 | 172 | 0 | 388 | 17 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 270 | 220 | 0 | 0 | 0 |  | 5777 | 3025 | 8802 | 4560 | 793 | 1471 | 1339 | 425 | 60 | 50 | 104 | 0 | 0 | 84.58
6:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 348 | 308 |  | 0 | 240 | 248 | 0 | 0 | 0 | 280 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 32 | 70 | 0 | 60 | 260 | 270 | 211 | 8 | 85 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 92 | 204 | 8 | 21 | 0 | 43 | 43 | 14 | 0 | 0 | 183 | 62 | 10 | 0 | 177 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 80 | 0 | 24 | 0 | 0 | 0 | 0 | 375 | 115 | 0 | 0 | 0 | 0 | 0 | 34 | 0 | 46 | 0 | 269 | 0 | 1 | 0 | 72 | 0 | 17 | 0 |  | 793 | 0 | 215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 90 | 0 | 167 | 0 | 23 | 0 | 153 | 0 | 308 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 260 | 220 | 0 | 0 | 0 |  | 5245 | 2559 | 7804 | 4466 | 793 | 1246 | 731 | 415 | 60 | 0 | 92 | 1 | 0 | 84.58
7:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 307 | 337 |  | 0 | 240 | 268 | 0 | 0 | 0 | 280 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 70 | 0 | 60 | 260 | 270 | 210 | 8 | 85 | 0 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 78 | 202 | 8 | 21 | 0 | 43 | 43 | 14 | 0 | 0 | 181 | 61 | 10 | 0 | 158 | 18 | 0 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 352 | 115 | 0 | 0 | 1 | 0 | 0 | 17 | 0 | 26 | 0 | 50 | 0 | 8 | 0 | 53 | 0 | 17 | 2 |  | 793 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 100 | 0 | 172 | 0 | 12 | 0 | 156 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 220 | 0 | 0 | 1 |  | 4823 | 2562 | 7385 | 4148 | 793 | 1305 | 565 | 423 | 60 | 0 | 78 | 13 | 0 | 84.58
8:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 307 | 308 |  | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 38 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 20 | 70 | 0 | 60 | 265 | 290 | 187 | 8 | 85 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 33 | 15 | 82 | 200 | 8 | 21 | 1 | 43 | 43 | 14 | 0 | 0 | 183 | 60 | 10 | 0 | 158 | 18 | 0 | 10 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 352 | 85 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 26 | 0 | 230 | 0 | 31 | 0 | 53 | 0 | 17 | 21 |  | 793 | 0 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 94 | 0 | 165 | 0 | 11 | 0 | 167 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 270 | 181 | 0 | 0 | 2 |  | 4953 | 2518 | 7471 | 4314 | 793 | 1211 | 530 | 423 | 60 | 0 | 82 | 58 | 0 | 0
9:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 307 | 308 |  | 0 | 240 | 265 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 0 | 25 | 21 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 70 | 0 | 80 | 260 | 290 | 181 | 8 | 86 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 88 | 198 | 8 | 21 | 2 | 44 | 42 | 14 | 0 | 0 | 181 | 63 | 10 | 0 | 132 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 85 | 0 | 0 | 4 | 0 | 0 | 17 | 0 | 8 | 0 | 262 | 0 | 42 | 0 | 53 | 0 | 17 | 6 |  | 794 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 0 | 0 | 158 | 0 | 0 | 92 | 0 | 164 | 0 | 11 | 0 | 178 | 0 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 270 | 140 | 0 | 0 | 2 |  | 4949 | 2545 | 7494 | 4381 | 794 | 1195 | 490 | 428 | 60 | 0 | 88 | 58 | 0 | 0
10:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 309 | 335 |  | 0 | 240 | 275 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 0 | 25 | 12 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 70 | 0 | 80 | 270 | 350 | 191 | 8 | 86 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 86 | 198 | 0 | 19 | 2 | 44 | 43 | 11 | 0 | 0 | 180 | 62 | 10 | 0 | 50 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 381 | 85 | 0 | 0 | 2 | 0 | 0 | 17 | 0 | 8 | 0 | 260 | 0 | 54 | 0 | 53 | 0 | 17 | 14 |  | 795 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 9 | 0 | 0 | 156 | 0 | 0 | 98 | 0 | 173 | 0 | 11 | 0 | 183 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 270 | 140 | 0 | 0 | 5 |  | 5021 | 2662 | 7683 | 4475 | 795 | 1268 | 492 | 426 | 60 | 0 | 86 | 81 | 0 | 0
11:00 | 0 | 0 | 0 | 170 | 0 | 12 | 0 | 351 | 345 |  | 0 | 240 | 275 | 0 | 0 | 0 | 250 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 4 | 25 | 8 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 39 | 70 | 0 | 80 | 265 | 270 | 193 | 8 | 86 | 20 | 20 | 0 | 5 | 0 | 0 | 0 | 22 | 11 | 25 | 15 | 88 | 192 | 4 | 19 | 2 | 42 | 42 | 11 | 0 | 0 | 176 | 60 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 378 | 85 | 0 | 0 | 3 | 0 | 0 | 17 | 0 | 8 | 0 | 256 | 0 | 57 | 0 | 53 | 0 | 17 | 10 |  | 795 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 9 | 0 | 0 | 155 | 0 | 0 | 96 | 0 | 172 | 0 | 13 | 0 | 184 | 0 | 388 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 270 | 141 | 0 | 0 | 5 |  | 5061 | 2682 | 7743 | 4515 | 795 | 1281 | 496 | 425 | 60 | 0 | 88 | 83 | 0 | 0
12:00 | 0 | 0 | 0 | 170 | 0 | 85 | 0 | 352 | 346 |  | 0 | 240 | 260 | 0 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 9 | 25 | 8 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 33 | 70 | 0 | 80 | 260 | 270 | 182 | 8 | 83 | 23 | 30 | 0 | 19 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 88 | 196 | 8 | 19 | 2 | 42 | 42 | 11 | 0 | 0 | 180 | 61 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 367 | 85 | 0 | 9 | 3 | 0 | 0 | 17 | 0 | 8 | 0 | 264 | 0 | 50 | 0 | 65 | 0 | 17 | 12 |  | 795 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 9 | 0 | 0 | 153 | 0 | 0 | 95 | 0 | 191 | 0 | 14 | 0 | 202 | 0 | 379 | 0 | 0 | 23 | 0 | 0 | 0 | 6 | 25 | 290 | 134 | 0 | 0 | 2 |  | 5196 | 2872 | 8068 | 4692 | 795 | 1358 | 557 | 443 | 60 | 0 | 88 | 75 | 0 | 0
13:00 | 0 | 0 | 0 | 170 | 0 | 95 | 0 | 325 | 322 |  | 0 | 240 | 275 | 0 | 0 | 0 | 270 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 8 | 0 | 0 | 28 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 35 | 70 | 0 | 80 | 270 | 280 | 190 | 8 | 138 | 23 | 54 | 0 | 39 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 96 | 192 | 8 | 19 | 3 | 42 | 42 | 11 | 0 | 0 | 230 | 60 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 372 | 109 | 0 | 17 | 1 | 0 | 0 | 17 | 0 | 8 | 0 | 230 | 0 | 53 | 0 | 114 | 0 | 17 | 17 |  | 796 | 0 | 372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 9 | 0 | 0 | 154 | 0 | 0 | 94 | 0 | 178 | 0 | 13 | 0 | 187 | 0 | 402 | 0 | 0 | 90 | 0 | 0 | 0 | 7 | 35 | 300 | 141 | 0 | 0 | 5 |  | 5417 | 2971 | 8388 | 4708 | 796 | 1423 | 737 | 454 | 88 | 0 | 96 | 86 | 0 | 0
14:00 | 0 | 0 | 0 | 170 | 0 | 97 | 0 | 342 | 321 |  | 0 | 240 | 265 | 0 | 0 | 0 | 300 | 0 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 8 | 25 | 21 | 0 | 0 | 28 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 70 | 0 | 80 | 260 | 270 | 182 | 8 | 138 | 23 | 25 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 100 | 193 | 8 | 19 | 2 | 43 | 42 | 11 | 0 | 0 | 270 | 60 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 366 | 115 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 265 | 0 | 45 | 0 | 116 | 0 | 17 | 9 |  | 796 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 23 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 9 | 0 | 0 | 154 | 0 | 0 | 101 | 0 | 176 | 0 | 13 | 0 | 185 | 0 | 405 | 0 | 0 | 90 | 0 | 0 | 0 | 4 | 35 | 300 | 141 | 0 | 0 | 5 |  | 5518 | 2972 | 8490 | 4835 | 796 | 1409 | 743 | 454 | 88 | 0 | 100 | 65 | 0 | 84.59
15:00 | 0 | 0 | 0 | 170 | 0 | 97 | 0 | 374 | 322 |  | 0 | 240 | 250 | 0 | 0 | 0 | 300 | 0 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 25 | 8 | 25 | 21 | 0 | 0 | 27 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 42 | 70 | 0 | 80 | 275 | 265 | 181 | 8 | 135 | 23 | 25 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 98 | 202 | 8 | 19 | 2 | 43 | 43 | 11 | 0 | 0 | 267 | 60 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 14 | 0 | 4 | 0 | 0 | 0 | 10 | 366 | 115 | 0 | 17 | 1 | 0 | 0 | 17 | 0 | 8 | 0 | 260 | 0 | 16 | 0 | 116 | 0 | 17 | 26 |  | 795 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 21 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 9 | 0 | 0 | 155 | 0 | 0 | 95 | 0 | 167 | 0 | 12 | 0 | 179 | 0 | 393 | 0 | 0 | 90 | 0 | 0 | 0 | 3 | 35 | 300 | 141 | 0 | 0 | 3 |  | 5538 | 2952 | 8490 | 4871 | 795 | 1395 | 738 | 455 | 87 | 0 | 98 | 51 | 0 | 84.59
16:00 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 373 | 322 |  | 0 | 240 | 250 | 0 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 17 | 25 | 8 | 25 | 21 | 0 | 0 | 26 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 48 | 0 | 21 | 22 | 70 | 0 | 80 | 275 | 265 | 181 | 8 | 137 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 92 | 201 | 8 | 19 | 0 | 43 | 43 | 14 | 0 | 0 | 269 | 40 | 10 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 24 | 0 | 17 | 2 | 0 | 0 | 10 | 366 | 55 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 260 | 0 | 8 | 0 | 35 | 0 | 17 | 14 |  | 795 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 69 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 9 | 0 | 0 | 154 | 0 | 0 | 70 | 0 | 159 | 0 | 12 | 0 | 178 | 0 | 402 | 0 | 0 | 90 | 0 | 0 | 0 | 3 | 35 | 270 | 141 | 0 | 0 | 1 |  | 5270 | 2865 | 8135 | 4771 | 795 | 1281 | 656 | 424 | 86 | 2 | 92 | 28 | 0 | 84.6
17:00 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 350 | 276 |  | 0 | 240 | 230 | 0 | 0 | 0 | 270 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 25 | 8 | 25 | 21 | 0 | 0 | 25 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 88 | 0 | 21 | 42 | 70 | 0 | 80 | 275 | 265 | 181 | 8 | 134 | 23 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 16 | 88 | 167 | 8 | 19 | 0 | 43 | 43 | 14 | 0 | 0 | 269 | 40 | 10 | 0 | 100 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 366 | 35 | 0 | 0 | 1 | 0 | 0 | 17 | 0 | 8 | 0 | 260 | 0 | 4 | 0 | 17 | 0 | 17 | 8 |  | 795 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 60 | 16 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 21 | 0 | 9 | 0 | 0 | 155 | 0 | 0 | 70 | 0 | 140 | 0 | 13 | 0 | 176 | 0 | 315 | 0 | 0 | 70 | 0 | 0 | 0 | 2 | 0 | 270 | 141 | 0 | 0 | 0 |  | 5024 | 2703 | 7727 | 4632 | 795 | 1169 | 516 | 425 | 85 | 2 | 88 | 15 | 0 | 84.6
18:00 | 0 | 0 | 0 | 170 | 0 | 43 | 0 | 321 | 256 |  | 0 | 240 | 275 | 0 | 0 | 0 | 270 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 25 | 21 | 0 | 0 | 25 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 58 | 0 | 21 | 42 | 70 | 0 | 80 | 280 | 275 | 160 | 8 | 137 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 16 | 84 | 166 | 8 | 19 | 0 | 43 | 43 | 14 | 0 | 0 | 268 | 40 | 10 | 0 | 100 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 10 | 310 | 35 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 8 | 0 | 200 | 0 | 1 | 0 | 17 | 0 | 17 | 4 |  | 781 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 20 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 9 | 0 | 0 | 152 | 0 | 0 | 70 | 0 | 140 | 0 | 13 | 0 | 140 | 0 | 362 | 0 | 0 | 0 | 0 | 35 | 0 | 2 | 0 | 270 | 140 | 0 | 0 | 0 |  | 4816 | 2582 | 7398 | 4323 | 781 | 1200 | 496 | 422 | 85 | 0 | 84 | 7 | 0 | 84.6
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 170 | 0 | 91 | 0 | 308 | 314 |  | 0 | 240 | 275 | 0 | 0 | 0 | 270 | 0 | 90 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 8 | 25 | 15 | 8 | 0 | 55 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 5 | 0 | 34 | 0 | 52 | 0 | 21 | 42 | 70 | 0 | 80 | 280 | 270 | 211 | 8 | 136 | 23 | 10 | 0 | 10 | 0 | 0 | 4 | 22 | 11 | 25 | 16 | 116 | 200 | 8 | 19 | 0 | 43 | 43 | 14 | 0 | 0 | 272 | 61 | 40 | 0 | 121 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 50 | 0 | 11 | 0 | 30 | 13 | 21 | 366 | 76 | 0 | 5 | 0 | 0 | 0 | 21 | 0 | 46 | 10 | 250 | 7 | 0 | 9 | 53 | 0 | 17 | 0 |  | 781 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 70 | 0 | 40 | 0 | 36 | 35 | 0 | 22 | 8 | 15 | 22 | 0 | 9 | 0 | 0 | 152 | 0 | 0 | 75 | 0 | 151 | 0 | 18 | 0 | 145 | 0 | 372 | 28 | 0 | 1 | 0 | 90 | 0 | 0 | 25 | 300 | 217 | 0 | 0 | 0 |  | 5709 | 3007 | 8716 | 4651 | 781 | 1438 | 1016 | 452 | 115 | 147 | 116 | 0 | 0 | 84.62
19:30 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 330 | 347 |  | 0 | 240 | 240 | 0 | 0 | 0 | 280 | 0 | 88 | 0 | 7 | 32 | 0 | 0 | 0 | 0 | 54 | 0 | 17 | 17 | 25 | 8 | 25 | 17 | 30 | 0 | 57 | 60 | 100 | 120 | 3 | 0 | 0 | 120 | 0 |  | 22 | 0 | 34 | 0 | 70 | 0 | 21 | 42 | 70 | 0 | 80 | 275 | 265 | 215 | 8 | 134 | 23 | 30 | 0 | 17 | 0 | 0 | 16 | 22 | 11 | 25 | 21 | 118 | 205 | 8 | 19 | 0 | 44 | 43 | 50 | 0 | 0 | 272 | 61 | 84 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 30 | 0 | 0 | 194 | 0 | 17 | 0 | 50 | 34 | 50 | 366 | 115 | 0 | 17 | 0 | 0 | 0 | 108 | 0 | 104 | 10 | 270 | 17 | 0 | 17 | 116 | 0 | 17 | 0 |  | 780 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 35 | 0 | 31 | 8 | 23 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 138 | 0 | 185 | 0 | 38 | 100 | 200 | 0 | 347 | 105 | 0 | 35 | 0 | 113 | 0 | 0 | 35 | 400 | 210 | 0 | 0 | 0 |  | 6518 | 3534 | 10052 | 4900 | 780 | 1574 | 1794 | 552 | 117 | 217 | 118 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 330 | 348 |  | 0 | 240 | 275 | 0 | 0 | 0 | 208 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 17 | 25 | 8 | 25 | 17 | 34 | 0 | 59 | 60 | 100 | 120 | 6 | 0 | 0 | 120 | 0 |  | 23 | 0 | 34 | 0 | 81 | 0 | 21 | 42 | 70 | 0 | 80 | 280 | 275 | 212 | 8 | 137 | 20 | 30 | 0 | 38 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 116 | 204 | 8 | 19 | 0 | 43 | 43 | 50 | 0 | 0 | 274 | 60 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 25 | 0 | 0 | 172 | 0 | 16 | 0 | 50 | 17 | 50 | 366 | 115 | 0 | 17 | 0 | 0 | 0 | 105 | 0 | 103 | 10 | 263 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 781 | 0 | 360 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 35 | 0 | 38 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 142 | 0 | 184 | 0 | 12 | 80 | 207 | 0 | 391 | 100 | 0 | 30 | 0 | 113 | 0 | 0 | 35 | 420 | 219 | 0 | 0 | 0 |  | 6384 | 3677 | 10061 | 4901 | 781 | 1620 | 1693 | 572 | 119 | 259 | 116 | 0 | 0 | 84.61
21:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 370 | 345 |  | 0 | 240 | 275 | 0 | 0 | 0 | 214 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 8 | 25 | 17 | 51 | 0 | 59 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 34 | 0 | 93 | 0 | 21 | 42 | 80 | 0 | 80 | 310 | 305 | 213 | 8 | 137 | 23 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 120 | 205 | 8 | 19 | 0 | 43 | 43 | 50 | 0 | 0 | 274 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 194 | 0 | 16 | 0 | 100 | 18 | 50 | 402 | 115 | 0 | 17 | 0 | 0 | 0 | 108 | 0 | 105 | 30 | 269 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 781 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 0 | 0 | 22 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 142 | 0 | 188 | 0 | 12 | 100 | 202 | 0 | 385 | 105 | 0 | 39 | 0 | 113 | 0 | 0 | 45 | 480 | 201 | 0 | 0 | 0 |  | 6733 | 3667 | 10400 | 5066 | 781 | 1598 | 1879 | 633 | 119 | 204 | 120 | 0 | 0 | 84.62
22:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 393 | 346 |  | 0 | 240 | 300 | 0 | 0 | 0 | 212 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 9 | 25 | 17 | 51 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 24 | 0 | 34 | 0 | 97 | 0 | 21 | 42 | 80 | 0 | 70 | 300 | 340 | 195 | 8 | 138 | 23 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 122 | 204 | 8 | 19 | 0 | 43 | 43 | 53 | 0 | 0 | 272 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 197 | 0 | 26 | 0 | 50 | 51 | 50 | 400 | 115 | 0 | 29 | 0 | 0 | 0 | 110 | 0 | 108 | 30 | 261 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 781 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 0 | 0 | 22 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 144 | 0 | 172 | 0 | 13 | 100 | 195 | 0 | 409 | 105 | 0 | 70 | 0 | 113 | 0 | 0 | 50 | 470 | 202 | 0 | 0 | 0 |  | 6803 | 3684 | 10487 | 5041 | 781 | 1649 | 1949 | 621 | 121 | 203 | 122 | 0 | 0 | 84.62
23:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 393 | 350 |  | 0 | 240 | 275 | 0 | 0 | 0 | 214 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 9 | 25 | 17 | 51 | 0 | 63 | 60 | 100 | 120 | 1 | 0 | 0 | 120 | 0 |  | 24 | 0 | 34 | 0 | 97 | 0 | 21 | 37 | 70 | 0 | 80 | 260 | 305 | 199 | 8 | 136 | 23 | 54 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 10 | 21 | 114 | 204 | 8 | 19 | 0 | 43 | 43 | 53 | 0 | 0 | 270 | 56 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 4 | 0 | 0 | 200 | 0 | 32 | 0 | 50 | 57 | 50 | 366 | 108 | 0 | 35 | 0 | 0 | 0 | 110 | 0 | 118 | 30 | 265 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 780 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 0 | 0 | 22 | 8 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 182 | 0 | 13 | 100 | 186 | 0 | 402 | 105 | 0 | 80 | 0 | 113 | 0 | 0 | 75 | 470 | 202 | 0 | 0 | 0 |  | 6665 | 3721 | 10386 | 4929 | 780 | 1644 | 1973 | 620 | 123 | 203 | 114 | 0 | 0 | 84.63
24:00 | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 392 | 349 |  | 0 | 240 | 255 | 0 | 0 | 0 | 219 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 9 | 25 | 17 | 34 | 0 | 63 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 |  | 24 | 0 | 0 | 0 | 97 | 0 | 21 | 42 | 70 | 0 | 80 | 260 | 305 | 196 | 8 | 136 | 23 | 53 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 114 | 205 | 8 | 19 | 0 | 43 | 43 | 53 | 0 | 0 | 272 | 56 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 19 | 11 | 0 | 0 | 0 | 0 | 194 | 0 | 32 | 0 | 50 | 100 | 50 | 366 | 108 | 0 | 52 | 0 | 0 | 0 | 110 | 0 | 119 | 30 | 270 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 781 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 35 | 0 | 22 | 8 | 12 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 144 | 0 | 177 | 0 | 12 | 0 | 186 | 0 | 298 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 75 | 430 | 182 | 0 | 0 | 0 |  | 6629 | 3475 | 10104 | 4894 | 781 | 1522 | 1943 | 580 | 123 | 147 | 114 | 0 | 0 | 84.63
KWH | 0 | 0 | 0 | 4189500 | 0 | 1353863 | 0 | 8503290 | 7694000 |  | 0 | 5642250 | 6363724 | 0 | 0 | 0 | 6796503 | 0 | 1442000 | 0 | 13824 | 129120 | 0 | 0 | 0 | 0 | 653760 | 327346 | 28263 | 244548 | 600000 | 195120 | 760300 | 491500 | 390720 | 0 | 1150036 | 1444000 | 2400000 | 2900000 | 32976 | 0 | 0 | 2898936 | 0 |  | 248640 | 0 | 169406 | 0 | 851520 | 0 | 507792 | 910560 | 1690506 | 0 | 1743132 | 6923400 | 6941000 | 4742000 | 200727 | 2611710 | 474624 | 665760 | 0 | 621192 | 0 | 0 | 18749 | 510984 | 259020 | 666100 | 403490 | 2423040 | 4645760 | 177600 | 425340 | 14450 | 1028000 | 1018957 | 711000 | 0 | 0 | 4852000 | 1397 | 1026240 | 0 | 3617000 | 390000 | 0 | 237600 | 0 | 394544 | 244100 | 0 | 82800 | 0 | 0 | 2248800 | 0 | 246240 | 3915 | 447360 | 730080 | 481745 | 8962000 | 2313600 | 129600 | 383054 | 17158 | 0 | 0 | 1354908 | 0 | 1412880 | 246720 | 5497500 | 61440 | 341670 | 23040 | 2123945 | 0 | 443160 | 146810 |  | 19114909 | 0 | 8088192 | 0 | 0 | 48000 | 0 | 0 | 0 | 2048 | 0 | 836000 | 483804 | 0 | 0 | 1619000 | 0 | 259088 | 0 | 392368 | 112560 | 0 | 127996 | 447840 | 281302 | 489840 | 0 | 246744 | 0 | 0 | 3793600 | 0 | 0 | 2731500 | 0 | 4332682 | 0 | 719231 | 479040 | 4576145 | 0 | 8886400 | 801600 | 0 | 1372128 | 0 | 1354377 | 0 | 35945 | 858720 | 8484000 | 4353900 | 0 | 0 | 33720 |  | 136711344 | 75362679 | 212074023 | 112402316 | 19114909 | 33996367 | 27262759 | 12277600 | 2594036 | 1409328 | 2423040 | 593668 | 0
Fuel Cost | 0 | 0 | 0 | 6158565 | 0 | 1787099.16 | 0 | 8588322.9 | 7924820 |  | 0 | 6150052.5 | 7063733.64 | 0 | 0 | 0 | 7068363.12 | 0 | 2494660 | 0 | 126074.88 | 1270540.8 | 0 | 0 | 0 | 0 | 4772448 | 2530384.58 | 278673.18 | 183411 | 450000 | 0 | 0 | 0 | 3778262.4 | 0 | 310509.72 | 389880 | 4344000 | 5249000 | 306347.04 | 0 | 0 | 4928191.2 | 0 |  | 0 | 0 | 1643238.2 | 0 | 7408224 | 0 | 639817.92 | 2704363.2 | 2501948.88 | 0 | 2562404.04 | 5123316 | 6941000 | 4362640 | 258937.83 | 3003466.5 | 536325.12 | 932064 | 0 | 1062238.32 | 0 | 0 | 179052.95 | 648949.68 | 194265 | 1165675 | 302617.5 | 18172800 | 4924505.6 | 1612608 | 540181.8 | 230333 | 1685920 | 1630331.2 | 1265580 | 0 | 0 | 5046080 | 2752.09 | 1960118.4 | 0 | 6257410 | 854100 | 0 | 484704 | 0 | 295908 | 185516 | 0 | 625968 | 0 | 0 | 11693760 | 0 | 2423001.6 | 45766.35 | 3645984 | 7921368 | 3396302.25 | 8334660 | 21100032 | 1224720 | 3336400.34 | 0 | 0 | 0 | 11909641.32 | 0 | 12108381.6 | 1643155.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110101875.84 | 0 | 8492601.6 | 0 | 0 | 665280 | 0 | 0 | 0 | 21463.04 | 0 | 944680 | 749896.2 | 0 | 0 | 3318950 | 0 | 2549425.92 | 0 | 3472456.8 | 866712 | 0 | 1240281.24 | 4339569.6 | 2728629.4 | 940492.8 | 0 | 186785.208 | 0 | 0 | 20561312 | 0 | 0 | 3195855 | 0 | 5719140.24 | 0 | 1078846.5 | 8148470.4 | 5354089.65 | 0 | 8797536 | 8368704 | 0 | 13021494.72 | 0 | 10509965.52 | 0 | 397192.25 | 6345940.8 | 37244760 | 0 | 0 | 0 | 0 |  | 252881872.01 | 269362406.728 | 522244278.738 | 124416405.248 | 110101875.84 | 36096748.91 | 160685380.02 | 57806072 | 700389.72 | 13591315.4 | 18172800 | 673291.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 170 | 0 | 85 | 0 | 352 | 346 |  | 0 | 240 | 260 | 0 | 0 | 0 | 300 | 0 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 16 | 25 | 9 | 25 | 8 | 0 | 0 | 0 | 60 | 100 | 120 | 0 | 0 | 0 | 120 | 0 |  | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 33 | 70 | 0 | 80 | 260 | 270 | 182 | 8 | 83 | 23 | 30 | 0 | 19 | 0 | 0 | 0 | 22 | 11 | 25 | 6 | 88 | 196 | 8 | 19 | 2 | 42 | 42 | 11 | 0 | 0 | 180 | 61 | 10 | 0 | 140 | 18 | 0 | 9 | 0 | 16 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 367 | 85 | 0 | 9 | 3 | 0 | 0 | 17 | 0 | 8 | 0 | 264 | 0 | 50 | 0 | 65 | 0 | 17 | 12 |  | 795 | 0 | 376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 22 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 9 | 0 | 0 | 153 | 0 | 0 | 95 | 0 | 191 | 0 | 14 | 0 | 202 | 0 | 379 | 0 | 0 | 23 | 0 | 0 | 0 | 6 | 25 | 290 | 134 | 0 | 0 | 2 |  | 8068 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 170 | 0 | 99 | 0 | 370 | 345 | 0 | 0 | 240 | 275 | 0 | 0 | 0 | 214 | 0 | 90 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 19 | 25 | 8 | 25 | 17 | 51 | 0 | 59 | 60 | 100 | 120 | 8 | 0 | 0 | 120 | 0 | 0 | 24 | 0 | 34 | 0 | 93 | 0 | 21 | 42 | 80 | 0 | 80 | 310 | 305 | 213 | 8 | 137 | 23 | 30 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 120 | 205 | 8 | 19 | 0 | 43 | 43 | 50 | 0 | 0 | 274 | 61 | 81 | 0 | 140 | 18 | 0 | 10 | 0 | 16 | 11 | 0 | 15 | 0 | 0 | 194 | 0 | 16 | 0 | 100 | 18 | 50 | 402 | 115 | 0 | 17 | 0 | 0 | 0 | 108 | 0 | 105 | 30 | 269 | 0 | 0 | 0 | 116 | 0 | 17 | 0 |  | 781 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 30 | 0 | 0 | 70 | 0 | 50 | 0 | 47 | 0 | 0 | 22 | 8 | 35 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 142 | 0 | 188 | 0 | 12 | 100 | 202 | 0 | 385 | 105 | 0 | 39 | 0 | 113 | 0 | 0 | 45 | 480 | 201 | 0 | 0 | 0 |  | 10400 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 170 | 0 | 100 | 0 | 412 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 90 | 0 | 102 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 10 | 25 | 24 | 52 | 0 | 59 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 42 | 80 | 0 | 80 | 330 | 360 | 210 | 8 | 137 | 23 | 55 | 0 | 43 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 148 | 205 | 8 | 21 | 0 | 44 | 43 | 51 | 0 | 0 | 275 | 60 | 84 | 0 | 150 | 18 | 0 | 10 | 0 | 19 | 11 | 200 | 270 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 260 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 699 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 20 | 60 | 0 | 66 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 35 | 0 | 30 | 52 | 34 | 22 | 0 | 11 | 0 | 0 | 150 | 10 | 10 | 144 | 0 | 200 | 0 | 82 | 100 | 200 | 0 | 400 | 105 | 200 | 90 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 90
Forecast for Day | 0 | 0 | 0 | 170 | 0 | 90 | 0 | 360 | 360 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 60 | 0 | 100 | 150 | 80 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 10 | 25 | 20 | 52 | 0 | 58 | 60 | 100 | 120 | 25 | 0 | 0 | 120 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 22 | 30 | 80 | 0 | 80 | 330 | 360 | 210 | 8 | 135 | 23 | 55 | 0 | 43 | 0 | 50 | 40 | 22 | 11 | 33 | 21 | 121 | 205 | 8 | 21 | 1.6 | 43 | 43 | 51 | 0 | 0 | 275 | 60 | 84 | 0 | 150 | 18 | 0 | 10 | 0 | 19 | 11 | 100 | 270 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 170 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 260 | 90 | 50 | 162 | 116 | 0 | 17 | 30 |  | 699 | 0 | 0 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 66 | 33 | 110 | 0 | 70 | 0 | 50 | 20 | 95 | 35 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 100 | 0 | 200 | 0 | 80 | 50 | 200 | 0 | 400 | 105 | 100 | 90 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 90 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 170 | 0 | 22 | 0 | 295 | 268 | 0 | 0 | 240 | 250 | 0 | 0 | 0 | 150 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 25 | 8 | 25 |  | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 21 | 42 | 70 | 0 | 80 | 275 | 275 | 216 | 8 | 134 | 23 | 20 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 25 | 9 | 74 | 204 | 8 | 19 | 1 | 43 | 43 | 11 | 0 | 0 | 270 | 20 | 10 | 0 | 100 | 18 | 0 | 10 | 0 | 19 | 11 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 319 | 65 | 0 | 17 | 0 | 0 | 0 | 17 | 0 | 17 | 0 | 200 | 0 | 20 | 0 | 17 | 0 | 17 | 7 | 0 | 686 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 17 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 0 | 0 | 154 | 0 | 0 | 80 | 0 | 159 | 0 | 13 | 0 | 148 | 0 | 293 | 0 | 0 | 0 | 0 | 34 | 0 | 1 | 0 | 270 | 120 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 7385 | 7:00
| Highest Generation |  | 10487 | 22:00
| Day Peak Generation |  | 8068 | 12:00
| Evening Peak Generation |  | 10400 | 21:00
| HVDC Max Flow |  | 812 | 1:00
| HVDC EvPeak Flow |  | 781 | 21:00
| Load factor L.F |  | 84.26%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-07-29
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-07-28 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 8068 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 6927 | MW
Evening Peak Generation : |  | 10400 | MW Hour : | 21:00 | Available Max Generation : |  | 14733 | MW
E.P. Demand (at gen end) : |  | 10400 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 10000 | MW
Maximum Generation : |  | 10487 | MW Hour : | 22:00 | Reserve(Generation end) |  | 4733 | MW
Total Gen. (MKWH) : |  | 212.074 | System Load Factor : | 84.26% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -216 | MW at | 24:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-07-29
Actual : | 84.69 | Ft.(MSL) , | Rule curve : | 88.49 | Ft.( MSL )
Gas Consumed : | Total = | 1231.58 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 160513154.158
: |  | Coal : | 57806072 | Oil : | 174276695.42 | Total : | 392595921.578
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 3563.7087 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1209.0725 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1082.7925 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 978.2181 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 884.0988 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 713.4294 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 402.4994 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 183.7837 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 550.215 |  |  | 0 | 0%
Total | 0 |  | 9567.8181 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4 & 7
3) Ashuganj-4 & 5
4) Kaptai-2
5) Raozan #2
6) Bhola 225 MW
7) Baghabari-71 MW
8) Bheramara 410 MW
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet CCPP ST was under shut down at 09:48 for cleaning cooling tower.
b) Ashuganj 132/33 kV Av transformer was under shut down from 09:24 to 18:12 due to energy meter
maintenance.
c) Bagerhat 132/33 kV T2 transformer was under shut down from 08:33 to 09:04 for C/M.
d) Bagerhat 132/33 kV T3 transformer was under shut down from 09:50 to 12:58 for C/M.
e) Jhenaidah-Chuadanga 132 kV Ckt was under shut down from 08:12 to 19:50 for D/W. |  |  |  |  | About 60 MW power interruption occurred under Jhenaidah S/S area
from 08:12 to 12:33.
f) Jhenaidah(O)-Jhenaidah(N) 132 kV Ckt was switched on at 12:33.
g) Jhenaidah(N) 132 kV Bus of 230/132 kV transformer were switched on at 12:33.
h) Mymensing-Netrokona 132 kV Ckt-1 was under shut down from 08:27 to 17:57 for C/M.
i) Purbasadipur 33 kV Bus & 132/33 kV T1 transformer was under shut down 08:15 10:12 for C/M. |  |  |  |  | About 30 MW power interruption occurred under Purbasadipur S/S
area from 08:15 10:12.
j) Bhola CCPP GT-1 was synchronized at 10:09.
k) Kabirpur-Manikganj 132 kV Ckt-1 tripped at 12:20 showing Dist. Z1, B-phase relay at Kabirpur end and
was switched on at 12:32.
l) Khulna(south)-Bheramara HVDC 230 kV Ckt-1 was switched on at 19:20.
m) Jhenaidah(N) 230/132 kV T01 transformer was switched on at 19:43.
n) Halishahar 132/33 kV T1 transformer was under shut down from 19:26 to 20:28 for C/M.
o) Jamalpur 132/33 kV T4 transformer was under shut down from 19:11 to 20:03 for C/M. |  |  |  |  | About 20 MW power interruption occurred under Jamalpur S/S area
from 19:11 to 20:03.
p) Niamatpur 132/33 kV T2 transformer was under shut down from 19:29 to 21:03 for C/M.
q) Siddhirganj 335 MW STG tripped at 19:51 due to LP control V/V problem.
r) Madunaghat 132/33 T1 & T2 transformers tripped at 21:16 due to loop burned of 33 kV new was feeder |  |  |  |  | About 43 MW power interruption occurred under Meghnaghat S/S
and was switched at 21:39. |  |  |  |  | area from 21:16 to 21:39.
s) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 00:03(29-07-2021) showing dist.Z4 at Dohazari end and
was switched on at 00:23(29-07-2021).
t) Mongla 132/33 T1 & T2 transformers tripped at 21:56 due to of 33 kV feeder fault and was switched
on 00:10(29-07-2021).
u) Mongla 132/33 T1 & T2 transformers tripped at 00:15(29-07-2021) due to of 33 kV feeder fault and |  |  |  |  | About 16 MW power interruption occurred under Mongla S/S area
was switched on 02:48(29-07-2021). |  |  |  |  | from 00:15(29-07-2021) to 02:48(29-07-2021).
v) Cox'sbazar 132/33 T1 & T2 transformers tripped at 23:29 due to of 33 kV feeder fault and was switched |  |  |  |  | About 40 MW power interruption occurred under Cox'sbazar S/S area
on 00:02(29-07-2021). |  |  |  |  | from 23:29 to 00:02(29-07-2021).
w) Bheramara CCPP ST was shut down at 00:18(29-07-2021) due to air filter replacement of GT.
x) Bheramara CCPP GT was shut down at 00:34(29-07-2021) due to air filter replacement of GT.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-07-28 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Gas shortage
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 170 | 4189500
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 0 | 0 | Under maint.
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 99 | 1353863
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 370 | 8503290 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 345 | 7694000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5642250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6363724 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 0 | 0 | Reserve.
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 244548 | Engine problem
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 90 | 1442000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 214 | 6796503 | ST Under maint.
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 0 | 13824 | Reserve.
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 653760
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 16 | 129120 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 327346
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 0 | 28263 | Reserve.
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 33 | 795120 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 760300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 17 | 491500 | Engine problem
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 390720
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 15 | 82800 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 16 | 246240 | Low demand
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 129600 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 0 | 61440 | Reserve.
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 0 | 23040 | Reserve.
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 146810
| Dhaka area Total |  |  |  | 5819 | 2104 | 46509561
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 32976 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 3915
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 0 | 0 | Reserve.
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 119 | 2594036 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 120 | 2898936 | Machine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 17 | 383054 | Low demand
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 34 | 169406 | Low demand
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 447360
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 507792
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 910560
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 93 | 851520 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 17158
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 0 | 0 | Reserve.
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Reserve.
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 108 | 1354908
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 30 | 246720 | Low demand
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2123945
| Chattogram area Total |  |  |  | 2382 | 1028 | 17842286
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 80 | 1690506 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1743132 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4742000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 6923400 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 305 | 6941000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 474624 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 30 | 665760 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 621192 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 50 | 481745 | Low demand
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 0 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 2611710 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 18 | 730080 | Low demand
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 510984
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 259020
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 120 | 2423040
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 666100 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 0 | 18749 | Reserve.
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 403490 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 0 | 0 | Reserve.
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 105 | 1412880
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443160 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1618 | 33963299
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 205 | 4645760
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 425340
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 177600 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 194 | 2248800
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2313600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 341670
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 248640
| Mymensingh Area Total |  |  |  | 709 | 565 | 10415860
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1028000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 43 | 1018957 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 0 | 0 | Under maint.
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 274 | 4852000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 711000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 244100
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 61 | 1397
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1026240
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 140 | 3617000
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 390000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 394544 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 0 | 0 | Under maint.
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 402 | 8962000 | FGMO
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 237600
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 269 | 5497500
| Sylhet Area Total |  |  |  | 2377 | 1418 | 27980338
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 781 | 19114909
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 0 | Reserve.
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 0 | 48000 | Reserve.
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 2048 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 360 | 8088192
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 479040
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 801600
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Reserve.
| Khulna Area Total |  |  |  | 2129 | 1346 | 28533789
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 483804
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 66 | 836000 | Gas shortage
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 719231 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 480 | 8484000
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 201 | 4353900
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 0 | 0
| Barisal Area Total |  |  |  | 2046 | 789 | 14876935
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 70 | 1619000 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 259088
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 0 | Reserve.
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 112560 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 22 | 127996 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 142 | 2731500 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4332682 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 202 | 4576145 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 385 | 8886400 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 281302 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 489840
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 246744
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 8 | 447840 | Low demand
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 47 | 392368 | Low demand
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 39 | 1372128 | Low demand
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 45 | 858720 | Low demand
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 33720
| Rajshahi Area Total |  |  |  | 2179 | 1266 | 26768033
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3793600 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1354377
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 35945
| Rangpur Area Total |  |  |  | 605 | 266 | 5183922
| Total |  |  |  | 21280 | 10400 | 212074023
| Eastern Grid Total |  |  |  | 14321 | 6733 | 136711344
| Western Grid Total |  |  |  | 6959 | 3667 | 75362679
| National Grid Total |  |  |  | 21280 | 10400 | 212074023
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-07-28
(a) ENTIRE EASTERN GRID : |  | 6259 | MW | (b) ENTIRE WESTERN GRID : |  | 3681 | MW
i) Dhaka area |  | 2831 | MW | i) Khulna area |  | 1362 | MW
ii) Chittagong area |  | 869 | MW | ii) Rajshahi area |  | 1273 | MW
iii) Comilla area |  | 1070 | MW | iii) Barisal area |  | 252 | MW
iv) Mymensingh area |  | 1000 | MW | iv) Rangpur area |  | 794 | MW
v) Sylhet area |  | 489 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 9940 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 74 | 22:00 | Kishoreganj | 138 | 1:00 | Jessore | 104 | 21:00
Munsiganj | 84 | 23:00 | Netrokona | 123 | 22:00 | Benapol | 58 | 20:00
Sonargaon | 49 | 1:00 | Jamalpur | 158 | 1:00 | Jhenida | 112 | 20:00
Shyampur | 64 | 23:00 | Sherpur | 134 | 20:00 | Bottail | 111 | 19:30
Bhulta | 68 | 1:00 | Srimongal | 55 | 19:30 | G.K Project | 59 | 20:00
Madanganj | 29 | 22:00 | Shahjibazar | 95 | 21:00 | Faridpur | 133 | 21:00
Shitalakhya | 57 | 14:00 | Fenchuganj | 45 | 19:30 | Rajbari | 46 | 19:30
Rahim steel | 0 | 1:00 | Kulawara | 46 | 21:00 | Madaripur | 90 | 21:00
Matuail | 24 | 1:00 | Sylhet | 115 | 1:00 | Sariatpur | 60 | 21:00
Ghorasal | 60 | 1:00 | Chatak | 33 | 21:00 | Gopalganj | 85 | 20:00
Narsingdi | 135 | 22:00 | Sunamganj | 50 | 1:00 | Bagerhat | 67 | 19:30
Haripur (SBU) | 49 | 0:00 | Biani Bazar | 69 | 1:00 | Mongla | 24 | 1:00
Sreenagar | 38 | 21:00 | Comilla (S) | 122 | 1:00 | Satkhira | 87 | 20:00
Ullon | 45 | 19:00 | Comilla(N) | 122 | 23:00 | Gallamari | 26 | 1:00
Hasnabad | 64 | 1:00 | Chandpur | 75 | 23:00 | Magura | 58 | 20:00
Magbazar | 71 | 12:00 | Feni | 104 | 21:00 | Norail | 40 | 19:30
Maniknagar | 58 | 11:00 | Chowmuhani | 176 | 22:00 | Chuadanga | 101 | 21:00
Bangabhaban | 11 | 10:00 | Ashuganj | 45 | 23:00 | Borguna | 6 | 21:00
Motijheel | 18 | 10:00 | Daudkandi | 128 | 21:00 | Barisal(N) | 37 | 21:00
Narinda | 34 | 1:00 | B.Baria | 161 | 22:00 | Barisal (S) | 82 | 12:00
Kazla | 58 | 0:00 | Ramganj | 78 | 23:00 | Patuakhali | 70 | 20:00
Dhanmondi | 119 | 13:00 | Chaddagram | 40 | 1:00 | Bhandaria | 32 | 22:00
Lalbag | 48 | 14:00 | PHP | 7 | 1:00 | Borhan Uddin | 46 | 22:00
Madartek | 62 | 23:00 | Kochua | 62 | 1:00 | Ishurdi | 60 | 20:00
Dhaka University | 17 | 12:00 | Madunaghat | 48 | 15:00 | Ruppur Paromanobik | 3 | 21:00
Aftabnagar | 8 | 10:00 | Hathazari | 71 | 23:00 | Natore | 132 | 21:00
Fatullah | 30 | 1:00 | Khulshi | 93 | 13:00 | Bogra | 136 | 21:00
Nawabganj | 49 | 22:00 | Halishahar | 58 | 18:30 | Noagaon | 114 | 21:00
Keraniganj | 46 | 1:00 | Baraulia | 54 | 19:00 | Rajshahi | 151 | 20:00
Mirpur | 90 | 23:00 | Sikalbaha | 21 | 19:30 | Rajshahi New | 14 | 21:00
Kalyanpur | 90 | 13:00 | Dohazari | 84 | 21:00 | C.Nawabganj | 62 | 21:00
Gulshan | 76 | 13:00 | Cox'sbazar | 79 | 19:00 | Amnura | 48 | 21:00
Uttara | 66 | 24:00 | Chandraghona | 26 | 19:30 | Pabna | 100 | 21:00
Uttara New | 12 | 13:00 | Kaptai | 4 | 19:00 | Shahjadpur | 87 | 21:00
Kamrangirchar | 55 | 23:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 94 | 21:00
Savar | 96 | 21:00 | Bakulia | 78 | 22:00 | Niyamatpur | 70 | 21:00
Bhasantec | 100 | 13:00 | Julda | 15 | 1:00 | Joypurhat | 60 | 21:00
Agargaon | 65 | 24:00 | TK chemical | 18 | 1:00 | Sherpur(Bogura) | 52 | 20:00
Satmosjid | 77 | 13:00 | Modern Steel | 0 | #N/A | Mohastangor | 68 | 20:00
Tongi | 68 | 13:00 | Shahmirpur | 16 | 2:00 | Bhangura | 32 | 21:00
Kabirpur | 128 | 19:30 | Khagrachhari | 26 | 19:30 | Rangpur | 140 | 21:00
Basundhara | 174 | 12:00 | Matarbari | 25 | 22:00 | Lalmonirhat | 47 | 21:00
Manikganj | 70 | 22:00 | Baroiar Hat | 38 | 19:30 | Saidpur | 107 | 20:00
Joydevpur | 99 | 19:30 | Rangamati | 10 | 12:00 | Purbasadipur | 114 | 19:30
New Tongi | 57 | 14:00 | Abul Khair 230 | 128 | 13:00 | Thakurgaon | 86 | 20:00
Kodda | 120 | 22:00 | BSRM | 1 | 1:00 | Palashbari | 120 | 1:00
Dhamrai | 74 | 1:00 | GPH Ispat | 96 | 23:00 | Barapukuria | 57 | 21:00
Rajendrapur | 76 | 22:00 | Agrabad | 58 | 14:00 | Panchagar | 54 | 5:00
Valuka | 82 | 15:00 | Goalpara | 22 | 19:30 | Joldhaka | 66 | 3:00
Tangail | 209 | 21:00 | Central S/S | 878 | 20:00 | Kurigram | 63 | 19:30
Mymensing | 210 | 2:00 | Noapara | 44 | 19:30 | Mithapukur | 33 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-07-28 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 402 | 18:00 | 396 | 1:00 | Kaliakoir | 395 | 0.41667 | 386 | 0.54167
| Bheramara | 406 | 18:30 | 398 | 20:00 | Bhulta | 388 | 0.77083 | 379 | 0.66667
| Ashuganj(N) | 392 | 6:00 | 385 | 14:00 | Gopalganj | 413 | 0.625 | 391 | 0.875
| Payra | 415 | 7:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 230 | 1:00 | 230 | 1:00 | Hathazari | 225 | 1:00 | 219 | 10:00
| Ishurdi | 235 | 18:30 | 225 | 3:00 | Megnaghat | 233 | 17:00 | 230 | 7:00
| Ashuganj | 238 | 6:00 | 235 | 1:00 | Fenchuganj | 236 | 5:00 | 233 | 10:00
| Serajganj | 230 | 18:00 | 225 | 2:00 | Siddhirganj | 233 | 6:00 | 229 | 13:00
| Baghabari | 232 | 18:00 | 225 | 1:00 | Maniknagar | 231 | 6:00 | 228 | 10:00
| Barapukuria | 233 | 18:00 | 222 | 15:00 | Agargaon | 229 | 17:00 | 223 | 13:00
| Bogra | 222 | 18:00 | 212 | 14:00 | Barisal | 248 | 24:00 | 236 | 23:00
| Rajshahi | 236 | 18:30 | 219 | 15:00 | Bhola 225 MW | 248 | 5:00 | 241 | 22:00
| Khulna South | 231 | 20:00 | 203 | 16:00 | AKSML | 228 | 24:00 | 219 | 10:00
| Rampura | 230 | 5:00 | 227 | 15:00 | BSRM | 229 | 24:00 | 222 | 10:00
| Haripur | 230 | 7:00 | 227 | 10:00 | Bibiyana | 238 | 17:00 | 234 | 10:00
| Hasnabad | 231 | 19:00 | 225 | 13:00 | Bhulta | 234 | 18:00 | 228 | 12:00
| Shyampur | 228 | 7:00 | 220 | 13:00 | Ashuganj (S) | 235 | 18:30 | 231 | 13:00
| Aminbazar | 230 | 1:00 | 225 | 2:00 | Kaliakoir | 228 | 6:00 | 223 | 13:00
| Tongi | 228 | 7:00 | 222 | 15:00 | GPH | 227 | 1:00 | 219 | 10:00
| Comilla (N) | 230 | 6:00 | 225 | 14:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 3:00 | 133 | 10:00 | Madanhat | 135 | 0.79167 | 130 | 0.375
| Munsiganj | 135 | 19:00 | 132 | 13:00 | Hathazari | 134 | 0.041667 | 130 | 0.45833
| Sonargaon | 133 | 19:30 | 131 | 1:00 | Khulshi | 133 | 0.875 | 126 | 0.41667
| Shyampur | 138 | 7:00 | 135 | 13:00 | Halishahar | 134 | 0.875 | 126 | 0.41667
| Bhulta | 130 | 5:00 | 127 | 10:00 | Baraulia | 134 | 0.875 | 128 | 0.41667
| Madanganj | 135 | 18:30 | 131 | 3:00 | Sikalbaha | 136 | 0.875 | 127 | 0.75
| Shitalakhya | 139 | 18:30 | 134 | 14:00 | Dohazari | 131 | 0.875 | 124 | 0.75
| Rahim steal | 135 | 7:00 | 133 | 23:00 | Cox'sbazar | 126 | 0.58333 | 119 | 0.45833
| Matuail | 135 | 3:00 | 133 | 10:00 | Chandraghona | 135 | 0.875 | 129 | 0.41667
| Ghorasal | 138 | 1:00 | 136 | 13:00 | Kaptai | 135 | 0.79167 | 130 | 0.29167
| Narsinghdi | 133 | 17:00 | 126 | 1:00 | A. Khaer Stl. | 133 | 0.875 | 128 | 0.375
| Haripur (SBU) | 135 | 6:00 | 133 | 1:00 | Bakulia | 134 | 0.875 | 126 | 0.45833
| Sreenagar | 131 | 18:30 | 128 | 1:00 | Julda | 135 | 0.041667 | 127 | 0.41667
| Ullon | 135 | 3:00 | 132 | 14:00 | TK Chemical | 134 | 0.875 | 127 | 0.41667
| Hasnabad | 138 | 18:30 | 135 | 9:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 136 | 4:00 | 131 | 11:00 | Shahmirpur | 135 | 0.875 | 126 | 0.33333
| Maniknagar | 136 | 7:00 | 133 | 11:00 | Khagrachhari | 133 | 0.8125 | 127 | 0.45833
| Bangabhaban | 136 | 7:00 | 133 | 11:00 | Matarbari | 130 | 0.95833 | 120 | 0.41667
| Motijheel | 136 | 7:00 | 133 | 11:00 | Baroiar Hat | 132 | 0.8125 | 127 | 0.66667
| Narinda | 136 | 7:00 | 133 | 11:00 | Rangamati | 134 | 21:00 | 128 | 10:00
| Kazla | 136 | 7:00 | 133 | 11:00 | Agrabad | 134 | 21:00 | 127 | 10:00
| Dhanmondi | 135 | 3:00 | 133 | 10:00 | Goalpara S/S | 139 | 20:00 | 123 | 0.66667
| Lalbag | 139 | 18:30 | 134 | 14:00 | Khulna Central S/S | 137 | 20:00 | 121 | 0.79167
| Madartek | 136 | 18:30 | 132 | 13:00 | Noapara | 136 | 19:30 | 119 | 0.125
| Dhaka University | 137 | 18:30 | 132 | 12:00 | Jessore | 132 | 10:00 | 117 | 0.79167
| Aftabnagar | 136 | 6:00 | 132 | 11:00 | Benapol | 133 | 0.41667 | 116 | 0.083333
| Fatullah | 138 | 6:00 | 136 | 1:00 | Jhenida | 132 | 10:00 | 113 | 0.041667
| Nawabganj | 131 | 7:00 | 127 | 11:00 | Bottail | 134 | 0.41667 | 124 | 0.041667
| Keraniganj | 131 | 7:00 | 128 | 13:00 | G.K Project | 139 | 0.41667 | 133 | 0.041667
| Mirpur | 138 | 18:30 | 132 | 13:00 | Faridpur | 138 | 0.375 | 129 | 0.875
| Kalyanpur | 137 | 5:00 | 134 | 12:00 | Rajbari | 138 | 0.79167 | 126 | 0.875
| Gulshan | 135 | 5:00 | 131 | 13:00 | Madaripur | 143 | 0.375 | 133 | 0.875
| Uttara | 136 | 19:00 | 133 | 12:00 | Shariyatpur S/S | 142 | 9:00 | 131 | 0.875
| Uttara New | 136 | 13:00 | 132 | 13:00 | Gopalganj | 146 | 0.70833 | 134 | 0.875
| Kamrangirchar | 139 | 19:00 | 134 | 14:00 | Bagerhat | 138 | 19:30 | 119 | 0.66667
| Savar | 132 | 1:00 | 131 | 13:00 | Mongla | 135 | 20:00 | 118 | 0.66667
| Bhasantec | 136 | 6:00 | 132 | 13:00 | Satkhira | 134 | 6:00 | 120 | 16:00
| Agargaon | 138 | 18:30 | 132 | 13:00 | Gallamari | 137 | 0.95833 | 123 | 16:00
| Satmosjid | 136 | 6:00 | 132 | 14:00 | Magura | 132 | 10:00 | 110 | 0.041667
| Tongi | 139 | 5:00 | 135 | 19:30 | Narail | 128 | 0.375 | 111 | 0.8125
| Kabirpur | 140 | 4:00 | 136 | 22:00 | Chuadanga | 130 | 20:00 | 101 | 0.8125
| Basundhara | 138 | 7:00 | 133 | 13:00 | Borguna | 143 | 12:00 | 134 | 0.91667
| Manikganj | 140 | 18:30 | 135 | 22:00 | Barisal(N) | 143 | 10:00 | 136 | 22:00
| Joydevpur | 140 | 19:30 | 133 | 1:00 | Barisal (S) | 142 | 0.20833 | 135 | 0.83333
| New Tongi | 139 | 18:30 | 134 | 13:00 | Patuakhali(S) | 142 | 0.41667 | 133 | 0.875
| Kodda | 135 | 8:00 | 129 | 13:00 | Bhandaria | 144 | 0.20833 | 132 | 0.91667
| Dhamrai | 134 | 6:00 | 130 | 22:00 | Ishurdi | 136 | 18:30 | 131 | 21:00
| Rajendrapur | 134 | 8:00 | 126 | 14:00 | Ruppur Paromanobik | 135 | 18:00 | 131 | 21:00
| Valuka | 130 | 18:30 | 113 | 1:00 | Natore | 133 | 18:30 | 126 | 15:00
| Tangail | 136 | 18:30 | 128 | 1:00 | Bogra | 132 | 18:30 | 124 | 14:00
| Mymensing | 128 | 6:00 | 117 | 1:00 | Noagaon | 129 | 18:00 | 118 | 15:00
| Kishorganj | 130 | 5:00 | 119 | 1:00 | Rajshahi | 131 | 18:30 | 123 | 15:00
| Netrokona | 124 | 6:00 | 111 | 1:00 | Rajshahi New | 133 | 18:30 | 123 | 15:00
| Jamalpur | 136 | 19:30 | 119 | 12:00 | C.Nawabganj | 130 | 18:00 | 120 | 15:00
| Sherpur | 133 | 19:30 | 116 | 12:00 | Amnura | 129 | 20:00 | 118 | 15:00
| Srimongal | 136 | 18:00 | 133 | 1:00 | Pabna | 134 | 18:00 | 128 | 21:00
| Shahjibazar | 135 | 19:30 | 131 | 2:00 | Shahjadpur | 139 | 18:00 | 134 | 9:00
| Fenchuganj | 135 | 9:00 | 132 | 1:00 | Serajganj | 130 | 18:00 | 127 | 1:00
| Khulawara | 134 | 17:00 | 131 | 1:00 | Niyamatpur | 126 | 18:00 | 114 | 21:00
| Sylhet | 133 | 18:00 | 130 | 1:00 | Joypurhat | 130 | 18:00 | 116 | 15:00
| Chatak | 132 | 5:00 | 127 | 24:00 | Sherpur(Bogura) | 131 | 18:00 | 125 | 15:00
| Sunamganj | 130 | 15:00 | 124 | 1:00 | Mohastangor | 130 | 18:00 | 121 | 14:00
| Biani Bazar | 133 | 16:00 | 125 | 1:00 | Bangura | 136 | 18:30 | 131 | 21:00
| Comilla(s) | 130 | 7:00 | 126 | 19:30 | Rangpur | 126 | 18:30 | 108 | 14:00
| Comilla(n) | 137 | 6:00 | 134 | 10:00 | Lalmonirhat | 125 | 18:00 | 111 | 14:00
| Chandpur | 133 | 1:00 | 129 | 16:00 | Saidpur | 126 | 18:00 | 112 | 15:00
| Feni | 131 | 6:00 | 125 | 16:00 | Purbasadipur | 126 | 18:30 | 106 | 14:00
| Chowmuhani | 129 | 4:00 | 124 | 15:00 | Thakurgaon | 125 | 18:30 | 105 | 14:00
| Ashuganj | 137 | 5:00 | 133 | 1:00 | Palashbari | 127 | 18:00 | 115 | 14:00
| Daudkandi | 133 | 18:00 | 129 | 1:00 | Barapukuria | 133 | 18:00 | 122 | 15:00
| B.Baria | 133 | 18:00 | 127 | 1:00 | Panchagar | 128 | 18:00 | 105 | 14:00
| Ramganj | 131 | 1:00 | 126 | 12:00 | Joldhaka | 124 | 0.77083 | 106 | 0.58333
| Chaddagram | 133 | 6:00 | 128 | 16:00 | Kurigram | 121 | 0.77083 | 105 | 0.58333
| PHP | 131 | 18:30 | 126 | 15:00 | Mithapukur | 127 | 0.75 | 114 | 0.58333
| Kochua | 134 | 18:30 | 130 | 14:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-07-28
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 216 | 6629 | 3475 | 10104 |  |  |  | QF-LDC-11
0:30 | 176 | 6588.5 | 3474.5 | 10063 | Date: | 2021-07-28
1:00 | 136 | 6548 | 3474 | 10022
1:30 | 141 | 6437 | 3404.5 | 9841.5
2:00 | 146 | 6326 | 3335 | 9661
2:30 | 124 | 6084.5 | 3313.5 | 9398 | [5 empty] | Gen. at Eve. Peak | 10400 | 10400 MW (21:00 )
3:00 | 102 | 5843 | 3292 | 9135 | [6 empty] | 21:00
3:30 | 101 | 5829.5 | 3214 | 9043.5 | [5 empty] | Gen. at Day Peak | 8068 | 8068 MW (12:00 )
4:00 | 100 | 5816 | 3136 | 8952 | [6 empty] | 12:00
4:30 | 130 | 5796.5 | 3080.5 | 8877 | [5 empty] | Highest Generation | 10487
5:00 | 160 | 5777 | 3025 | 8802 | [6 empty] | 22:00
5:30 | 164 | 5511 | 2792 | 8303
6:00 | 168 | 5245 | 2559 | 7804
6:30 | 151 | 5034 | 2560.5 | 7594.5
7:00 | 134 | 4823 | 2562 | 7385
7:30 | 122 | 4888 | 2540 | 7428
8:00 | 110 | 4953 | 2518 | 7471
8:30 | 95 | 4951 | 2531.5 | 7482.5
9:00 | 80 | 4949 | 2545 | 7494
9:30 | 116 | 4985 | 2603.5 | 7588.5
10:00 | 152 | 5021 | 2662 | 7683
10:30 | 96 | 5041 | 2672 | 7713
11:00 | 40 | 5061 | 2682 | 7743
11:30 | 31 | 5128.5 | 2777 | 7905.5
12:00 | 22 | 5196 | 2872 | 8068
12:30 | 69 | 5306.5 | 2921.5 | 8228
13:00 | 116 | 5417 | 2971 | 8388
13:30 | 89 | 5467.5 | 2971.5 | 8439
14:00 | 62 | 5518 | 2972 | 8490
14:30 | 37 | 5528 | 2962 | 8490
15:00 | 12 | 5538 | 2952 | 8490
15:30 | 17 | 5404 | 2908.5 | 8312.5
16:00 | 22 | 5270 | 2865 | 8135
16:30 | 16 | 5147 | 2784 | 7931
17:00 | 10 | 5024 | 2703 | 7727
17:30 | 63 | 4920 | 2642.5 | 7562.5
18:00 | 116 | 4816 | 2582 | 7398
18:30 | 85 | 5262.5 | 2794.5 | 8057
19:00 | 54 | 5709 | 3007 | 8716
19:30 | 134 | 6518 | 3534 | 10052
20:00 | 12 | 6384 | 3677 | 10061 |  |  |  | Executive Engineer
20:30 | 76 | 6558.5 | 3672 | 10230.5 |  |  |  | Network Operation Division
21:00 | 140 | 6733 | 3667 | 10400
21:30 | 128 | 6768 | 3675.5 | 10443.5
22:00 | 116 | 6803 | 3684 | 10487 |  |  |  |  | Page 6 of 7
22:30 | 84 | 6734 | 3702.5 | 10436.5
23:00 | 52 | 6665 | 3721 | 10386
23:30 | 134 | 6647 | 3598 | 10245
24:00 | 216 | 6629 | 3475 | 10104
10400 MW (21:00 )
8068 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-07-28 |  | Energy | 212074023
[11 empty] | 2021-07-28 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4894 | 781 | 1522 | 1973 | 580 | 123 | 147 | 0 | 114 | 0
0:30 | 4890.5 | 796.5 | 1552.5 | 1985.5 | 517.5 | 91.5 | 126 | 0 | 118 | 0 | Date: | 2021-07-28
1:00 | 4887 | 812 | 1583 | 1998 | 455 | 60 | 105 | 0 | 122 | 0
1:30 | 4897.5 | 808.5 | 1576 | 1850.5 | 450.5 | 60 | 77.5 | 0 | 121 | 0 | [7 empty] | Total Energy | 212.074 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4908 | 805 | 1569 | 1703 | 446 | 60 | 50 | 0 | 120 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4873.5 | 797.5 | 1539.5 | 1524 | 435.5 | 60 | 50 | 0 | 118 | 0 | [7 empty] | Energy Requirement | 212.074
3:00 | 4839 | 790 | 1510 | 1345 | 425 | 60 | 50 | 0 | 116 | 0
3:30 | 4765 | 791.5 | 1490.5 | 1349.5 | 425 | 60 | 50 | 0 | 112 | 0 | [6 empty] | Shortage
4:00 | 4691 | 793 | 1471 | 1354 | 425 | 60 | 50 | 0 | 108 | 0
4:30 | 4625.5 | 793 | 1471 | 1346.5 | 425 | 60 | 50 | 0 | 106 | 0
5:00 | 4560 | 793 | 1471 | 1339 | 425 | 60 | 50 | 0 | 104 | 0
5:30 | 4513 | 793 | 1358.5 | 1035 | 420 | 60 | 25 | 0 | 98 | 0.5
6:00 | 4466 | 793 | 1246 | 731 | 415 | 60 | 0 | 0 | 92 | 1
6:30 | 4307 | 793 | 1275.5 | 648 | 419 | 60 | 0 | 0 | 85 | 7 |  |  |  |  | Coal
7:00 | 4148 | 793 | 1305 | 565 | 423 | 60 | 0 | 0 | 78 | 13
7:30 | 4231 | 793 | 1258 | 547.5 | 423 | 60 | 0 | 0 | 80 | 35.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4314 | 793 | 1211 | 530 | 423 | 60 | 0 | 0 | 82 | 58
8:30 | 4347.5 | 793.5 | 1203 | 510 | 425.5 | 60 | 0 | 0 | 85 | 58
9:00 | 4381 | 794 | 1195 | 490 | 428 | 60 | 0 | 0 | 88 | 58
9:30 | 4428 | 794.5 | 1231.5 | 491 | 427 | 60 | 0 | 0 | 87 | 69.5
10:00 | 4475 | 795 | 1268 | 492 | 426 | 60 | 0 | 0 | 86 | 81
10:30 | 4495 | 795 | 1274.5 | 494 | 425.5 | 60 | 0 | 0 | 87 | 82
11:00 | 4515 | 795 | 1281 | 496 | 425 | 60 | 0 | 0 | 88 | 83
11:30 | 4603.5 | 795 | 1319.5 | 526.5 | 434 | 60 | 0 | 0 | 88 | 79
12:00 | 4692 | 795 | 1358 | 557 | 443 | 60 | 0 | 0 | 88 | 75
12:30 | 4700 | 795.5 | 1390.5 | 647 | 448.5 | 74 | 0 | 0 | 92 | 80.5
13:00 | 4708 | 796 | 1423 | 737 | 454 | 88 | 0 | 0 | 96 | 86
13:30 | 4708 | 796 | 1423 | 737 | 454 | 88 | 0 | 0 | 96 | 86
14:00 | 4708 | 796 | 1423 | 737 | 454 | 88 | 0 | 0 | 96 | 86
14:30 | 4789.5 | 795.5 | 1409 | 737.5 | 454.5 | 87.5 | 0 | 0 | 97 | 68.5
15:00 | 4871 | 795 | 1395 | 738 | 455 | 87 | 0 | 0 | 98 | 51
15:30 | 4821 | 795 | 1338 | 697 | 439.5 | 86.5 | 1 | 0 | 95 | 39.5
16:00 | 4771 | 795 | 1281 | 656 | 424 | 86 | 2 | 0 | 92 | 28
16:30 | 4701.5 | 795 | 1225 | 586 | 424.5 | 85.5 | 2 | 0 | 90 | 21.5
17:00 | 4632 | 795 | 1169 | 516 | 425 | 85 | 2 | 0 | 88 | 15
17:30 | 4477.5 | 788 | 1184.5 | 506 | 423.5 | 85 | 1 | 0 | 86 | 11
18:00 | 4323 | 781 | 1200 | 496 | 422 | 85 | 0 | 0 | 84 | 7
18:30 | 4487 | 781 | 1319 | 756 | 437 | 100 | 73.5 | 0 | 100 | 3.5
19:00 | 4651 | 781 | 1438 | 1016 | 452 | 115 | 147 | 0 | 116 | 0
19:30 | 4900 | 780 | 1574 | 1794 | 552 | 117 | 217 | 0 | 118 | 0
20:00 | 4901 | 781 | 1620 | 1693 | 572 | 119 | 259 | 0 | 116 | 0
20:30 | 4983.5 | 781 | 1609 | 1786 | 602.5 | 119 | 231.5 | 0 | 118 | 0
21:00 | 5066 | 781 | 1598 | 1879 | 633 | 119 | 204 | 0 | 120 | 0
21:30 | 5053.5 | 781 | 1623.5 | 1914 | 627 | 120 | 203.5 | 0 | 121 | 0
22:00 | 5041 | 781 | 1649 | 1949 | 621 | 121 | 203 | 0 | 122 | 0
22:30 | 4985 | 780.5 | 1646.5 | 1961 | 620.5 | 122 | 203 | 0 | 118 | 0
23:00 | 4929 | 780 | 1644 | 1973 | 620 | 123 | 203 | 0 | 114 | 0
23:30 | 4911.5 | 780.5 | 1583 | 1973 | 600 | 123 | 175 | 0 | 114 | 0 | Max Temp. in Dhaka |  | 31.0° C
24:00 | 4894 | 781 | 1522 | 1973 | 580 | 123 | 147 | 0 | 114 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-07-28
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | [12 empty] | 28 | 28 | 27 | 26 | 25 | 25 |  | 55 | 57 | 59 | 59 | 61 | 63 | 63 | 1150036
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1444000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [20 empty] | 3 | 6 | 8 |  | 1 | 8 | 32976
| Teknaf 20MW PP (Solartech) | [14 empty] | 0 | 2 | 0 | [9 empty] | 3915
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2898936
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 34 | 34 | 34 | 34 | 34 | 34 | 0 | 169406
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 55 | 54 | [9 empty] | 9 | 17 | 17 | 17 | 17 |  |  |  | 5 | 17 | 17 | 17 | 29 | 35 | 52 | 383054
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 57 | 60 | 37 | 37 | 90 | 37 | 38 | 38 | 37 | 37 | 37 | 35 | 37 | 60 | 57 | 35 | 36 | 35 |  | 90 | 88 | 90 | 90 | 90 | 90 | 37 | 1442000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 332 | 330 | 334 | 280 | 280 | 250 | 250 | 250 | 250 | 300 | 270 | 300 | 300 | 300 | 270 | 270 |  | 270 | 280 | 208 | 214 | 212 | 214 | 219 | 6796503
18 | Kodda 300 MW PP Unit-2 (Summit) | [19 empty] | 15 | 30 | 25 | 15 | 15 | 4 | 0 | 82800
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 |  | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 4189500
24
25 | Ghorasal 365 MW CCPP Unit-7
26
28 | Ashuganj TPP Unit- 3 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 70 | 70 | 70 | 80 | 80 | 70 | 70 | 1690506
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 70 | 80 | 80 | 1743132
32 | Ashuganj 50 MW PP | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 |  |  | 23 | 23 | 20 | 23 | 23 | 23 | 23 | 474624
33 | Ashuganj 225 MW CCPP | 205 | 213 | 208 | 210 | 204 | 211 | 210 | 187 | 181 | 191 | 193 | 182 | 190 | 182 | 181 | 181 | 181 | 160 |  | 211 | 215 | 212 | 213 | 195 | 199 | 196 | 4742000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 285 | 290 | 270 | 270 | 270 | 290 | 290 | 350 | 270 | 270 | 280 | 270 | 265 | 265 | 265 | 275 |  | 270 | 265 | 275 | 305 | 340 | 305 | 305 | 6941000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 275 | 285 | 260 | 260 | 260 | 265 | 260 | 270 | 265 | 260 | 270 | 260 | 275 | 275 | 275 | 280 |  | 280 | 275 | 280 | 310 | 300 | 260 | 260 | 6923400
35 | Ashuganj 55 MW PP (Precision) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 54 | 25 | 25 | 10 | 10 | 10 |  | 10 | 30 | 30 | 30 | 51 | 54 | 53 | 665760
36 | Chandpur 150 MW CCPP | 83 | 83 | 86 | 86 | 85 | 85 | 85 | 85 | 86 | 86 | 86 | 83 | 138 | 138 | 135 | 137 | 134 | 137 |  | 136 | 134 | 137 | 137 | 138 | 136 | 136 | 2611710
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 380 | 359 | 361 | 362 | 362 | 348 | 307 | 307 | 307 | 309 | 351 | 352 | 325 | 342 | 374 | 373 | 350 | 321 |  | 308 | 330 | 330 | 370 | 393 | 393 | 392 | 8503290
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5642250
41 | Haripur 360MW CCPP(HPL) | 308 | 308 | 309 | 308 | 308 | 308 | 337 | 308 | 308 | 335 | 345 | 346 | 322 | 321 | 322 | 322 | 276 | 256 |  | 314 | 347 | 348 | 345 | 346 | 350 | 349 | 7694000
42 | RPCL 210MW CCPP | 203 | 204 | 201 | 201 | 203 | 204 | 202 | 200 | 198 | 198 | 192 | 196 | 192 | 193 | 202 | 201 | 167 | 166 |  | 200 | 205 | 204 | 205 | 204 | 204 | 205 | 4645760
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 8 | 31 | 42 | 54 | 57 | 50 | 53 | 45 | 16 | 8 | 4 | 1 | [8 empty] | 341670
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 42 | 42 | 42 | 43 | 43 | 43 | 43 | 43 |  | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 1028000
45 | Fenchugonj CCPP Phase-2 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 42 | 43 | 42 | 42 | 42 | 42 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1018957
46 | Shajibazar 330 MW CCPP | 182 | 182 | 182 | 182 | 182 | 183 | 181 | 183 | 181 | 180 | 176 | 180 | 230 | 270 | 267 | 269 | 269 | 268 |  | 272 | 272 | 274 | 274 | 272 | 270 | 272 | 4852000
47 | Shahjibazar GTPP Unit- 8 & 9 | 61 | 61 | 61 | 61 | 61 | 62 | 61 | 60 | 63 | 62 | 60 | 61 | 60 | 60 | 60 | 40 | 40 | 40 |  | 61 | 61 | 60 | 61 | 61 | 56 | 56 | 1397
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 40 | 84 | 81 | 81 | 81 | 81 | 81 | 1026240
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 212 | 191 | 191 | 191 | 177 | 158 | 158 | 132 | 50 | 140 | 140 | 140 | 140 | 140 | 140 | 100 | 100 |  | 121 | 140 | 140 | 140 | 140 | 140 | 140 | 3617000
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 390000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 9 | 9 | 9 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 237600
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244100
55 | Fenchugonj 51 MW PP (Barakatullah) | 52 | 52 | 52 | 53 | 53 | 14 | 14 | 14 | 14 | 11 | 11 | 11 | 11 | 11 | 11 | 14 | 14 | 14 |  | 14 | 50 | 50 | 50 | 53 | 53 | 53 | 711000
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 394544
57 | Bibiana-II 341 MW CCPP (Summit)
| Bibiyana South 400 MW | 240 | 270 | 269 | 267 | 220 | 269 | 50 | 230 | 262 | 260 | 256 | 264 | 230 | 265 | 260 | 260 | 260 | 200 |  | 250 | 270 | 263 | 269 | 261 | 265 | 270 | 5497500
58 | Nababganj 55 MW PP (Southern power ) | [19 empty] | 17 | 17 |  |  |  |  | 0 | 28263
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | [14 empty] | 5 | 22 | 23 | 24 | 24 | 24 | 24 | 248640
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 507792
61 | Narshingdi 22 MW PP (Doreen) | 17 | 16 | [7 empty] | 16 | 16 | 16 | 16 | 16 | 17 | 17 | 17 |  |  |  | 17 | 17 | 19 | 19 | 19 | 19 | 244548
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 425340
63 | Impoprt (Tripura) | 122 | 120 | 116 | 108 | 104 | 92 | 78 | 82 | 88 | 86 | 88 | 88 | 96 | 100 | 98 | 92 | 88 | 84 |  | 116 | 118 | 116 | 120 | 122 | 114 | 114 | 2423040
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 4 | 26 | 32 | 42 | 20 | 42 | 42 | 39 | 33 | 35 | 42 | 42 | 22 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 37 | 42 | 910560
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510984
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 259020
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 10 | 25 | 666100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 15 | 15 | 15 | 15 | 6 | 6 | 6 | 6 | 6 | 16 | 16 |  | 16 | 21 | 21 | 21 | 21 | 21 | 21 | 403490
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 0 | 4 | 9 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 9 | 9 | 9 | 195120
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 760300
72 | Rupganj 33 MW PP(Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 12 | 8 | 8 | 8 | 21 | 21 | 21 | 21 | 21 |  | 15 | 17 | 17 | 17 | 17 | 17 | 17 | 491500
73 | Ghorashal 108MW PP (Regent) | 98 | 99 | 14 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 85 | 95 | 97 | 97 | 43 | 43 | 43 |  | 91 | 99 | 99 | 99 | 99 | 99 | 99 | 1353863
Feni Lanka Power
| Chowmuhani 113 MW | 108 | 108 | 108 | 108 | 110 | 46 | 26 | 26 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 46 | 104 | 103 | 105 | 108 | 118 | 119 | 1412880
| Manikgonj 162MW PP(MPGL) | [19 empty] | 9 | 17 |  |  |  |  | 0 | 23040
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 51 | 51 | 16 | 16 | 16 | [14 empty] | 8 | 30 | 34 | 51 | 51 | 51 | 34 | 390720
79 | Kodda 150MW PP | 32 | [19 empty] | 32 | 16 | 16 | 16 | 16 | 16 | 129120
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 4 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 177600
81 | Jangalia 52 MW PP (Lakdanavi) | [19 empty] | 4 | 16 | [5 empty] | 18749
| Gazipur 100 MW PP | 35 | 17 | 17 | 17 | 17 | [20 empty] | 0 | 129600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 2 | 3 | 3 | 1 | 0 | 1 | 0 | 1 | 0 | [8 empty] | 17158
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 110 | 110 | 68 | 68 | 68 | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 21 | 108 | 105 | 108 | 110 | 110 | 110 | 1354908
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 237 | 243 | 270 | 274 | 256 | 248 | 268 | 270 | 265 | 275 | 275 | 260 | 275 | 265 | 250 | 250 | 230 | 275 |  | 275 | 240 | 275 | 275 | 300 | 275 | 255 | 6363724
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 35 | [18 empty] | 7 | 17 |  |  |  |  | 0 | 61440
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [25 empty] | 0 | 0
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 19 | 39 | 43 | 43 | 10 | 10 | 10 |  | 10 | 17 | 38 | 43 | 43 | 43 | 43 | 621192
94 | Gagnagar 102 MW PP (Digital Power) | [19 empty] | 5 | 7 |  |  |  |  | 0 | 13824
95 | Patenga 50MW PP (Baraka) | [25 empty] | 0 | 0
96 | Chattogram 108 MW PP (ECPV) |  |  | 1 | 5 | 7 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 48 | 88 | 58 |  | 52 | 70 | 81 | 93 | 97 | 97 | 97 | 851520
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | [25 empty] | 0 | 0
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | [17 empty] | 17 |  | 17 | 55 | 55 | 55 | 55 | 327346
101 | Kushiara 163 MW CCPP (KP)
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 3 | 2 | 2 |  | 0 | [9 empty] | 14450
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 35 | 18 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  |  |  | 54 | 54 | 35 | 54 | 54 | 54 | 54 | 653760
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 193 | 193 | 193 | 194 | 193 | 80 | [7 empty] | 8 | 14 | 24 | 8 | 8 |  | 50 | 194 | 172 | 194 | 197 | 200 | 194 | 2248800
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | [5 empty] | 24 | 24 | 17 | [6 empty] | 4 | 17 |  |  |  | 11 | 17 | 16 | 16 | 26 | 32 | 32 | 246240
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 10 | [17 empty] | 30 | 50 | 50 | 100 | 50 | 50 | 50 | 447360
116 | Chandpur 200MW (Desh energy) | 135 | 140 | 34 | 34 | 34 | [14 empty] | 13 | 34 | 17 | 18 | 51 | 57 | 100 | 730080
117 | Ashuganj 150MW PP (Midland) | 45 | 50 | [9 empty] | 3 | 10 | 10 | 10 | 10 | 10 | 10 |  | 21 | 50 | 50 | 50 | 50 | 50 | 50 | 481745
118 | Bibiyana-III 400 MW CCPP | 401 | 400 | 402 | 400 | 398 | 375 | 352 | 352 | 352 | 381 | 378 | 367 | 372 | 366 | 366 | 366 | 366 | 310 |  | 366 | 366 | 366 | 402 | 400 | 366 | 366 | 8962000
| Jamalpur 115 MW PP (United) | 98 | 107 | 107 | 107 | 107 | 115 | 115 | 85 | 85 | 85 | 85 | 85 | 109 | 115 | 115 | 55 | 35 | 35 |  | 76 | 115 | 115 | 115 | 115 | 108 | 108 | 2313600
| Anwara 300 MW PP (United) | [25 empty] | 0 | 0
| Juldah unit-2 (Acorn) | 80 | [18 empty] | 10 | 10 | 10 | 30 | 30 | 30 | 30 | 246720
| Anlima Energy Ltd. | 116 | 116 | 115 | 116 | 116 | 72 | 53 | 53 | 53 | 53 | 53 | 65 | 114 | 116 | 116 | 35 | 17 | 17 |  | 53 | 116 | 116 | 116 | 116 | 116 | 116 | 2123945
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443160
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 2 | 21 | 6 | 14 | 10 | 12 | 17 | 9 | 26 | 14 | 8 | 4 | [8 empty] | 146810
120 | Eastern Zone Total | 6548 | 6326 | 5843 | 5816 | 5777 | 5245 | 4823 | 4953 | 4949 | 5021 | 5061 | 5196 | 5417 | 5518 | 5538 | 5270 | 5024 | 4816 |  | 5709 | 6518 | 6384 | 6733 | 6803 | 6665 | 6629 | 136711344
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP
| Khulna 225 MW CCPP | [21 empty] | 40 |  |  |  | 0 | 48000
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 53 | 17 | 17 | 17 | [14 empty] | 28 | 105 | 100 | 105 | 105 | 105 | 105 | 801600
130
131
132 | United Payra Power Ltd. | [25 empty] | 0 | 0
133 | Bhola Nutan Biddut BD LTD (GAS) | 220 | 205 | 221 | 220 | 220 | 220 | 220 | 181 | 140 | 140 | 141 | 134 | 141 | 141 | 141 | 141 | 141 | 140 |  | 217 | 210 | 219 | 201 | 202 | 202 | 182 | 4353900
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 85 | 85 | 83 | 84 | 62 | 23 | 12 | 11 | 11 | 11 | 13 | 14 | 13 | 13 | 12 | 12 | 13 | 13 |  | 18 | 38 | 12 | 12 | 13 | 13 | 12 | 719231
| Bhola 225 MW CCPP | [10 empty] | 15 | 60 | 66 | 66 | 65 | 69 | 60 | 68 |  | 65 | 69 | 66 | 66 | 65 | 65 | 61 | 836000
140 | Bhola 33 MW PP (Venture) | 16 | 16 | 13 | 13 | 13 | 14 | 18 | 17 | 20 | 18 | 22 | 22 | 23 | 23 | 21 | 16 | 16 | 20 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 483804
141 | Noapara 100 MW PP (Bangla Trac) | [20 empty] | 100 | 80 | 100 | 100 | 100 | 0 | 479040
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP | [15 empty] | 2 | 2 | [9 empty] | 2048
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 812 | 805 | 790 | 793 | 793 | 793 | 793 | 793 | 794 | 795 | 795 | 795 | 796 | 796 | 795 | 795 | 795 | 781 |  | 781 | 780 | 781 | 781 | 781 | 780 | 781 | 19114909
147 | Bheramara 410 MW CCPP | 405 | 405 | 395 | 250 | 150 | 215 | 220 | 220 | 270 | 315 | 315 | 376 | 372 | 370 | 390 | 380 | 390 | 300 |  | 300 | 300 | 360 | 360 | 350 | 360 | 360 | 8088192
148 | Payra 1320 MW | 300 | 290 | 270 | 270 | 270 | 260 | 270 | 270 | 270 | 270 | 270 | 290 | 300 | 300 | 300 | 270 | 270 | 270 |  | 300 | 400 | 420 | 480 | 470 | 470 | 430 | 8484000
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 155 | 156 | 155 | 155 | 155 | 155 | 153 | 153 | 158 | 156 | 155 | 153 | 154 | 154 | 155 | 154 | 155 | 152 |  | 152 | 152 | 152 | 153 | 151 | 150 | 150 | 3793600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 50 | 50 | 50 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1619000
| Baghabari 50 MW Peaking PP | [19 empty] | 40 | 50 | 50 | 50 | 50 | 50 | 50 | 259088
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 2 | 5 | 5 | 2 | 5 | 5 | 3 | 1 | 0 | 0 | [8 empty] | 33720
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 144 | 121 | 110 | 115 | 90 | 100 | 94 | 92 | 98 | 96 | 95 | 94 | 101 | 95 | 70 | 70 | 70 |  | 75 | 138 | 142 | 142 | 144 | 144 | 144 | 2731500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 167 | 171 | 174 | 175 | 183 | 167 | 172 | 165 | 164 | 173 | 172 | 191 | 178 | 176 | 167 | 159 | 140 | 140 |  | 151 | 185 | 184 | 188 | 172 | 182 | 177 | 4332682
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 183 | 179 | 174 | 172 | 153 | 156 | 167 | 178 | 183 | 184 | 202 | 187 | 185 | 179 | 178 | 176 | 140 |  | 145 | 200 | 207 | 202 | 195 | 186 | 186 | 4576145
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 335 | 335 | 387 | 388 | 388 | 308 | 335 | 333 | 333 | 385 | 388 | 379 | 402 | 405 | 393 | 402 | 315 | 362 |  | 372 | 347 | 391 | 385 | 409 | 402 | 298 | 8886400
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 489840
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 |  | 9 | 11 | 11 | 11 | 11 | 11 | 11 | 246744
165 | Amnura 50 MW PP(Sinha) | 35 | [18 empty] | 35 | 35 | 35 |  |  |  | 35 | 112560
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 22 | 31 | 38 | 22 | 22 | 22 | 22 | 127996
168 | Santahar 50 MW Peaking PP | 26 | 26 | 26 | 26 | 26 | [14 empty] | 15 | 23 | 34 | 35 | 34 | 34 | 12 | 281302
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 447840
170 | Chapainawabganj 100 MW Peaking PP | 47 | 24 | 24 | 24 | 24 | [14 empty] | 36 | 47 | 47 | 47 | 47 | 47 | 47 | 392368
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | [6 empty] | 23 | 90 | 90 | 90 | 90 | 70 |  |  | 1 | 35 | 30 | 39 | 70 | 80 | 94 | 1372128
172 | Confidence Power Bogura Unit-1 113 MW | 75 | 75 | 75 | 75 | 75 | [6 empty] | 25 | 35 | 35 | 35 | 35 |  |  |  | 25 | 35 | 35 | 45 | 50 | 75 | 75 | 858720
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [9 empty] | 0 |  | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 50 | [11 empty] | 35 |  | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 1354377
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 1 | 2 | 4 | 6 | 6 | 7 | 4 | 3 | 3 | 2 | 2 | [8 empty] | 35945
178
178