## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-08-07 | Saturday
|  |  | Date (day): | 2021-08-07 |  | Saturday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14257.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14902 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-08-06 | 2021-08-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 185 | 185 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 0 | 300 | 310 | 310 |  | 55 | Under maint.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 368 | 391 | 390 | 390 |  |  | FGMO
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 341 | 344 | 360 | 360
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 290 | 275 | 285 | 285 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 0 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 30 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 332 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 0 | 85 | 94 | 94 |  | 8 | Engine problem
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 115 | 115 | 150 |  | 16
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 39 | 47 | 49 | 49 |  | 31 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 0 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 11 | 264 | 285 | 285
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 130 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 54 | 92 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 68 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 23 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 2296 | 3308 | 3875 | 4130 | 579 | 815
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 0 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 4 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 118 | 120 | 120 | 110 |  | Low water level
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Machine problem
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 17 | 42 | 10 | 35
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 83 | 83 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 33 | 16 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 70 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1028 | 1070 | 1504 | 1604 | 301 | 484
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 201 | 213 | 215 | 215 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 335 | 310 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 300 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 57 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 16 | 16 | 16 | 179 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 43 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 75 | 150 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 135 | 135 | 137 |  | 26 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 88 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 104 | 128 | 138 | 163
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 43 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 20 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 105 | 109 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 36 | 36 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1706 | 2035 | 2238 | 2365 | 443 | 102
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 200 | 208 | 200 | 200
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 80 | 179 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 79 | 106 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 25 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 435 | 544 | 592.6 | 566 | 0 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 20 | 30 | 30 |  | 60 | GT-3 under S/D
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 159 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 61 | 62 | 62 | 62
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 145 | 140 | 140 |  | 91 | ST Under maint.
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 295 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 387 | 400 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint. |  | 2021-11-08
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1439 | 1463 | 1537 | 1537 | 170 | 661
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 684 | 446 | 696 | 696
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 20 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 155 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 390 | 410 | 380 | 400 | 10
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 45 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1119 | 1236 | 1556 | 1706 | 10 | 83
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 31 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 89 | 88 | 89 | 89 |  | 105 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 12 | 12 | 12 | 83 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 300 | 520 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 221 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 643 | 907 | 1236 | 1236 | 83 | 105
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 28 | 0 | 0 |  | 71 | Under maint
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 35 | 35 |  | 15 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 128 | 122 | 150 | 150 | 60 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 0 | 0 | 0 | 0 | 220 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 190 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 396 | 405 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 42 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 100 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 36 | 94 | 94 | 94 |  | 19 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 95 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 818 | 1348 | 1445 | 1472 | 500 | 155
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 150 | 155 | 153 | 153 | 121 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 70 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 227 | 268 | 274 | 286 | 121 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 9711 | 12179 | 14257.6 | 14902 | 2207 | 2682
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9102.6173 | 11416 | 13364.3782 | 13968.4073
| A. |  | 2021-08-06 | (Yesterday) |  |  |  |  | Friday
| 1 | Highest Generation : |  |  | 12179 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 8983 | MW at | 9:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12179 | MW
| 3 | Day peak Generation : |  |  | 9711 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11416 | MW
| 4 | Evening peak Generation : |  |  | 12179 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 255.125 | MKWHr | By Solar | 0.69912 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 149.6833 | MKWHr |  | By Oil: | 70.7142 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.4921 | MKWHr |  | By Hydro: | 2.7501 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2207 | MW | Dhaka | 3559 | 3559 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2682 | MW | Chittagong | 1092 | 1092 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4889 | MW | Khulna | 1574 | 1574 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1176.83 | MMCFD |  |  | Rajshahi | 1302 | 1302 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 163761065.55 | ii) Oil : | Taka | 490205952.88 | Comilla | 1155 | 1155 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 67506921 | Total | Taka | 721473939.43 | Mymensingh | 1062 | 1062 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 6.167 | MKWHr. | Sylhet | 460 | 460 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -560 | MW (E to W) at | 21:00 | hrs | Barisal | 377 | 377 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -710 | MW at | 19:00 | hrs | Rangpur | 835 | 835 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.4° C |  |  | Total | 11416 | 11416 |  | 0
| B. |  | 2021-08-07 | (Today) |  |  |  | Saturday |  |  | Probable max. temperature in Dhaka |  |  | 31.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12700 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14902 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10200 | MW
| 4 | Reserve(Generation end) |  |  |  | 2202 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 266.0389 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8816 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 14.0895 | MKWHr. | ii) HVDC Flow at Peak Time |  | 446 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6966 | MKWHr. | iii) Maximum HVDC Flow : |  | 684 | MW at | 8:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 86.27 |  | (b) Today: | 86.5 |  | (c) Rule Curve: |  | 90.6
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-08-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 390 | 346 |  | 0 | 240 | 250 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 94 | 133 | 86 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 8 | 0 | 58 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 100 | 95 | 50 | 20 | 40 | 0 | 0 | 80 | 260 | 265 | 213 | 8 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 128 | 203 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 57 | 84 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 253 | 0 | 0 | 176 | 0 | 149 | 0 | 100 | 200 | 150 | 340 | 106 | 105 | 105 | 0 | 33 | 0 | 106 | 105 | 110 | 100 | 0 | 91 | 0 | 144 | 116 | 0 | 36 | 0 |  | 681 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 50 | 26 | 93 | 35 | 0 | 23 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 144 | 0 | 0 | 0 | 12 | 70 | 199 | 0 | 400 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 500 | 219 | 0 | 35 | 0 |  | 8332 | 3713 | 12045 | 4208 | 681 | 2114 | 3766 | 653 | 118 | 377 | 128 | 0 | 0 | 86.24
2:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 375 | 313 |  | 0 | 240 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 94 | 98 | 20 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 90 | 95 | 49 | 20 | 40 | 0 | 0 | 80 | 260 | 265 | 212 | 8 | 137 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 126 | 203 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 57 | 84 | 0 | 150 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 272 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 200 | 150 | 340 | 106 | 0 | 105 | 0 | 33 | 0 | 110 | 114 | 107 | 100 | 0 | 90 | 0 | 144 | 116 | 0 | 36 | 0 |  | 673 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 50 | 26 | 93 | 35 | 0 | 16 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 138 | 0 | 0 | 0 | 12 | 20 | 198 | 0 | 407 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 480 | 219 | 0 | 17 | 0 |  | 8042 | 3589 | 11631 | 4156 | 673 | 2077 | 3534 | 633 | 117 | 315 | 126 | 0 | 0 | 86.25
3:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 371 | 313 |  | 0 | 240 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 8 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 90 | 95 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 265 | 213 | 8 | 138 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 122 | 208 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 159 | 57 | 84 | 0 | 150 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 272 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 150 | 340 | 106 | 0 | 105 | 0 | 33 | 0 | 106 | 20 | 110 | 100 | 0 | 90 | 0 | 144 | 116 | 0 | 36 | 0 |  | 679 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 50 | 26 | 93 | 35 | 0 | 0 | 52 | 32 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 114 | 0 | 0 | 0 | 12 | 0 | 191 | 0 | 404 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 420 | 219 | 0 | 0 | 0 |  | 7767 | 3447 | 11214 | 4126 | 679 | 2084 | 3247 | 573 | 118 | 265 | 122 | 0 | 0 | 86.26
4:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 372 | 313 |  | 0 | 240 | 270 | 0 | 0 | 30 | 300 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 90 | 95 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 265 | 211 | 8 | 136 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 118 | 208 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 57 | 84 | 0 | 150 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 273 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 150 | 340 | 106 | 0 | 105 | 0 | 33 | 0 | 110 | 0 | 109 | 100 | 0 | 90 | 0 | 144 | 116 | 0 | 36 | 0 |  | 679 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 52 | 26 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 116 | 0 | 0 | 0 | 12 | 0 | 192 | 0 | 397 | 105 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 420 | 219 | 0 | 0 | 0 |  | 7679 | 3328 | 11007 | 4128 | 679 | 2079 | 3162 | 573 | 117 | 151 | 118 | 0 | 0 | 86.26
5:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 372 | 312 |  | 0 | 240 | 235 | 0 | 0 | 0 | 300 | 0 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 95 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 265 | 212 | 8 | 134 | 23 | 55 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 25 | 21 | 112 | 208 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 57 | 84 | 0 | 150 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 273 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 200 | 150 | 336 | 106 | 0 | 105 | 0 | 33 | 0 | 110 | 0 | 119 | 100 | 0 | 90 | 0 | 144 | 116 | 0 | 36 | 0 |  | 679 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 117 | 0 | 0 | 0 | 12 | 0 | 190 | 0 | 375 | 35 | 0 | 94 | 0 | 113 | 0 | 0 | 95 | 400 | 186 | 0 | 0 | 0 |  | 7534 | 3066 | 10600 | 4122 | 679 | 2032 | 2949 | 556 | 118 | 32 | 112 | 0 | 0 | 86.27
6:00 | 0 | 0 | 0 | 185 | 0 | 101 | 0 | 334 | 275 |  | 0 | 240 | 270 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 23 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 85 | 0 | 20 | 42 | 0 | 0 | 80 | 260 | 265 | 212 | 8 | 136 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 21 | 11 | 25 | 21 | 104 | 208 | 0 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 57 | 84 | 0 | 150 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 15 | 0 | 0 | 180 | 0 | 149 | 0 | 100 | 136 | 150 | 340 | 106 | 0 | 105 | 0 | 33 | 0 | 110 | 0 | 119 | 100 | 0 | 60 | 1 | 108 | 116 | 0 | 36 | 1 |  | 680 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 93 | 0 | 0 | 0 | 12 | 0 | 154 | 0 | 345 | 35 | 0 | 35 | 0 | 100 | 0 | 0 | 0 | 300 | 219 | 0 | 0 | 0 |  | 6946 | 2648 | 9594 | 3890 | 680 | 1976 | 2368 | 456 | 118 | 0 | 104 | 2 | 0 | 86.27
7:00 | 0 | 0 | 0 | 185 | 0 | 53 | 0 | 332 | 277 |  | 0 | 240 | 275 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 23 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 85 | 0 | 20 | 36 | 0 | 0 | 80 | 275 | 285 | 213 | 8 | 137 | 23 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 98 | 208 | 0 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 61 | 84 | 0 | 100 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 130 | 0 | 149 | 0 | 100 | 51 | 10 | 396 | 115 | 0 | 105 | 1 | 33 | 0 | 110 | 0 | 119 | 100 | 0 | 54 | 13 | 35 | 116 | 0 | 36 | 2 |  | 679 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 98 | 0 | 0 | 0 | 12 | 0 | 167 | 0 | 353 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 300 | 221 | 0 | 0 | 1 |  | 6563 | 2553 | 9116 | 3936 | 679 | 1917 | 1894 | 455 | 120 | 0 | 98 | 17 | 0 | 86.28
8:00 | 0 | 0 | 0 | 185 | 0 | 52 | 0 | 332 | 277 |  | 0 | 240 | 285 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 13 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 82 | 0 | 20 | 30 | 0 | 0 | 80 | 285 | 280 | 189 | 8 | 138 | 23 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 19 | 92 | 205 | 0 | 19 | 1 | 43 | 30 | 50 | 0 | 163 | 160 | 63 | 84 | 0 | 100 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 138 | 0 | 100 | 17 | 10 | 402 | 115 | 0 | 105 | 2 | 33 | 0 | 110 | 0 | 115 | 100 | 0 | 53 | 27 | 35 | 116 | 0 | 36 | 9 |  | 684 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 95 | 0 | 0 | 0 | 12 | 0 | 176 | 0 | 354 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 223 | 0 | 0 | 2 |  | 6471 | 2547 | 9018 | 3933 | 684 | 1910 | 1784 | 453 | 121 | 0 | 92 | 41 | 0 | 0
9:00 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 331 | 277 |  | 0 | 240 | 280 | 0 | 0 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 13 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 82 | 0 | 20 | 28 | 0 | 0 | 80 | 290 | 285 | 212 | 8 | 137 | 23 | 55 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 19 | 92 | 203 | 0 | 19 | 1 | 43 | 30 | 50 | 0 | 163 | 159 | 63 | 84 | 0 | 100 | 0 | 0 | 10 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 130 | 0 | 100 | 17 | 10 | 402 | 115 | 0 | 105 | 3 | 33 | 0 | 110 | 0 | 115 | 100 | 0 | 53 | 32 | 35 | 116 | 0 | 36 | 0 |  | 684 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 98 | 0 | 0 | 0 | 11 | 0 | 180 | 0 | 352 | 0 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 300 | 221 | 0 | 0 | 4 |  | 6429 | 2554 | 8983 | 3968 | 684 | 1852 | 1771 | 455 | 121 | 0 | 92 | 40 | 0 | 0
10:00 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 350 | 349 |  | 0 | 240 | 260 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 16 | 25 | 18 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 82 | 0 | 18 | 13 | 0 | 0 | 80 | 275 | 300 | 183 | 8 | 138 | 23 | 52 | 0 | 10 | 0 | 0 | 0 | 22 | 11 | 25 | 19 | 96 | 204 | 0 | 19 | 2 | 43 | 0 | 50 | 0 | 163 | 158 | 63 | 81 | 0 | 120 | 0 | 0 | 9 | 305 | 24 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 130 | 0 | 100 | 23 | 15 | 402 | 88 | 0 | 105 | 3 | 33 | 0 | 110 | 0 | 117 | 100 | 0 | 53 | 25 | 35 | 116 | 0 | 36 | 29 |  | 684 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 154 | 0 | 0 | 117 | 0 | 0 | 0 | 12 | 0 | 179 | 0 | 373 | 10 | 0 | 1 | 0 | 65 | 0 | 1 | 0 | 300 | 221 | 0 | 0 | 4 |  | 6491 | 2683 | 9174 | 4046 | 684 | 1930 | 1779 | 454 | 121 | 0 | 96 | 64 | 0 | 0
11:00 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 368 | 344 |  | 0 | 240 | 285 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 18 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 83 | 0 | 18 | 13 | 0 | 0 | 80 | 305 | 330 | 197 | 8 | 138 | 23 | 52 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 18 | 92 | 203 | 6 | 19 | 2 | 43 | 0 | 50 | 0 | 163 | 158 | 61 | 81 | 0 | 145 | 0 | 0 | 9 | 300 | 24 | 5 | 0 | 0 | 0 | 0 | 80 | 0 | 130 | 1 | 100 | 50 | 38 | 402 | 88 | 0 | 105 | 5 | 33 | 0 | 110 | 0 | 110 | 100 | 0 | 53 | 57 | 35 | 116 | 0 | 36 | 36 |  | 683 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 122 | 0 | 0 | 0 | 11 | 0 | 177 | 0 | 400 | 17 | 0 | 30 | 0 | 70 | 0 | 7 | 0 | 300 | 220 | 0 | 0 | 4 |  | 6724 | 2750 | 9474 | 4161 | 683 | 1962 | 1893 | 450 | 121 | 0 | 92 | 112 | 0 | 0
12:00 | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 368 | 341 |  | 0 | 240 | 290 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 14 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 83 | 0 | 18 | 17 | 0 | 0 | 80 | 335 | 345 | 201 | 8 | 138 | 23 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 16 | 104 | 200 | 8 | 19 | 1 | 43 | 0 | 50 | 0 | 163 | 157 | 61 | 84 | 0 | 145 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 11 | 0 | 0 | 80 | 0 | 130 | 4 | 100 | 88 | 75 | 387 | 79 | 0 | 105 | 4 | 33 | 0 | 110 | 0 | 105 | 100 | 0 | 54 | 25 | 68 | 116 | 0 | 36 | 23 |  | 684 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 128 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 396 | 45 | 0 | 36 | 0 | 70 | 0 | 7 | 0 | 300 | 218 | 0 | 0 | 4 |  | 6904 | 2807 | 9711 | 4258 | 684 | 1988 | 2041 | 450 | 118 | 0 | 104 | 68 | 0 | 0
13:00 | 0 | 0 | 0 | 185 | 35 | 0 | 0 | 391 | 340 |  | 0 | 240 | 285 | 0 | 0 | 7 | 324 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 10 | 25 | 33 | 0 | 0 | 56 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 76 | 0 | 18 | 27 | 0 | 0 | 80 | 305 | 300 | 183 | 8 | 135 | 23 | 51 | 0 | 43 | 0 | 0 | 4 | 22 | 0 | 25 | 16 | 110 | 183 | 8 | 19 | 3 | 44 | 0 | 53 | 0 | 163 | 157 | 61 | 84 | 0 | 138 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 69 | 0 | 0 | 120 | 0 | 138 | 4 | 100 | 137 | 143 | 404 | 79 | 0 | 105 | 1 | 69 | 0 | 110 | 21 | 111 | 100 | 0 | 80 | 54 | 90 | 116 | 0 | 36 | 25 |  | 517 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 8 | 0 | 0 | 152 | 0 | 0 | 126 | 0 | 0 | 0 | 10 | 0 | 189 | 0 | 403 | 80 | 0 | 72 | 0 | 78 | 0 | 7 | 20 | 350 | 218 | 0 | 0 | 5 |  | 7286 | 2775 | 10061 | 4177 | 517 | 2004 | 2536 | 502 | 116 | 0 | 110 | 99 | 0 | 0
14:00 | 0 | 0 | 0 | 185 | 35 | 0 | 0 | 379 | 323 |  | 0 | 240 | 280 | 0 | 0 | 30 | 322 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 10 | 25 | 33 | 0 | 0 | 55 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 76 | 0 | 18 | 30 | 0 | 0 | 80 | 290 | 300 | 181 | 8 | 137 | 23 | 49 | 0 | 43 | 0 | 0 | 16 | 22 | 0 | 25 | 18 | 110 | 200 | 8 | 19 | 1 | 43 | 0 | 53 | 0 | 110 | 156 | 60 | 82 | 0 | 138 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 168 | 0 | 0 | 150 | 0 | 149 | 1 | 100 | 195 | 148 | 353 | 79 | 0 | 105 | 0 | 33 | 0 | 110 | 34 | 108 | 100 | 0 | 91 | 47 | 90 | 116 | 0 | 36 | 31 |  | 446 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 112 | 0 | 0 | 0 | 10 | 0 | 188 | 0 | 348 | 105 | 0 | 94 | 0 | 90 | 0 | 5 | 35 | 360 | 218 | 0 | 0 | 4 |  | 7354 | 2716 | 10070 | 4103 | 446 | 1848 | 2848 | 511 | 115 | 0 | 110 | 89 | 0 | 86.29
15:00 | 0 | 0 | 0 | 185 | 35 | 0 | 0 | 364 | 338 |  | 0 | 240 | 285 | 0 | 0 | 30 | 318 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 14 | 25 | 33 | 0 | 0 | 53 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 76 | 0 | 18 | 20 | 0 | 0 | 80 | 310 | 315 | 192 | 8 | 138 | 23 | 48 | 0 | 43 | 0 | 0 | 28 | 22 | 0 | 25 | 20 | 114 | 198 | 8 | 19 | 2 | 44 | 0 | 53 | 0 | 163 | 154 | 60 | 81 | 0 | 140 | 0 | 0 | 10 | 310 | 24 | 8 | 0 | 195 | 0 | 0 | 158 | 0 | 149 | 1 | 100 | 199 | 150 | 403 | 78 | 0 | 105 | 1 | 33 | 0 | 110 | 34 | 108 | 100 | 0 | 91 | 39 | 90 | 116 | 0 | 35 | 26 |  | 447 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 124 | 0 | 0 | 0 | 11 | 0 | 188 | 0 | 347 | 105 | 0 | 94 | 0 | 92 | 0 | 5 | 35 | 390 | 216 | 0 | 0 | 3 |  | 7570 | 2779 | 10349 | 4198 | 447 | 1933 | 2926 | 541 | 113 | 0 | 114 | 77 | 0 | 86.3
16:00 | 0 | 0 | 0 | 185 | 35 | 0 | 0 | 363 | 343 |  | 0 | 240 | 250 | 0 | 0 | 15 | 320 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 16 | 25 | 33 | 0 | 0 | 54 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 77 | 0 | 20 | 24 | 0 | 0 | 110 | 290 | 300 | 180 | 16 | 136 | 23 | 48 | 0 | 43 | 0 | 0 | 43 | 22 | 0 | 25 | 20 | 108 | 200 | 8 | 19 | 1 | 44 | 0 | 52 | 0 | 163 | 156 | 62 | 81 | 0 | 140 | 0 | 0 | 10 | 280 | 24 | 8 | 0 | 195 | 0 | 0 | 170 | 0 | 149 | 2 | 100 | 200 | 150 | 391 | 78 | 0 | 105 | 1 | 33 | 0 | 110 | 17 | 108 | 100 | 0 | 90 | 31 | 90 | 116 | 0 | 35 | 13 |  | 446 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 19 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 123 | 0 | 0 | 0 | 11 | 0 | 187 | 0 | 298 | 105 | 0 | 35 | 0 | 113 | 0 | 4 | 0 | 390 | 217 | 0 | 0 | 3 |  | 7406 | 2638 | 10044 | 4156 | 446 | 1870 | 2749 | 542 | 114 | 4 | 108 | 55 | 0 | 86.3
17:00 | 0 | 0 | 0 | 185 | 65 | 0 | 0 | 362 | 338 |  | 0 | 240 | 280 | 0 | 0 | 15 | 321 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 16 | 25 | 33 | 0 | 0 | 54 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 83 | 0 | 20 | 25 | 0 | 0 | 110 | 295 | 310 | 181 | 16 | 138 | 23 | 50 | 0 | 43 | 0 | 0 | 12 | 22 | 0 | 25 | 20 | 100 | 200 | 8 | 19 | 0 | 44 | 0 | 53 | 0 | 163 | 158 | 63 | 84 | 0 | 140 | 0 | 0 | 10 | 285 | 24 | 8 | 0 | 130 | 0 | 0 | 70 | 0 | 143 | 0 | 70 | 100 | 150 | 393 | 78 | 0 | 68 | 0 | 16 | 0 | 68 | 17 | 75 | 50 | 0 | 53 | 9 | 35 | 116 | 0 | 17 | 11 |  | 446 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 114 | 0 | 0 | 0 | 12 | 0 | 177 | 0 | 345 | 35 | 0 | 35 | 0 | 39 | 0 | 2 | 0 | 370 | 215 | 0 | 0 | 2 |  | 6732 | 2449 | 9181 | 4190 | 446 | 1920 | 1863 | 522 | 114 | 2 | 100 | 24 | 0 | 86.31
18:00 | 0 | 0 | 0 | 185 | 105 | 0 | 0 | 362 | 301 |  | 0 | 240 | 285 | 0 | 0 | 15 | 326 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 16 | 25 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 89 | 0 | 20 | 42 | 0 | 0 | 110 | 290 | 320 | 191 | 16 | 138 | 23 | 57 | 0 | 43 | 0 | 0 | 8 | 22 | 0 | 25 | 20 | 96 | 200 | 8 | 19 | 0 | 44 | 0 | 14 | 0 | 163 | 159 | 40 | 40 | 0 | 140 | 0 | 0 | 10 | 290 | 24 | 0 | 0 | 130 | 0 | 0 | 70 | 0 | 121 | 0 | 30 | 100 | 150 | 352 | 78 | 0 | 51 | 0 | 16 | 0 | 68 | 17 | 35 | 30 | 0 | 17 | 1 | 35 | 116 | 0 | 17 | 2 |  | 446 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 20 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 104 | 0 | 0 | 0 | 13 | 0 | 171 | 0 | 353 | 35 | 0 | 35 | 0 | 35 | 0 | 1 | 0 | 370 | 150 | 0 | 0 | 0 |  | 6444 | 2392 | 8836 | 4178 | 446 | 1777 | 1691 | 520 | 117 | 7 | 96 | 4 | 0 | 86.32
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 185 | 170 | 0 | 0 | 367 | 326 |  | 0 | 240 | 285 | 0 | 0 | 20 | 328 | 0 | 0 | 0 | 48 | 110 | 28 | 0 | 0 | 0 | 54 | 55 | 40 | 12 | 25 | 16 | 25 | 33 | 4 | 0 | 57 | 60 | 100 | 120 | 10 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 30 | 89 | 14 | 20 | 42 | 0 | 0 | 110 | 295 | 310 | 209 | 16 | 138 | 23 | 57 | 0 | 43 | 0 | 50 | 12 | 22 | 11 | 28 | 20 | 126 | 200 | 8 | 19 | 0 | 44 | 20 | 19 | 0 | 163 | 158 | 61 | 65 | 0 | 145 | 0 | 0 | 10 | 295 | 24 | 0 | 0 | 200 | 0 | 0 | 108 | 0 | 131 | 0 | 60 | 130 | 150 | 374 | 78 | 30 | 70 | 0 | 49 | 0 | 85 | 30 | 47 | 50 | 0 | 35 | 0 | 82 | 116 | 0 | 31 | 0 |  | 446 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 50 | 5 | 78 | 35 | 0 | 26 | 10 | 29 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 97 | 0 | 0 | 0 | 12 | 2 | 168 | 0 | 400 | 80 | 50 | 50 | 0 | 96 | 0 | 0 | 50 | 400 | 194 | 0 | 16 | 0 |  | 7545 | 2986 | 10531 | 4345 | 446 | 1934 | 2592 | 551 | 117 | 420 | 126 | 0 | 0 | 86.35
19:30 | 0 | 0 | 0 | 185 | 180 | 0 | 0 | 356 | 344 |  | 0 | 240 | 235 | 0 | 0 | 55 | 282 | 0 | 0 | 0 | 94 | 150 | 74 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 16 | 25 | 33 | 8 | 0 | 57 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 89 | 50 | 20 | 42 | 0 | 0 | 95 | 260 | 300 | 211 | 16 | 135 | 23 | 57 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 31 | 20 | 124 | 205 | 8 | 19 | 0 | 43 | 20 | 52 | 0 | 110 | 159 | 40 | 80 | 0 | 100 | 0 | 0 | 10 | 260 | 24 | 0 | 0 | 264 | 0 | 0 | 180 | 0 | 149 | 0 | 76 | 200 | 150 | 351 | 78 | 35 | 105 | 0 | 16 | 0 | 110 | 114 | 106 | 50 | 0 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 446 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 50 | 17 | 94 | 35 | 0 | 30 | 10 | 32 | 21 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 130 | 0 | 0 | 0 | 12 | 100 | 200 | 0 | 417 | 105 | 180 | 60 | 0 | 97 | 0 | 0 | 90 | 480 | 206 | 0 | 35 | 0 |  | 8091 | 3562 | 11653 | 4269 | 446 | 1941 | 3627 | 632 | 117 | 497 | 124 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 185 | 210 | 0 | 0 | 367 | 345 |  | 0 | 240 | 285 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 94 | 115 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 22 | 25 | 33 | 0 | 0 | 56 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 10 | 82 | 18 | 20 | 42 | 0 | 0 | 80 | 275 | 320 | 212 | 16 | 137 | 23 | 57 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 31 | 20 | 124 | 204 | 8 | 19 | 0 | 43 | 20 | 52 | 0 | 110 | 160 | 40 | 84 | 0 | 100 | 0 | 0 | 10 | 265 | 24 | 0 | 0 | 263 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 200 | 150 | 373 | 105 | 0 | 105 | 0 | 16 | 0 | 110 | 114 | 105 | 50 | 0 | 91 | 0 | 162 | 116 | 0 | 36 | 0 |  | 446 | 0 | 410 | 0 | 0 | 60 | 0 | 0 | 20 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 50 | 35 | 94 | 35 | 0 | 31 | 30 | 32 | 21 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 133 | 0 | 0 | 0 | 12 | 95 | 206 | 0 | 400 | 105 | 100 | 78 | 0 | 113 | 0 | 0 | 95 | 490 | 222 | 0 | 35 | 0 |  | 8075 | 3632 | 11707 | 4369 | 446 | 1951 | 3570 | 643 | 116 | 488 | 124 | 0 | 0 | 86.34
21:00 | 0 | 0 | 0 | 185 | 300 | 0 | 0 | 391 | 344 |  | 0 | 240 | 275 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 85 | 115 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 22 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 83 | 19 | 20 | 42 | 0 | 0 | 80 | 310 | 300 | 213 | 16 | 135 | 23 | 57 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 20 | 128 | 208 | 8 | 19 | 0 | 43 | 20 | 50 | 0 | 163 | 159 | 62 | 84 | 0 | 145 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 264 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 200 | 150 | 400 | 106 | 0 | 105 | 0 | 16 | 0 | 110 | 114 | 109 | 70 | 0 | 92 | 0 | 162 | 116 | 0 | 36 | 0 |  | 446 | 0 | 410 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 50 | 28 | 94 | 35 | 0 | 30 | 42 | 31 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 122 | 0 | 0 | 0 | 12 | 100 | 190 | 0 | 405 | 105 | 100 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 35 | 0 |  | 8420 | 3759 | 12179 | 4621 | 446 | 2034 | 3583 | 675 | 118 | 574 | 128 | 0 | 0 | 86.35
22:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 395 | 345 |  | 0 | 240 | 270 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 22 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 0 | 84 | 0 | 20 | 42 | 0 | 0 | 80 | 310 | 300 | 214 | 16 | 135 | 0 | 54 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 15 | 21 | 130 | 212 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 161 | 61 | 84 | 0 | 145 | 0 | 0 | 10 | 285 | 24 | 0 | 0 | 264 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 200 | 150 | 400 | 106 | 0 | 105 | 0 | 16 | 0 | 110 | 70 | 108 | 100 | 0 | 93 | 0 | 162 | 116 | 0 | 36 | 0 |  | 682 | 0 | 370 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 50 | 28 | 94 | 35 | 0 | 30 | 52 | 31 | 21 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 132 | 0 | 0 | 0 | 12 | 100 | 186 | 0 | 393 | 105 | 0 | 94 | 0 | 0 | 0 | 0 | 95 | 530 | 221 | 0 | 35 | 0 |  | 8294 | 3754 | 12048 | 4580 | 682 | 2012 | 3322 | 681 | 118 | 523 | 130 | 0 | 0 | 86.36
23:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 395 | 343 |  | 0 | 240 | 285 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 27 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 87 | 0 | 20 | 42 | 0 | 0 | 80 | 325 | 320 | 213 | 16 | 137 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 21 | 128 | 210 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 161 | 61 | 84 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 3 | 0 | 260 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 200 | 150 | 400 | 107 | 0 | 105 | 0 | 49 | 0 | 110 | 70 | 109 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 531 | 0 | 365 | 0 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 50 | 27 | 94 | 35 | 0 | 30 | 52 | 31 | 21 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 131 | 0 | 0 | 0 | 12 | 100 | 195 | 0 | 408 | 105 | 0 | 94 | 0 | 0 | 0 | 0 | 95 | 540 | 221 | 0 | 35 | 0 |  | 8406 | 3632 | 12038 | 4655 | 531 | 2030 | 3376 | 692 | 118 | 508 | 128 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 395 | 345 |  | 0 | 240 | 280 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 94 | 64 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 27 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 34 | 0 | 96 | 0 | 20 | 42 | 0 | 0 | 80 | 310 | 305 | 212 | 16 | 137 | 23 | 56 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 126 | 208 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 61 | 84 | 0 | 145 | 0 | 0 | 9 | 300 | 24 | 8 | 0 | 265 | 0 | 0 | 181 | 0 | 149 | 0 | 100 | 200 | 150 | 388 | 115 | 0 | 105 | 0 | 65 | 0 | 110 | 88 | 110 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 446 | 0 | 355 | 0 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 50 | 27 | 94 | 35 | 0 | 30 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 144 | 0 | 0 | 0 | 12 | 100 | 202 | 0 | 408 | 105 | 0 | 94 | 0 | 54 | 0 | 0 | 95 | 550 | 220 | 0 | 35 | 0 |  | 8436 | 3622 | 12058 | 4636 | 446 | 2040 | 3480 | 704 | 118 | 508 | 126 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 4473000 | 1736009 | 749590 | 0 | 8960000 | 7742000 |  | 0 | 5641750 | 6571811 | 0 | 0 | 661535 | 7341603 | 0 | 0 | 0 | 886140 | 944160 | 249681 | 0 | 0 | 0 | 1246680 | 1242511 | 981227 | 345096 | 600000 | 435600 | 642300 | 828100 | 53760 | 0 | 1286110 | 1464000 | 2400000 | 2900000 | 53915 | 0 | 0 | 0 | 0 |  | 588240 | 0 | 272554 | 606000 | 2063040 | 184800 | 458928 | 773760 | 0 | 0 | 2043672 | 7279400 | 7191000 | 4890000 | 284363 | 3277330 | 509544 | 1293120 | 0 | 920660 | 0 | 49264 | 580814 | 510120 | 193680 | 593100 | 489200 | 2696640 | 4783600 | 152640 | 425124 | 14500 | 1030000 | 708000 | 1152600 | 0 | 3780573 | 3673000 | 1378752 | 1920960 | 0 | 3243100 | 0 | 0 | 252000 | 7187500 | 567984 | 112656 | 0 | 3976908 | 0 | 0 | 3432000 | 0 | 3468816 | 13365 | 2280000 | 3535200 | 2959054 | 9045000 | 2287200 | 230400 | 2478971 | 22080 | 777818 | 0 | 2667152 | 921120 | 2541840 | 2200320 | 0 | 1769280 | 327540 | 2491200 | 2801400 | 0 | 855720 | 239867 |  | 14089455 | 0 | 9167616 | 0 | 0 | 598179 | 0 | 0 | 150720 | 0 | 0 | 2136070 | 636778 | 0 | 0 | 0 | 0 | 423200 | 228035 | 884600 | 334210 | 0 | 176330 | 1117920 | 297010 | 489120 | 0 | 253170 | 0 | 0 | 3773400 | 0 | 0 | 2967700 | 0 | 0 | 0 | 283301 | 644160 | 4733100 | 0 | 9099636 | 1648320 | 342930 | 1591296 | 0 | 1813142 | 0 | 41446 | 1108224 | 10718700 | 5153045 | 0 | 292800 | 40320 |  | 179891047 | 75233933 | 255124980 | 102322554 | 14089455 | 47360756 | 66690195 | 14492100 | 2750110 | 4024052 | 2696640 | 699118 | 0
Fuel Cost | 0 | 0 | 0 | 6575310 | 1926969.99 | 989458.8 | 0 | 9049600 | 7974260 |  | 0 | 6149507.5 | 7294710.21 | 0 | 0 | 5596586.1 | 7635267.12 | 0 | 0 | 0 | 8081596.8 | 9290534.4 | 2302058.82 | 0 | 0 | 0 | 9100764 | 9604610.03 | 9674898.22 | 258822 | 450000 | 0 | 0 | 0 | 519859.2 | 0 | 347249.7 | 395280 | 4344000 | 5249000 | 500870.35 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2643773.8 | 5787300 | 17948448 | 1463616 | 578249.28 | 2298067.2 | 0 | 0 | 3004197.84 | 5386756 | 7191000 | 4498800 | 366828.27 | 3768929.5 | 575784.72 | 1810368 | 0 | 1574328.6 | 0 | 497566.4 | 5546773.7 | 647852.4 | 145260 | 1037925 | 366900 | 20224800 | 5070616 | 1385971.2 | 539907.48 | 231130 | 1689200 | 1132800 | 2051628 | 0 | 4309853.22 | 3819920 | 2716141.44 | 3669033.6 | 0 | 5610563 | 0 | 0 | 514080 | 7259375 | 425988 | 85618.56 | 0 | 30065424.48 | 0 | 0 | 17846400 | 0 | 34133149.44 | 156236.85 | 18582000 | 38356920 | 20861330.7 | 8411850 | 20859264 | 2177280 | 21591837.41 | 0 | 5880304.08 | 0 | 23444266.08 | 9192777.6 | 21783568.8 | 14654131.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 81155260.8 | 0 | 9625996.8 | 0 | 0 | 8290760.94 | 0 | 0 | 1581052.8 | 0 | 0 | 2413759.1 | 987005.9 | 0 | 0 | 0 | 0 | 4164288 | 2316835.6 | 7828710 | 2573417 | 0 | 1708637.7 | 10832644.8 | 2880997 | 939110.4 | 0 | 191649.69 | 0 | 0 | 20451828 | 0 | 0 | 3472209 | 0 | 0 | 0 | 424951.5 | 10957161.6 | 5537727 | 0 | 9008639.64 | 17208460.8 | 5833239.3 | 15101399.04 | 0 | 14069981.92 | 0 | 457978.3 | 8189775.36 | 47055093 | 0 | 0 | 0 | 0 |  | 529183304.09 | 295258570.99 | 824441875.08 | 113434569.92 | 81155260.8 | 50326495.63 | 449002796.24 | 67506921 | 742529.7 | 41203156.64 | 20224800 | 845345.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 185 | 0 | 0 | 0 | 368 | 341 |  | 0 | 240 | 290 | 0 | 0 | 0 | 325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 14 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 83 | 0 | 18 | 17 | 0 | 0 | 80 | 335 | 345 | 201 | 8 | 138 | 23 | 51 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 25 | 16 | 104 | 200 | 8 | 19 | 1 | 43 | 0 | 50 | 0 | 163 | 157 | 61 | 84 | 0 | 145 | 0 | 0 | 10 | 310 | 24 | 5 | 0 | 11 | 0 | 0 | 80 | 0 | 130 | 4 | 100 | 88 | 75 | 387 | 79 | 0 | 105 | 4 | 33 | 0 | 110 | 0 | 105 | 100 | 0 | 54 | 25 | 68 | 116 | 0 | 36 | 23 |  | 684 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 128 | 0 | 0 | 0 | 11 | 0 | 173 | 0 | 396 | 45 | 0 | 36 | 0 | 70 | 0 | 7 | 0 | 300 | 218 | 0 | 0 | 4 |  | 9711 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 185 | 300 | 0 | 0 | 391 | 344 | 0 | 0 | 240 | 275 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 85 | 115 | 30 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 22 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 0 | 83 | 19 | 20 | 42 | 0 | 0 | 80 | 310 | 300 | 213 | 16 | 135 | 23 | 57 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 25 | 20 | 128 | 208 | 8 | 19 | 0 | 43 | 20 | 50 | 0 | 163 | 159 | 62 | 84 | 0 | 145 | 0 | 0 | 10 | 295 | 24 | 8 | 0 | 264 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 200 | 150 | 400 | 106 | 0 | 105 | 0 | 16 | 0 | 110 | 114 | 109 | 70 | 0 | 92 | 0 | 162 | 116 | 0 | 36 | 0 |  | 446 | 0 | 410 | 0 | 0 | 155 | 0 | 0 | 20 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 50 | 28 | 94 | 35 | 0 | 30 | 42 | 31 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 122 | 0 | 0 | 0 | 12 | 100 | 190 | 0 | 405 | 105 | 100 | 94 | 0 | 113 | 0 | 0 | 95 | 520 | 221 | 0 | 35 | 0 |  | 12179 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 390 | 360 | 0 | 0 | 240 | 285 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 94 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 24 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 21 | 35 | 0 | 0 | 80 | 330 | 330 | 215 | 16 | 137 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 163 | 200 | 8 | 21 | 0 | 43 | 30 | 51 | 0 | 163 | 160 | 62 | 84 | 0 | 140 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 285 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 696 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 20 | 60 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 35 | 0 | 35 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 153 | 10 | 10 | 150 | 0 | 0 | 0 | 12 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 390 | 360 | 0 | 0 | 240 | 285 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 94 | 115 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 24 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 21 | 10 | 0 | 0 | 80 | 330 | 330 | 215 | 16 | 135 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 138 | 200 | 8 | 21 | 1.6 | 43 | 30 | 51 | 0 | 163 | 160 | 62 | 84 | 0 | 140 | 18 | 0 | 10 | 341 | 24 | 11 | 100 | 285 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 150 | 400 | 115 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 0 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 696 | 0 | 380 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 35 | 0 | 35 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 150 | 0 | 0 | 0 | 12 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 332 | 287 | 0 | 0 | 240 | 280 | 0 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 0 | 0 | 25 | 24 | 25 |  | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 20 | 5 | 0 | 0 | 80 | 290 | 285 | 193 | 16 | 137 | 20 | 56 | 0 | 10 | 0 | 0 | 0 | 21 | 11 | 33 | 21 | 96 | 212 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 110 | 160 | 61 | 84 | 0 | 120 | 0 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 77 | 0 | 100 | 329 | 45 | 0 | 105 | 2 | 0 | 0 | 110 | 0 | 85 | 80 | 0 | 0 | 7 | 0 | 116 | 0 | 36 | 2 | 0 | 450 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 0 | 0 | 152 | 0 | 0 | 121 | 0 | 0 | 0 | 11 | 0 | 116 | 0 | 418 | 53 | 0 | 50 | 0 | 113 | 0 | 3 | 0 | 370 | 221 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 8983 | 9:00
| Highest Generation |  | 12179 | 21:00
| Day Peak Generation |  | 9711 | 12:00
| Evening Peak Generation |  | 12179 | 21:00
| HVDC Max Flow |  | 684 | 8:00
| HVDC EvPeak Flow |  | 446 | 21:00
| Load factor L.F |  | 87.28%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-08-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-08-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9711 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 8816 | MW
Evening Peak Generation : |  | 12179 | MW Hour : | 21:00 | Available Max Generation : |  | 14902 | MW
E.P. Demand (at gen end) : |  | 12179 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 12700 | MW
Maximum Generation : |  | 12179 | MW Hour : | 21:00 | Reserve(Generation end) |  | 2202 | MW
Total Gen. (MKWH) : |  | 255.125 | System Load Factor : | 87.28% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -710 | MW at | 19:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-08-07
Actual : | 86.5 | Ft.(MSL) , | Rule curve : | 90.6 | Ft.( MSL )
Gas Consumed : | Total = | 1176.83 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 163761065.55
: |  | Coal : | 67506921 | Oil : | 490205952.88 | Total : | 721473939.43
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4427.5661 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1509.0948 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1352.7185 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1222.5153 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1104.6481 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 891.4207 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 493.9639 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 229.3984 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 687.5293 |  |  | 0 | 115672%
Total | 0 |  | 11918.8552 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4,7
3) Ashuganj-4
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Tongi 132/33 kV T-3 transformer was shut down at 09:42 for D/W.
b) Gallamari 132/33 kV T-2 transformer was under shut down from 11:56 to 12:56 due to red hot |  |  |  |  | About 10 MW power interruption occurred under Gallamari S/S
maintenance at 33 kV Bus isolator of city main feeder. |  |  |  |  | area from 11:56 to 12:56.
c) Hathazari-Baroirhat 132 kV Ckt-1 tripped at 10:37 showing Dist. C-phase relay at Hathazari end and
was switched on at 10:50.
d) Ghorasal unit-7 GT was synchronized at 12:11.
e) Rampura-Gulshan 132 kV Ckt-1 tripped at 15:46 showing Diff, Dist. Y-phase relay & LA burst at
Rampura end and was switched on at 21:06.
f) Fenchuganj unit-3 was synchronized at 18:22.
g) Ghorasal unit-7 ST was synchronized at 16:13.
h) Rangpur Confidence 113 MW tripped at 21:38 showing O/V, O/F relay.
i) Hathazari-Madunaghat 132 kV Ckt-1 tripped at 03:23(07-08-2021) showing Dist.Z1 R-phase relay at
Hathazari end and was switched on at 04:01(07-08-2021)
j) Khulshi-Halishahar 132 kV Ckt-1 tripped at 03:09(07-08-2021) showing Dist.Z1 R,Y-phase relay at Khulshi
end & Dist.Z1, A B C relay at Halishahar end and was switched on at 04:12(07-08-2021)
k) Khulshi-Halishahar 132 kV Ckt-2 tripped at 03:28(07-08-2021) showing Dist. Z2 relay at Khulshi end &
Dist.Z1, C-phase relay at Halishahar end and was switched on at 04:21(07-08-2021)
l) Palashbari-Mohosthnghar 132 kV Ckt-1 tripped at 05:35(07-08-2021) showing Dist. A-phase relay at
Polashbari end.
m) Palashbari-Mohosthnghar 132 kV Ckt-2 tripped at 05:35(07-08-2021) showing Dist. Z1 A B C-phase
,E/F relay at Palashbari end & Dist. Z1 A-phase relay at Mahasthangar end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-08-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 185 | 4473000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 1736009
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 749590 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 391 | 8960000 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 344 | 7742000
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5641750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 275 | 6571811 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 661535
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 30 | 249681 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 345096
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7341603
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 85 | 886140 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1246680
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 115 | 944160 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1242511
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 981227
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1035600 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 642300 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 828100
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 0 | 53760 | Reserve.
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 264 | 3976908 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3468816
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 0 | 230400 | Reserve.
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 92 | 1769280 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2491200
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 239867
| Dhaka area Total |  |  |  | 5819 | 3308 | 64509024
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 0 | 53915 | Reserve.
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 13365
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 184800 | High voltage
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 118 | 2750110 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Machine problem
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2478971
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 272554 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 0 | 606000 | High voltage
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2280000
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 458928
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 42 | 773760
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 83 | 2063040 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22080
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 777818 | Transformer O/L
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer O/L
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2667152
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 70 | 2200320 | High voltage
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2801400
| Chattogram area Total |  |  |  | 2382 | 1070 | 25704213
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 2043672 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 213 | 4890000
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 310 | 7279400 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 7191000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 509544 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 57 | 1293120
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 16 | 284363 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 920660 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 2959054
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 49264 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3277330 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 3535200
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 510120
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 193680
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 2696640
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 593100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 580814 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 489200 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 921120
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 109 | 2541840
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 36 | 855720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2035 | 43614841
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 208 | 4783600
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 425124
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 152640 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14500
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 179 | 3432000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 2287200 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 327540
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 588240
| Mymensingh Area Total |  |  |  | 709 | 544 | 12010844
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1030000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 20 | 708000 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3780573
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 159 | 3673000 | Machine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1152600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 112656 | Machine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 62 | 1378752
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1920960
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 3243100 | ST Under maint.
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 567984
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 295 | 7187500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 400 | 9045000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 252000
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1463 | 34052125
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 446 | 14089455
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 20 | 150720 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 155 | 598179
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9167616
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 644160
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1648320
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1236 | 26298450
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 31 | 636778
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2136070 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 12 | 283301 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 10718700
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 5153045
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 292800 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 907 | 19220694
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 423200
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 28 | 228035 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 334210 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 176330 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 122 | 2967700 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 0 | 0 | Under maint.
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 190 | 4733100 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 405 | 9099636 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 297010 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 489120
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 253170
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 42 | 1117920 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 884600 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 100 | 342930 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 1591296 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1108224 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 40320
| Rajshahi Area Total |  |  |  | 2179 | 1348 | 24086801
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3773400 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1813142
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 41446
| Rangpur Area Total |  |  |  | 605 | 268 | 5627988
| Total |  |  |  | 21280 | 12179 | 255124980
| Eastern Grid Total |  |  |  | 14321 | 8420 | 179891047
| Western Grid Total |  |  |  | 6959 | 3759 | 75233933
| National Grid Total |  |  |  | 21280 | 12179 | 255124980
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-08-06
(a) ENTIRE EASTERN GRID : |  | 7328 | MW | (b) ENTIRE WESTERN GRID : |  | 4088 | MW
i) Dhaka area |  | 3559 | MW | i) Khulna area |  | 1574 | MW
ii) Chittagong area |  | 1092 | MW | ii) Rajshahi area |  | 1302 | MW
iii) Comilla area |  | 1155 | MW | iii) Barisal area |  | 377 | MW
iv) Mymensingh area |  | 1062 | MW | iv) Rangpur area |  | 835 | MW
v) Sylhet area |  | 460 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11416 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 104 | 23:00 | Kishoreganj | 150 | 23:00 | Jessore | 115 | 20:00
Munsiganj | 102 | 0:00 | Netrokona | 122 | 19:30 | Benapol | 62 | 21:00
Sonargaon | 67 | 0:00 | Jamalpur | 153 | 2:00 | Jhenida | 120 | 21:00
Shyampur | 164 | 0:00 | Sherpur | 144 | 21:00 | Bottail | 128 | 23:00
Bhulta | 160 | 23:00 | Srimongal | 53 | 22:00 | G.K Project | 60 | 21:00
Madanganj | 53 | 18:00 | Shahjibazar | 106 | 21:00 | Faridpur | 140 | 1:00
Shitalakhya | 87 | 1:00 | Fenchuganj | 47 | 22:00 | Rajbari | 50 | 20:00
Rahim steel | 0 | 1:00 | Kulawara | 47 | 20:00 | Madaripur | 106 | 22:00
Matuail | 51 | 7:00 | Sylhet | 123 | 19:00 | Sariatpur | 68 | 22:00
Ghorasal | 70 | 1:00 | Chatak | 29 | 1:00 | Gopalganj | 95 | 22:00
Narsingdi | 161 | 21:00 | Sunamganj | 53 | 21:00 | Bagerhat | 105 | 21:00
Haripur (SBU) | 78 | 1:00 | Biani Bazar | 62 | 1:00 | Mongla | 34 | 1:00
Sreenagar | 41 | 22:00 | Comilla (S) | 130 | 22:00 | Satkhira | 109 | 22:00
Ullon | 60 | 19:00 | Comilla(N) | 129 | 21:00 | Gallamari | 31 | 23:00
Hasnabad | 72 | 22:00 | Chandpur | 73 | 19:00 | Magura | 58 | 20:00
Magbazar | 66 | 13:00 | Feni | 116 | 21:00 | Norail | 44 | 20:00
Maniknagar | 50 | 4:00 | Chowmuhani | 212 | 21:00 | Chuadanga | 103 | 21:00
Bangabhaban | 4 | 1:00 | Ashuganj | 31 | 1:00 | Borguna | 20 | 23:00
Motijheel | 18 | 12:00 | Daudkandi | 136 | 20:00 | Barisal(N) | 46 | 1:00
Narinda | 40 | 1:00 | B.Baria | 167 | 21:00 | Barisal (S) | 106 | 22:00
Kazla | 78 | 23:00 | Ramganj | 90 | 1:00 | Patuakhali | 119 | 22:00
Dhanmondi | 97 | 19:00 | Chaddagram | 45 | 22:00 | Bhandaria | 54 | 1:00
Lalbag | 69 | 1:00 | PHP | 10 | 4:00 | Borhan Uddin | 46 | 23:00
Madartek | 71 | 1:00 | Kochua | 68 | 22:00 | Ishurdi | 65 | 19:30
Dhaka University | 16 | 19:00 | Madunaghat | 54 | 19:00 | Ruppur Paromanobik | 3 | 1:00
Aftabnagar | 9 | 12:00 | Hathazari | 87 | 19:00 | Natore | 130 | 21:00
Fatullah | 43 | 0:00 | Khulshi | 156 | 14:00 | Bogra | 164 | 21:00
Nawabganj | 53 | 22:00 | Halishahar | 70 | 13:00 | Noagaon | 113 | 1:00
Keraniganj | 54 | 1:00 | Baraulia | 73 | 23:00 | Rajshahi | 140 | 20:00
Mirpur | 98 | 15:00 | Sikalbaha | 34 | 5:00 | Rajshahi New | 14 | 19:30
Kalyanpur | 96 | 19:00 | Dohazari | 96 | 19:00 | C.Nawabganj | 61 | 21:00
Gulshan | 66 | 19:00 | Cox'sbazar | 96 | 1:00 | Amnura | 52 | 21:00
Uttara | 78 | 19:00 | Chandraghona | 26 | 19:30 | Pabna | 97 | 21:00
Uttara New | 11 | 19:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 90 | 21:00
Kamrangirchar | 67 | 19:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 97 | 22:00
Savar | 129 | 15:00 | Bakulia | 87 | 1:00 | Niyamatpur | 76 | 23:00
Bhasantec | 115 | 19:00 | Julda | 19 | 1:00 | Joypurhat | 58 | 21:00
Agargaon | 71 | 19:00 | TK chemical | 28 | 1:00 | Sherpur(Bogura) | 53 | 20:00
Satmosjid | 86 | 19:00 | Modern Steel | 0 | #N/A | Mohastangor | 70 | 1:00
Tongi | 96 | 15:00 | Shahmirpur | 23 | 1:00 | Bhangura | 34 | 19:30
Kabirpur | 183 | 21:00 | Khagrachhari | 28 | 16:00 | Rangpur | 149 | 19:00
Basundhara | 185 | 18:30 | Matarbari | 35 | 1:00 | Lalmonirhat | 49 | 19:00
Manikganj | 80 | 21:00 | Baroiar Hat | 48 | 15:00 | Saidpur | 101 | 1:00
Joydevpur | 130 | 1:00 | Rangamati | 12 | 18:30 | Purbasadipur | 110 | 22:00
New Tongi | 78 | 1:00 | Abul Khair 230 | 151 | 23:00 | Thakurgaon | 102 | 21:00
Kodda | 206 | 21:00 | BSRM | 152 | 7:00 | Palashbari | 124 | 19:00
Dhamrai | 84 | 22:00 | GPH Ispat | 82 | 8:00 | Barapukuria | 54 | 1:00
Rajendrapur | 94 | 1:00 | Agrabad | 64 | 19:00 | Panchagar | 56 | 19:00
Valuka | 112 | 0:00 | Goalpara | 24 | 21:00 | Joldhaka | 62 | 1:00
Tangail | 215 | 21:00 | Central S/S | 102 | 20:00 | Kurigram | 66 | 19:30
Mymensing | 225 | 20:00 | Noapara | 49 | 21:00 | Mithapukur | 36 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-08-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 411 | 18:30 | 402 | 10:00 | Kaliakoir | 403 | 0.16667 | 392 | 0.45833
| Bheramara | 407 | 5:00 | 395 | 22:00 | Bhulta | 393 | 0.75 | 384 | 0.41667
| Ashuganj(N) | 397 | 18:30 | 390 | 10:00 | Gopalganj | 406 | 0.625 | 385 | 0.875
| Payra | 413 | 20:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 21:00 | 230 | 1:00 | Hathazari | 227 | 1:00 | 224 | 8:00
| Ishurdi | 235 | 16:00 | 224 | 22:00 | Megnaghat | 238 | 16:00 | 232 | 12:00
| Ashuganj | 244 | 18:30 | 238 | 10:00 | Fenchuganj | 244 | 18:30 | 240 | 1:00
| Serajganj | 230 | 6:00 | 225 | 1:00 | Siddhirganj | 235 | 4:00 | 231 | 10:00
| Baghabari | 230 | 3:00 | 225 | 11:00 | Maniknagar | 233 | 4:00 | 228 | 12:00
| Barapukuria | 233 | 18:30 | 223 | 1:00 | Agargaon | 232 | 18:30 | 225 | 11:00
| Bogra | 223 | 14:00 | 212 | 23:00 | Barisal | 241 | 13:00 | 230 | 21:00
| Rajshahi | 231 | 16:00 | 219 | 12:00 | Bhola 225 MW | 243 | 7:00 | 235 | 23:00
| Khulna South | 226 | 24:00 | 207 | 19:30 | AKSML | 229 | 13:00 | 225 | 5:00
| Rampura | 232 | 18:30 | 229 | 12:00 | BSRM | 231 | 18:30 | 213 | 16:00
| Haripur | 233 | 19:30 | 227 | 12:00 | Bibiyana | 244 | 5:00 | 235 | 21:00
| Hasnabad | 232 | 1:00 | 230 | 4:00 | Bhulta | 235 | 6:00 | 230 | 12:00
| Shyampur | 231 | 20:00 | 220 | 11:00 | Ashuganj (S) | 241 | 5:00 | 235 | 9:00
| Aminbazar | 234 | 1:00 | 227 | 2:00 | Kaliakoir | 234 | 18:30 | 226 | 10:00
| Tongi | 234 | 1:00 | 225 | 10:00 | GPH | 230 | 16:00 | 226 | 8:00
| Comilla (N) | 234 | 19:30 | 230 | 9:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 133 | 10:00 | Madanhat | 138 | 0.77083 | 135 | 0.20833
| Munsiganj | 138 | 19:30 | 133 | 7:00 | Hathazari | 135 | 0.041667 | 134 | 0.16667
| Sonargaon | 136 | 2:00 | 133 | 9:00 | Khulshi | 134 | 0.25 | 131 | 0.5
| Shyampur | 139 | 19:30 | 135 | 11:00 | Halishahar | 136 | 0.083333 | 133 | 0.5
| Bhulta | 133 | 19:30 | 128 | 1:00 | Baraulia | 136 | 0.29167 | 133 | 0.41667
| Madanganj | 136 | 19:30 | 131 | 11:00 | Sikalbaha | 137 | 0.66667 | 133 | 0.75
| Shitalakhya | 141 | 19:30 | 131 | 12:00 | Dohazari | 131 | 0.20833 | 129 | 0.041667
| Rahim steal | 0 | 1:00 | 0 | 1:00 | Cox'sbazar | 123 | 0.25 | 113 | 0.8125
| Matuail | 135 | 1:00 | 133 | 10:00 | Chandraghona | 136 | 0.25 | 134 | 0.041667
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 134 | 0.041667 | 134 | 0.041667
| Narsinghdi | 136 | 6:00 | 126 | 22:00 | A. Khaer Stl. | 134 | 0.041667 | 133 | 0.95833
| Haripur (SBU) | 137 | 19:30 | 133 | 11:00 | Bakulia | 137 | 0.79167 | 133 | 0.91667
| Sreenagar | 133 | 2:00 | 128 | 10:00 | Julda | 138 | 0.041667 | 134 | 0.70833
| Ullon | 136 | 4:00 | 132 | 12:00 | TK Chemical | 137 | 0.77083 | 133 | 0.25
| Hasnabad | 137 | 19:00 | 134 | 10:00 | Modern Steel | 0 | #N/A | 0 | #N/A
| Magbazar | 135 | 3:00 | 132 | 11:00 | Shahmirpur | 137 | 0.25 | 133 | 0.75
| Maniknagar | 136 | 2:00 | 134 | 11:00 | Khagrachhari | 135 | 0.66667 | 132 | 0.5
| Bangabhaban | 136 | 2:00 | 134 | 11:00 | Matarbari | 124 | 0.25 | 119 | 0.79167
| Motijheel | 136 | 2:00 | 134 | 11:00 | Baroiar Hat | 134 | 0.77083 | 132 | 0.041667
| Narinda | 136 | 2:00 | 134 | 11:00 | Rangamati | 135 | 4:00 | 133 | 22:00
| Kazla | 136 | 2:00 | 134 | 11:00 | Agrabad | 134 | 1:00 | 132 | 17:00
| Dhanmondi | 136 | 4:00 | 133 | 12:00 | Goalpara S/S | 137 | 23:00 | 126 | 0.79167
| Lalbag | 138 | 17:00 | 131 | 12:00 | Khulna Central S/S | 137 | 5:00 | 126 | 0.041667
| Madartek | 136 | 4:00 | 132 | 12:00 | Noapara | 136 | 5:00 | 123 | 0.041667
| Dhaka University | 137 | 19:30 | 131 | 12:00 | Jessore | 128 | 16:00 | 119 | 0.8125
| Aftabnagar | 136 | 4:00 | 132 | 12:00 | Benapol | 130 | 0.66667 | 116 | 0.16667
| Fatullah | 139 | 19:00 | 135 | 12:00 | Jhenida | 126 | 16:00 | 116 | 0.041667
| Nawabganj | 133 | 19:30 | 128 | 10:00 | Bottail | 131 | 0.75 | 124 | 0.8125
| Keraniganj | 134 | 19:30 | 129 | 10:00 | G.K Project | 138 | 0.25 | 133 | 0.79167
| Mirpur | 139 | 5:00 | 135 | 12:00 | Faridpur | 136 | 0.77083 | 128 | 0.875
| Kalyanpur | 140 | 5:00 | 136 | 12:00 | Rajbari | 135 | 0.25 | 126 | 0.875
| Gulshan | 135 | 5:00 | 133 | 12:00 | Madaripur | 139 | 0.375 | 130 | 0.875
| Uttara | 140 | 5:00 | 135 | 12:00 | Shariyatpur S/S | 139 | 7:00 | 129 | 0.875
| Uttara New | 139 | 4:00 | 134 | 10:00 | Gopalganj | 142 | 0.25 | 130 | 0.875
| Kamrangirchar | 138 | 4:00 | 131 | 12:00 | Bagerhat | 137 | 5:00 | 120 | 0.041667
| Savar | 141 | 19:30 | 135 | 11:00 | Mongla | 132 | 4:00 | 123 | 0.45833
| Bhasantec | 138 | 19:30 | 133 | 12:00 | Satkhira | 135 | 5:00 | 122 | 1:00
| Agargaon | 138 | 19:30 | 134 | 12:00 | Gallamari | 138 | 0.20833 | 126 | 2:00
| Satmosjid | 138 | 19:30 | 134 | 12:00 | Magura | 125 | 7:00 | 114 | 0.041667
| Tongi | 138 | 18:00 | 131 | 12:00 | Narail | 125 | 0.77083 | 113 | 0.041667
| Kabirpur | 138 | 17:00 | 132 | 21:00 | Chuadanga | 130 | 8:00 | 117 | 0.8125
| Basundhara | 135 | 18:30 | 127 | 12:00 | Borguna | 138 | 18:30 | 127 | 0.95833
| Manikganj | 140 | 19:00 | 131 | 12:00 | Barisal(N) | 140 | 7:00 | 131 | 22:00
| Joydevpur | 141 | 18:00 | 135 | 8:00 | Barisal (S) | 138 | 0.41667 | 129 | 0.91667
| New Tongi | 136 | 1:00 | 129 | 11:00 | Patuakhali(S) | 135 | 0.375 | 127 | 0.91667
| Kodda | 135 | 1:00 | 124 | 12:00 | Bhandaria | 135 | 0.29167 | 122 | 0.95833
| Dhamrai | 136 | 18:00 | 131 | 1:00 | Ishurdi | 136 | 16:00 | 130 | 19:00
| Rajendrapur | 135 | 1:00 | 123 | 12:00 | Ruppur Paromanobik | 136 | 18:30 | 132 | 19:30
| Valuka | 124 | 6:00 | 109 | 1:00 | Natore | 135 | 16:00 | 127 | 19:00
| Tangail | 135 | 18:00 | 123 | 22:00 | Bogra | 133 | 18:00 | 125 | 7:00
| Mymensing | 128 | 7:00 | 114 | 1:00 | Noagaon | 132 | 18:30 | 119 | 1:00
| Kishorganj | 131 | 18:30 | 120 | 22:00 | Rajshahi | 133 | 13:00 | 128 | 12:00
| Netrokona | 125 | 6:00 | 109 | 21:00 | Rajshahi New | 135 | 16:00 | 128 | 12:00
| Jamalpur | 134 | 6:00 | 120 | 2:00 | C.Nawabganj | 135 | 18:30 | 127 | 4:00
| Sherpur | 133 | 6:00 | 115 | 19:30 | Amnura | 135 | 18:30 | 126 | 12:00
| Srimongal | 141 | 8:00 | 135 | 1:00 | Pabna | 134 | 18:00 | 128 | 19:00
| Shahjibazar | 139 | 7:00 | 133 | 1:00 | Shahjadpur | 138 | 13:00 | 133 | 12:00
| Fenchuganj | 139 | 8:00 | 135 | 13:00 | Serajganj | 132 | 13:00 | 125 | 1:00
| Khulawara | 137 | 8:00 | 134 | 1:00 | Niyamatpur | 128 | 18:30 | 114 | 3:00
| Sylhet | 134 | 7:00 | 130 | 1:00 | Joypurhat | 131 | 18:30 | 118 | 1:00
| Chatak | 134 | 17:00 | 130 | 1:00 | Sherpur(Bogura) | 132 | 18:30 | 124 | 1:00
| Sunamganj | 131 | 7:00 | 124 | 21:00 | Mohastangor | 130 | 18:30 | 121 | 1:00
| Biani Bazar | 134 | 20:00 | 127 | 1:00 | Bangura | 135 | 17:00 | 130 | 12:00
| Comilla(s) | 128 | 4:00 | 124 | 22:00 | Rangpur | 128 | 6:00 | 109 | 2:00
| Comilla(n) | 140 | 19:00 | 136 | 9:00 | Lalmonirhat | 125 | 14:00 | 112 | 10:00
| Chandpur | 140 | 1:00 | 133 | 9:00 | Saidpur | 128 | 6:00 | 114 | 1:00
| Feni | 137 | 19:00 | 132 | 22:00 | Purbasadipur | 126 | 13:00 | 106 | 1:00
| Chowmuhani | 133 | 19:30 | 129 | 0:00 | Thakurgaon | 126 | 14:00 | 107 | 1:00
| Ashuganj | 141 | 18:00 | 135 | 22:00 | Palashbari | 126 | 14:00 | 116 | 19:00
| Daudkandi | 136 | 19:30 | 131 | 22:00 | Barapukuria | 133 | 18:30 | 123 | 1:00
| B.Baria | 137 | 18:00 | 129 | 22:00 | Panchagar | 127 | 13:00 | 105 | 1:00
| Ramganj | 135 | 18:30 | 131 | 9:00 | Joldhaka | 127 | 0.25 | 107 | 0.041667
| Chaddagram | 138 | 19:30 | 132 | 9:00 | Kurigram | 125 | 0.77083 | 110 | 0.041667
| PHP | 136 | 19:30 | 130 | 11:00 | Mithapukur | 129 | 0.25 | 116 | 0.91667
| Kochua | 138 | 18:30 | 134 | 8:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-08-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 460 | 8436 | 3622 | 12058 |  |  |  | QF-LDC-11
0:30 | 475 | 8384 | 3667.5 | 12051.5 | Date: | 2021-08-06
1:00 | 490 | 8332 | 3713 | 12045
1:30 | 469 | 8187 | 3651 | 11838
2:00 | 448 | 8042 | 3589 | 11631
2:30 | 436 | 7904.5 | 3518 | 11422.5 | [5 empty] | Gen. at Eve. Peak | 12179 | 12179 MW (21:00 )
3:00 | 424 | 7767 | 3447 | 11214 | [6 empty] | 21:00
3:30 | 399 | 7723 | 3387.5 | 11110.5 | [5 empty] | Gen. at Day Peak | 9711 | 9711 MW (12:00 )
4:00 | 374 | 7679 | 3328 | 11007 | [6 empty] | 12:00
4:30 | 327 | 7606.5 | 3197 | 10803.5 | [5 empty] | Highest Generation | 12179
5:00 | 280 | 7534 | 3066 | 10600 | [6 empty] | 21:00
5:30 | 259 | 7240 | 2857 | 10097
6:00 | 238 | 6946 | 2648 | 9594
6:30 | 208 | 6754.5 | 2600.5 | 9355
7:00 | 178 | 6563 | 2553 | 9116
7:30 | 137 | 6517 | 2550 | 9067
8:00 | 96 | 6471 | 2547 | 9018
8:30 | 92 | 6450 | 2550.5 | 9000.5
9:00 | 88 | 6429 | 2554 | 8983
9:30 | 97 | 6460 | 2618.5 | 9078.5
10:00 | 106 | 6491 | 2683 | 9174
10:30 | 90 | 6607.5 | 2716.5 | 9324
11:00 | 74 | 6724 | 2750 | 9474
11:30 | 151 | 6814 | 2778.5 | 9592.5
12:00 | 228 | 6904 | 2807 | 9711
12:30 | 340 | 7095 | 2791 | 9886
13:00 | 452 | 7286 | 2775 | 10061
13:30 | 436 | 7320 | 2745.5 | 10065.5
14:00 | 420 | 7354 | 2716 | 10070
14:30 | 399 | 7462 | 2747.5 | 10209.5
15:00 | 378 | 7570 | 2779 | 10349
15:30 | 383 | 7488 | 2708.5 | 10196.5
16:00 | 388 | 7406 | 2638 | 10044
16:30 | 372 | 7069 | 2543.5 | 9612.5
17:00 | 356 | 6732 | 2449 | 9181
17:30 | 348 | 6588 | 2420.5 | 9008.5
18:00 | 340 | 6444 | 2392 | 8836
18:30 | 525 | 6994.5 | 2689 | 9683.5
19:00 | 710 | 7545 | 2986 | 10531
19:30 | 534 | 8091 | 3562 | 11653
20:00 | 536 | 8075 | 3632 | 11707 |  |  |  | Executive Engineer
20:30 | 548 | 8247.5 | 3695.5 | 11943 |  |  |  | Network Operation Division
21:00 | 560 | 8420 | 3759 | 12179
21:30 | 484 | 8357 | 3756.5 | 12113.5
22:00 | 408 | 8294 | 3754 | 12048 |  |  |  |  | Page 6 of 7
22:30 | 432 | 8350 | 3693 | 12043
23:00 | 456 | 8406 | 3632 | 12038
23:30 | 458 | 8421 | 3627 | 12048
24:00 | 460 | 8436 | 3622 | 12058
12179 MW (21:00 )
9711 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-08-06 |  | Energy | 255124980
[11 empty] | 2021-08-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4636 | 446 | 2040 | 3376 | 704 | 118 | 508 | 0 | 126 | 0
0:30 | 4422 | 563.5 | 2077 | 3571 | 678.5 | 118 | 442.5 | 0 | 127 | 0 | Date: | 2021-08-06
1:00 | 4208 | 681 | 2114 | 3766 | 653 | 118 | 377 | 0 | 128 | 0
1:30 | 4182 | 677 | 2095.5 | 3650 | 643 | 117.5 | 346 | 0 | 127 | 0 | [7 empty] | Total Energy | 255.125 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4156 | 673 | 2077 | 3534 | 633 | 117 | 315 | 0 | 126 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4141 | 676 | 2080.5 | 3390.5 | 603 | 117.5 | 290 | 0 | 124 | 0 | [7 empty] | Energy Requirement | 255.125
3:00 | 4126 | 679 | 2084 | 3247 | 573 | 118 | 265 | 0 | 122 | 0
3:30 | 4127 | 679 | 2081.5 | 3204.5 | 573 | 117.5 | 208 | 0 | 120 | 0 | [6 empty] | Shortage
4:00 | 4128 | 679 | 2079 | 3162 | 573 | 117 | 151 | 0 | 118 | 0
4:30 | 4125 | 679 | 2055.5 | 3055.5 | 564.5 | 117.5 | 91.5 | 0 | 115 | 0
5:00 | 4122 | 679 | 2032 | 2949 | 556 | 118 | 32 | 0 | 112 | 0
5:30 | 4006 | 679.5 | 2004 | 2658.5 | 506 | 118 | 16 | 0 | 108 | 1
6:00 | 3890 | 680 | 1976 | 2368 | 456 | 118 | 0 | 0 | 104 | 2
6:30 | 3913 | 679.5 | 1946.5 | 2131 | 455.5 | 119 | 0 | 0 | 101 | 9.5 |  |  |  |  | Coal
7:00 | 3936 | 679 | 1917 | 1894 | 455 | 120 | 0 | 0 | 98 | 17
7:30 | 3934.5 | 681.5 | 1913.5 | 1839 | 454 | 120.5 | 0 | 0 | 95 | 29 |  |  |  | Oil |  |  |  | ,
8:00 | 3933 | 684 | 1910 | 1784 | 453 | 121 | 0 | 0 | 92 | 41
8:30 | 3950.5 | 684 | 1881 | 1777.5 | 454 | 121 | 0 | 0 | 92 | 40.5
9:00 | 3968 | 684 | 1852 | 1771 | 455 | 121 | 0 | 0 | 92 | 40
9:30 | 4007 | 684 | 1891 | 1775 | 454.5 | 121 | 0 | 0 | 94 | 52
10:00 | 4046 | 684 | 1930 | 1779 | 454 | 121 | 0 | 0 | 96 | 64
10:30 | 4103.5 | 683.5 | 1946 | 1836 | 452 | 121 | 0 | 0 | 94 | 88
11:00 | 4161 | 683 | 1962 | 1893 | 450 | 121 | 0 | 0 | 92 | 112
11:30 | 4209.5 | 683.5 | 1975 | 1967 | 450 | 119.5 | 0 | 0 | 98 | 90
12:00 | 4258 | 684 | 1988 | 2041 | 450 | 118 | 0 | 0 | 104 | 68
12:30 | 4217.5 | 600.5 | 1996 | 2288.5 | 476 | 117 | 0 | 0 | 107 | 83.5
13:00 | 4177 | 517 | 2004 | 2536 | 502 | 116 | 0 | 0 | 110 | 99
13:30 | 4177 | 517 | 2004 | 2536 | 502 | 116 | 0 | 0 | 110 | 99
14:00 | 4177 | 517 | 2004 | 2536 | 502 | 116 | 0 | 0 | 110 | 99
14:30 | 4187.5 | 482 | 1968.5 | 2731 | 521.5 | 114.5 | 0 | 0 | 112 | 88
15:00 | 4198 | 447 | 1933 | 2926 | 541 | 113 | 0 | 0 | 114 | 77
15:30 | 4177 | 446.5 | 1901.5 | 2837.5 | 541.5 | 113.5 | 2 | 0 | 111 | 66
16:00 | 4156 | 446 | 1870 | 2749 | 542 | 114 | 4 | 0 | 108 | 55
16:30 | 4173 | 446 | 1895 | 2306 | 532 | 114 | 3 | 0 | 104 | 39.5
17:00 | 4190 | 446 | 1920 | 1863 | 522 | 114 | 2 | 0 | 100 | 24
17:30 | 4184 | 446 | 1848.5 | 1777 | 521 | 115.5 | 4.5 | 0 | 98 | 14
18:00 | 4178 | 446 | 1777 | 1691 | 520 | 117 | 7 | 0 | 96 | 4
18:30 | 4261.5 | 446 | 1855.5 | 2141.5 | 535.5 | 117 | 213.5 | 0 | 111 | 2
19:00 | 4345 | 446 | 1934 | 2592 | 551 | 117 | 420 | 0 | 126 | 0
19:30 | 4269 | 446 | 1941 | 3627 | 632 | 117 | 497 | 0 | 124 | 0
20:00 | 4369 | 446 | 1951 | 3570 | 643 | 116 | 488 | 0 | 124 | 0
20:30 | 4495 | 446 | 1992.5 | 3576.5 | 659 | 117 | 531 | 0 | 126 | 0
21:00 | 4621 | 446 | 2034 | 3583 | 675 | 118 | 574 | 0 | 128 | 0
21:30 | 4600.5 | 564 | 2023 | 3452.5 | 678 | 118 | 548.5 | 0 | 129 | 0
22:00 | 4580 | 682 | 2012 | 3322 | 681 | 118 | 523 | 0 | 130 | 0
22:30 | 4617.5 | 606.5 | 2021 | 3349 | 686.5 | 118 | 515.5 | 0 | 129 | 0
23:00 | 4655 | 531 | 2030 | 3376 | 692 | 118 | 508 | 0 | 128 | 0
23:30 | 4645.5 | 488.5 | 2035 | 3376 | 698 | 118 | 508 | 0 | 127 | 0 | Max Temp. in Dhaka |  | 34.4° C
24:00 | 4636 | 446 | 2040 | 3376 | 704 | 118 | 508 | 0 | 126 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-08-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 58 | 57 | 58 | 57 | 58 | 58 | 60 | 61 | 61 | 61 | 61 | 58 | 56 | 55 | 53 | 54 | 54 | 57 |  | 57 | 57 | 56 | 58 | 58 | 58 | 58 | 1286110
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1464000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | 25 | 0 | [17 empty] | 10 | 25 |  |  |  |  | 0 | 53915
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 4 | 1 | 1 | 2 | [10 empty] | 13365
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 34 | 34 | 272554
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 68 | 51 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 2478971
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | [5 empty] | 49264
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 335 | 300 | 300 | 300 | 300 | 250 | 250 | 250 | 250 | 280 | 280 | 325 | 324 | 322 | 318 | 320 | 321 | 326 |  | 328 | 282 | 280 | 332 | 335 | 332 | 335 | 7341603
18 | Kodda 300 MW PP Unit-2 (Summit) | 253 | 272 | 272 | 273 | 273 | 15 | [5 empty] | 11 | 69 | 168 | 195 | 195 | 130 | 130 |  | 200 | 264 | 263 | 264 | 264 | 260 | 265 | 3976908
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 284363
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 |  | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 4473000
24
25 | Ghorasal 365 MW CCPP Unit-7 | [12 empty] | 35 | 35 | 35 | 35 | 65 | 105 |  | 170 | 180 | 210 | 300 | 310 | 310 | 310 | 1736009
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 110 | 110 | 110 |  | 110 | 95 | 80 | 80 | 80 | 80 | 80 | 2043672
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 |  | 23 | 23 | 509544
33 | Ashuganj 225 MW CCPP | 213 | 212 | 213 | 211 | 212 | 212 | 213 | 189 | 212 | 183 | 197 | 201 | 183 | 181 | 192 | 180 | 181 | 191 |  | 209 | 211 | 212 | 213 | 214 | 213 | 212 | 4890000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 265 | 265 | 265 | 285 | 280 | 285 | 300 | 330 | 345 | 300 | 300 | 315 | 300 | 310 | 320 |  | 310 | 300 | 320 | 300 | 300 | 320 | 305 | 7191000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 260 | 260 | 260 | 275 | 285 | 290 | 275 | 305 | 335 | 305 | 290 | 310 | 290 | 295 | 290 |  | 295 | 260 | 275 | 310 | 310 | 325 | 310 | 7279400
35 | Ashuganj 55 MW PP (Precision) | 55 | 55 | 55 | 56 | 55 | 56 | 55 | 55 | 55 | 52 | 52 | 51 | 51 | 49 | 48 | 48 | 50 | 57 |  | 57 | 57 | 57 | 57 | 54 | 56 | 56 | 1293120
36 | Chandpur 150 MW CCPP | 136 | 137 | 138 | 136 | 134 | 136 | 137 | 138 | 137 | 138 | 138 | 138 | 135 | 137 | 138 | 136 | 138 | 138 |  | 138 | 135 | 137 | 135 | 135 | 137 | 137 | 3277330
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 390 | 375 | 371 | 372 | 372 | 334 | 332 | 332 | 331 | 350 | 368 | 368 | 391 | 379 | 364 | 363 | 362 | 362 |  | 367 | 356 | 367 | 391 | 395 | 395 | 395 | 8960000
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5641750
41 | Haripur 360MW CCPP(HPL) | 346 | 313 | 313 | 313 | 312 | 275 | 277 | 277 | 277 | 349 | 344 | 341 | 340 | 323 | 338 | 343 | 338 | 301 |  | 326 | 344 | 345 | 344 | 345 | 343 | 345 | 7742000
42 | RPCL 210MW CCPP | 203 | 203 | 208 | 208 | 208 | 208 | 208 | 205 | 203 | 204 | 203 | 200 | 183 | 200 | 198 | 200 | 200 | 200 |  | 200 | 205 | 204 | 208 | 212 | 210 | 208 | 4783600
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 13 | 27 | 32 | 25 | 57 | 25 | 54 | 47 | 39 | 31 | 9 | 1 | [8 empty] | 327540
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 44 | 44 | 44 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1030000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | [10 empty] | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 708000
46 | Shajibazar 330 MW CCPP | 160 | 160 | 159 | 160 | 160 | 160 | 160 | 160 | 159 | 158 | 158 | 157 | 157 | 156 | 154 | 156 | 158 | 159 |  | 158 | 159 | 160 | 159 | 161 | 161 | 160 | 3673000
47 | Shahjibazar GTPP Unit- 8 & 9 | 57 | 57 | 57 | 57 | 57 | 57 | 61 | 63 | 63 | 63 | 61 | 61 | 61 | 60 | 60 | 62 | 63 | 40 |  | 61 | 40 | 40 | 62 | 61 | 61 | 61 | 1378752
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 84 | 84 | 82 | 81 | 81 | 84 | 40 |  | 65 | 80 | 84 | 84 | 84 | 84 | 84 | 1920960
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 150 | 150 | 150 | 150 | 150 | 100 | 100 | 100 | 120 | 145 | 145 | 138 | 138 | 140 | 140 | 140 | 140 |  | 145 | 100 | 100 | 145 | 145 | 145 | 145 | 3243100
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 252000
54 | Hobiganj 11MW PP Cofidence-E | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 | 8 | 8 | [5 empty] | 8 |  | 3 | 8 | 112656
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 53 | 53 | 53 | 52 | 53 | 14 |  | 19 | 52 | 52 | 50 | 50 | 50 | 50 | 1152600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 567984
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 290 | 290 | 300 | 280 | 300 | 300 | 300 | 305 | 300 | 310 | 310 | 280 | 310 | 280 | 285 | 290 |  | 295 | 260 | 265 | 295 | 285 | 290 | 300 | 7187500
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 | 55 | 55 | 17 | 17 |  | 40 | 55 | 55 | 55 | 55 | 55 | 55 | 981227
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 23 | 22 | 24 | 24 | 25 | 24 | 24 | 24 | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 588240
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 458928
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 |  | 16 | 16 | 16 | 20 | 20 | 20 | 20 | [5 empty] | 12 | 19 | 20 | 20 | 20 | 20 | 21 | 345096
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 425124
63 | Impoprt (Tripura) | 128 | 126 | 122 | 118 | 112 | 104 | 98 | 92 | 92 | 96 | 92 | 104 | 110 | 110 | 114 | 108 | 100 | 96 |  | 126 | 124 | 124 | 128 | 130 | 128 | 126 | 2696640
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 42 | 36 | 30 | 28 | 13 | 13 | 17 | 27 | 30 | 20 | 24 | 25 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 773760
65 | Feni 22MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 510120
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | [7 empty] | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 193680
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 28 | 31 | 31 | 25 | 15 | 25 | 33 | 593100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 18 | 16 | 16 | 18 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 21 | 21 | 21 | 489200
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 13 | 13 | 18 | 18 | 14 | 10 | 10 | 14 | 16 | 16 | 16 |  | 16 | 16 | 22 | 22 | 22 | 27 | 27 | 435600
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 642300
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 828100
73 | Ghorashal 108MW PP (Regent) | 101 | 101 | 101 | 101 | 101 | 101 | 53 | 52 | [17 empty] | 0 | 749590
| Feni Lanka Power | 105 | 114 | 20 | [9 empty] | 21 | 34 | 34 | 17 | 17 | 17 |  | 30 | 114 | 114 | 114 | 70 | 70 | 88 | 921120
| Chowmuhani 113 MW | 110 | 107 | 110 | 109 | 119 | 119 | 119 | 115 | 115 | 117 | 110 | 105 | 111 | 108 | 108 | 108 | 75 | 35 |  | 47 | 106 | 105 | 109 | 108 | 109 | 110 | 2541840
| Manikgonj 162MW PP(MPGL) | 144 | 144 | 144 | 144 | 144 | 108 | 35 | 35 | 35 | 35 | 35 | 68 | 90 | 90 | 90 | 90 | 35 | 35 |  | 82 | 162 | 162 | 162 | 162 | 162 | 162 | 2491200
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 8 | [18 empty] | 4 | 8 |  |  |  |  | 0 | 53760
79 | Kodda 150MW PP | 133 | 98 | 64 | 32 | 32 | [14 empty] | 110 | 150 | 115 | 115 | 64 | 64 | 64 | 944160
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | [5 empty] | 6 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 152640
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | [7 empty] | 4 | 16 | 28 | 43 | 12 | 8 |  | 12 | 43 | 43 | 43 | 43 | 43 | 43 | 580814
| Gazipur 100 MW PP | 105 | [18 empty] | 30 | 35 |  |  |  |  | 0 | 230400
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 3 | 5 | 4 | 1 | 0 | 1 | 1 | 0 | [9 empty] | 22080
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 106 | 110 | 106 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 68 | 68 |  | 85 | 110 | 110 | 110 | 110 | 110 | 110 | 2667152
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 86 | 20 | [17 empty] | 28 | 74 | 50 | 30 |  |  | 0 | 249681
86 | Meghnaghat CCPP ( Summit) | 250 | 270 | 270 | 270 | 235 | 270 | 275 | 285 | 280 | 260 | 285 | 290 | 285 | 280 | 285 | 250 | 280 | 285 |  | 285 | 235 | 285 | 275 | 270 | 285 | 280 | 6571811
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 90 | 90 | 90 | 90 | 60 | 54 | 53 | 53 | 53 | 53 | 54 | 80 | 91 | 91 | 90 | 53 | 17 |  | 35 | 90 | 91 | 92 | 93 | 94 | 94 | 1769280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 100 | 90 | 90 | 90 | [8 empty] | 30 | 30 | 50 | 10 | 10 | 10 |  | 30 | 10 | 10 |  |  |  | 0 | 606000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 10 | 10 | 10 | 10 | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 920660
94 | Gagnagar 102 MW PP (Digital Power) | 94 | 94 | 8 | [9 empty] | 32 | 32 | 32 | 7 | 7 | 7 |  | 48 | 94 | 94 | 85 | 94 | 94 | 94 | 886140
95 | Patenga 50MW PP (Baraka) | 50 | 49 | [17 empty] | 14 | 50 | 18 | 19 |  |  | 0 | 184800
96 | Chattogram 108 MW PP (ECPV) | 95 | 95 | 95 | 95 | 95 | 85 | 85 | 82 | 82 | 82 | 83 | 83 | 76 | 76 | 76 | 77 | 83 | 89 |  | 89 | 89 | 82 | 83 | 84 | 87 | 96 | 2063040
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 30 | [8 empty] | 7 | 30 | 30 | 15 | 15 | 15 |  | 20 | 55 | 55 | 55 | 55 | 55 | 55 | 661535
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1242511
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 163 | 163 | 163 | 163 |  | 163 | 110 | 110 | 163 | 163 | 163 | 163 | 3780573
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 2 | 2 | 1 | 3 | 1 | 2 | 1 | 0 | 0 | [8 empty] | 14500
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1246680
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 176 | 179 | 180 | 180 | 180 | 180 | 130 | 80 | 80 | 80 | 80 | 80 | 120 | 150 | 158 | 170 | 70 | 70 |  | 108 | 180 | 179 | 179 | 179 | 183 | 181 | 3432000
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 138 | 130 | 130 | 130 | 130 | 138 | 149 | 149 | 149 | 143 | 121 |  | 131 | 149 | 149 | 149 | 149 | 149 | 149 | 3468816
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 30 |  | 60 | 76 | 100 | 100 | 100 | 100 | 100 | 2280000
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 136 | 51 | 17 | 17 | 23 | 50 | 88 | 137 | 195 | 199 | 200 | 100 | 100 |  | 130 | 200 | 200 | 200 | 200 | 200 | 200 | 3535200
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 150 | 150 | 150 | 10 | 10 | 10 | 15 | 38 | 75 | 143 | 148 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2959054
118 | Bibiyana-III 400 MW CCPP | 340 | 340 | 340 | 340 | 336 | 340 | 396 | 402 | 402 | 402 | 402 | 387 | 404 | 353 | 403 | 391 | 393 | 352 |  | 374 | 351 | 373 | 400 | 400 | 400 | 388 | 9045000
| Jamalpur 115 MW PP (United) | 106 | 106 | 106 | 106 | 106 | 106 | 115 | 115 | 115 | 88 | 88 | 79 | 79 | 79 | 78 | 78 | 78 | 78 |  | 78 | 78 | 105 | 106 | 106 | 107 | 115 | 2287200
| Anwara 300 MW PP (United) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 69 | 33 | 33 | 33 | 16 | 16 |  | 49 | 16 | 16 | 16 | 16 | 49 | 65 | 777818
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 30 |  | 50 | 50 | 50 | 70 | 100 | 100 | 100 | 2200320
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2801400
| Bhairob 54.5 MW | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 35 | 35 | 17 | 17 |  | 31 | 35 | 36 | 36 | 36 | 36 | 36 | 855720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 2 | 9 |  | 29 | 36 | 23 | 25 | 31 | 26 | 13 | 11 | 2 | [8 empty] | 239867
120 | Eastern Zone Total | 8332 | 8042 | 7767 | 7679 | 7534 | 6946 | 6563 | 6471 | 6429 | 6491 | 6724 | 6904 | 7286 | 7354 | 7570 | 7406 | 6732 | 6444 |  | 7545 | 8091 | 8075 | 8420 | 8294 | 8406 | 8436 | 179891047
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 0 | [13 empty] | 4 | 2 | 7 |  | 21 | 23 | 20 | 20 | 20 | 20 | 20 | 150720
| Khulna 225 MW CCPP | [21 empty] | 60 | 155 | 155 | 158 | 158 | 598179
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 35 | 35 | 0 |  |  | 10 | 17 | 45 | 80 | 105 | 105 | 105 | 35 | 35 |  | 80 | 105 | 105 | 105 | 105 | 105 | 105 | 1648320
130
131
132 | United Payra Power Ltd. | 35 | 17 | 0 | [16 empty] | 16 | 35 | 35 | 35 | 35 | 35 | 35 | 292800
133 | Bhola Nutan Biddut BD LTD (GAS) | 219 | 219 | 219 | 219 | 186 | 219 | 221 | 223 | 221 | 221 | 220 | 218 | 218 | 218 | 216 | 217 | 215 | 150 |  | 194 | 206 | 222 | 221 | 221 | 221 | 220 | 5153045
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [25 empty] | 0 | 0
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 11 | 11 | 10 | 10 | 11 | 11 | 12 | 13 |  | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 283301
| Bhola 225 MW CCPP | 88 | 88 | 87 | 88 | 88 | 88 | 89 | 89 | 89 | 88 | 88 | 89 | 89 | 88 | 88 | 88 | 88 | 88 |  | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 2136070
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 30 | 31 | 31 | 26 | 23 | 20 | 21 | 22 | 25 | 25 | 25 | 25 | 26 | 25 | 22 | 25 |  | 31 | 31 | 32 | 31 | 33 | 31 | 30 | 636778
141 | Noapara 100 MW PP (Bangla Trac) | 70 | 20 | 0 | [16 empty] | 2 | 100 | 95 | 100 | 100 | 100 | 100 | 644160
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 681 | 673 | 679 | 679 | 679 | 680 | 679 | 684 | 684 | 684 | 683 | 684 | 517 | 446 | 447 | 446 | 446 | 446 |  | 446 | 446 | 446 | 446 | 682 | 531 | 446 | 14089455
147 | Bheramara 410 MW CCPP | 410 | 410 | 410 | 410 | 410 | 320 | 320 | 320 | 320 | 370 | 365 | 390 | 355 | 355 | 375 | 355 | 355 | 370 |  | 370 | 410 | 410 | 410 | 370 | 365 | 355 | 9167616
148 | Payra 1320 MW | 500 | 480 | 420 | 420 | 400 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 350 | 360 | 390 | 390 | 370 | 370 |  | 400 | 480 | 490 | 520 | 530 | 540 | 550 | 10718700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 153 | 153 | 153 | 153 | 156 | 156 | 155 | 153 | 155 | 154 | 150 | 150 | 152 | 151 | 151 | 152 | 152 | 150 |  | 151 | 152 | 153 | 155 | 151 | 152 | 154 | 3773400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 50 | 50 | 50 | 0 | [15 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 423200
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 4 | 4 | 4 | 4 | 5 | 4 | 3 | 3 | 2 | 0 | [8 empty] | 40320
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 144 | 138 | 114 | 116 | 117 | 93 | 98 | 95 | 98 | 117 | 122 | 128 | 126 | 112 | 124 | 123 | 114 | 104 |  | 97 | 130 | 133 | 122 | 132 | 131 | 144 | 2967700
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
Sirajgonj 225 MW CCPP Unit-2 (Gas)
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 199 | 198 | 191 | 192 | 190 | 154 | 167 | 176 | 180 | 179 | 177 | 173 | 189 | 188 | 188 | 187 | 177 | 171 |  | 168 | 200 | 206 | 190 | 186 | 195 | 202 | 4733100
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 400 | 407 | 404 | 397 | 375 | 345 | 353 | 354 | 352 | 373 | 400 | 396 | 403 | 348 | 347 | 298 | 345 | 353 |  | 400 | 417 | 400 | 405 | 393 | 408 | 408 | 9099636
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 26 | 26 | 26 | 0 | [15 empty] | 5 | 17 | 35 | 28 | 28 | 27 | 27 | 228035
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 489120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 253170
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 0 | [15 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 334210
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | 23 | 16 | 0 | [16 empty] | 26 | 30 | 31 | 30 | 30 | 30 | 30 | 176330
168 | Santahar 50 MW Peaking PP | 32 | 32 | 32 | 26 | 0 | [14 empty] | 29 | 32 | 32 | 31 | 31 | 31 | 31 | 297010
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 8 |  | 10 | 10 | 30 | 42 | 52 | 52 | 52 | 1117920
170 | Chapainawabganj 100 MW Peaking PP | 93 | 93 | 93 | 93 | 0 | [14 empty] | 78 | 94 | 94 | 94 | 94 | 94 | 94 | 884600
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 50 | 180 | 100 | 100 |  |  | 0 | 342930
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 35 | 0 |  |  | 1 | 30 | 36 | 72 | 94 | 94 | 35 | 35 | 35 |  | 50 | 60 | 78 | 94 | 94 | 94 | 94 | 1591296
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 0 | [6 empty] | 20 | 35 | 35 |  |  |  |  | 50 | 90 | 95 | 95 | 95 | 95 | 95 | 1108224
173 | Rangpur 20 MW GTPP |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 100 | 50 | 34 | 34 | 65 | 70 | 70 | 78 | 90 | 92 | 113 | 39 | 35 |  | 96 | 97 | 113 | 113 |  |  | 54 | 1813142
177 | Sympa Solar Power 8MW | [9 empty] | 1 | 7 | 7 | 7 | 5 | 5 | 4 | 2 | 1 | [8 empty] | 41446
178
178