## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-08-09 | Monday
|  |  | Date (day): | 2021-08-09 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14059.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14879 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-08-08 | 2021-08-09 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 185 | 185
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 341 | 281 | 280 | 280 |  | 132 | ST Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 346 | 298 | 280 | 280 | 80 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 285 | 285 | 285 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 74 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 330 | 332 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 50 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 52 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 64 | 133 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 35 | 35 |  | 20 | Engine problem
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 48 | 53 | 49 | 49 |  | 31 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 16 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 130 | 275 | 285 | 285
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 21 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 25 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 101 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 98 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 70 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 53 | 75 | 75 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 2797 | 3397 | 3672 | 3928 | 767 | 943
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 13 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 121 | 120 | 120 | 120 | 110 |  | Low water level
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 51 | 51 | 51 | 51 |  | Fuel shortage
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 20 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 13 | 5 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 77 | 90 | 97 | 97 |  | 11 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 6 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 0 | 16 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 50 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 116 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 930 | 1106 | 1499 | 1589 | 301 | 484
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 |  |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 215 | 215 | 215 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 260 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 285 | 265 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 54 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 16 | 36 | 36 | 36 | 159 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 148 | 150 | 150 | 150
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 138 | 137 | 137 | 137 |  | 26 | Machine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 85 | 136 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 142 | 138 | 163
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 0 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 49 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 13 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 50 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 114 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 107 | 117 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1580 | 2042 | 2260 | 2385 | 423 | 102
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 159 | 140 | 150 | 52 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 191 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 111 | 111 | 112 | 112
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 30 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 23 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 446 | 512 | 529.6 | 513 | 52 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 30 | 30 |  | 60 | GT-4 under S/D
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 159 | 160 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 62 | 64 | 62 | 62
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 145 | 145 | 145 | 145 |  | 86 | ST Under maint.
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 352 | 367 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 0 | 0 | 0 | 0 |  | 383 | Under maint. |  | 2021-11-08
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1374 | 1441 | 1542 | 1542 | 170 | 656
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 693 | 546 | 699 | 699
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 15 | 0 | 20 |  | 34 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 100 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 410 | 380 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1065 | 1276 | 1559 | 1709 | 0 | 83
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 24 | 30 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 88 | 88 | 89 | 89 |  | 105 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 10 | 12 | 12 | 83 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 350 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 222 | 200 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 695 | 875 | 1236 | 1236 | 83 | 105
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 0 | 26 |  | 45 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 35 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 35 | 35 |  | 15 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 64 | 124 | 0 | 140 | 70 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 165 | 178 | 200 | 210 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 151 | 165 | 200 | 200 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 344 | 394 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 22 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 95 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 94 | 94 |  | 19 | Engine problem
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 95 | 95 | 95 |  | 18 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 0 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 983 | 1391 | 1488 | 1691 | 290 | 136
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 155 | 151 | 153 | 153 | 121 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 99 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 5 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 260 | 250 | 274 | 286 | 121 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 10130 | 12290 | 14059.6 | 14879 | 2207 | 2786
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9601.6574 | 11649 | 13326.3043 | 14102.9675
| A. |  | 2021-08-08 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12290 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9118 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12290 | MW
| 3 | Day peak Generation : |  |  | 10130 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11649 | MW
| 4 | Evening peak Generation : |  |  | 12290 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 257.5292 | MKWHr | By Solar | 0.45009 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 155.0689 | MKWHr |  | By Oil: | 67.4643 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 14.9675 | MKWHr |  | By Hydro: | 2.7711 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2207 | MW | Dhaka | 3884 | 3884 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2786 | MW | Chittagong | 1137 | 1137 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4993 | MW | Khulna | 1523 | 1523 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1196.09 | MMCFD |  |  | Rajshahi | 1271 | 1271 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 169963559.386 | ii) Oil : | Taka | 465586814.49 | Comilla | 1158 | 1158 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 69563027 | Total | Taka | 705113400.876 | Mymensingh | 1038 | 1038 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.376 | MKWHr. | Sylhet | 493 | 493 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -368 | MW (E to W) at | 21:00 | hrs | Barisal | 333 | 333 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -452 | MW at | 2:00 | hrs | Rangpur | 812 | 812 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.4° C |  |  | Total | 11649 | 11649 |  | 0
| B. |  | 2021-08-09 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 33.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14879 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10900 | MW
| 4 | Reserve(Generation end) |  |  |  | 1879 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 272.4068 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9504 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 13.9302 | MKWHr. | ii) HVDC Flow at Peak Time |  | 546 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8771 | MKWHr. | iii) Maximum HVDC Flow : |  | 693 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 87.04 |  | (b) Today: | 87.63 |  | (c) Rule Curve: |  | 91.56
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-08-08
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 392 | 348 |  | 0 | 240 | 270 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 48 | 100 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 97 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 270 | 216 | 16 | 135 | 23 | 0 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 30 | 21 | 126 | 181 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 62 | 70 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 277 | 0 | 0 | 183 | 0 | 70 | 0 | 100 | 200 | 150 | 402 | 112 | 105 | 105 | 0 | 33 | 0 | 110 | 17 | 119 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 559 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 35 | 0 | 0 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 117 | 0 | 183 | 0 | 11 | 0 | 180 | 0 | 395 | 105 | 0 | 94 | 0 | 106 | 0 | 0 | 95 | 490 | 221 | 0 | 0 | 0 |  | 8140 | 3383 | 11523 | 4684 | 559 | 1943 | 3275 | 640 | 118 | 178 | 126 | 0 | 0 | 86.91
2:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 391 | 349 |  | 0 | 240 | 280 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 97 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 270 | 215 | 16 | 137 | 23 | 0 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 30 | 21 | 122 | 194 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 61 | 81 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 11 | 0 | 232 | 0 | 0 | 183 | 0 | 26 | 0 | 100 | 155 | 150 | 402 | 112 | 105 | 105 | 0 | 16 | 0 | 105 | 0 | 119 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 36 | 0 |  | 549 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 115 | 0 | 211 | 0 | 11 | 0 | 185 | 0 | 408 | 35 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 490 | 222 | 0 | 0 | 0 |  | 7879 | 3224 | 11103 | 4724 | 549 | 1968 | 2933 | 642 | 117 | 48 | 122 | 0 | 0 | 86.94
3:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 392 | 343 |  | 0 | 240 | 280 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 97 | 0 | 20 | 40 | 0 | 0 | 80 | 270 | 300 | 214 | 16 | 137 | 23 | 21 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 30 | 21 | 118 | 194 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 62 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 125 | 0 | 0 | 182 | 0 | 0 | 0 | 100 | 100 | 150 | 402 | 112 | 105 | 105 | 0 | 0 | 0 | 110 | 0 | 119 | 100 | 0 | 53 | 0 | 162 | 116 | 0 | 17 | 0 |  | 547 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 106 | 0 | 216 | 0 | 11 | 0 | 178 | 0 | 403 | 35 | 0 | 94 | 0 | 106 | 0 | 0 | 35 | 470 | 221 | 0 | 0 | 0 |  | 7641 | 3134 | 10775 | 4754 | 547 | 1998 | 2602 | 623 | 117 | 16 | 118 | 0 | 0 | 86.97
4:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 393 | 342 |  | 0 | 240 | 260 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 24 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 97 | 0 | 20 | 40 | 0 | 0 | 80 | 265 | 305 | 214 | 16 | 135 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 30 | 21 | 116 | 199 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 159 | 62 | 81 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 162 | 0 | 0 | 0 | 100 | 100 | 150 | 402 | 112 | 72 | 105 | 0 | 0 | 0 | 110 | 0 | 118 | 100 | 0 | 53 | 0 | 162 | 116 | 0 | 17 | 0 |  | 547 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 152 | 0 | 0 | 90 | 0 | 216 | 0 | 11 | 0 | 186 | 0 | 404 | 17 | 0 | 35 | 0 | 90 | 0 | 0 | 35 | 470 | 221 | 0 | 0 | 0 |  | 7455 | 3033 | 10488 | 4744 | 547 | 2023 | 2303 | 622 | 117 | 16 | 116 | 0 | 0 | 87
5:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 392 | 347 |  | 0 | 240 | 288 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 24 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 97 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 300 | 214 | 16 | 138 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 30 | 21 | 116 | 208 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 161 | 61 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 17 | 150 | 402 | 112 | 72 | 105 | 0 | 0 | 0 | 110 | 0 | 115 | 100 | 0 | 34 | 0 | 90 | 116 | 0 | 17 | 0 |  | 547 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 124 | 0 | 216 | 0 | 11 | 0 | 185 | 0 | 411 | 17 | 0 | 35 | 0 | 35 | 0 | 0 | 35 | 440 | 221 | 0 | 0 | 0 |  | 7260 | 2990 | 10250 | 4784 | 547 | 2043 | 2036 | 591 | 117 | 16 | 116 | 0 | 0 | 87.02
6:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 391 | 347 |  | 0 | 240 | 275 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 8 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 21 | 25 | 24 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 92 | 0 | 20 | 40 | 0 | 0 | 80 | 260 | 300 | 215 | 16 | 137 | 23 | 55 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 30 | 21 | 110 | 200 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 110 | 159 | 62 | 81 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 40 | 17 | 50 | 400 | 112 | 35 | 17 | 0 | 0 | 0 | 100 | 0 | 8 | 20 | 0 | 17 | 2 | 17 | 116 | 0 | 13 | 1 |  | 548 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 116 | 0 | 191 | 0 | 11 | 0 | 179 | 0 | 323 | 17 | 0 | 43 | 0 | 70 | 0 | 0 | 70 | 430 | 222 | 0 | 0 | 0 |  | 6550 | 2910 | 9460 | 4723 | 548 | 1889 | 1473 | 581 | 117 | 16 | 110 | 3 | 0 | 87.04
7:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 375 | 346 |  | 0 | 240 | 290 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 21 | 25 | 24 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 90 | 0 | 20 | 37 | 0 | 0 | 80 | 280 | 315 | 214 | 16 | 137 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 8 | 30 | 15 | 98 | 196 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 110 | 160 | 61 | 78 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 20 | 17 | 20 | 401 | 112 | 17 | 17 | 0 | 0 | 0 | 51 | 0 | 8 | 20 | 0 | 17 | 7 | 17 | 53 | 0 | 17 | 2 |  | 547 | 0 | 400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 109 | 0 | 174 | 0 | 11 | 0 | 176 | 0 | 280 | 17 | 0 | 90 | 0 | 107 | 0 | 0 | 95 | 410 | 180 | 0 | 0 | 1 |  | 6272 | 2930 | 9202 | 4699 | 547 | 1806 | 1364 | 561 | 117 | 0 | 98 | 10 | 0 | 87.06
8:00 | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 368 | 346 |  | 0 | 240 | 290 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 85 | 0 | 0 | 5 | 0 | 0 | 80 | 280 | 315 | 214 | 16 | 138 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 30 | 11 | 104 | 182 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 110 | 160 | 63 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 0 | 38 | 17 | 30 | 402 | 112 | 17 | 18 | 1 | 0 | 0 | 51 | 0 | 8 | 40 | 0 | 17 | 17 | 17 | 53 | 0 | 17 | 3 |  | 547 | 0 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 151 | 0 | 0 | 104 | 0 | 178 | 0 | 11 | 0 | 176 | 0 | 280 | 17 | 0 | 94 | 0 | 107 | 0 | 0 | 95 | 390 | 180 | 0 | 0 | 0 |  | 6228 | 2890 | 9118 | 4601 | 547 | 1775 | 1412 | 541 | 117 | 0 | 104 | 21 | 0 | 87.08
9:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 368 | 342 |  | 0 | 240 | 285 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 24 | 33 | 33 | 0 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 80 | 0 | 20 | 3 | 0 | 0 | 80 | 270 | 305 | 217 | 16 | 138 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 18 | 8 | 30 | 11 | 108 | 167 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 63 | 84 | 0 | 145 | 0 | 0 | 10 | 305 | 24 | 0 | 0 | 0 | 0 | 0 | 45 | 0 | 0 | 5 | 50 | 20 | 56 | 403 | 111 | 20 | 51 | 2 | 0 | 0 | 60 | 0 | 23 | 50 | 0 | 20 | 1 | 30 | 75 | 0 | 17 | 8 |  | 547 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 101 | 0 | 180 | 0 | 11 | 0 | 180 | 0 | 290 | 17 | 0 | 94 | 0 | 107 | 0 | 2 | 95 | 370 | 182 | 0 | 0 | 0 |  | 6413 | 2878 | 9291 | 4547 | 547 | 1844 | 1584 | 525 | 118 | 0 | 108 | 18 | 0 | 87.1
10:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 349 | 342 |  | 0 | 240 | 280 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 23 | 33 | 33 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 78 | 0 | 20 | 2 | 0 | 0 | 80 | 265 | 295 | 215 | 16 | 139 | 20 | 0 | 0 | 35 | 0 | 0 | 0 | 18 | 8 | 30 | 11 | 106 | 156 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 130 | 160 | 64 | 84 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 47 | 0 | 0 | 45 | 0 | 39 | 12 | 50 | 51 | 135 | 400 | 111 | 55 | 51 | 1 | 0 | 0 | 68 | 0 | 55 | 50 | 0 | 53 | 10 | 54 | 115 | 0 | 17 | 8 |  | 693 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 150 | 0 | 0 | 78 | 0 | 168 | 0 | 11 | 0 | 130 | 0 | 290 | 17 | 0 | 94 | 0 | 107 | 0 | 2 | 95 | 350 | 182 | 0 | 0 | 0 |  | 6668 | 2909 | 9577 | 4413 | 693 | 1731 | 1981 | 500 | 120 | 0 | 106 | 33 | 0 | 87.12
11:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 341 | 342 |  | 0 | 240 | 250 | 0 | 0 | 55 | 337 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 23 | 33 | 33 | 0 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 77 | 0 | 20 | 2 | 0 | 0 | 80 | 260 | 285 | 217 | 16 | 135 | 20 | 51 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 30 | 13 | 112 | 156 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 130 | 159 | 64 | 81 | 0 | 145 | 0 | 0 | 10 | 295 | 24 | 5 | 0 | 62 | 0 | 0 | 50 | 0 | 82 | 11 | 90 | 51 | 155 | 400 | 112 | 70 | 70 | 3 | 0 | 0 | 110 | 0 | 92 | 50 | 0 | 53 | 5 | 72 | 116 | 0 | 17 | 19 |  | 693 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 38 | 0 | 170 | 0 | 11 | 0 | 130 | 0 | 293 | 17 | 0 | 94 | 0 | 102 | 0 | 5 | 95 | 350 | 182 | 0 | 0 | 0 |  | 6936 | 2871 | 9807 | 4350 | 693 | 1785 | 2201 | 503 | 120 | 0 | 112 | 43 | 0 | 87.14
12:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 341 | 346 |  | 0 | 240 | 270 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 55 | 35 | 0 | 25 | 23 | 33 | 33 | 16 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 77 | 0 | 20 | 2 | 0 | 0 | 80 | 260 | 285 | 182 | 16 | 138 | 20 | 55 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 0 | 13 | 112 | 155 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 130 | 159 | 62 | 84 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 130 | 0 | 0 | 100 | 0 | 98 | 13 | 90 | 85 | 148 | 352 | 111 | 70 | 105 | 6 | 0 | 0 | 110 | 0 | 107 | 50 | 0 | 53 | 30 | 108 | 116 | 0 | 17 | 14 |  | 693 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 64 | 0 | 165 | 0 | 11 | 0 | 151 | 0 | 344 | 17 | 0 | 94 | 0 | 100 | 0 | 5 | 95 | 350 | 222 | 0 | 0 | 0 |  | 7127 | 3003 | 10130 | 4272 | 693 | 1871 | 2488 | 505 | 121 | 0 | 112 | 68 | 0 | 87.16
13:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 341 | 342 |  | 0 | 240 | 290 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 49 | 55 | 35 | 16 | 25 | 27 | 33 | 33 | 25 | 0 | 60 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 77 | 0 | 20 | 6 | 0 | 0 | 80 | 295 | 300 | 182 | 16 | 138 | 20 | 55 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 20 | 110 | 139 | 8 | 19 | 2 | 43 | 30 | 50 | 0 | 163 | 159 | 63 | 84 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 5 | 0 | 145 | 0 | 0 | 70 | 0 | 97 | 19 | 100 | 85 | 150 | 238 | 111 | 70 | 105 | 5 | 0 | 0 | 110 | 0 | 108 | 60 | 0 | 53 | 41 | 108 | 116 | 0 | 17 | 15 |  | 693 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 109 | 0 | 166 | 0 | 11 | 0 | 166 | 0 | 407 | 17 | 0 | 94 | 0 | 100 | 0 | 5 | 95 | 350 | 222 | 0 | 0 | 2 |  | 7218 | 3130 | 10348 | 4309 | 693 | 1978 | 2544 | 505 | 120 | 0 | 110 | 89 | 0 | 87.18
14:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 324 | 316 |  | 0 | 240 | 285 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 17 | 25 | 27 | 33 | 33 | 25 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 77 | 0 | 20 | 3 | 0 | 0 | 80 | 290 | 300 | 194 | 16 | 138 | 23 | 54 | 0 | 35 | 0 | 0 | 25 | 19 | 11 | 33 | 20 | 124 | 138 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 130 | 156 | 61 | 84 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 0 | 0 | 143 | 0 | 0 | 70 | 0 | 98 | 17 | 100 | 85 | 150 | 240 | 111 | 70 | 105 | 1 | 0 | 0 | 108 | 17 | 106 | 90 | 0 | 53 | 43 | 112 | 116 | 0 | 17 | 14 |  | 618 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 108 | 0 | 172 | 0 | 11 | 0 | 175 | 0 | 348 | 17 | 0 | 94 | 0 | 100 | 0 | 0 | 95 | 370 | 221 | 0 | 0 | 1 |  | 7175 | 3053 | 10228 | 4296 | 618 | 1865 | 2607 | 525 | 117 | 0 | 124 | 76 | 0 | 87.2
15:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 368 | 302 |  | 0 | 240 | 270 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 82 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 17 | 25 | 25 | 33 | 0 | 25 | 0 | 55 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 77 | 0 | 20 | 3 | 0 | 0 | 80 | 260 | 265 | 182 | 16 | 134 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 19 | 11 | 33 | 21 | 130 | 142 | 8 | 19 | 0 | 43 | 30 | 47 | 0 | 163 | 158 | 62 | 83 | 0 | 145 | 0 | 0 | 10 | 305 | 24 | 0 | 0 | 145 | 0 | 0 | 99 | 0 | 102 | 9 | 100 | 94 | 150 | 340 | 111 | 70 | 105 | 3 | 0 | 0 | 106 | 52 | 107 | 90 | 0 | 65 | 21 | 162 | 116 | 0 | 17 | 17 |  | 547 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 106 | 0 | 175 | 0 | 11 | 0 | 164 | 0 | 408 | 45 | 0 | 94 | 0 | 99 | 0 | 3 | 95 | 370 | 221 | 0 | 0 | 1 |  | 7414 | 3031 | 10445 | 4344 | 547 | 1953 | 2777 | 525 | 115 | 0 | 130 | 54 | 0 | 87.22
16:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 260 | 318 |  | 0 | 240 | 270 | 0 | 0 | 55 | 327 | 0 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 25 | 33 | 17 | 25 | 0 | 55 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 84 | 0 | 20 | 3 | 0 | 0 | 80 | 260 | 265 | 182 | 16 | 133 | 20 | 52 | 0 | 43 | 0 | 0 | 40 | 21 | 11 | 33 | 21 | 124 | 145 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 160 | 64 | 83 | 0 | 145 | 0 | 0 | 10 | 285 | 24 | 5 | 0 | 145 | 0 | 0 | 120 | 0 | 115 | 10 | 100 | 100 | 150 | 331 | 115 | 70 | 105 | 2 | 0 | 0 | 110 | 52 | 103 | 90 | 0 | 75 | 28 | 154 | 116 | 0 | 17 | 8 |  | 547 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 3 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 154 | 0 | 0 | 103 | 0 | 156 | 0 | 11 | 0 | 195 | 0 | 380 | 53 | 0 | 94 | 0 | 106 | 0 | 2 | 95 | 370 | 202 | 0 | 0 | 1 |  | 7367 | 3010 | 10377 | 4241 | 547 | 1903 | 2869 | 524 | 115 | 3 | 124 | 51 | 0 | 87.24
17:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 267 | 314 |  | 0 | 240 | 260 | 0 | 0 | 30 | 329 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 25 | 33 | 33 | 25 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 84 | 0 | 20 | 6 | 0 | 0 | 80 | 260 | 265 | 182 | 16 | 133 | 20 | 52 | 0 | 43 | 0 | 0 | 43 | 21 | 11 | 33 | 21 | 120 | 157 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 163 | 158 | 63 | 81 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 95 | 0 | 0 | 60 | 0 | 90 | 3 | 50 | 68 | 150 | 322 | 111 | 70 | 105 | 0 | 0 | 0 | 110 | 17 | 99 | 30 | 0 | 55 | 14 | 72 | 116 | 0 | 17 | 3 |  | 547 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 8 | 0 | 0 | 156 | 0 | 0 | 109 | 0 | 159 | 0 | 11 | 0 | 177 | 0 | 392 | 35 | 0 | 94 | 0 | 109 | 0 | 2 | 95 | 350 | 209 | 0 | 0 | 0 |  | 6853 | 2990 | 9843 | 4260 | 547 | 1914 | 2353 | 506 | 117 | 4 | 120 | 22 | 0 | 87.26
18:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 282 | 274 |  | 0 | 240 | 290 | 0 | 0 | 30 | 270 | 0 | 0 | 0 | 64 | 16 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 19 | 25 | 25 | 33 | 33 | 25 | 0 | 58 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 84 | 0 | 20 | 2 | 0 | 0 | 80 | 275 | 285 | 160 | 16 | 136 | 23 | 55 | 0 | 43 | 0 | 0 | 50 | 21 | 11 | 33 | 21 | 112 | 158 | 8 | 19 | 0 | 43 | 30 | 14 | 0 | 110 | 161 | 64 | 30 | 0 | 110 | 0 | 0 | 10 | 270 | 18 | 11 | 0 | 95 | 0 | 0 | 60 | 0 | 70 | 1 | 50 | 51 | 150 | 322 | 111 | 70 | 105 | 0 | 0 | 0 | 110 | 17 | 65 | 30 | 0 | 53 | 4 | 72 | 116 | 0 | 17 | 1 |  | 547 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 88 | 26 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 8 | 16 | 0 | 22 | 0 | 8 | 0 | 0 | 154 | 0 | 0 | 101 | 0 | 156 | 0 | 11 | 0 | 179 | 0 | 402 | 35 | 0 | 50 | 0 | 70 | 0 | 1 | 35 | 340 | 161 | 0 | 0 | 0 |  | 6585 | 2728 | 9313 | 4170 | 547 | 1686 | 2147 | 494 | 118 | 32 | 112 | 7 | 0 | 87.28
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 280 | 318 |  | 0 | 240 | 290 | 0 | 0 | 32 | 330 | 0 | 0 | 0 | 102 | 48 | 43 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 17 | 33 | 33 | 33 | 0 | 59 | 60 | 100 | 120 | 2 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 3 | 90 | 7 | 20 | 8 | 0 | 0 | 80 | 285 | 290 | 213 | 16 | 137 | 20 | 56 | 0 | 43 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 136 | 158 | 8 | 19 | 0 | 43 | 30 | 23 | 0 | 163 | 160 | 63 | 81 | 0 | 135 | 0 | 0 | 10 | 290 | 18 | 11 | 28 | 145 | 52 | 0 | 100 | 62 | 107 | 0 | 100 | 73 | 150 | 380 | 111 | 73 | 105 | 0 | 16 | 0 | 110 | 80 | 88 | 50 | 0 | 60 | 0 | 115 | 116 | 0 | 17 | 0 |  | 546 | 0 | 400 | 0 | 0 | 55 | 0 | 0 | 22 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 34 | 4 | 90 | 35 | 0 | 28 | 16 | 30 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 105 | 0 | 162 | 0 | 11 | 12 | 180 | 0 | 412 | 105 | 0 | 56 | 0 | 97 | 0 | 0 | 75 | 400 | 161 | 0 | 7 | 0 |  | 7756 | 3345 | 11101 | 4471 | 546 | 1884 | 2982 | 551 | 119 | 412 | 136 | 0 | 0 | 87.36
19:30 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 282 | 312 |  | 0 | 240 | 275 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 102 | 82 | 72 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 17 | 33 | 33 | 50 | 0 | 59 | 60 | 100 | 120 | 16 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 90 | 30 | 20 | 9 | 0 | 0 | 80 | 260 | 265 | 214 | 16 | 137 | 23 | 56 | 0 | 43 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 144 | 159 | 8 | 19 | 0 | 44 | 30 | 53 | 0 | 163 | 159 | 64 | 81 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 11 | 100 | 245 | 55 | 25 | 186 | 97 | 140 | 0 | 100 | 136 | 150 | 367 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 117 | 50 | 0 | 74 | 0 | 162 | 116 | 0 | 17 | 0 |  | 546 | 0 | 405 | 0 | 0 | 100 | 0 | 0 | 26 | 0 | 0 | 88 | 31 | 0 | 0 | 0 | 0 | 34 | 4 | 95 | 35 | 0 | 31 | 34 | 32 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 122 | 0 | 202 | 0 | 10 | 100 | 197 | 0 | 399 | 105 | 0 | 60 | 0 | 99 | 0 | 0 | 95 | 510 | 162 | 0 | 17 | 0 |  | 8466 | 3724 | 12190 | 4512 | 546 | 1897 | 3805 | 662 | 119 | 505 | 144 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 283 | 302 |  | 0 | 240 | 265 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 102 | 98 | 73 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 27 | 33 | 33 | 51 | 0 | 59 | 60 | 100 | 120 | 23 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 90 | 40 | 20 | 8 | 0 | 0 | 80 | 260 | 265 | 215 | 36 | 135 | 23 | 56 | 0 | 43 | 0 | 50 | 43 | 21 | 11 | 33 | 21 | 144 | 158 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 65 | 81 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 11 | 50 | 263 | 21 | 25 | 186 | 100 | 149 | 0 | 100 | 136 | 150 | 368 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 114 | 50 | 0 | 75 | 0 | 162 | 116 | 0 | 17 | 0 |  | 546 | 0 | 410 | 0 | 0 | 100 | 0 | 0 | 19 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 43 | 10 | 95 | 35 | 0 | 31 | 43 | 31 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 123 | 0 | 193 | 0 | 11 | 100 | 197 | 0 | 393 | 105 | 0 | 70 | 0 | 99 | 0 | 0 | 95 | 500 | 202 | 0 | 17 | 0 |  | 8446 | 3771 | 12217 | 4521 | 546 | 1932 | 3777 | 650 | 119 | 528 | 144 | 0 | 0 | 87.33
21:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 298 |  | 0 | 240 | 285 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 102 | 64 | 74 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 90 | 50 | 20 | 13 | 0 | 0 | 80 | 260 | 265 | 215 | 36 | 137 | 23 | 54 | 0 | 43 | 0 | 50 | 49 | 21 | 11 | 33 | 21 | 142 | 159 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 64 | 81 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 11 | 50 | 275 | 21 | 25 | 191 | 101 | 149 | 0 | 100 | 136 | 150 | 367 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 117 | 50 | 0 | 75 | 0 | 162 | 116 | 0 | 35 | 0 |  | 546 | 0 | 410 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 43 | 30 | 95 | 35 | 0 | 31 | 43 | 31 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 124 | 0 | 178 | 0 | 10 | 100 | 165 | 0 | 394 | 105 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 530 | 200 | 0 | 17 | 0 |  | 8498 | 3792 | 12290 | 4475 | 546 | 1937 | 3879 | 681 | 120 | 510 | 142 | 0 | 0 | 87.36
22:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 285 | 283 |  | 0 | 240 | 290 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 102 | 64 | 74 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 96 | 18 | 20 | 35 | 0 | 0 | 80 | 275 | 280 | 213 | 36 | 137 | 23 | 52 | 0 | 43 | 0 | 50 | 51 | 21 | 11 | 33 | 21 | 144 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 163 | 161 | 61 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 275 | 21 | 0 | 191 | 42 | 149 | 0 | 100 | 136 | 150 | 380 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 119 | 50 | 0 | 73 | 0 | 162 | 116 | 0 | 35 | 0 |  | 547 | 0 | 405 | 0 | 0 | 70 | 0 | 0 | 15 | 0 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 43 | 30 | 95 | 35 | 0 | 31 | 43 | 31 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 102 | 0 | 179 | 0 | 11 | 100 | 197 | 0 | 415 | 105 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 550 | 200 | 0 | 17 | 0 |  | 8405 | 3814 | 12219 | 4524 | 547 | 1977 | 3726 | 701 | 120 | 480 | 144 | 0 | 0 | 87.39
23:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 285 | 304 |  | 0 | 240 | 290 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 102 | 64 | 74 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 28 | 33 | 43 | 0 | 61 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 20 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 270 | 280 | 214 | 36 | 139 | 23 | 53 | 0 | 43 | 0 | 50 | 45 | 22 | 11 | 33 | 21 | 142 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 61 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 275 | 0 | 0 | 180 | 42 | 149 | 0 | 100 | 145 | 150 | 380 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 110 | 50 | 0 | 73 | 0 | 162 | 116 | 0 | 35 | 0 |  | 543 | 0 | 380 | 0 | 0 | 70 | 0 | 0 | 15 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 43 | 26 | 95 | 35 | 0 | 30 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 62 | 0 | 194 | 0 | 11 | 100 | 190 | 0 | 416 | 105 | 0 | 94 | 0 | 100 | 0 | 0 | 95 | 550 | 200 | 0 | 17 | 0 |  | 8377 | 3756 | 12133 | 4461 | 543 | 1999 | 3691 | 701 | 121 | 475 | 142 | 0 | 0 | 87.42
24:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 280 | 318 |  | 0 | 240 | 305 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 102 | 64 | 73 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 30 | 28 | 33 | 24 | 0 | 61 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 20 | 96 | 19 | 20 | 39 | 0 | 0 | 80 | 290 | 300 | 212 | 36 | 138 | 23 | 52 | 0 | 43 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 140 | 157 | 8 | 21 | 0 | 43 | 30 | 53 | 0 | 163 | 161 | 61 | 81 | 0 | 145 | 0 | 0 | 10 | 300 | 24 | 11 | 0 | 275 | 0 | 0 | 179 | 0 | 149 | 0 | 100 | 177 | 150 | 398 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 109 | 50 | 0 | 75 | 0 | 162 | 116 | 0 | 36 | 0 |  | 541 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 88 | 29 | 0 | 0 | 0 | 0 | 43 | 26 | 95 | 35 | 0 | 30 | 52 | 31 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 57 | 0 | 192 | 0 | 11 | 0 | 196 | 0 | 414 | 105 | 0 | 94 | 0 | 106 | 0 | 0 | 95 | 520 | 200 | 0 | 17 | 0 |  | 8341 | 3570 | 11911 | 4526 | 541 | 2011 | 3581 | 670 | 121 | 321 | 140 | 0 | 0 | 87.45
KWH | 0 | 0 | 0 | 3402000 | 7314064 | 0 | 0 | 8095848 | 7800000 |  | 0 | 5547000 | 6642735 | 0 | 0 | 1282726 | 7883985 | 0 | 0 | 0 | 1338336 | 692160 | 446104 | 0 | 0 | 0 | 1302840 | 1157545 | 893811 | 311724 | 600000 | 593640 | 786900 | 795900 | 433440 | 0 | 1307089 | 1464000 | 2300000 | 2900000 | 143377 | 0 | 0 | 0 | 0 |  | 593280 | 0 | 299751 | 123000 | 2117760 | 175200 | 465792 | 444480 | 0 | 0 | 1923456 | 6796400 | 6992000 | 4981000 | 518545 | 3263350 | 460152 | 1159680 | 0 | 988432 | 0 | 257984 | 545726 | 477792 | 236880 | 719600 | 478330 | 2877120 | 3933280 | 193920 | 430668 | 4400 | 1030000 | 714840 | 1174200 | 0 | 3669545 | 3657000 | 1492608 | 1803840 | 0 | 3442750 | 0 | 0 | 255600 | 7203000 | 572544 | 178176 | 155328 | 3239235 | 107118 | 54969 | 2872800 | 341367 | 1768464 | 95715 | 1957440 | 2274240 | 3358836 | 8852000 | 2654400 | 1861200 | 2224727 | 21000 | 155564 | 0 | 2519125 | 780900 | 2239440 | 1519680 | 0 | 1400640 | 175880 | 2829600 | 2679709 | 0 | 548280 | 110787 |  | 13930181 | 0 | 9278600 | 0 | 0 | 413859 | 0 | 0 | 110060 | 0 | 0 | 2134052 | 649400 | 0 | 0 | 0 | 0 | 224544 | 106888 | 613640 | 225420 | 0 | 166310 | 1030560 | 208320 | 502560 | 0 | 177048 | 0 | 0 | 3743400 | 0 | 0 | 2494000 | 0 | 4568191 | 0 | 269660 | 478080 | 4547573 | 0 | 8890545 | 1202400 | 0 | 2084256 | 0 | 2323228 | 0 | 29405 | 1985952 | 11224100 | 4910291 | 0 | 108000 | 12900 |  | 178885749 | 78643423 | 257529172 | 109282143 | 13930181 | 45786778 | 64370758 | 14967500 | 2771089 | 3093516 | 2877120 | 450087 | 0
Fuel Cost | 0 | 0 | 0 | 5000940 | 8118611.04 | 0 | 0 | 8176806.48 | 8034000 |  | 0 | 6046230 | 7373435.85 | 0 | 0 | 10851861.96 | 8199344.4 | 0 | 0 | 0 | 12205624.32 | 6810854.4 | 4113078.88 | 0 | 0 | 0 | 9510732 | 8947822.85 | 8812976.46 | 233793 | 450000 | 0 | 0 | 0 | 4191364.8 | 0 | 352914.03 | 395280 | 4163000 | 5249000 | 1331972.33 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2907584.7 | 1174650 | 18424512 | 1387584 | 586897.92 | 1320105.6 | 0 | 0 | 2827480.32 | 5029336 | 6992000 | 4582520 | 668923.05 | 3752852.5 | 519971.76 | 1623552 | 0 | 1690218.72 | 0 | 2605638.4 | 5211683.3 | 606795.84 | 177660 | 1259300 | 358747.5 | 21578400 | 4169276.8 | 1760793.6 | 546948.36 | 70136 | 1689200 | 1143744 | 2090076 | 0 | 4183281.3 | 3803280 | 2940437.76 | 3445334.4 | 0 | 5955957.5 | 0 | 0 | 521424 | 7275030 | 429408 | 135413.76 | 2642129.28 | 24488616.6 | 1818863.64 | 919081.68 | 14938560 | 5707656.24 | 17401685.76 | 1118908.35 | 15953136 | 24675504 | 23679793.8 | 8232360 | 24208128 | 17588340 | 19377372.17 | 0 | 1176063.84 | 0 | 22143108.75 | 7793382 | 19192000.8 | 10121068.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80237842.56 | 0 | 9742530 | 0 | 0 | 5736085.74 | 0 | 0 | 1154529.4 | 0 | 0 | 2411478.76 | 1006570 | 0 | 0 | 0 | 0 | 2209512.96 | 1085982.08 | 5430714 | 1735734 | 0 | 1611543.9 | 9986126.4 | 2020704 | 964915.2 | 0 | 134025.336 | 0 | 0 | 20289228 | 0 | 0 | 2917980 | 0 | 6030012.12 | 0 | 404490 | 8132140.8 | 5320660.41 | 0 | 8801639.55 | 12553056 | 0 | 19779589.44 | 0 | 18028249.28 | 0 | 324925.25 | 14676185.28 | 49273799 | 0 | 0 | 0 | 0 |  | 517191557.6 | 292000249.466 | 809191807.066 | 121887769.566 | 80237842.56 | 48075789.82 | 434013664.91 | 69563027 | 748194.03 | 31573149.58 | 21578400 | 1513969.6 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 341 | 346 |  | 0 | 240 | 270 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 52 | 55 | 35 | 0 | 25 | 23 | 33 | 33 | 16 | 0 | 61 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 77 | 0 | 20 | 2 | 0 | 0 | 80 | 260 | 285 | 182 | 16 | 138 | 20 | 55 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 0 | 13 | 112 | 155 | 8 | 19 | 0 | 43 | 30 | 50 | 0 | 130 | 159 | 62 | 84 | 0 | 145 | 0 | 0 | 10 | 280 | 24 | 5 | 0 | 130 | 0 | 0 | 100 | 0 | 98 | 13 | 90 | 85 | 148 | 352 | 111 | 70 | 105 | 6 | 0 | 0 | 110 | 0 | 107 | 50 | 0 | 53 | 30 | 108 | 116 | 0 | 17 | 14 |  | 693 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 0 | 0 | 155 | 0 | 0 | 64 | 0 | 165 | 0 | 11 | 0 | 151 | 0 | 344 | 17 | 0 | 94 | 0 | 100 | 0 | 5 | 95 | 350 | 222 | 0 | 0 | 0 |  | 10130 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 298 | 0 | 0 | 240 | 285 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 102 | 64 | 74 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 51 | 20 | 90 | 50 | 20 | 13 | 0 | 0 | 80 | 260 | 265 | 215 | 36 | 137 | 23 | 54 | 0 | 43 | 0 | 50 | 49 | 21 | 11 | 33 | 21 | 142 | 159 | 8 | 19 | 0 | 43 | 30 | 53 | 0 | 163 | 160 | 64 | 81 | 0 | 145 | 0 | 0 | 10 | 290 | 24 | 11 | 50 | 275 | 21 | 25 | 191 | 101 | 149 | 0 | 100 | 136 | 150 | 367 | 111 | 105 | 105 | 0 | 16 | 0 | 110 | 114 | 117 | 50 | 0 | 75 | 0 | 162 | 116 | 0 | 35 | 0 |  | 546 | 0 | 410 | 0 | 0 | 100 | 0 | 0 | 15 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 43 | 30 | 95 | 35 | 0 | 31 | 43 | 31 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 124 | 0 | 178 | 0 | 10 | 100 | 165 | 0 | 394 | 105 | 0 | 94 | 0 | 99 | 0 | 0 | 95 | 530 | 200 | 0 | 17 | 0 |  | 12290 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 280 | 280 | 0 | 0 | 240 | 285 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 150 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 24 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 21 | 20 | 0 | 0 | 80 | 330 | 330 | 215 | 36 | 137 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 163 | 150 | 8 | 21 | 0 | 43 | 30 | 51 | 0 | 163 | 160 | 62 | 84 | 0 | 145 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 285 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 150 | 400 | 112 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 0 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 699 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 20 | 60 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 43 | 26 | 95 | 35 | 0 | 35 | 52 | 33 | 22 | 0 | 11 | 0 | 0 | 153 | 10 | 10 | 140 | 0 | 210 | 0 | 12 | 100 | 200 | 0 | 400 | 105 | 200 | 94 | 100 | 113 | 0 | 0 | 95 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 185 | 310 | 0 | 0 | 280 | 280 | 0 | 0 | 240 | 285 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 133 | 85 | 0 | 0 | 0 | 54 | 55 | 35 | 20 | 25 | 24 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 51 | 100 | 97 | 50 | 21 | 5 | 0 | 0 | 80 | 330 | 330 | 215 | 36 | 137 | 23 | 55 | 0 | 43 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 138 | 140 | 8 | 21 | 1.6 | 43 | 30 | 51 | 0 | 163 | 160 | 62 | 84 | 0 | 145 | 18 | 0 | 10 | 341 | 24 | 11 | 100 | 285 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 150 | 400 | 112 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 0 | 75 | 50 | 162 | 116 | 0 | 17 | 30 |  | 699 | 0 | 380 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 43 | 0 | 95 | 35 | 0 | 35 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 |  | 0 | 200 | 0 | 12 | 50 | 200 | 0 | 400 | 105 | 100 | 94 | 100 | 113 | 0 | 8 | 95 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 285 | 334 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 24 | 33 |  | 0 | 0 | 57 | 60 | 100 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 90 | 0 | 20 | 5 | 0 | 0 | 80 | 260 | 270 | 215 | 36 | 137 | 17 | 52 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 21 | 106 | 173 | 8 | 21 | 1 | 43 | 30 | 50 | 0 | 130 | 160 | 61 | 78 | 0 | 90 | 0 | 0 | 10 | 295 | 24 | 11 | 0 | 15 | 0 | 0 | 8 | 0 | 35 | 10 | 50 | 85 | 142 | 315 | 112 | 17 | 51 | 1 | 16 | 0 | 110 | 0 | 109 | 50 | 0 | 75 | 13 | 162 | 116 | 0 | 17 | 9 | 0 | 686 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 5 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 179 | 0 | 389 | 53 | 0 | 35 | 0 | 49 | 0 | 1 | 0 | 420 | 160 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 9118 | 8:00
| Highest Generation |  | 12290 | 21:00
| Day Peak Generation |  | 10130 | 12:00
| Evening Peak Generation |  | 12290 | 21:00
| HVDC Max Flow |  | 693 | 10:00
| HVDC EvPeak Flow |  | 546 | 21:00
| Load factor L.F |  | 87.31%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-08-09
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-08-08 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10130 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9504 | MW
Evening Peak Generation : |  | 12290 | MW Hour : | 21:00 | Available Max Generation : |  | 14879 | MW
E.P. Demand (at gen end) : |  | 12290 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12290 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1879 | MW
Total Gen. (MKWH) : |  | 257.5292 | System Load Factor : | 87.31% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -452 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-08-09
Actual : | 87.63 | Ft.(MSL) , | Rule curve : | 91.56 | Ft.( MSL )
Gas Consumed : | Total = | 1196.09 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 169963559.386
: |  | Coal : | 69563027 | Oil : | 465586814.49 | Total : | 705113400.876
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4580.032 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1562.047 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1400.3589 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1265.6323 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1143.5738 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 922.8351 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 510.1068 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.4492 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 711.7645 |  |  | 0 | 0%
Total | 0 |  | 12333.7996 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-4
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Chatak 132/33 kV T-3 transformer was under shut down from 08:43 to 09:49 for C/M.
b) Jamalpur 132/33 kV T-4 transformer was under shut down from 10:35 to 12:16 for D/W.
c) Aminbazar 230/132 T01 transformer was under shut down from 10:35 to 12:16 for D/W.
d) Sirajganj 132/33 T-1 transformer was under shut down from 08:39 to 09:19 for C/M by PBS. |  |  |  |  | About 15 MW power interruption occurred under Sirajganj S/S
area from 08:39 to 09:19.
e) Bogura-Sirajganj 230 kV Ckt-2 was under shut down from 14:20 to 17:03 for C/M.
f) Chapainawabganj 132/22 kV T-1 transformer was charged at 14:52.
g) Keraniganj-Lalbagh 132 kV Ckt-1 charged at 13:46 from Keraniganj end.
h) Keraniganj-Lalbagh 132 kV Ckt-2 charged at 13:42 from Keraniganj end.
i) Keraniganj-Lalbagh 132 kV Ckt-3 charged at 13:47 from Keraniganj end.
j) Keraniganj-Kamrangichar 132 kV Ckt charged at 13:44 from Keraniganj end.
k) Rangpur Confidence-Mithapukur 132 kV Ckt-2 was shut down at 17:02 for SF6 gas pressure low at
Rangpur Confidence GIS.
l) Bogura 132/33 kV T-1 transformer was under shut down from 16:12 to 17:09 for C/M by NESCO. |  |  |  |  | About 60 MW power interruption occurred under Bogura S/S
area from 16:12 to 17:09.
m) Kabirpur 132 kV Bus-Coupler open at 21:23.
n) Haripur EGCB 412 MW ST was shut down at 15:45 due to leakage.
o) Sirajganj unit-1 Forced shut down at 00:19(09/8/2021) due to low gas pressure.
p) Sirajganj Unit-2 CCPP tripped at 00:31(09/8/2021) due to tripping of GBS and GT was synchronized at
02:06 and ST was synchronized at 03:30.
q) Nawabganj 132/33 kV T-2 transformer was under shut down from 07:12(09/8/2021) to 08:42 for D/W. |  |  |  |  | About 10 MW power interruption occurred under Nawabganj S/S
area from 07:12(09/8/2021) to 08:42.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-08-08 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 3402000
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7314064 | Gas shortage
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 281 | 8095848 | FGMO
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 298 | 7800000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5547000 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6642735 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1282726
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 74 | 446104 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 311724
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 332 | 7883985
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1338336
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1302840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 64 | 692160 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1157545
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 893811 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1193640 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 786900
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 795900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 433440
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 275 | 3239235 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 21 | 107118 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 25 | 54969 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 101 | 341367
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1768464
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1861200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 75 | 1400640 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 2829600
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 110787
| Dhaka area Total |  |  |  | 5819 | 3397 | 69034138
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 143377
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 95715
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 175200
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 120 | 2771089 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2224727
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 51 | 299751 | Fuel shortage
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 20 | 123000 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1957440
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 465792
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 13 | 444480
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 2117760 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 21000
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 16 | 155564 | Transformer O/L
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer O/L
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2519125
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 50 | 1519680
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 116 | 2679709
| Chattogram area Total |  |  |  | 2382 | 1106 | 22913409
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1923456 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4981000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 6796400 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 265 | 6992000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 460152 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1159680
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 518545 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 988432 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 150 | 3358836
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 257984
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 3263350 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 136 | 2274240
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 477792
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236880
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 142 | 2877120
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 719600
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 49 | 545726 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 478330 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 50 | 155328 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 780900
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 117 | 2239440
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 548280 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2042 | 42033471
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 159 | 3933280 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 430668
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 193920 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 4400
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 191 | 2872800
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 111 | 2654400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 175880
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 593280
| Mymensingh Area Total |  |  |  | 709 | 512 | 10858628
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1030000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 714840 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3669545
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3657000 | Machine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1174200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 178176
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 64 | 1492608
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1803840
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 145 | 3442750 | ST Under maint.
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 572544
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7203000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8852000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 255600
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 0 | 0 | Under maint.
| Sylhet Area Total |  |  |  | 2377 | 1441 | 34046103
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 546 | 13930181
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 15 | 110060 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 100 | 413859 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9278600 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 478080
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1202400
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1276 | 25413180
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 30 | 649400
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2134052 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 10 | 269660 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 11224100
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 200 | 4910291
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 108000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 875 | 19295503
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 224544 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 106888 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 225420 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 166310 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 124 | 2494000 | FGMO
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 178 | 4568191 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 165 | 4547573 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 394 | 8890545 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 208320 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 502560
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 177048
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 1030560
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 95 | 613640 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2084256 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 95 | 1985952 | Engine problem
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 12900
| Rajshahi Area Total |  |  |  | 2179 | 1391 | 27838707
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 151 | 3743400 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 99 | 2323228 | Engine problem
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 29405
| Rangpur Area Total |  |  |  | 605 | 250 | 6096033
| Total |  |  |  | 21280 | 12290 | 257529172
| Eastern Grid Total |  |  |  | 14321 | 8498 | 178885749
| Western Grid Total |  |  |  | 6959 | 3792 | 78643423
| National Grid Total |  |  |  | 21280 | 12290 | 257529172
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-08-08
(a) ENTIRE EASTERN GRID : |  | 7710 | MW | (b) ENTIRE WESTERN GRID : |  | 3939 | MW
i) Dhaka area |  | 3884 | MW | i) Khulna area |  | 1523 | MW
ii) Chittagong area |  | 1137 | MW | ii) Rajshahi area |  | 1271 | MW
iii) Comilla area |  | 1158 | MW | iii) Barisal area |  | 333 | MW
iv) Mymensingh area |  | 1038 | MW | iv) Rangpur area |  | 812 | MW
v) Sylhet area |  | 493 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11649 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 122 | 12:00 | Kishoreganj | 152 | 19:00 | Jessore | 114 | 19:30
Munsiganj | 102 | 0:00 | Netrokona | 121 | 20:00 | Benapol | 58 | 19:30
Sonargaon | 68 | 1:00 | Jamalpur | 141 | 19:30 | Jhenida | 114 | 20:00
Shyampur | 170 | 13:00 | Sherpur | 126 | 1:00 | Bottail | 142 | 19:30
Bhulta | 177 | 1:00 | Srimongal | 54 | 19:30 | G.K Project | 60 | 19:30
Madanganj | 63 | 12:00 | Shahjibazar | 111 | 21:00 | Faridpur | 139 | 22:00
Shitalakhya | 112 | 12:00 | Fenchuganj | 45 | 21:00 | Rajbari | 50 | 19:30
Rahim steel | 7 | 15:00 | Kulawara | 41 | 22:00 | Madaripur | 102 | 21:00
Matuail | 57 | 12:00 | Sylhet | 106 | 19:00 | Sariatpur | 66 | 21:00
Ghorasal | 75 | 22:00 | Chatak | 30 | 21:00 | Gopalganj | 89 | 21:00
Narsingdi | 165 | 21:00 | Sunamganj | 50 | 21:00 | Bagerhat | 94 | 20:00
Haripur (SBU) | 83 | 22:00 | Biani Bazar | 63 | 20:00 | Mongla | 38 | 19:30
Sreenagar | 40 | 21:00 | Comilla (S) | 144 | 19:30 | Satkhira | 98 | 20:00
Ullon | 61 | 15:00 | Comilla(N) | 125 | 21:00 | Gallamari | 34 | 19:30
Hasnabad | 70 | 15:00 | Chandpur | 78 | 0:00 | Magura | 56 | 20:00
Magbazar | 82 | 12:00 | Feni | 115 | 19:00 | Norail | 41 | 20:00
Maniknagar | 62 | 13:00 | Chowmuhani | 190 | 19:00 | Chuadanga | 100 | 19:30
Bangabhaban | 6 | 10:00 | Ashuganj | 44 | 2:00 | Borguna | 16 | 21:00
Motijheel | 20 | 11:00 | Daudkandi | 146 | 21:00 | Barisal(N) | 42 | 21:00
Narinda | 44 | 13:00 | B.Baria | 156 | 21:00 | Barisal (S) | 101 | 23:00
Kazla | 76 | 10:00 | Ramganj | 100 | 22:00 | Patuakhali | 102 | 23:00
Dhanmondi | 126 | 14:00 | Chaddagram | 43 | 22:00 | Bhandaria | 50 | 21:00
Lalbag | 83 | 13:00 | PHP | 10 | 6:00 | Borhan Uddin | 40 | 1:00
Madartek | 67 | 23:00 | Kochua | 70 | 19:00 | Ishurdi | 66 | 20:00
Dhaka University | 22 | 12:00 | Madunaghat | 56 | 19:30 | Ruppur Paromanobik | 2 | 1:00
Aftabnagar | 9 | 13:00 | Hathazari | 89 | 20:00 | Natore | 126 | 21:00
Fatullah | 54 | 15:00 | Khulshi | 165 | 19:30 | Bogra | 154 | 21:00
Nawabganj | 51 | 23:00 | Halishahar | 84 | 19:00 | Noagaon | 113 | 20:00
Keraniganj | 57 | 21:00 | Baraulia | 89 | 11:00 | Rajshahi | 151 | 21:00
Mirpur | 105 | 19:00 | Sikalbaha | 38 | 16:00 | Rajshahi New | 13 | 19:30
Kalyanpur | 96 | 15:00 | Dohazari | 100 | 21:00 | C.Nawabganj | 62 | 22:00
Gulshan | 76 | 14:00 | Cox'sbazar | 96 | 19:00 | Amnura | 50 | 21:00
Uttara | 76 | 16:00 | Chandraghona | 26 | 19:30 | Pabna | 98 | 19:30
Uttara New | 12 | 11:00 | Kaptai | 4 | 19:00 | Shahjadpur | 85 | 21:00
Kamrangirchar | 81 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 88 | 21:00
Savar | 162 | 15:00 | Bakulia | 90 | 12:00 | Niyamatpur | 72 | 21:00
Bhasantec | 115 | 15:00 | Julda | 22 | 12:00 | Joypurhat | 55 | 24:00
Agargaon | 76 | 14:00 | TK chemical | 28 | 20:00 | Sherpur(Bogura) | 55 | 19:30
Satmosjid | 84 | 19:00 | Modern Steel | 0 | #N/A | Mohastangor | 66 | 24:00
Tongi | 108 | 11:00 | Shahmirpur | 22.7 | 21:00 | Bhangura | 30 | 19:30
Kabirpur | 238 | 9:00 | Khagrachhari | 24 | 14:00 | Rangpur | 140 | 19:30
Basundhara | 197 | 12:00 | Matarbari | 31.5 | 19:30 | Lalmonirhat | 50 | 19:30
Manikganj | 80 | 21:00 | Baroiar Hat | 40 | 19:00 | Saidpur | 104 | 21:00
Joydevpur | 156 | 19:30 | Rangamati | 10 | 12:00 | Purbasadipur | 110 | 23:00
New Tongi | 106 | 12:00 | Abul Khair 230 | 156 | 1:00 | Thakurgaon | 90 | 20:00
Kodda | 254 | 12:00 | BSRM | 160 | 16:00 | Palashbari | 114 | 19:30
Dhamrai | 94 | 21:00 | GPH Ispat | 93 | 9:00 | Barapukuria | 55 | 21:00
Rajendrapur | 100 | 19:30 | Agrabad | 52 | 19:00 | Panchagar | 57 | 20:00
Valuka | 116 | 19:00 | Goalpara | 20 | 1:00 | Joldhaka | 60 | 1:00
Tangail | 194 | 21:00 | Central S/S | 93 | 19:30 | Kurigram | 60 | 1:00
Mymensing | 209 | 21:00 | Noapara | 45 | 19:30 | Mithapukur | 37 | 16:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-08-08 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 20:00 | 401 | 9:00 | Kaliakoir | 401 | 0.25 | 388 | 0.375
| Bheramara | 407 | 20:00 | 401 | 10:00 | Bhulta | 391 | 0.77083 | 382 | 0.41667
| Ashuganj(N) | 396 | 13:00 | 391 | 9:00 | Gopalganj | 406 | 0.625 | 390 | 0.83333
| Payra | 411 | 20:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 238 | 18:00 | 230 | 7:00 | Hathazari | 228 | 20:00 | 220 | 6:00
| Ishurdi | 235 | 6:00 | 225 | 24:00 | Megnaghat | 238 | 15:00 | 232 | 5:00
| Ashuganj | 242 | 16:00 | 240 | 1:00 | Fenchuganj | 243 | 19:30 | 239 | 2:00
| Serajganj | 232 | 9:00 | 225 | 22:00 | Siddhirganj | 235 | 20:00 | 230 | 7:00
| Baghabari | 234 | 15:00 | 227 | 19:30 | Maniknagar | 233 | 20:00 | 228 | 12:00
| Barapukuria | 236 | 10:00 | 224 | 22:00 | Agargaon | 233 | 8:00 | 226 | 9:00
| Bogra | 227 | 11:00 | 213 | 22:00 | Barisal | 240 | 20:00 | 232 | 21:00
| Rajshahi | 229 | 7:00 | 219 | 13:00 | Bhola 225 MW | 244 | 16:00 | 237 | 21:00
| Khulna South | 228 | 18:30 | 209 | 2:00 | AKSML | 231 | 20:00 | 222 | 7:00
| Rampura | 231 | 19:00 | 229 | 9:00 | BSRM | 230 | 19:30 | 224 | 7:00
| Haripur | 232 | 20:00 | 227 | 9:00 | Bibiyana | 242 | 1:00 | 236 | 17:00
| Hasnabad | 234 | 19:00 | 230 | 1:00 | Bhulta | 235 | 20:00 | 230 | 10:00
| Shyampur | 232 | 20:00 | 220 | 9:00 | Ashuganj (S) | 239 | 18:30 | 235 | 10:00
| Aminbazar | 234 | 1:00 | 227 | 2:00 | Kaliakoir | 233 | 19:30 | 226 | 8:00
| Tongi | 234 | 23:00 | 224 | 7:00 | GPH | 229 | 20:00 | 222 | 6:00
| Comilla (N) | 233 | 19:30 | 228 | 6:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 136 | 20:00 | 133 | 7:00 | Madanhat | 137 | 0.83333 | 133 | 0.25
| Munsiganj | 138 | 20:00 | 132 | 10:00 | Hathazari | 136 | 0.83333 | 130 | 0.25
| Sonargaon | 134 | 19:30 | 132 | 1:00 | Khulshi | 134 | 0.8125 | 127 | 0.29167
| Shyampur | 139 | 20:00 | 135 | 9:00 | Halishahar | 136 | 0.8125 | 128 | 0.33333
| Bhulta | 130 | 4:00 | 126 | 8:00 | Baraulia | 136 | 0.83333 | 129 | 0.29167
| Madanganj | 138 | 19:30 | 131 | 12:00 | Sikalbaha | 137 | 0.041667 | 131 | 0.25
| Shitalakhya | 139 | 19:30 | 132 | 10:00 | Dohazari | 132 | 0.45833 | 126 | 0.25
| Rahim steal | 136 | 19:00 | 133 | 7:00 | Cox'sbazar | 122 | 0.45833 | 108 | 0.79167
| Matuail | 136 | 20:00 | 133 | 7:00 | Chandraghona | 136 | 0.8125 | 131 | 0.29167
| Ghorasal | 140 | 1:00 | 136 | 12:00 | Kaptai | 134 | 0.041667 | 134 | 0.041667
| Narsinghdi | 134 | 18:30 | 126 | 22:00 | A. Khaer Stl. | 134 | 0.041667 | 132 | 0.29167
| Haripur (SBU) | 136 | 22:00 | 133 | 10:00 | Bakulia | 135 | 0.041667 | 126 | 0.29167
| Sreenagar | 134 | 19:30 | 128 | 10:00 | Julda | 137 | 0.041667 | 130 | 0.25
| Ullon | 135 | 19:30 | 132 | 10:00 | TK Chemical | 136 | 0.70833 | 131 | 0.20833
| Hasnabad | 137 | 19:30 | 133 | 9:00 | Modern Steel
| Magbazar | 135 | 2:00 | 130 | 10:00 | Shahmirpur | 137 | 0.83333 | 128 | 0.29167
| Maniknagar | 136 | 1:00 | 133 | 10:00 | Khagrachhari | 134 | 0.58333 | 129 | 0.29167
| Bangabhaban | 136 | 1:00 | 133 | 10:00 | Matarbari | 126 | 0.45833 | 118 | 0.29167
| Motijheel | 136 | 1:00 | 133 | 10:00 | Baroiar Hat | 134 | 0.66667 | 128 | 0.29167
| Narinda | 136 | 1:00 | 133 | 10:00 | Rangamati | 135 | 16:00 | 131 | 7:00
| Kazla | 136 | 1:00 | 133 | 10:00 | Agrabad | 135 | 19:00 | 129 | 7:00
| Dhanmondi | 136 | 19:30 | 132 | 12:00 | Goalpara S/S | 140 | 18:30 | 128 | 0.125
| Lalbag | 136 | 1:00 | 132 | 10:00 | Khulna Central S/S | 139 | 18:30 | 127 | 0
| Madartek | 135 | 1:00 | 132 | 9:00 | Noapara | 137 | 16:00 | 123 | 0
| Dhaka University | 135 | 1:00 | 132 | 9:00 | Jessore | 133 | 18:00 | 121 | 0.041667
| Aftabnagar | 135 | 1:00 | 132 | 11:00 | Benapol | 133 | 0.75 | 119 | 0
| Fatullah | 139 | 19:30 | 135 | 9:00 | Jhenida | 131 | 18:00 | 117 | 0
| Nawabganj | 134 | 19:30 | 128 | 12:00 | Bottail | 134 | 0.77083 | 126 | 0.041667
| Keraniganj | 135 | 20:00 | 129 | 10:00 | G.K Project | 139 | 0.66667 | 132 | 0.79167
| Mirpur | 135 | 21:00 | 128 | 8:00 | Faridpur | 135 | 0.66667 | 129 | 0.875
| Kalyanpur | 135 | 20:00 | 129 | 9:00 | Rajbari | 134 | 0.75 | 126 | 0.875
| Gulshan | 135 | 20:00 | 131 | 12:00 | Madaripur | 139 | 0.375 | 130 | 0.95833
| Uttara | 134 | 19:30 | 128 | 9:00 | Shariyatpur S/S | 139 | 11:00 | 131 | 0.875
| Uttara New | 134 | 1:00 | 128 | 9:00 | Gopalganj | 142 | 0.75 | 133 | 0.875
| Kamrangirchar | 137 | 20:00 | 132 | 10:00 | Bagerhat | 135 | 18:00 | 122 | 0.125
| Savar | 136 | 1:00 | 129 | 7:00 | Mongla | 134 | 16:00 | 123 | 0.125
| Bhasantec | 138 | 20:00 | 133 | 10:00 | Satkhira | 137 | 18:30 | 127 | 3:00
| Agargaon | 138 | 1:00 | 134 | 9:00 | Gallamari | 139 | 0.75 | 128 | 3:00
| Satmosjid | 138 | 19:30 | 134 | 9:00 | Magura | 130 | 17:00 | 115 | 0
| Tongi | 137 | 23:00 | 131 | 8:00 | Narail | 130 | 0.75 | 117 | 0
| Kabirpur | 135 | 20:00 | 126 | 9:00 | Chuadanga | 132 | 17:00 | 118 | 0
| Basundhara | 135 | 22:00 | 128 | 9:00 | Borguna | 137 | 18:00 | 129 | 0.83333
| Manikganj | 141 | 13:00 | 132 | 8:00 | Barisal(N) | 139 | 8:00 | 131 | 22:00
| Joydevpur | 139 | 0:00 | 133 | 9:00 | Barisal (S) | 137 | 0.33333 | 131 | 0.8125
| New Tongi | 136 | 21:00 | 130 | 9:00 | Patuakhali(S) | 135 | 0.33333 | 128 | 0.875
| Kodda | 135 | 22:00 | 125 | 8:00 | Bhandaria | 135 | 0.33333 | 125 | 0.95833
| Dhamrai | 135 | 21:00 | 131 | 9:00 | Ishurdi | 136 | 6:00 | 131 | 21:00
| Rajendrapur | 138 | 1:00 | 131 | 9:00 | Ruppur Paromanobik | 136 | 6:00 | 131 | 21:00
| Valuka | 129 | 13:00 | 111 | 22:00 | Natore | 136 | 6:00 | 128 | 21:00
| Tangail | 134 | 11:00 | 125 | 1:00 | Bogra | 137 | 12:00 | 125 | 21:00
| Mymensing | 133 | 13:00 | 116 | 22:00 | Noagaon | 132 | 17:00 | 120 | 22:00
| Kishorganj | 133 | 11:00 | 119 | 22:00 | Rajshahi | 135 | 18:30 | 128 | 21:00
| Netrokona | 129 | 12:00 | 111 | 22:00 | Rajshahi New | 134 | 7:00 | 128 | 14:00
| Jamalpur | 138 | 13:00 | 124 | 23:00 | C.Nawabganj | 135 | 18:30 | 126 | 14:00
| Sherpur | 137 | 12:00 | 123 | 21:00 | Amnura | 135 | 18:30 | 123 | 2:00
| Srimongal | 140 | 7:00 | 133 | 1:00 | Pabna | 135 | 6:00 | 128 | 22:00
| Shahjibazar | 138 | 9:00 | 132 | 1:00 | Shahjadpur | 139 | 11:00 | 135 | 1:00
| Fenchuganj | 138 | 9:00 | 135 | 1:00 | Serajganj | 134 | 8:00 | 127 | 21:00
| Khulawara | 137 | 8:00 | 134 | 1:00 | Niyamatpur | 130 | 11:00 | 117 | 21:00
| Sylhet | 134 | 7:00 | 131 | 1:00 | Joypurhat | 131 | 10:00 | 118 | 22:00
| Chatak | 134 | 9:00 | 128 | 23:00 | Sherpur(Bogura) | 137 | 17:00 | 126 | 3:00
| Sunamganj | 131 | 7:00 | 125 | 23:00 | Mohastangor | 137 | 17:00 | 122 | 21:00
| Biani Bazar | 133 | 6:00 | 128 | 1:00 | Bangura | 136 | 5:00 | 132 | 1:00
| Comilla(s) | 127 | 6:00 | 123 | 19:00 | Rangpur | 131 | 10:00 | 115 | 22:00
| Comilla(n) | 140 | 20:00 | 135 | 5:00 | Lalmonirhat | 130 | 5:00 | 115 | 22:00
| Chandpur | 139 | 1:00 | 133 | 6:00 | Saidpur | 130 | 7:00 | 114 | 1:00
| Feni | 135 | 16:00 | 129 | 5:00 | Purbasadipur | 130 | 6:00 | 108 | 22:00
| Chowmuhani | 132 | 6:00 | 130 | 1:00 | Thakurgaon | 129 | 6:00 | 108 | 19:30
| Ashuganj | 140 | 18:00 | 135 | 1:00 | Palashbari | 132 | 10:00 | 115 | 19:30
| Daudkandi | 138 | 19:30 | 131 | 9:00 | Barapukuria | 136 | 10:00 | 124 | 22:00
| B.Baria | 134 | 6:00 | 128 | 1:00 | Panchagar | 129 | 6:00 | 105 | 19:30
| Ramganj | 134 | 23:00 | 128 | 5:00 | Joldhaka | 128 | 0.58333 | 109 | 0.875
| Chaddagram | 135 | 18:00 | 130 | 6:00 | Kurigram | 132 | 0.25 | 113 | 0.95833
| PHP | 134 | 16:00 | 128 | 6:00 | Mithapukur | 135 | 0.70833 | 118 | 0.91667
| Kochua | 136 | 1:00 | 132 | 5:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-08-08
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 366 | 8341 | 3570 | 11911 |  |  |  | QF-LDC-11
0:30 | 408 | 8240.5 | 3476.5 | 11717 | Date: | 2021-08-08
1:00 | 450 | 8140 | 3383 | 11523
1:30 | 451 | 8009.5 | 3303.5 | 11313
2:00 | 452 | 7879 | 3224 | 11103
2:30 | 426 | 7760 | 3179 | 10939 | [5 empty] | Gen. at Eve. Peak | 12290 | 12290 MW (21:00 )
3:00 | 400 | 7641 | 3134 | 10775 | [6 empty] | 21:00
3:30 | 376 | 7548 | 3083.5 | 10631.5 | [5 empty] | Gen. at Day Peak | 10130 | 10130 MW (12:00 )
4:00 | 352 | 7455 | 3033 | 10488 | [6 empty] | 12:00
4:30 | 334 | 7357.5 | 3011.5 | 10369 | [5 empty] | Highest Generation | 12290
5:00 | 316 | 7260 | 2990 | 10250 | [6 empty] | 21:00
5:30 | 205 | 6905 | 2950 | 9855
6:00 | 94 | 6550 | 2910 | 9460
6:30 | 50 | 6411 | 2920 | 9331
7:00 | 6 | 6272 | 2930 | 9202
7:30 | 13 | 6250 | 2910 | 9160
8:00 | 20 | 6228 | 2890 | 9118
8:30 | 42 | 6320.5 | 2884 | 9204.5
9:00 | 64 | 6413 | 2878 | 9291
9:30 | 81 | 6540.5 | 2893.5 | 9434
10:00 | 98 | 6668 | 2909 | 9577
10:30 | 59 | 6802 | 2890 | 9692
11:00 | 20 | 6936 | 2871 | 9807
11:30 | 46 | 7031.5 | 2937 | 9968.5
12:00 | 72 | 7127 | 3003 | 10130
12:30 | 37 | 7172.5 | 3066.5 | 10239
13:00 | 2 | 7218 | 3130 | 10348
13:30 | 3 | 7196.5 | 3091.5 | 10288
14:00 | 4 | 7175 | 3053 | 10228
14:30 | 29 | 7294.5 | 3042 | 10336.5
15:00 | 54 | 7414 | 3031 | 10445
15:30 | 32 | 7390.5 | 3020.5 | 10411
16:00 | 10 | 7367 | 3010 | 10377
16:30 | 86 | 7110 | 3000 | 10110
17:00 | 162 | 6853 | 2990 | 9843
17:30 | 112 | 6719 | 2859 | 9578
18:00 | 62 | 6585 | 2728 | 9313
18:30 | 134 | 7170.5 | 3036.5 | 10207
19:00 | 206 | 7756 | 3345 | 11101
19:30 | 374 | 8466 | 3724 | 12190
20:00 | 350 | 8446 | 3771 | 12217 |  |  |  | Executive Engineer
20:30 | 359 | 8472 | 3781.5 | 12253.5 |  |  |  | Network Operation Division
21:00 | 368 | 8498 | 3792 | 12290
21:30 | 352 | 8451.5 | 3803 | 12254.5
22:00 | 336 | 8405 | 3814 | 12219 |  |  |  |  | Page 6 of 7
22:30 | 318 | 8391 | 3785 | 12176
23:00 | 300 | 8377 | 3756 | 12133
23:30 | 333 | 8359 | 3663 | 12022
24:00 | 366 | 8341 | 3570 | 11911
12290 MW (21:00 )
10130 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-08-08 |  | Energy | 257529172
[11 empty] | 2021-08-08 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4526 | 541 | 2011 | 3691 | 670 | 121 | 321 | 0 | 140 | 0
0:30 | 4605 | 550 | 1977 | 3483 | 655 | 119.5 | 249.5 | 0 | 133 | 0 | Date: | 2021-08-08
1:00 | 4684 | 559 | 1943 | 3275 | 640 | 118 | 178 | 0 | 126 | 0
1:30 | 4704 | 554 | 1955.5 | 3104 | 641 | 117.5 | 113 | 0 | 124 | 0 | [7 empty] | Total Energy | 257.5292 | Total Energy Gen 257.529 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 257.529 MKWHr
2:00 | 4724 | 549 | 1968 | 2933 | 642 | 117 | 48 | 0 | 122 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4739 | 548 | 1983 | 2767.5 | 632.5 | 117 | 32 | 0 | 120 | 0 | [7 empty] | Energy Requirement | 257.5292
3:00 | 4754 | 547 | 1998 | 2602 | 623 | 117 | 16 | 0 | 118 | 0
3:30 | 4749 | 547 | 2010.5 | 2452.5 | 622.5 | 117 | 16 | 0 | 117 | 0 | [6 empty] | Shortage
4:00 | 4744 | 547 | 2023 | 2303 | 622 | 117 | 16 | 0 | 116 | 0
4:30 | 4764 | 547 | 2033 | 2169.5 | 606.5 | 117 | 16 | 0 | 116 | 0
5:00 | 4784 | 547 | 2043 | 2036 | 591 | 117 | 16 | 0 | 116 | 0
5:30 | 4753.5 | 547.5 | 1966 | 1754.5 | 586 | 117 | 16 | 0 | 113 | 1.5
6:00 | 4723 | 548 | 1889 | 1473 | 581 | 117 | 16 | 0 | 110 | 3
6:30 | 4711 | 547.5 | 1847.5 | 1418.5 | 571 | 117 | 8 | 0 | 104 | 6.5 |  |  |  |  | Coal
7:00 | 4699 | 547 | 1806 | 1364 | 561 | 117 | 0 | 0 | 98 | 10
7:30 | 4650 | 547 | 1790.5 | 1388 | 551 | 117 | 0 | 0 | 101 | 15.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4601 | 547 | 1775 | 1412 | 541 | 117 | 0 | 0 | 104 | 21
8:30 | 4574 | 547 | 1809.5 | 1498 | 533 | 117.5 | 0 | 0 | 106 | 19.5
9:00 | 4547 | 547 | 1844 | 1584 | 525 | 118 | 0 | 0 | 108 | 18
9:30 | 4480 | 620 | 1787.5 | 1782.5 | 512.5 | 119 | 0 | 0 | 107 | 25.5
10:00 | 4413 | 693 | 1731 | 1981 | 500 | 120 | 0 | 0 | 106 | 33
10:30 | 4381.5 | 693 | 1758 | 2091 | 501.5 | 120 | 0 | 0 | 109 | 38
11:00 | 4350 | 693 | 1785 | 2201 | 503 | 120 | 0 | 0 | 112 | 43
11:30 | 4311 | 693 | 1828 | 2344.5 | 504 | 120.5 | 0 | 0 | 112 | 55.5
12:00 | 4272 | 693 | 1871 | 2488 | 505 | 121 | 0 | 0 | 112 | 68
12:30 | 4290.5 | 693 | 1924.5 | 2516 | 505 | 120.5 | 0 | 0 | 111 | 78.5
13:00 | 4309 | 693 | 1978 | 2544 | 505 | 120 | 0 | 0 | 110 | 89
13:30 | 4309 | 693 | 1978 | 2544 | 505 | 120 | 0 | 0 | 110 | 89
14:00 | 4309 | 693 | 1978 | 2544 | 505 | 120 | 0 | 0 | 110 | 89
14:30 | 4326.5 | 620 | 1965.5 | 2660.5 | 515 | 117.5 | 0 | 0 | 120 | 71.5
15:00 | 4344 | 547 | 1953 | 2777 | 525 | 115 | 0 | 0 | 130 | 54
15:30 | 4292.5 | 547 | 1928 | 2823 | 524.5 | 115 | 1.5 | 0 | 127 | 52.5
16:00 | 4241 | 547 | 1903 | 2869 | 524 | 115 | 3 | 0 | 124 | 51
16:30 | 4250.5 | 547 | 1908.5 | 2611 | 515 | 116 | 3.5 | 0 | 122 | 36.5
17:00 | 4260 | 547 | 1914 | 2353 | 506 | 117 | 4 | 0 | 120 | 22
17:30 | 4215 | 547 | 1800 | 2250 | 500 | 117.5 | 18 | 0 | 116 | 14.5
18:00 | 4170 | 547 | 1686 | 2147 | 494 | 118 | 32 | 0 | 112 | 7
18:30 | 4320.5 | 546.5 | 1785 | 2564.5 | 522.5 | 118.5 | 222 | 0 | 124 | 3.5
19:00 | 4471 | 546 | 1884 | 2982 | 551 | 119 | 412 | 0 | 136 | 0
19:30 | 4512 | 546 | 1897 | 3805 | 662 | 119 | 505 | 0 | 144 | 0
20:00 | 4521 | 546 | 1932 | 3777 | 650 | 119 | 528 | 0 | 144 | 0
20:30 | 4498 | 546 | 1934.5 | 3828 | 665.5 | 119.5 | 519 | 0 | 143 | 0
21:00 | 4475 | 546 | 1937 | 3879 | 681 | 120 | 510 | 0 | 142 | 0
21:30 | 4499.5 | 546.5 | 1957 | 3802.5 | 691 | 120 | 495 | 0 | 143 | 0
22:00 | 4524 | 547 | 1977 | 3726 | 701 | 120 | 480 | 0 | 144 | 0
22:30 | 4492.5 | 545 | 1988 | 3708.5 | 701 | 120.5 | 477.5 | 0 | 143 | 0
23:00 | 4461 | 543 | 1999 | 3691 | 701 | 121 | 475 | 0 | 142 | 0
23:30 | 4493.5 | 542 | 2005 | 3691 | 685.5 | 121 | 398 | 0 | 141 | 0 | Max Temp. in Dhaka |  | 32.4° C
24:00 | 4526 | 541 | 2011 | 3691 | 670 | 121 | 321 | 0 | 140 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 257.529 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 257.529 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-08-08
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 58 | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 60 | 60 | 61 | 60 | 57 | 55 | 55 | 57 | 58 |  | 59 | 59 | 59 | 60 | 60 | 61 | 61 | 1307089
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1464000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2300000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
5 | Raozan 25 MW PP | [19 empty] | 2 | 16 | 23 | 25 | 25 | 25 | 25 | 143377
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 0 | 0 | 5 | 12 | 11 | 13 | 19 | 17 | 9 | 10 | 3 | 1 | [8 empty] | 95715
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | [19 empty] | 51 | 51 | 51 | 51 | 51 | 51 | 17 | 299751
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 17 | 17 | 18 | 51 | 51 | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2224727
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 28 | 100 | 50 | 50 |  |  |  | 155328
14 | Titas 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 50 | 50 | 50 | 0 | 257984
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 333 | 335 | 335 | 335 | 335 | 335 | 290 | 290 | 334 | 334 | 337 | 330 | 325 | 280 | 332 | 327 | 329 | 270 |  | 330 | 331 | 332 | 332 | 330 | 331 | 331 | 7883985
18 | Kodda 300 MW PP Unit-2 (Summit) | 277 | 232 | 125 | 0 | [5 empty] | 47 | 62 | 130 | 145 | 143 | 145 | 145 | 95 | 95 |  | 145 | 245 | 263 | 275 | 275 | 275 | 275 | 3239235
19 | Ashuganj 195MW PP (APSCL-United) | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 36 | 36 | 36 | 36 | 36 | 518545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 185 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 3402000
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7314064
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1923456
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 20 | 20 | 23 |  | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 460152
33 | Ashuganj 225 MW CCPP | 216 | 215 | 214 | 214 | 214 | 215 | 214 | 214 | 217 | 215 | 217 | 182 | 182 | 194 | 182 | 182 | 182 | 160 |  | 213 | 214 | 215 | 215 | 213 | 214 | 212 | 4981000
34 | Ashuganj 450 MW CCPP(South) | 270 | 270 | 300 | 305 | 300 | 300 | 315 | 315 | 305 | 295 | 285 | 285 | 300 | 300 | 265 | 265 | 265 | 285 |  | 290 | 265 | 265 | 265 | 280 | 280 | 300 | 6992000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 270 | 265 | 260 | 260 | 280 | 280 | 270 | 265 | 260 | 260 | 295 | 290 | 260 | 260 | 260 | 275 |  | 285 | 260 | 260 | 260 | 275 | 270 | 290 | 6796400
35 | Ashuganj 55 MW PP (Precision) |  | 0 | 21 | 55 | 55 | 55 | 56 | 56 | 56 |  | 51 | 55 | 55 | 54 | 55 | 52 | 52 | 55 |  | 56 | 56 | 56 | 54 | 52 | 53 | 52 | 1159680
36 | Chandpur 150 MW CCPP | 135 | 137 | 137 | 135 | 138 | 137 | 137 | 138 | 138 | 139 | 135 | 138 | 138 | 138 | 134 | 133 | 133 | 136 |  | 137 | 137 | 135 | 137 | 137 | 139 | 138 | 3263350
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 392 | 391 | 392 | 393 | 392 | 391 | 375 | 368 | 368 | 349 | 341 | 341 | 341 | 324 | 368 | 260 | 267 | 282 |  | 280 | 282 | 283 | 281 | 285 | 285 | 280 | 8095848
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5547000
41 | Haripur 360MW CCPP(HPL) | 348 | 349 | 343 | 342 | 347 | 347 | 346 | 346 | 342 | 342 | 342 | 346 | 342 | 316 | 302 | 318 | 314 | 274 |  | 318 | 312 | 302 | 298 | 283 | 304 | 318 | 7800000
42 | RPCL 210MW CCPP | 181 | 194 | 194 | 199 | 208 | 200 | 196 | 182 | 167 | 156 | 156 | 155 | 139 | 138 | 142 | 145 | 157 | 158 |  | 158 | 159 | 158 | 159 | 157 | 157 | 157 | 3933280
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 2 | 7 | 17 | 1 | 10 | 5 | 30 | 41 | 43 | 21 | 28 | 14 | 4 | [8 empty] | 175880
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 1030000
45 | Fenchugonj CCPP Phase-2 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 714840
46 | Shajibazar 330 MW CCPP | 160 | 160 | 160 | 159 | 161 | 159 | 160 | 160 | 160 | 160 | 159 | 159 | 159 | 156 | 158 | 160 | 158 | 161 |  | 160 | 159 | 160 | 160 | 161 | 160 | 161 | 3657000
47 | Shahjibazar GTPP Unit- 8 & 9 | 62 | 61 | 62 | 62 | 61 | 62 | 61 | 63 | 63 | 64 | 64 | 62 | 63 | 61 | 62 | 64 | 63 | 64 |  | 63 | 64 | 65 | 64 | 61 | 61 | 61 | 1492608
48 | Shahjibazar 86MW PP (Shahjibazar) | 70 | 81 | 81 | 81 | 81 | 81 | 78 | 81 | 84 | 84 | 81 | 84 | 84 | 84 | 83 | 83 | 81 | 30 |  | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 1803840
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 145 | 110 |  | 135 | 145 | 145 | 145 | 145 | 145 | 145 | 3442750
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 255600
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 0 |  | 5 | 5 | 5 | 5 |  |  | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 178176
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 50 | 50 | 50 | 47 | 50 | 50 | 14 |  | 23 | 53 | 53 | 53 | 53 | 53 | 53 | 1174200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 18 |  | 18 | 24 | 24 | 24 | 24 | 24 | 24 | 572544
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 280 | 300 | 290 | 300 | 290 | 300 | 300 | 305 | 290 | 295 | 280 | 290 | 300 | 305 | 285 | 280 | 270 |  | 290 | 290 | 280 | 290 | 300 | 300 | 300 | 7203000
Bibiyana South 400 MW
58 | Nababganj 55 MW PP (Southern power ) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 893811
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 25 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 593280
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 465792
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [5 empty] | 16 | 17 | 17 |  |  | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 311724
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 21 | 21 | 21 | 430668
63 | Impoprt (Tripura) | 126 | 122 | 118 | 116 | 116 | 110 | 98 | 104 | 108 | 106 | 112 | 112 | 110 | 124 | 130 | 124 | 120 | 112 |  | 136 | 144 | 144 | 142 | 144 | 142 | 140 | 2877120
64 | Malancha, Ctg. EPZ (United) | 40 | 40 | 40 | 40 | 40 | 40 | 37 | 5 | 3 | 2 | 2 | 2 | 6 | 3 | 3 | 3 | 6 | 2 |  | 8 | 9 | 8 | 13 | 35 | 37 | 39 | 444480
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 477792
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236880
67 | Jangalia 33MW PP (Summit) | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 719600
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 15 | 11 | 11 | 11 | 13 | 13 | 20 | 20 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 478330
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 23 | 23 | 23 | 27 | 27 | 25 | 25 | 25 | 25 |  | 17 | 17 | 27 | 28 | 30 | 30 | 30 | 593640
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 28 | 28 | 786900
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 17 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 795900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 17 | 0 | [11 empty] | 17 | 52 | 52 | 17 | 17 |  | 80 | 114 | 114 | 114 | 114 | 114 | 114 | 780900
| Chowmuhani 113 MW | 119 | 119 | 119 | 118 | 115 | 8 | 8 | 8 | 23 | 55 | 92 | 107 | 108 | 106 | 107 | 103 | 99 | 65 |  | 88 | 117 | 114 | 117 | 119 | 110 | 109 | 2239440
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 90 | 17 | 17 | 17 | 30 | 54 | 72 | 108 | 108 | 112 | 162 | 154 | 72 | 72 |  | 115 | 162 | 162 | 162 | 162 | 162 | 162 | 2829600
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [11 empty] | 16 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 50 | 51 | 51 | 51 | 43 | 24 | 433440
79 | Kodda 150MW PP | 100 | 48 | 16 | 16 | 16 | 16 | [11 empty] | 16 |  | 48 | 82 | 98 | 64 | 64 | 64 | 64 | 692160
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 193920
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 0 | [10 empty] | 8 | 25 | 25 | 40 | 43 | 50 |  | 43 | 43 | 43 | 49 | 51 | 45 | 43 | 545726
| Gazipur 100 MW PP | 105 | 105 | 105 | 72 | 72 | 35 | 17 | 17 | 20 | 55 | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 70 |  | 73 | 105 | 105 | 105 | 105 | 105 | 105 | 1861200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 1 | 2 | 1 | 3 | 6 | 5 | 1 | 3 | 2 | 0 | [9 empty] | 21000
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 110 | 105 | 110 | 110 | 110 | 100 | 51 | 51 | 60 | 68 | 110 | 110 | 110 | 108 | 106 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2519125
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [19 empty] | 43 | 72 | 73 | 74 | 74 | 74 | 73 | 446104
86 | Meghnaghat CCPP ( Summit) | 270 | 280 | 280 | 260 | 288 | 275 | 290 | 290 | 285 | 280 | 250 | 270 | 290 | 285 | 270 | 270 | 260 | 290 |  | 290 | 275 | 265 | 285 | 290 | 290 | 305 | 6642735
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 94 | 94 | 53 | 53 | 34 | 17 | 17 | 17 | 20 | 53 | 53 | 53 | 53 | 53 | 65 | 75 | 55 | 53 |  | 60 | 74 | 75 | 75 | 73 | 73 | 75 | 1400640
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 0 | [16 empty] | 3 | 20 | 20 | 20 | 20 | 20 | 20 | 123000
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 988432
94 | Gagnagar 102 MW PP (Digital Power) | 48 | 24 | 16 | 8 | 8 | 8 | 8 | 8 | 24 | 40 | 40 | 50 | 64 | 64 | 82 | 91 | 64 | 64 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1338336
95 | Patenga 50MW PP (Baraka) | [19 empty] | 7 | 30 | 40 | 50 | 18 | 19 | 19 | 175200
96 | Chattogram 108 MW PP (ECPV) | 97 | 97 | 97 | 97 | 97 | 92 | 90 | 85 | 80 | 78 | 77 | 77 | 77 | 77 | 77 | 84 | 84 | 84 |  | 90 | 90 | 90 | 90 | 96 | 96 | 96 | 2117760
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 30 | 30 |  | 32 | 55 | 55 | 55 | 55 | 55 | 55 | 1282726
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1157545
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 110 | 110 | 110 | 163 | 130 | 130 | 130 | 163 | 130 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3669545
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | [8 empty] | 4400
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 52 | 49 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1302840
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 52 | 55 | 21 | 21 | 21 |  | 0 | 107118
105 | Bramhangoan 100 MW PP (Aggreko) | [20 empty] | 25 | 25 | 25 |  |  | 0 | 54969
106 | Mymensingh 200 MW PP (United) | 183 | 183 | 182 | 162 | 100 | 100 | 45 | 45 | 45 | 45 | 50 | 100 | 70 | 70 | 99 | 120 | 60 | 60 |  | 100 | 186 | 186 | 191 | 191 | 180 | 179 | 2872800
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 62 | 97 | 100 | 101 | 42 | 42 | 0 | 341367
114 | Kodda 149 MW PP Unit-1 (Summit) | 70 | 26 | 0 | [5 empty] | 0 | 39 | 82 | 98 | 97 | 98 | 102 | 115 | 90 | 70 |  | 107 | 140 | 149 | 149 | 149 | 149 | 149 | 1768464
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 40 | 20 | 38 | 50 | 50 | 90 | 90 | 100 | 100 | 100 | 100 | 50 | 50 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1957440
116 | Chandpur 200MW (Desh energy) | 200 | 155 | 100 | 100 | 17 | 17 | 17 | 17 | 20 | 51 | 51 | 85 | 85 | 85 | 94 | 100 | 68 | 51 |  | 73 | 136 | 136 | 136 | 136 | 145 | 177 | 2274240
117 | Ashuganj 150MW PP (Midland) | 150 | 150 | 150 | 150 | 150 | 50 | 20 | 30 | 56 | 135 | 155 | 148 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3358836
118 | Bibiyana-III 400 MW CCPP | 402 | 402 | 402 | 402 | 402 | 400 | 401 | 402 | 403 | 400 | 400 | 352 | 238 | 240 | 340 | 331 | 322 | 322 |  | 380 | 367 | 368 | 367 | 380 | 380 | 398 | 8852000
| Jamalpur 115 MW PP (United) | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 112 | 111 | 111 | 112 | 111 | 111 | 111 | 111 | 115 | 111 | 111 |  | 111 | 111 | 111 | 111 | 111 | 111 | 111 | 2654400
| Anwara 300 MW PP (United) | 33 | 16 | 0 | [16 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 155564
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 20 | 20 | 40 | 50 | 50 | 50 | 50 | 60 | 90 | 90 | 90 | 30 | 30 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1519680
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 53 | 53 | 75 | 115 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 2679709
| Bhairob 54.5 MW | 36 | 36 | 17 | 17 | 17 | 13 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 35 | 35 | 35 | 36 | 548280
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 2 | 3 | 8 | 8 | 19 | 14 | 15 | 14 | 17 | 8 | 3 | 1 | [8 empty] | 110787
120 | Eastern Zone Total | 8140 | 7879 | 7641 | 7455 | 7260 | 6550 | 6272 | 6228 | 6413 | 6668 | 6936 | 7127 | 7218 | 7175 | 7414 | 7367 | 6853 | 6585 |  | 7756 | 8466 | 8446 | 8498 | 8405 | 8377 | 8341 | 178885749
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 3 | 4 | 4 |  | 22 | 26 | 19 | 15 | 15 | 15 | 15 | 110060
| Khulna 225 MW CCPP | [19 empty] | 55 | 100 | 100 | 100 | 70 | 70 | 0 | 413859
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 45 | 53 | 35 | 35 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1202400
130
131
132 | United Payra Power Ltd. | [19 empty] | 7 | 17 | 17 | 17 | 17 | 17 | 17 | 108000
133 | Bhola Nutan Biddut BD LTD (GAS) | 221 | 222 | 221 | 221 | 221 | 222 | 180 | 180 | 182 | 182 | 182 | 222 | 222 | 221 | 221 | 202 | 209 | 161 |  | 161 | 162 | 202 | 200 | 200 | 200 | 200 | 4910291
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 10 | 11 | 10 | 11 | 11 | 11 | 269660
| Bhola 225 MW CCPP | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2134052
140 | Bhola 33 MW PP (Venture) | 31 | 30 | 31 | 32 | 30 | 26 | 24 | 22 | 24 | 24 | 25 | 24 | 25 | 25 | 24 | 25 | 25 | 26 |  | 30 | 31 | 32 | 30 | 33 | 30 | 29 | 649400
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 12 | 100 | 100 | 100 | 100 | 100 | 0 | 478080
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 559 | 549 | 547 | 547 | 547 | 548 | 547 | 547 | 547 | 693 | 693 | 693 | 693 | 618 | 547 | 547 | 547 | 547 |  | 546 | 546 | 546 | 546 | 547 | 543 | 541 | 13930181
147 | Bheramara 410 MW CCPP | 360 | 355 | 355 | 360 | 365 | 355 | 400 | 380 | 365 | 360 | 355 | 355 | 355 | 385 | 355 | 355 | 355 | 310 |  | 400 | 405 | 410 | 410 | 405 | 380 | 395 | 9278600
148 | Payra 1320 MW | 490 | 490 | 470 | 470 | 440 | 430 | 410 | 390 | 370 | 350 | 350 | 350 | 350 | 370 | 370 | 370 | 350 | 340 |  | 400 | 510 | 500 | 530 | 550 | 550 | 520 | 11224100
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 152 | 153 | 152 | 151 | 151 | 151 | 151 | 155 | 150 | 153 | 155 | 155 | 155 | 155 | 154 | 156 | 154 |  | 151 | 152 | 150 | 151 | 151 | 151 | 150 | 3743400
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 34 | 34 | 43 | 43 | 43 | 43 | 43 | 224544
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 1 | 1 | 0 | 0 | [8 empty] | 12900
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 117 | 115 | 106 | 90 | 124 | 116 | 109 | 104 | 101 | 78 | 38 | 64 | 109 | 108 | 106 | 103 | 109 | 101 |  | 105 | 122 | 123 | 124 | 102 | 62 | 57 | 2494000
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 211 | 216 | 216 | 216 | 191 | 174 | 178 | 180 | 168 | 170 | 165 | 166 | 172 | 175 | 156 | 159 | 156 |  | 162 | 202 | 193 | 178 | 179 | 194 | 192 | 4568191
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 180 | 185 | 178 | 186 | 185 | 179 | 176 | 176 | 180 | 130 | 130 | 151 | 166 | 175 | 164 | 195 | 177 | 179 |  | 180 | 197 | 197 | 165 | 197 | 190 | 196 | 4547573
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 395 | 408 | 403 | 404 | 411 | 323 | 280 | 280 | 290 | 290 | 293 | 344 | 407 | 348 | 408 | 380 | 392 | 402 |  | 412 | 399 | 393 | 394 | 415 | 416 | 414 | 8890545
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [17 empty] | 4 |  | 4 | 4 | 10 | 30 | 30 | 26 | 26 | 106888
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 502560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 177048
165 | Amnura 50 MW PP(Sinha) | 35 | 0 | [17 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 225420
166 | Katakhali 50 MW PP (Northern)
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 28 | 31 | 31 | 31 | 31 | 30 | 30 | 166310
168 | Santahar 50 MW Peaking PP | 31 | 0 | [17 empty] | 30 | 32 | 31 | 31 | 31 | 31 | 31 | 208320
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 16 |  | 16 | 34 | 43 | 43 | 43 | 52 | 52 | 1030560
170 | Chapainawabganj 100 MW Peaking PP | 47 | 0 | [17 empty] | 90 | 95 | 95 | 95 | 95 | 95 | 95 | 613640
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 35 | 35 | 43 | 90 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 50 |  | 56 | 60 | 70 | 94 | 94 | 94 | 94 | 2084256
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 35 | 35 | 35 | 70 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 95 | 35 |  | 75 | 95 | 95 | 95 | 95 | 95 | 95 | 1985952
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0
176 | Rangpur 113 MW PP (Confidence) | 106 | 99 | 106 | 90 | 35 | 70 | 107 | 107 | 107 | 107 | 102 | 100 | 100 | 100 | 99 | 106 | 109 | 70 |  | 97 | 99 | 99 | 99 | 99 | 100 | 106 | 2323228
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 2 | 2 | 5 | 5 | 5 |  | 3 | 2 | 2 | 1 | [8 empty] | 29405
178
178