## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:June 2021
Sl. | Items | Current Month |  | Previous Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-06-01 |  | 2021-05-01 |  | 2020-06-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13014 | 2021-06-02 | 13417 | 2021-05-22 | 12070 | 24/06/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 22:00 |  | 20:00
2 | Minimum Generation (MW) | 7369 | 2021-06-18 | 6470 | 2021-05-14 | 6656.5 | 05/06/20 | - | -
|  |  | 9:00 |  | 9:00 |  | 7:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13014 | 2021-06-02 | 13417 | 2021-05-22 | 12070 | 24/06/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 21:00 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 9351 | 2021-06-01 | 12021 | 2021-05-23 | 10183.6 | 24/06/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13014 | 2021-06-02 | 13417 | 2021-05-22 | 12070 | 24/06/20 | 14097 | 2021-04-27
|  |  | 19:00 |  | 19:00 |  | 21:00 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 11972.1667 |  | 11615.0323 |  | 10925.7667 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10113.8333 |  | 9675.8387 |  | 9156.325 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 933 | 2021-04-29 18:00 | 933 | 2021-04-29 18:00 | 950 | 04/06/2020 | 956 | 27/3/2019
|  |  | 18:00 |  | 18:00 |  | 2:30 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 187 | 2021-04-18 | 187 | 2021-04-18 | 182 | 09/06/2020 | 194 | 12/06/19
|  |  | 18:00 |  | 18:00 |  | 21:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1824.666 |  | 1736.8634 |  | 3156.9465 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 133.138 |  | 108.694 |  | 79.8302
22 | Net Generation of BPDB (MKWH) | 1691.528 |  | 1628.1694 |  | 3077.1163
23 | Net Generation of IPP (MKWH) | 4415.8372 |  | 4485.1096 |  | 2233.4592
24 | Net Generation of REB (MKWH) | 133.1241 |  | 122.6176 |  | 148.3631
24 | Net Generation of Rental Power Plant (MKWH) | 485.0104 |  | 487.59 |  | 560.7517
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 6725.4996 |  | 6723.4866 |  | 6019.6903 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 4718.5487 |  | 4753.881 |  | 4101.8172 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 291.9991 |  | 247.9394 |  | 302.7603 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1394.2185 |  | 1303.8078 |  | 1221.1035 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 17.4436 |  | 16.1091 |  | 62.4299 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 15.602 |  | 21.292 |  | 4.9313 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 420.8257 |  | 489.1513 |  | 406.4783 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 711.7673 |  | 716.5811 |  | 736.3907 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 78.1871 |  | 75.6219 |  | 78.6605 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:June 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13014 | 2021-06-02 | 21:00
Generation Period
| Dhaka | MW | 4333
| Chattogram | MW | 1190
| Cumilla | MW | 1240
| Mymensingh | MW | 1013
| Sylhet | MW | 523
a) | Total supply in East zone | MW | 8299
| Khulna | MW | 1569
| Barisal | MW | 381
| Rajshahi | MW | 1342
| Rangpur | MW | 789
b) | Total supply in West zone | MW | 4081
c) | Total supply in both zone ( a+b) | MW | 12380
Ref: | 27.21.0000.603.16.087.20.417 | Date: 18/07/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:June 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 450 | 2021-06-25 | 20:00
| b) Ishurdi end | MW | 268 | 2021-06-15 | 16:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 680 | 2021-06-15 | 16:00
| b) Ishurdi end | MW | 170 | 2021-06-25 | 20:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | - | -
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 3.53
| b) Ishurdi end | MKWH | 57.2
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 55.49
| b) Ishurdi end | MKWH | 3.43
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 300 | 2021-06-25 | 19:30
| b)Serajganj end | MW | 280 | 2021-06-15 | 16:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 260 | 2021-06-15 | 15:00
| b)Sirajganj end | MW | 250 | 2021-06-25 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 1.652 | 2021-06-25
| b)Sirajganj end | MKWH | - | -
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 1.65 | 2021-06-25
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 17.96
| b)Sirajganj end | MKWH | 42.45
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 41.63
| b)Sirajganj end | MKWH | 18.09
30 | Transmission loss of EWI /NO-2 | % | 1.145
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-23
Page: 1/2 | [8 empty] | QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month:June 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Madanganj | 132/33 kV Transformers- T1 | 2021-06-07 01:50 | 2021-06-07 02:34 | 0:44 | T | Tripped showing backup protection | 25 | 18.3333 | Power interruption
Srinagar | 132 kV bus-1 | 2021-06-09 06:45 | 2021-06-09 08:44 | 1:59 | T | Tripped showing bus bar protection | 0 | 0 | No interruption
Matuail | 132/33 kV Transformers- T2 | 2021-06-09 13:25 | 2021-06-09 14:14 | 0:49 | T | Tripped showing no relay | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformers- T2 | 2021-06-13 22:33 | 2021-06-14 00:34 | 2:01 | E/O | Due to red-hot maint | 50 | 100.8333 | Power interruption
Munshiganj | 33 kV Bus | 2021-06-14 06:06 | 2021-06-14 08:46 | 2:40 | E/O | Due to red-hot maint | 60 | 160 | Power interruption
Tangail | 33 kV Bus section-3 | 2021-06-16 23:57 | 2021-06-17 00:20 | 0:23 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Uttara | 132/33 kV Transformers- GT1,GT2 | 2021-06-17 12:59 | 2021-06-17 13:15 | 0:16 | T | Tripped showing O/C relay | 22 | 5.8667 | Power interruption
Uttara | 132/33 kV Transformers- GT2 | 2021-06-17 12:59 | 2021-06-17 13:40 | 0:41 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Mymensing | 132/33 kV Transformers- T1,T2 | 2021-06-17 20:36 | 2021-06-17 20:45 | 0:09 | T | Tripped showing operating SPS | 60 | 9 | Power interruption
Satmosjid | 132/33 kV Transformers- T2 | 2021-06-19 19:00 | 2021-06-19 23:36 | 4:36 | T | Tripped showing K86, PRD relays | 0 | 0 | No interruption
Aminbazar | 230/132 kV transformer T-2 | 2021-06-21 05:33 | 2021-06-21 05:33 | 0:00 | T | Tripped showing E/F relay at 132 kV end | 0 | 0 | No interruption
Narinda | 132/33 kV Transformers- T1,T2 | 2021-06-23 14:15 | 2021-06-23 15:45 | 1:30 | T | Tripped showing gen trip,O/C relay | 35 | 52.5 | Power interruption
Manikganj | 132/33 kV Transformers- T3 | 2021-06-24 07:45 | 2021-06-24 07:45 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Netrokona | 132/33 kV Transformers- T1 | 2021-06-26 08:21 | 2021-06-26 13:21 | 5:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Savar | 33 kV Bus-B | 2021-06-26 12:04 | 2021-06-26 14:54 | 2:50 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformers- T1 | 2021-06-28 10:30 | 2021-06-28 13:25 | 2:55 | E/O | Due to red-hot maint | 35 | 102.0833 | Power interruption
Kabirpur | 132/33 kV Transformers- T3 | 2021-06-28 11:15 | 2021-06-28 13:34 | 2:19 | E/O | Due to clearance for above the work | 65 | 150.5833 | Power interruption
Kabirpur | 132/33 kV Transformers- T3 under 33 kV bus | 2021-06-28 14:55 | 2021-06-28 16:22 | 1:27 | E/O | Due to red-hot maint | 60 | 87 | Power interruption
Tangail | 132/33 kV Transformers- T2 under 33 kV bus | 2021-06-28 16:22 | 2021-06-28 21:18 | 4:56 | E/O | Due to red-hot maint | 70 | 345.3333 | Power interruption
|  |  | Total : | 35:15 |  | Unserved Energy: |  | 1031.5333
Dhaka (South) Grid Circle :
Hasnabad | 230/132 kV transformer T01 | 2021-06-20 07:25 | 2021-06-20 23:36 | 16:11 | T | Tripped showing Diff. relays | 0 | 0 | No interruption
Rampura | 230/132 kV transformer T02 | 2021-06-24 05:38 | 2021-06-24 08:35 | 2:57 | T | Due to auxiliary 33 kV E/F | 0 | 0 | No interruption
Shyampur | 132/33 kv transformers T-1 | 2021-06-24 00:22 | 2021-06-24 17:14 | 16:52 | T | Tripped showing TCSR,main protection relay | 30 | 506 | Power interruption
Shyampur | 132/33 kv transformers GT-2 | 2021-06-25 11:23 | 2021-06-25 11:59 | 0:36 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 36:36 |  | Unserved Energy: |  | 506
Chattogram Grid Circle :
Juldah | 132/33 kv transformers T-1 | 2021-06-01 14:40 | 2021-06-01 17:20 | 2:40 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Bakulia | 132/33 kv transformers T-1 | 2021-06-01 17:53 | 2021-06-01 18:13 | 0:20 | E/O | Due to red-hot maint | 20 | 6.6667 | Power interruption
Bakulia | 132/33 kv transformers T-2 | 2021-06-01 15:23 | 2021-06-01 16:17 | 0:54 | E/O | Due to red-hot maint | 25 | 22.5 | Power interruption
Sikalbaha | 132/33 kv transformers T-3 | 2021-06-05 08:28 | 2021-06-05 10:14 | 1:46 | E/O | Due to red-hot maint by BPDB | 0 | 0 | No interruption
Sikalbaha | 132/33 kv transformers T-4 | 2021-06-05 09:06 | 2021-06-05 09:06 | 0:00 | T | Due to 11 kV feeder fault | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T1 and T-3 | 2021-06-06 14:42 | 2021-06-06 15:13 | 0:31 | T | Tripped showing O/C relay | 48 | 24.8 | Power interruption
Madunaghat | 33 kV Bus-1 | 2021-06-11 10:38 | 2021-06-11 11:31 | 0:53 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Madunaghat | 132/33 kv transformers T-1& 33 kV Bus | 2021-06-13 09:45 | 2021-06-13 11:11 | 1:26 | E/O | Due to red hot maintenance | 20 | 28.6667 | Power interruption
Madunaghat | 132/33 kv transformers T-1 | 2021-06-18 21:04 | 2021-06-18 21:04 | 0:00 | E/O | Due to 33 kV WASA feeder fault | 0 | 0 | No interruption
Madunaghat | 132/33 kv transformers T-2 | 2021-06-18 21:07 | 2021-06-18 21:16 | 0:09 | E/O | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
|  |  | Total : | 8:39 |  | Unserved Energy: |  | 82.6333
Cumilla Grid Circle :
Ramganj | 132/33 kV Transformer-T2 | 2021-06-02 16:07 | 2021-06-02 17:31 | 1:24 | T | Tripped showing O/C relay | 40 | 56 | Power interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-06-02 07:50 | 2021-06-02 08:48 | 0:58 | T | Tripped showing O/C relay | 26 | 25.1333 | Power interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-06-02 09:15 | 2021-06-02 09:31 | 0:16 | T | Due to trial of 33 kV incoming CB of BPDB | 5 | 1.3333 | Power interruption
Sunamganj | 132/33 kV Transformer-T2 | 2021-06-10 15:03 | 2021-06-10 19:29 | 4:26 | T | Tripped showing Diff. relays at 33 kV end | 0 | 0 | No interruption
Kachua | 132/33 kV Transformer-T1 | 2021-06-12 09:52 | 2021-06-12 11:22 | 1:30 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sylhet | 132/33 kV Transformer-T1 | 2021-06-15 18:33 | 2021-06-15 19:35 | 1:02 | T | Tripped showing O/C & E/F relays | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2021-06-15 20:50 | 2021-06-15 21:07 | 0:17 | T | Tripped showing O/C relays | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T4 | 2021-06-15 20:50 | 2021-06-15 21:04 | 0:14 | T | Tripped showing O/C relays | 100 | 23.3333 | Power interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2021-06-15 21:09 | 2021-06-15 21:22 | 0:13 | T | Tripped showing O/C & E/F relays | 0 | 0 | No interruption
Cumilla(N) | 132/33 kV Transformer-T3 | 2021-06-16 06:55 | 2021-06-16 07:08 | 0:13 | T | Tripped showing O/C relays | 0 | 0 | No interruption
Sreemangal | 132/33 kV Transformer-T2 and T3 | 2021-06-17 09:53 | 2021-06-17 09:59 | 0:06 | T | Tripped showing REB feeder fault. | 0 | 0 | No interruption
Cumilla | 132/33 kV Transformer-T3 | 2021-06-27 11:44 | 2021-06-27 12:08 | 0:24 | T | Tripped showing O/C & Jaforganj feeder fault | 0 | 0 | No interruption
Cumilla | 132/33 kV Transformer-T4 | 2021-06-27 11:44 | 2021-06-27 12:07 | 0:23 | T | Tripped showing O/C relays | 64 | 23.3333 | Power interruption
Ashuganj | 230 kV Bus-1 | 2021-06-27 11:44 | 2021-06-27 12:07 | 0:23 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 11:49 |  |  |  | 129.1333
Khulna Grid Circle :
Faridpur | 33 kV bus section-2 | 2021-06-01 21:25 | 2021-06-01 21:56 | 0:31 | E/O | Due to red-hot maintenance | 12 | 6.2 | Power interruption
Mongla | 132/33 kV transformer T-1 ,T2 | 2021-06-03 04:00 | 2021-06-03 04:57 | 0:57 | T | Tripped showing instantaneous E/F relay | 36 | 34.2 | Power interruption
Narail | 132/33 kV Transformer-T1 | 2021-06-07 12:31 | 2021-06-07 13:23 | 0:52 | E/O | Due to red-hot maintenance | 13 | 11.2667 | Power interruption
Barisal(N) | 132/33 kV Transformer-T5 | 2021-06-14 11:30 | 2021-06-14 15:25 | 3:55 | E/O | Due to flashing from 33 kV R-phase isolator | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T1 | 2021-06-16 12:43 | 2021-06-16 13:09 | 0:26 | T | Tripped showing no relay | 58 | 25.1333 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2021-06-16 12:43 | 2021-06-16 14:42 | 1:59 | T | Tripped showing no relay | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2021-06-16 12:43 | 2021-06-16 16:36 | 3:53 | T | Tripped showing no relay | 0 | 0 | No interruption
Khulna© | 132/33 kV Transformer-T1 | 2021-06-18 04:27 | 2021-06-18 05:07 | 0:40 | T | Tripped showing dist.E/F & O/C relays | 24 | 16 | Power interruption
Madaripur | 132/33 kV Transformer-T3 | 2021-06-18 20:09 | 2021-06-18 21:26 | 1:17 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Gopalganj | 400/132 kV Transformer T02 | 2021-06-19 07:37 | 2021-06-19 07:37 | 0:00 | T | Tripped showing PRD | 0 | 0 | No interruption
Gopalganj | 400/132 kV Transformer T01 | 2021-06-19 07:37 | 2021-06-19 08:02 | 0:25 | T | Tripped showing PRD | 0 | 0 | No interruption
Faridpur | 132/33 kV Transformer-T1 | 2021-06-20 08:16 | 2021-06-20 08:53 | 0:37 | E/O | Due to red-hot maintenance | 0 | 0 | No interruption
Barishal(O) | 33 kV Bus-1 of 132/33 kV Transformer-T1 | 2021-06-27 07:14 | 2021-06-27 08:38 | 1:24 | E/O | Due to red-hot maintenance | 20 | 28 | Power interruption
Madaripur | 132/33 kV Transformer-T1 | 2021-06-28 12:25 | 2021-06-28 12:41 | 0:16 | T | Due to 33 kV Taker hat feeder Y phase breaker burst | 62 | 16.5333 | Power interruption
Madaripur | 132/33 kV Transformer-T2 | 2021-06-28 12:25 | 2021-06-28 12:47 | 0:22 | T | Due to 33 kV Taker hat feeder Y phase breaker burst | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T3 | 2021-06-28 12:25 | 2021-06-28 12:53 | 0:28 | T | Due to 33 kV Taker hat feeder Y phase breaker burst | 0 | 0 | No interruption
Jhenaidah | 132/33 kV transformer T1 | 2021-06-23 08:19 | 2021-06-23 09:47 | 1:28 | E/O | Due to red-hot maint | 45 | 66 | Power interruption
Gopalganj Old | 132/33 kV Transformer-T2 | 2021-06-29 14:46 | 2021-06-29 16:46 | 2:00 | T | Due to 33 kV incoming CB Y- pole problem | 39 | 78 | Power interruption
Gopalganj Old | 132/33 kV Transformer-T3 | 2021-06-29 21:45 | 2021-06-29 21:52 | 0:07 | T | Tripped showing E/F relays at 33 kV end | 60 | 7 | Power interruption
Gopalganj Old | 132/33 kV Transformer-T1 | 2021-06-29 14:46 | 2021-06-29 16:46 | 2:00 | T | Due to 33 kV incoming CB Y- pole problem | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T1 | 2021-06-29 19:51 | 2021-06-29 20:50 | 0:59 | T | Due to 33 kV incoming CB Y- pole problem | 0 | 0 | No interruption
Mongla | 132/33 kV Transformer-T2 | 2021-06-29 19:51 | 2021-06-29 20:54 | 1:03 | T | Due to 33 kV feeder fault | 0 | 0 | No interruption
|  |  | Total : | 25:39 |  | Unserved Energy: |  | 288.3333
HVDC Grid Circle : Nil
Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
Barapukuria | 132/33 kV transformer T4 & 33 kV bus | 2021-06-03 20:47 | 2021-06-03 21:58 | 1:11 | E/O | Due to red-hot maint | 32 | 37.8667 | Power interruption
Shahjadpur | 132/33 kV transformer T3 | 2021-06-06 03:05 | 2021-06-06 15:44 | 12:39 | E/O | Due to red-hot maint | 11 | 139.15 | Power interruption
Mohasthangarh | 132/33 kV transformer T1 & 33 kV bus | 2021-06-07 07:06 | 2021-06-07 09:17 | 2:11 | E/O | Due to red-hot maint | 10 | 21.8333 | Power interruption
Shahjadpur | 132/33 kV Transformer-T-2 | 2021-06-08 07:35 | 2021-06-08 09:02 | 1:27 | E/O | Due to bushing clamp Y-phase sparking | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T1 | 2021-06-08 08:22 | 2021-06-08 09:27 | 1:05 | E/O | Due to red-hot maint | 20 | 21.6667 | Power interruption
Saidpur | 132/33 kV Transformer-T2 | 2021-06-08 09:40 | 2021-06-08 09:40 | 0:00 | E/O | Due to 33 kV Y phase CT burst | 0 | 0 | No interruption
Ishwardi | 230/132kV Transformer-T3 | 2021-06-08 10:53 | 2021-06-08 13:19 | 2:26 | T | Tripped showing L/O,OLTC relay | 0 | 0 | No interruption
Rajshahi(O) | 132/33 kV transformer T3 | 2021-06-08 22:28 | 2021-06-09 00:12 | 1:44 | E/O | Due to red-hot maint | 35 | 60.6667 | Power interruption
Palashbari | 132/33 kV transformer T2 | 2021-06-10 11:06 | 2021-06-10 11:45 | 0:39 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura( Sherpur) | 132/33 kV transformer T1 | 2021-06-10 12:23 | 2021-06-10 14:20 | 1:57 | T | Due to basbar protection trip | 0 | 0 | No interruption
Rangpur | 132/33 kV transformer T3 | 2021-06-10 15:48 | 2021-06-10 18:13 | 2:25 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2021-06-15 22:10 | 2021-06-15 23:10 | 1:00 | E/O | Due to 33 kV B-phase CT problem | 60 | 60 | Power interruption
Rajshahi | 132/33 kV transformer T2 | 2021-06-16 17:24 | 2021-06-16 18:48 | 1:24 | E/O | Due to attend 33 kV DC fail | 0 | 0 | No interruption
Bhangura | 132/33 kV transformer T2 | 2021-06-16 20:32 | 2021-06-16 21:20 | 0:48 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Polashbari | 132/33 kV transformer T1 | 2021-06-16 23:30 | 2021-06-17 00:20 | 0:50 | E/O | Due to red-hot maint | 15 | 12.5 | Power interruption
Ishwardi | 230/132kV Transformer- T02 | 2021-06-18 20:29 | 2021-06-18 20:48 | 0:19 | E/O | Due to winding temperature | 0 | 0 | No interruption
Ishwardi | 230/132kV Transformer- T02 | 2021-06-18 23:40 | 2021-06-18 23:48 | 0:08 | T | Due to winding temperature | 0 | 0 | No interruption
Ishwardi | 230/132kV Transformer- T02 | 2021-06-19 04:00 | 2021-06-19 10:57 | 6:57 | T | Due to winding temperature | 0 | 0 | No interruption
Ishwardi | 230/132kV Transformer- T03 | 2021-06-19 10:33 | 2021-06-19 15:56 | 5:23 | T | Due to problem with tap change | 0 | 0 | No interruption
Rajshahi new | 132/33 kV transformer T2 | 2021-06-21 07:25 | 2021-06-21 08:52 | 1:27 | E/O | Due to red-hot maint | 6 | 8.7 | Power interruption
Saidpur | 132/33 kV transformer T2 | 2021-06-21 15:20 | 2021-06-21 17:20 | 2:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Ishurdi | 230/132kV Transformer- T02 | 2021-06-28 20:02 | 2021-06-28 20:20 | 0:18 | T | Due to winding temperature high | 0 | 0 | No interruption
Bogura old | 132/33 kV Transformer-T3 | 2021-06-30 11:29 | 2021-06-30 13:34 | 2:05 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Bogura | 230/132kV Transformer- T1 | 2021-06-30 21:53 | 2021-06-30 21:59 | 0:06 | T | Due to line overload | 0 | 0 | No interruption
|  |  | Total : | 50:29 |  |  |  | 362.3833
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 168:27 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:June 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-01 04:50 | 2021-06-01 05:08 | 0:18 | T | Tripped showing dist relay | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-01 05:39 | 2021-06-01 06:05 | 0:26 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV lines-1 & 2 | 2021-06-01 05:39 | 2021-06-01 06:05 | 0:26 | T | Tripped showing SPS | 44 | 19.0667 | Power interruption
Kodda | Kodda-Gazipur 100 MW 132 kV line | 2021-06-01 05:35 | 2021-06-01 06:07 | 0:32 | T | Tripped showing O/L relay | 0 | 0 | No interruption
Ashuganj | Sirajganj-Ashuganj 230 kV line-1 | 2021-06-01 05:42 | 2021-06-01 05:42 | 0:00 | T | Tripped showing dist.Z1,SOTF relay | 0 | 0 | No interruption
Ashuganj | Sirajganj-Ashuganj 230 kV line-1 | 2021-06-01 08:13 | 2021-06-01 14:06 | 5:53 | T | Tripped showing dist.Z1,SOTF relay | 0 | 0 | No interruption
| Sirajganj-Ashuganj 230 kV line-1 | 2021-06-01 14:39 | 2021-06-01 14:53 | 0:14 | T | Tripped showing dist.Z1,SOTF relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Joydevpur 132 kV line-1 | 2021-06-03 06:35 | 2021-06-03 06:38 | 0:03 | T | Tripped Due to DC MCB fail | 30 | 1.5 | Power interruption
Joydevpur | Joydevpur-Kodda 132 kV line-1,2 | 2021-06-03 06:13 | 2021-06-03 06:13 | 0:00 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj 132 kV line-2 | 2021-06-04 15:42 | 2021-06-04 15:42 | 0:00 | E/O | Due to R-phase PT problem | 0 | 0 | No interruption
Mymensing | Mymensing-Kishoreganj 132 kV line-2 | 2021-06-04 18:34 | 2021-06-04 19:02 | 0:28 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV line-2 | 2021-06-04 07:10 | 2021-06-04 08:29 | 1:19 | T | Tripped showing dist relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV line-2 | 2021-06-04 07:10 | 2021-06-04 07:23 | 0:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-1 | 2021-06-06 03:38 | 2021-06-06 04:26 | 0:48 | T | Tripped showing dist relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV line-2 | 2021-06-06 08:45 | 2021-06-06 13:13 | 4:28 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Keraniganj | Keraniganj-Srinagar 132 kV line-2 | 2021-06-06 13:18 | 2021-06-06 13:56 | 0:38 | T | Tripped showing dist relay | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2021-06-06 14:51 | 2021-06-06 15:03 | 0:12 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV line-2 | 2021-06-06 16:17 | 2021-06-06 16:39 | 0:22 | T | Tripped showing auto reclosure block | 0 | 0 | No interruption
Agargaon | Agargaon-Cantonment 132 kV line-1 | 2021-06-08 22:54 | 2021-06-08 22:54 | 0:00 | T | Tripped showing differential relay | 0 | 0 | No interruption
Ghorashal AIS | Ghorashal AIS-GIS 230 kV line | 2021-06-09 14:25 | 2021-06-09 19:25 | 5:00 | T | Tripped showing no relay | 0 | 0 | No interruption
Ullon | Ullon-Haripur 132 kV line-1 | 2021-06-10 14:07 | 2021-06-10 14:17 | 0:10 | T | Tripped showing Diff. Z-1 relays | 0 | 0 | No interruption
Tangail | Tangail-Kaliakoir 132 kV line-1 | 2021-06-11 00:52 | 2021-06-11 01:01 | 0:09 | T | Tripped showing dist relay | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2021-06-11 10:39 | 2021-06-11 15:05 | 4:26 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj(S) | Ashuganj(S)-Ghorashal 230 kV line-2 | 2021-06-11 18:59 | 2021-06-11 20:10 | 1:11 | T | Tripped showing dist relay | 0 | 0 | No interruption
Ashuganj | Ashuganj(S)-Ghorashal 230 kV line-1 | 2021-06-13 17:25 | 2021-06-13 17:43 | 0:18 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1,2 | 2021-06-17 05:05 | 2021-06-17 05:46 | 0:41 | T | Tripped showing dist relay | 49 | 33.4833 | Power interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2021-06-18 02:43 | 2021-06-18 03:36 | 0:53 | T | Tripped showing dist relay | 80 | 70.6667 | Power interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-18 19:15 | 2021-06-18 19:27 | 0:12 | T | Tripped showing dist relay | 0 | 0 | No interruption
Maniknagar | Maniknagar-Narinda 132 kV line-2 | 2021-06-23 14:15 | 2021-06-23 18:36 | 4:21 | T | Tripped showing pilot wire protection, gen trip | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Kodda-300 MW P/S 230 kV line | 2021-06-25 09:02 | 2021-06-25 10:22 | 1:20 | E/O | Due to CB gas leakage at Kodda end. | 0 | 0 | No interruption
Ashuganj | Ashuganj-Kishorganj 132 kV line-1 | 2021-06-26 17:15 | 2021-06-26 17:19 | 0:04 | T | Tripped showing dist relay | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Cumilla(N) 230 kV line-1 | 2021-06-30 13:00 | 2021-06-30 14:50 | 1:50 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Tangail 132 kV line-1 & 2 | 2021-06-30 18:00 | 2021-06-30 18:21 | 0:21 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 29:27 |  | Unserved Energy: |  | 124.7167
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2021-06-01 07:55 | 2021-06-01 07:55 | 0:00 | T | Tripped showing O/C,E/F relay | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Matuail 132 kV line | 2021-06-09 13:25 | 2021-06-09 13:39 | 0:14 | T | Tripped showing dist relay | 60 | 14 | Power interruption
Siddhirganj | Siddhirganj S/S-Siddhirganj GT-2 132 kV line | 2021-06-09 13:25 | 2021-06-09 13:47 | 0:22 | T | Tripped showing L/O . | 0 | 0 | No interruption
Haripur | Haripur-Ullon 132 kV line | 2021-06-15 16:50 | 2021-06-15 17:05 | 0:15 | T | Tripped showing O/C relay | 110 | 27.5 | Power interruption
Siddirganj | Siddirganj-Ullon 132 kV line-1 & 2 | 2021-06-15 16:50 | 2021-06-15 17:13 | 0:23 | T | Tripped showing dist relay | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 360 MW P.P. 230 kV line-1 | 2021-06-18 10:15 | 2021-06-18 11:20 | 1:05 | T | Tripped showing dist relay | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 360 MW P.P. 230 kV line-2 | 2021-06-18 10:15 | 2021-06-18 13:39 | 3:24 | T | Tripped showing Dist. O/C relay | 0 | 0 | No interruption
|  |  | Total : | 5:43 |  | Unserved Energy: |  | 41.5
Chattogram Grid Circle :
Hathazari | Hathazari-Baroirhat 132 kV line-1 | 2021-06-01 03:23 | 2021-06-01 03:57 | 0:34 | T | Tripped showing dist.Z1,E/F relay | 0 | 0 | No interruption
Hathazari | Hathazari-Baroirhat 132 kV line-2 | 2021-06-01 03:23 | 2021-06-01 03:59 | 0:36 | T | Tripped showing dist.Z1,E/F relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Kaptai 132 kV line-1 | 2021-06-01 04:44 | 2021-06-01 05:11 | 0:27 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-1 | 2021-06-04 04:43 | 2021-06-04 05:17 | 0:34 | T | Tripped showing dist. relay | 20 | 11.3333 | Power interruption
Hathazari | Hathazari-Kaptai 132 kV line-1 | 2021-06-04 04:54 | 2021-06-04 05:02 | 0:08 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sikalbaha | Sikalbaha-Madunaghat 132 kV both lines | 2021-06-06 10:37 | 2021-06-06 10:54 | 0:17 | T | Tripped showing E/F relay | 270 | 76.5 | Power interruption
Sikalbaha | Bakulia-Khulshi 132 kV both lines | 2021-06-06 10:37 | 2021-06-06 10:54 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
GPH | GPH-BSRM 230 kV line | 2021-06-15 13:18 | 2021-06-15 13:41 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-06-17 04:56 | 2021-06-17 05:28 | 0:32 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-1 | 2021-06-19 04:05 | 2021-06-19 19:27 | 15:22 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Bakulia | Bakulia-Sikalbaha 132 kV line-1 | 2021-06-24 14:50 | 2021-06-24 15:14 | 0:24 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-2 | 2021-06-30 10:48 | 2021-06-30 12:20 | 1:32 | T | Tripped showing dist. relay | 95 | 145.6667 | Power interruption
Kaptai | Kaptai-Chandraghona 132 kV line-2 | 2021-06-29 12:12 | 2021-06-29 16:55 | 4:43 | T | Tripped showing dist. O/C relay | 0 | 0 | No interruption
Rampur | Rampur-Halishar 132 kV line-1 | 2021-06-29 18:31 | 2021-06-29 18:31 | 0:00 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Hathazari S/S- | Hathazari S/S-Hathazari P/S 132 kV | 2021-06-30 14:05 | 2021-06-30 14:05 | 0:00 | T | Due to R-phase PT burst at S/S end. | 0 | 0 | No interruption
|  |  | Total : | 25:49 |  | Unserved Energy: |  | 233.5
Cumilla Grid Circle :
Ashuganj | Sirajganj-Ashuganj 230 kV line-1 | 2021-06-01 05:42 | 2021-06-01 05:42 | 0:00 | T | Tripped showing dist.Z1,SOTF relay | 0 | 0 | No interruption
Ashuganj | Sirajganj-Ashuganj 230 kV line-2 | 2021-06-01 05:42 | 2021-06-01 05:42 | 0:00 | T | Tripped showing dist.Z1,SOTF relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Kulaura 132 kV line-1,2 | 2021-06-04 04:49 | 2021-06-04 05:15 | 0:26 | T | Tripped showing dist. relay | 30 | 13 | Power interruption
Fenchuganj | Fenchuganj S/S-Sylhet 132 kV line | 2021-06-04 03:21 | 2021-06-04 03:39 | 0:18 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Shahjibazar | Shahjibazar-B.Baria 132 kV both lines | 2021-06-06 07:10 | 2021-06-06 07:19 | 0:09 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Bhulta 400 kV line-1 | 2021-06-06 04:34 | 2021-06-06 07:19 | 2:45 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sylhet | Sylhet-Chatak 132 kV line-2 | 2021-06-07 05:10 | 2021-06-07 05:21 | 0:11 | T | Tripped showing dist. relay | 25 | 4.5833 | Power interruption
Chandpur | Chandpur-Ramganj 132 kV line-1 | 2021-06-12 09:29 | 2021-06-12 11:30 | 2:01 | T | Tripped showing E/F,O/C relays | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Srimongal 132 kV line-1 | 2021-06-13 06:15 | 2021-06-13 06:38 | 0:23 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Sunamganj | Sunamganj-Chatak 132 kV line | 2021-06-15 18:14 | 2021-06-15 18:25 | 0:11 | T | Tripped showing dist. relay | 24 | 4.4 | Power interruption
Ramganj | Ramganj-Chandpur Desh 132 kV line-1 | 2021-06-16 12:08 | 2021-06-16 13:02 | 0:54 | E/O | Due to red hot maintenance | 0 | 0 | No interruption
Feni | Feni-Baroirhat 132 kV line | 2021-06-26 18:38 | 2021-06-26 18:38 | 0:00 | T | Due to LA burst at Feni end showing dist. relay | 0 | 0 | No interruption
Feni | Feni-Chaddogram 132 kV line-2 | 2021-06-29 06:10 | 2021-06-29 06:27 | 0:17 | T | Tripped showing dist. relay | 0 | 0 | No interruption
Chowmuhoni | Chowmuhoni-Feni 132 kV | 2021-06-22 15:01 | 2021-06-22 17:14 | 2:13 | T | Tripped showing dist. relay | 36 | 79.8 | Power interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-2 | 2021-06-29 10:01 | 2021-06-29 12:34 | 2:33 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-2 | 2021-06-29 12:34 | 2021-06-29 13:10 | 0:36 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-1 | 2021-06-29 12:26 | 2021-06-29 12:26 | 0:00 | T | Tripped showing Diff. relay | 0 | 0 | No interruption
|  |  | Total : | 12:57 |  | Unserved Energy: |  | 101.7833
Khulna Grid Circle :
Barisal | Barisal-Patuakhali 132 kV line | 2021-06-01 22:14 | 2021-06-01 22:30 | 0:16 | T | Tripped showing dist relay | 45 | 12 | Power interruption
Gopalganj- | Gopalganj-Madaripur 132 kV line-2 | 2021-06-05 14:46 | 2021-06-05 15:19 | 0:33 | T | Tripped showing dist relay | 0 | 0 | No interruption
Madaripur | Madaripur-Shariatpur 132 kV line-2 | 2021-06-05 15:06 | 2021-06-05 16:09 | 1:03 | T | Tripped showing dist , O/C relay | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2021-06-05 19:39 | 2021-06-05 20:08 | 0:29 | T | Tripped showing dist relay | 0 | 0 | No interruption
Orion Rupsha | Orion Rupsha-Goalpara 132 kV line | 2021-06-06 17:44 | 2021-06-06 17:58 | 0:14 | T | Tripped showing dist relay | 0 | 0 | No interruption
Barishal | Barishal-Bhandaria 132 kV line | 2021-06-07 13:40 | 2021-06-07 13:50 | 0:10 | T | Tripped showing dist relay | 0 | 0 | No interruption
Orion Rupsha P.P | Orion Rupsha P.P.-Goalpara 132 kV line-1 | 2021-06-27 16:40 | 2021-06-27 16:58 | 0:18 | T | Tripped showing dist relay | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gallamari 132 kV line-1,2 | 2021-06-20 12:53 | 2021-06-20 12:53 | 0:00 | T | Tripped showing E/F relay. | 0 | 0 | No interruption
|  |  | Total : | 3:03 |  | Unserved Energy: |  | 12
HVDC Grid Circle :
HVDC | HVDC-Bahrampur 400 kV line -1 | 2021-06-07 16:28 | 2021-06-07 16:50 | 0:22 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Naogaon | Naogaon-Shantahar PP 132 kV line | 2021-06-03 17:23 | 2021-06-03 17:40 | 0:17 | T | Tripped showing O/C,E/F relay | 0 | 0 | No interruption
Bogura | Bogura-Mohastanghor 132 kV line-1 | 2021-06-03 17:22 | 2021-06-03 17:35 | 0:13 | T | Tripped showing dist relay | 0 | 0 | No interruption
Pabna | Pabna-Shahjadpur 132 kV line-1 | 2021-06-06 16:01 | 2021-06-06 16:56 | 0:55 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur(Bogura) 132 kV line-1 | 2021-06-07 17:40 | 2021-06-07 18:34 | 0:54 | T | Tripped showing no relay | 0 | 0 | No interruption
Bogura | Bogura-Sherpur(Bogura) 132 kV line-1 | 2021-06-10 12:23 | 2021-06-10 14:15 | 1:52 | T | Tripped showing basbar protection trip | 0 | 0 | No interruption
Sirajganj | Sirajganj-Bogura Sherpur 132 kV line-1 | 2021-06-10 12:23 | 2021-06-10 14:13 | 1:50 | T | Tripped showing Directional E/F relays | 0 | 0 | No interruption
Naogaon | Naogaon-Shantahar P/P 132 kV line-1 | 2021-06-11 17:05 | 2021-06-11 17:05 | 0:00 | E/O | Due to CB problem at Shantahar P/P end. | 0 | 0 | No interruption
Naogaon | Naogaon-Shantahar P/P 132 kV line | 2021-06-19 11:10 | 2021-06-19 18:02 | 6:52 | E/O | Due to CB problem at Shantahar P/P end. | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV line-1 | 2021-06-26 11:21 | 2021-06-26 11:40 | 0:19 | T | Tripped showing dist relay | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-2 | 2021-06-26 19:26 | 2021-06-26 20:27 | 1:01 | T | Tripped showing O/C, E/.F relay | 150 | 152.5 | Power interruption
Naogaon | Naogaon-Santahar 132 kV line | 2021-06-26 19:26 | 2021-06-26 19:26 | 0:00 | T | Tripped showing Dir. O/C relay | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur confidence 132 kV line-1 | 2021-06-28 19:19 | 2021-06-28 19:40 | 0:21 | T | Tripped showing dist relay | 0 | 0 | No interruption
Rangpur S/S | Rangpur S/S-Rangpur confidence 132 kV line-2 | 2021-06-28 19:19 | 2021-06-28 19:45 | 0:26 | T | Tripped showing dist relay | 0 | 0 | No interruption
Amnura | Amnura-Rajshahi(new) 132 kV line | 2021-06-29 03:48 | 2021-06-29 04:26 | 0:38 | T | Tripped showing dist relay | 0 | 0 | No interruption
|  |  | Total : | 15:38 |  | Unserved Energy: |  | 152.5
Others :Nil
Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 92:37 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:June 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Kishoreganj | 132/33 kV Transformer-T1 | 2021-06-02 08:32 | 2021-06-02 15:28 | 6:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T1 | 2021-06-02 12:22 | 2021-06-02 12:28 | 0:06 | S/O | Due to harmonic test . | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2021-06-02 13:25 | 2021-06-02 14:10 | 0:45 | S/O | Due to harmonic test . | 0 | 0 | No interruption
Ghorasal | 230 kV bus coupler-2 | 2021-06-03 06:47 | 2021-06-03 06:47 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T2 | 2021-06-03 09:20 | 2021-06-03 09:20 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi 678B CB | 2021-06-03 11:26 | 2021-06-03 12:36 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Joydevpur | 132/33 kV Transformer-T2 | 2021-06-03 13:03 | 2021-06-03 13:56 | 0:53 | S/O | Due to C/M work | 40 | 35.3333 | Power interruption
Kabirpur | 132/33 kV Transformer-T1 | 2021-06-04 06:07 | 2021-06-04 10:28 | 4:21 | S/O | Due to C/M work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T1 | 2021-06-04 07:15 | 2021-06-04 15:02 | 7:47 | S/O | Due to D/W work | 10 | 77.8333 | Power interruption
Madanganj | 132 kV bus-1 | 2021-06-04 09:40 | 2021-06-04 15:58 | 6:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-04 08:40 | 2021-06-04 17:46 | 9:06 | S/O | Due to C/M work | 0 | 0 | No interruption
New Tongi | 132/33 kV Transformer-T2 | 2021-06-04 15:05 | 2021-06-04 19:10 | 4:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2021-06-05 09:45 | 2021-06-05 17:22 | 7:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-05 09:43 | 2021-06-05 17:32 | 7:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T3 | 2021-06-05 14:43 | 2021-06-05 15:11 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-06 08:35 | 2021-06-06 17:01 | 8:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T1 | 2021-06-07 07:18 | 2021-06-07 07:18 | 0:00 | S/O | Due to replacing 132 kV CT. | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-07 09:07 | 2021-06-07 16:45 | 7:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2021-06-07 12:07 | 2021-06-07 13:27 | 1:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV Transformer-T2 | 2021-06-08 09:58 | 2021-06-08 10:52 | 0:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T1 | 2021-06-08 13:36 | 2021-06-08 14:35 | 0:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Madanganj | 132/33 kV Transformer-T2 | 2021-06-09 13:36 | 2021-06-08 14:50 |  | S/O | After maintenance work | 0 | 0 | No interruption
Keraniganj | 230/132 kV Transformer- T01 | 2021-06-09 10:18 | 2021-06-09 10:18 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Rampura | 132 kV Bus-1 | 2021-06-09 09:49 | 2021-06-09 10:18 | 0:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV Transformer-T3 | 2021-06-09 14:20 | 2021-06-09 14:40 | 0:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-06-09 16:32 | 2021-06-09 16:49 | 0:17 | S/O | Due to C/M work | 20 | 5.6667 | Power interruption
Bhaluka | 132/33 kV Transformer-T2 | 2021-06-09 16:38 | 2021-06-09 16:44 | 0:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | 132 kV reserve Bus | 2021-06-11 09:24 | 2021-06-11 16:28 | 7:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-11 08:29 | 2021-06-11 17:26 | 8:57 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur(Mym.) | 132/33 kV Transformer-T1 with 33 kV Bus | 2021-06-12 06:52 | 2021-06-12 12:22 | 5:30 | S/O | Due to D/W work | 25 | 137.5 | Power interruption
Mymensingh | 132/33 kV Transformer-T1 with 33 kV Bus | 2021-06-12 07:14 | 2021-06-12 08:27 | 1:13 | S/O | Due to C/M work | 20 | 24.3333 | Power interruption
Aminbazar | 230/132 kV Transformer-T3 | 2021-06-12 09:57 | 2021-06-12 13:05 | 3:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T1,T2 | 2021-06-12 08:03 | 2021-06-12 18:36 | 10:33 | S/O | Due to C/M work | 50 | 527.5 | Power interruption
Saver | 132/33 kV Transformer-T3 | 2021-06-12 09:07 | 2021-06-12 16:37 | 7:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230 Bus coupler | 2021-06-13 11:49 | 2021-06-13 16:35 | 4:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | 132/33 kV Transformer-T3,T4 | 2021-06-13 08:52 | 2021-06-13 16:40 | 7:48 | S/O | Due to C/M work | 100 | 780 | Power interruption
Nawabganj | 33 kV Bus-1 & 2 | 2021-06-15 07:32 | 2021-06-15 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T2 | 2021-06-15 09:08 | 2021-06-15 16:05 | 6:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 with 33 kV Bus | 2021-06-16 11:32 | 2021-06-16 13:01 | 1:29 | S/O | Due to C/M work | 14 | 20.7667 | Power interruption
Keraniganj | 132/33 kV Transformer-T1 | 2021-06-16 12:09 | 2021-06-16 15:31 | 3:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Jamalpur | 132/33 kV Transformer-T4 | 2021-06-17 14:10 | 2021-06-17 15:11 | 1:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Kishorganj | 132/33 kV Transformer-T3 | 2021-06-17 14:36 | 2021-06-17 14:54 | 0:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Satmosjid | 132/33 kV Transformer-T2 | 2021-06-18 13:05 | 2021-06-18 13:12 | 0:07 | S/O | Due to removing Sack | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-06-18 09:39 | 2021-06-18 18:10 | 8:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | 132/33 kV Transformer-T1 | 2021-06-23 09:26 | 2021-06-23 13:44 | 4:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-25 09:09 | 2021-06-25 20:55 | 11:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T1 with 33 kV Bus-1 | 2021-06-25 09:30 | 2021-06-25 12:51 | 3:21 | S/O | Due to C/M work | 17 | 56.95 | Power interruption
Savar | 132/33 kV Transformer-T1 | 2021-06-26 13:10 | 2021-06-26 14:57 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV Transformer-T1 | 2021-06-27 07:03 | 2021-06-27 07:03 | 0:00 | S/O | Due to replacing of 132 kV CT. | 0 | 0 | No interruption
Kaliakoir | 132 kV Bus-2 | 2021-06-27 11:37 | 2021-06-27 11:37 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kaliakoir | 230 kV Bus-2 | 2021-06-27 10:57 | 2021-06-27 18:23 | 7:26 | S/O | Due to D/W work | 0 | 0 | No interruption
Savar | 132/33 kV Transformer-T3 | 2021-06-27 08:28 | 2021-06-27 16:36 | 8:08 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 400 kV Bus-1&2 and 400 kV dia 01 | 2021-06-27 15:50 | 2021-06-27 15:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | 132 kV reserve Bus | 2021-06-28 07:09 | 2021-06-28 07:09 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrokona | 132/33 kV Transformer-T2 | 2021-06-28 08:55 | 2021-06-28 12:52 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV Transformer-T2 | 2021-06-28 11:05 | 2021-06-28 13:22 | 2:17 | S/O | Due to C/M work | 0 | 0 | No interruption
Narail | 132/33 kV Transformer-T2 with 33 kV bus section-1 | 2021-06-28 08:21 | 2021-06-28 09:56 | 1:35 | S/O | Due to C/M work | 13 | 20.5833 | Power interruption
Netrokona | 132/33 kV Transformer-T2 | 2021-06-28 13:10 | 2021-06-28 13:41 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 230 kV Bus-1 | 2021-06-30 11:08 | 2021-06-30 17:04 | 5:56 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 207:06 |  | Unserved Energy: |  | 1686.4667
Dhaka (South) Grid Circle :
Haripur | 230 kV mid breakerof T2 trans | 2021-06-03 20:33 | 2021-06-03 20:49 | 0:16 | S/O | Due to protection test. | 0 | 0 | No interruption
Haripur | 230 kV Bus-2 |  | 2021-06-03 18:43 |  | S/O | After maintenance work | 0 | 0 | No interruption
Haripur | 230/132 kV transformer T-2 |  | 2021-06-03 18:45 |  | S/O | After maintenance work | 0 | 0 | No interruption
Rampura | 132 kV Bus-2 | 2021-06-20 10:43 | 2021-06-20 17:36 | 6:53 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrokona | 132/33 kV Transformer-T1 | 2021-06-20 15:01 | 2021-06-20 15:16 | 0:15 | S/O | Due to D/W work | 0 | 0 | No interruption
Netrokona | 132/33 kV Transformer-T3 | 2021-06-20 15:16 | 2021-06-20 16:05 | 0:49 | S/O | Due to D/W work | 0 | 0 | No interruption
Aftabnagar | 132/33 kV Transformer-T2 | 2021-06-17 15:39 | 2021-06-17 16:57 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 132 kV bus-A | 2021-06-28 09:13 | 2021-06-28 11:07 | 2:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 11:49 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | 132/33 kV Transformer-T2 | 2021-06-03 06:28 | 2021-06-03 06:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
GPH | 230 kV Bus-2 | 2021-06-06 12:27 | 2021-06-06 12:27 | 0:00 | S/O | Due to testing work. | 0 | 0 | No interruption
Sikalbaha | 231 kV Bus-1 | 2021-06-07 11:08 | 2021-06-07 11:08 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishar | 132/33 kV Transformer-T1 | 2021-06-11 08:26 | 2021-06-11 11:50 | 3:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | 132/33 kv transformers T-2 | 2021-06-16 08:17 | 2021-06-17 20:20 | 36:03 | S/O | Due to C/M work | 16 | 576.8 | Power interruption
Hathazari | 230/132 kV transformers MT-03 | 2021-06-16 11:34 | 2021-06-16 16:27 | 4:53 | S/O | Due to C/M work | 0 | 0 | No interruption
Madunaghat | 132/33 kv transformers T-1 | 2021-06-18 07:42 | 2021-06-18 07:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-3 | 2021-06-20 10:23 | 2021-06-20 12:58 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-1 | 2021-06-21 10:01 | 2021-06-21 11:28 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 230 kV Bus-2 | 2021-06-21 10:30 | 2021-06-21 10:30 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-2 | 2021-06-21 11:36 | 2021-06-21 12:07 | 0:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-3 | 2021-06-29 19:32 | 2021-06-29 21:44 | 2:12 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 51:05 |  | Unserved Energy : |  | 576.8
Cumilla Grid Circle :
Chandraghona | 132 kV bus coupler |  | 2021-06-02 16:38 |  | S/O | After maintenance work | 0 | 0 | No interruption
Ashuganj | 230 kV bus-1 | 2021-06-03 10:57 | 2021-06-03 18:01 | 7:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | 230 kV GIS Bus | 2021-06-06 12:27 | 2021-06-06 17:32 | 5:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Kamrangichar | 132/33 kV transformer GT1 | 2021-06-11 13:04 | 2021-06-11 14:03 | 0:59 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangichar | 132/33 kV transformer GT-2 & GT-3 | 2021-06-11 15:03 | 2021-06-11 15:38 | 0:35 | S/O | Due to test | 0 | 0 | No interruption
Ashuganj | 230 kV 230 Bus coupler | 2021-06-13 10:28 | 2021-06-13 10:28 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T-4 | 2021-06-14 09:01 | 2021-06-14 17:24 | 8:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Biyanibazar | 33 kV Bus with transformer T-1 & T-2 | 2021-06-15 09:12 | 2021-06-15 12:40 | 3:28 | S/O | Due to C/M work | 30 | 104 | Power interruption
Ashuganj | 230 kV Bus-1(GIS section) | 2021-06-15 13:24 | 2021-06-15 13:24 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Cumilla(N) | 230/132 kV transformer T-1 | 2021-06-17 08:58 | 2021-06-17 08:58 | 0:00 | S/O | Due to bushing replacement. | 0 | 0 | No interruption
Netrokona | 132/33 kV transformer T1 | 2021-06-19 14:17 | 2021-06-19 14:56 | 0:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Feni | 132/33 kV transformer T1 with 33 kV Bus | 2021-06-21 07:48 | 2021-06-21 08:54 | 1:06 | S/O | Due to C/M work | 17 | 18.7 | Power interruption
Chandpur | 132 kV Bus-A | 2021-06-24 07:11 | 2021-06-24 07:11 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T1 and 132 kV Bus-B | 2021-06-26 16:44 | 2021-06-26 20:42 | 3:58 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | 132/33 kV transformer T2 | 2021-06-29 13:48 | 2021-06-29 19:20 | 5:32 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 36:49 |  | Unserved Energy : |  | 122.7
Khulna Grid Circle :
Barisal(N) | 132/33 kV transformer T4 & T5 | 2021-06-02 07:29 | 2021-06-02 09:12 | 1:43 | S/O | Due to C/M work | 18 | 30.9 | Power interruption
Mongla | 132/33 kV Transformer-T2 | 2021-06-02 14:21 | 2021-06-02 15:38 | 1:17 | S/O | Due to C/M work | 15 | 19.25 | Power interruption
Gollamari | 132/33 kV Transformer-T2 | 2021-06-05 10:47 | 2021-06-05 13:45 | 2:58 | S/O | Due to new feeder connection. | 12 | 35.6 | Power interruption
Satkhira | 132/33 kV Transformer-T2 | 2021-06-05 11:10 | 2021-06-05 11:35 | 0:25 | S/O | Due to tap position difference | 10 | 4.1667 | Power interruption
Chuadanga | 132/33 kV Transformer-T2 | 2021-06-06 06:32 | 2021-06-06 06:32 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chuadanga | 132/33 kV Transformer-T2 | 2021-06-07 06:30 | 2021-06-07 16:10 | 9:40 | S/O | Due to D/W work | 10 | 96.6667 | Power interruption
Khulna(S) | 230 kV Bus-2 | 2021-06-07 08:25 | 2021-06-07 12:45 | 4:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Barisal(S) | 132/33 kV Transformer-T1r with 33 kV bus | 2021-06-09 07:12 | 2021-06-09 08:18 | 1:06 | S/O | Due to C/M work | 20 | 22 | Power interruption
Chuadanga | 132/33 kV Transformer-T2 | 2021-06-09 06:20 | 2021-06-09 09:26 | 3:06 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1 | 2021-06-09 17:18 | 2021-06-09 19:07 | 1:49 | S/O | Due to C/M work | 30 | 54.5 | Power interruption
Gopalganj | 132/33 kV Transformer-T1 | 2021-06-09 17:51 | 2021-06-09 19:05 | 1:14 | S/O | Due to C/M work | 30 | 37 | Power interruption
Kustia | 132/33 kV Transformer-T1 | 2021-06-11 07:03 | 2021-06-11 07:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(New) | 400/132 kV Transformer-T02 | 2021-06-11 10:51 | 2021-06-11 11:43 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj(New) | 400/132 kV Transformer-T01 | 2021-06-11 09:13 | 2021-06-11 11:45 | 2:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T1 | 2021-06-12 08:03 | 2021-06-12 09:15 | 1:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T1with 33 kV bus | 2021-06-15 08:17 | 2021-06-15 11:06 | 2:49 | S/O | Due to PBS work | 26 | 73.2333 | Power interruption
Barguna | 132/33 kV Transformer-T1 | 2021-06-17 08:04 | 2021-06-17 09:56 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV Transformer-T2 | 2021-06-18 07:44 | 2021-06-18 10:17 | 2:33 | S/O | Due to C/M work | 15 | 38.25 | Power interruption
Gollamari | 132 kV Bus-1 | 2021-06-18 09:15 | 2021-06-18 17:20 | 8:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Satkhira | 132/33 kV Transformer-T2 | 2021-06-19 08:24 | 2021-06-19 10:08 | 1:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2021-06-19 11:54 | 2021-06-19 13:30 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Gallamari | 132/33 kV Transformer-T1 | 2021-06-24 08:23 | 2021-06-24 09:59 | 1:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kV Transformer-T1,T2 | 2021-06-24 10:24 | 2021-06-24 11:13 | 0:49 | S/O | Due to C/M work | 19 | 15.5167 | Power interruption
Bagerhat | 132/33 kV Transformer-T1,T2 | 2021-06-25 07:57 | 2021-06-25 08:46 | 0:49 | S/O | Due to LT bus-1 armouring | 24 | 19.6 | Power interruption
Khulna(S) | 230 kV Bus-1 | 2021-06-26 08:12 | 2021-06-26 08:12 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | 231 kV Bus-1 | 2021-06-28 10:40 | 2021-06-28 17:45 | 7:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Madaripur | 132/33 kV Transformer-T2 | 2021-06-29 07:42 | 2021-06-29 08:58 | 1:16 | S/O | Due to C/M work | 20 | 25.3333 | Power interruption
|  |  | Total : | 62:28 |  | Unserved Energy : |  | 472.0167
HVDC Grid Circle :Nil
HVDC | HVDC 20DF13 shunt reactor | 2021-06-05 09:13 | 2021-06-05 11:20 | 2:07 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | Bheramara HVDC 20DF41 filter | 2021-06-06 11:23 | 2021-06-06 13:04 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
HVDC | Bheramara HVDC Pole-1 | 2021-06-12 06:16 | 2021-06-12 06:16 | 0:00 | S/O | Due to valve cooling strainer maint | 0 | 0 | No interruption
|  |  | Total : | 3:48 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Rajshahi(N) | 132 kV bus coupler breaker | 2021-06-01 11:02 | 2021-06-01 11:39 | 0:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi(N) | 133 kV bus coupler breaker | 2021-06-01 09:47 | 2021-06-01 14:30 | 4:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T3 | 2021-06-03 08:58 | 2021-06-03 10:45 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T3 | 2021-06-04 08:24 | 2021-06-04 09:51 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 | 2021-06-05 07:40 | 2021-06-05 07:40 | 0:00 | S/O | Due to CT replacement work | 0 | 0 | No interruption
Mithapukur | 132/33 kV Transformer-T1 | 2021-06-06 09:48 | 2021-06-06 13:47 | 3:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV Transformer-T1 | 2021-06-07 11:07 | 2021-06-07 14:43 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T3 | 2021-06-07 14:13 | 2021-06-07 15:13 | 1:00 | S/O | Due to CB gas refill | 0 | 0 | No interruption
Chapainawabganj | 132/33 kV Transformer-T1 | 2021-06-08 10:20 | 2021-06-09 15:06 | 28:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2021-06-09 15:30 | 2021-06-10 18:12 | 26:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T4 | 2021-06-09 20:18 | 2021-06-09 20:59 | 0:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | 132/33 kV Transformer-T4 | 2021-06-10 11:50 | 2021-06-10 15:50 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 33 kV Bus of 132/33 kV Transformer-T1,T2 | 2021-06-12 06:27 | 2021-06-12 09:14 | 2:47 | S/O | Due to D/W work | 50 | 139.1667 | Power interruption
Saidpur | 132/33 kV Transformer-T2 | 2021-06-12 10:15 | 2021-06-12 12:35 | 2:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T1 | 2021-06-13 09:47 | 2021-06-13 11:05 | 1:18 | S/O | Due to D/W work | 16 | 20.8 | Power interruption
Polashbari | 132/33 kV Transformer-T3,T4 and 33 kV Bus | 2021-06-14 12:30 | 2021-06-14 14:20 | 1:50 | S/O | Due to C/M work | 22 | 40.3333 | Power interruption
Mohasthangarh | 132/33 kV Transformer-T2 | 2021-06-14 09:59 | 2021-06-14 17:05 | 7:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 132/33 kV Transformer-T5 | 2021-06-14 12:14 | 2021-06-14 13:52 | 1:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | 33 kV Bus of 132/33 kV Transformer-T2 | 2021-06-18 08:13 | 2021-06-18 10:01 | 1:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV Transformer-T2 | 2021-06-18 09:40 | 2021-06-18 15:26 | 5:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Pabna | 132/33 kV Transformer-T3 | 2021-06-23 09:32 | 2021-06-23 13:44 | 4:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalmonirhat | 132/33 kV Transformer-T1 | 2021-06-24 12:29 | 2021-06-24 15:05 | 2:36 | S/O | Due to tan delta test | 0 | 0 | No interruption
Polashbari | 132/33 kV Transformer-T3 | 2021-06-26 12:05 | 2021-06-26 16:58 | 4:53 | S/O | Due to tan delta test | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T3 | 2021-06-27 06:34 | 2021-06-27 06:34 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 113:32 |  | Unserved Energy : |  | 200.3
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 486:37 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:June 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Ghorashal | Ghorashal-Ishordi 230 kV line-1 |  | 2021-06-01 14:55 |  | S/O | After maintenance work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-1 | 2021-06-02 06:54 | 2021-06-02 06:54 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Meghnaghat 230 kV line-2 | 2021-06-02 10:29 | 2021-06-02 19:27 | 8:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Dhamrai | Dhamrai-Kaliakoir 132 kV line-2 | 2021-06-03 06:05 | 2021-06-03 06:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | Jamalpur-UMPL 132 kV line-2 | 2021-06-03 07:13 | 2021-06-03 07:13 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV line-1 | 2021-06-03 09:08 | 2021-06-03 16:10 | 7:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV line-1 & 2 | 2021-06-04 09:57 | 2021-06-04 14:39 | 4:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Ullon 132 kV line-1 | 2021-06-04 15:09 | 2021-06-04 18:05 | 2:56 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-06-05 09:52 | 2021-06-05 21:17 | 11:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Dhamrai 132 kV line-2 |  | 2021-06-05 18:03 |  | S/O | After maintenance work | 0 | 0 | No interruption
Kodda | Kodda-Kabirpur 132 Kv line-2 | 2021-06-06 09:02 | 2021-06-06 13:11 | 4:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-1 | 2021-06-06 15:07 | 2021-06-06 15:35 | 0:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ishurdi 230 kV line-2 |  | 2021-06-06 17:19 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV line-2 | 2021-06-07 09:44 | 2021-06-07 18:28 | 8:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV line-2 | 2021-06-08 09:05 | 2021-06-08 16:17 | 7:12 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj PP 132 kV line-2 | 2021-06-08 10:26 | 2021-06-08 16:04 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV line-2 | 2021-06-09 10:26 | 2021-06-09 16:04 | 5:38 | S/O | Due to Dist. Relay testing. | 0 | 0 | No interruption
Mymensingh | Mymensingh-Netrokona 132 kV line-2 | 2021-06-10 07:25 | 2021-06-10 07:25 | 0:00 | S/O | Due to Dist. Relay replacing. | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-1 | 2021-06-11 07:23 | 2021-06-11 07:23 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbag | Lalbag-Kamrangichar 132 kV line |  | 2021-06-11 11:06 |  | S/O | After maintenance work | 0 | 0 | No interruption
Bibiyana | Bibiyana-Kaliakoir 400 kV line-2 | 2021-06-12 06:23 | 2021-06-12 08:32 | 2:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV line-2 | 2021-06-12 09:15 | 2021-06-12 17:45 | 8:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV | 2021-06-13 09:16 | 2021-06-13 17:29 | 8:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV line-2 | 2021-06-14 09:59 | 2021-06-14 17:05 | 7:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sitalakhya | Sitalakhya-Crown Cement 132 kV line |  | 2021-06-14 16:09 |  | S/O | After maintenance work | 0 | 0 | No interruption
Mymensing | Mymensing-Netrokona 132 kV line-2 | 2021-06-16 11:46 | 2021-06-16 19:37 | 7:51 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj GIS | Keraniganj GIS - Lalbag-1,2,3 132 kV lines | 2021-06-16 11:46 | 2021-06-16 11:46 | 0:00 | S/O | Due to OPGW work | 0 | 0 | No interruption
Savar | Savar-Manikganj P/S 132 kV line-1 | 2021-06-17 08:18 | 2021-06-17 13:39 | 5:21 | S/O | Due to D/W work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1,2 | 2021-06-17 13:01 | 2021-06-17 13:01 | 0:00 | S/O | Due to stringing of tower No. 66 to 67 | 0 | 0 | No interruption
Sitalakkhya | Sitalakkhya-Digital P.P. 132 kV | 2021-06-18 10:03 | 2021-06-18 10:55 | 0:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbagh 132 kV line-1,2 | 2021-06-18 11:14 | 2021-06-18 20:55 | 9:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Mogbazar 132 kV line-2 | 2021-06-18 15:17 | 2021-06-18 15:17 | 0:00 | S/O | Due to hook up Ullon 132 kV S/S | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbag 132 kV line-1,2 | 2021-06-18 07:32 | 2021-06-18 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Bibiyana 400 kV line-2 | 2021-06-21 06:57 | 2021-06-21 06:57 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj 132 kV line-1 | 2021-06-21 08:22 | 2021-06-21 08:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line | 2021-06-21 09:26 | 2021-06-21 21:16 | 11:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Bosila-Aminbazar 132 kV line | 2021-06-22 09:26 | 2021-06-22 21:16 | 11:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Kallyanpur | Kallyanpur-Lalbag 132 kV line-1,2 | 2021-06-23 09:46 | 2021-06-23 15:18 | 5:32 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tongi 132 kV line-1 | 2021-06-24 06:04 | 2021-06-24 10:23 | 4:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-24 10:28 | 2021-06-24 15:50 | 5:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-1 | 2021-06-25 06:32 | 2021-06-26 19:36 | 37:04 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbag | Lalbag-Kallyanpur 132 kV line-1,2 | 2021-06-25 07:35 | 2021-06-25 07:35 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbag | Lalbag-Kallyanpur 132 kV line-1,2 | 2021-06-26 06:39 | 2021-06-26 06:39 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Bosila(PP)-Aminbazar line | 2021-06-27 06:50 | 2021-06-27 06:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbagh | Lalbagh-Kallyanpur 132 kV line-1 | 2021-06-27 06:53 | 2021-06-27 06:53 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Jamalpur 132 kV line-1 | 2021-06-27 09:47 | 2021-06-27 16:46 | 6:59 | S/O | Due to Armouring the Conductor | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj 132 kV line-1 | 2021-06-27 12:36 | 2021-06-27 15:31 | 2:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Savar | Savar-Manikganj 132 kV line-1 | 2021-06-27 13:04 | 2021-06-27 18:56 | 5:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Manikganj P.P. 132 kV line-2 | 2021-06-27 15:41 | 2021-06-27 17:59 | 2:18 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-28 07:22 | 2021-06-28 07:22 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Lalbag | Lalbag-Kallyanpur 132 kV line-1,2 | 2021-06-28 08:37 | 2021-06-28 20:55 | 12:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | Mymensingh-Kishoreganj 132 kV line-2 | 2021-06-28 11:20 | 2021-06-28 13:44 | 2:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | Aminbazar-Lalbag-Bosila 132 kV line-1,2 | 2021-06-29 06:43 | 2021-06-29 06:43 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 Kv line-1 | 2021-06-29 12:52 | 2021-06-29 17:06 | 4:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 Kv line-1 | 2021-06-30 07:12 | 2021-06-30 07:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Kabirpur 132 kV line-2 | 2021-06-30 07:45 | 2021-06-30 07:45 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 229:32 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Haripur | Haripur-Bhulta 132 kV | 2021-06-01 16:28 | 2021-06-01 17:58 | 1:30 | S/O | Due to sky wire removed | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 230 kV line-2 | 2021-06-01 20:40 | 2021-06-01 22:02 | 1:22 | S/O | Due to CVT changing | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV line-3 | 2021-06-01 08:27 | 2021-06-01 15:16 | 6:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddhirganj 132 kV line-1 | 2021-06-05 08:26 | 2021-06-05 15:20 | 6:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 230 kV line-2 | 2021-06-05 10:06 | 2021-06-05 11:49 | 1:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj S/S | Siddhirganj S/S-Siddhirganj GT-2 P.P. 132 kV line |  | 2021-06-05 17:14 |  | S/O | After maintenance work | 0 | 0 | No interruption
Siddirganj S/S | Siddirganj S/S- Siddirganj peaking P/S 132 kV line | 2021-06-15 10:17 | 2021-06-15 12:55 | 2:38 | S/O | Due to maint.work at P/S end | 0 | 0 | No interruption
Shyampur | Shyampur-Hasnabad 230 kV line-1 | 2021-06-17 09:41 | 2021-06-17 17:39 | 7:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Matuail | Matuail-Siddhirganj 132 kV line | 2021-06-19 08:50 | 2021-06-19 14:01 | 5:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV line | 2021-06-05 07:38 | 2021-06-05 07:38 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Brammangaon 132 kV line | 2021-06-09 06:42 | 2021-06-09 06:42 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakhya 132 kV line | 2021-06-09 07:14 | 2021-06-09 07:14 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangichar 132 kV line | 2021-06-11 11:30 | 2021-06-11 12:14 | 0:44 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-APR 230 kV line | 2021-06-15 08:55 | 2021-06-15 18:41 | 9:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Keraniganj APR 230 kV line | 2021-06-15 09:04 | 2021-06-15 18:57 | 9:53 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 452:18 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2021-06-01 10:58 | 2021-06-01 11:46 | 0:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-31 | 2021-06-01 08:40 | 2021-06-01 10:21 | 1:41 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 | 2021-06-02 06:24 | 2021-06-02 16:37 | 10:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandraghona | Chandraghona-Rangamati 132 kV line-2 | 2021-06-02 14:32 | 2021-06-02 16:47 | 2:15 | S/O | Due to protection test | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-1 | 2021-06-03 07:09 | 2021-06-03 07:09 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Julda | Julda-Halishahar 132 kV line |  | 2021-06-10 03:53 |  | S/O | After maintenance work | 0 | 0 | No interruption
Dohazari | Dohazari-(Matarbari)-Cox's Bazar 132 kV line | 2021-06-12 05:50 | 2021-06-12 18:24 | 12:34 | S/O | Due to D/W work | 30 | 377 | Power interruption
Hathazari | Hathazari-Khulshi 132 kV line | 2021-06-12 06:50 | 2021-06-12 06:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV line | 2021-06-12 06:50 | 2021-06-12 06:50 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-2 | 2021-06-13 06:15 | 2021-06-13 06:15 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox's Bazar 132 kV line-1 | 2021-06-17 07:26 | 2021-06-17 17:59 | 10:33 | S/O | Due to D/W work | 10 | 105.5 | Power interruption
Halishahar | Halishahar-Kulshi 132 kV line-2 | 2021-06-20 13:35 | 2021-06-20 15:02 | 1:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowmuhoni | Chowmuhoni-Feni 132 kV line-1 | 2021-06-23 08:59 | 2021-06-23 14:49 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Raozan 230 kV line-2 | 2021-06-23 10:15 | 2021-06-23 17:35 | 7:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV line-1 | 2021-06-25 08:07 | 2021-06-25 08:07 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Matarbari | Matarbari-Cox'sbazar 132 kV line | 2021-06-26 06:02 | 2021-06-26 06:02 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ashuganj(S) 230 kV line-1 | 2021-06-28 08:20 | 2021-06-28 11:19 | 2:59 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampur | Rampur-Kulshi 132 kV line | 2021-06-30 16:36 | 2021-06-30 16:36 | 0:00 | S/O | Due to modification T-connection. | 0 | 0 | No interruption
|  |  | Total : | 55:40 |  | Unserved Energy: |  | 482.5
Cumilla Grid Circle :
Ashuganj | Ashuganj-Sirajganj 230 kV line-1 | 2021-06-01 17:00 | 2021-06-01 18:31 | 1:31 | S/O | Due to remove kite | 0 | 0 | No interruption
Feni | Feni-Chowmuhoni 132 kV line-2 | 2021-06-03 09:22 | 2021-06-03 11:52 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 132 kV line-2 |  | 2021-06-12 16:41 |  | S/O | After maintenance | 0 | 0 | No interruption
Chowddagram | Chowddagram-Comilla(N) 132 kV line-2 | 2021-06-16 11:37 | 2021-06-16 12:47 | 1:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Chowddagram | Chowddagram-Feni 132 kV line-2 | 2021-06-17 10:18 | 2021-06-17 14:28 | 4:10 | S/O | Due to protection test. | 0 | 0 | No interruption
Chowmuhoni | Chowmuhoni-Feni 132 kV line | 2021-06-22 15:01 | 2021-06-22 17:14 | 2:13 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV line-1 | 2021-06-25 06:43 | 2021-06-25 06:43 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Chandpur | Chandpur-Kachua 132 kV line-2 | 2021-06-26 06:25 | 2021-06-26 06:25 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Baroirhat 132 kV line-1 | 2021-06-27 08:57 | 2021-06-27 15:26 | 6:29 | S/O | Due to LA replacement | 0 | 0 | No interruption
Chandpur Desh P.P | Chandpur Desh P.P.-Chandpur S/S 132 kV line-1,2 | 2021-06-28 07:12 | 2021-06-28 07:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Feni | Feni-Chowmuhuni 132 kV line-2 | 2021-06-29 14:29 | 2021-06-29 17:27 | 2:58 | S/O | Due to protection test. | 0 | 0 | No interruption
|  |  | Total : | 21:01 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Gopalganj(New) | Gopalganj(New)-Payra 400 kV line-2 | 2021-06-11 09:03 | 2021-06-11 11:50 | 2:47 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Satkhira 132 kV line-2 | 2021-06-14 09:03 | 2021-06-14 12:26 | 3:23 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Mongla 132 kV line-2 | 2021-06-14 16:10 | 2021-06-14 16:10 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Barishal(N) | Barishal(N)-Madaripur 132 kV line-2 | 2021-06-15 13:48 | 2021-06-15 14:49 | 1:01 | S/O | Due to removing kite | 0 | 0 | No interruption
Gopalganj(O) | Gopalganj(O)-Gopalganj(N) 132 kV line | 2021-06-18 08:14 | 2021-06-18 17:57 | 9:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Payra | Payra-Gopalganj 400 kV line | 2021-06-19 13:58 | 2021-06-19 15:11 | 1:13 | S/O | Due to paralleling T2 transformer | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Naogaon 132 kV line-2 | 2021-06-29 11:36 | 2021-06-29 14:20 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 20:51 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC | HVDC Bheramara-Bahrampur 400 kV line-3 |  | 2021-06-14 18:31 |  | S/O | After maintenance | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Polashbari | Polashbari-Mithapukur 132 kV line-1 | 2021-06-07 14:20 | 2021-06-07 14:58 | 0:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mithapukur 132 kV line-2 | 2021-06-07 15:02 | 2021-06-07 15:48 | 0:46 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Natore 132 kV line-1 | 2021-06-13 09:15 | 2021-06-13 13:17 | 4:02 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1 | 2021-06-14 18:16 | 2021-06-14 18:46 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-1,2 | 2021-06-17 09:22 | 2021-06-17 18:24 | 9:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Jaldhaka | Jaldhaka-Saidpur 132 kV line-2 | 2021-06-19 08:20 | 2021-06-19 20:20 | 12:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-2 | 2021-06-24 06:36 | 2021-06-24 13:03 | 6:27 | S/O | Due to D/W work | 0 | 0 | No interruption
Naogaon | Naogaon-Shantahar 132 kV line-1 | 2021-06-24 10:25 | 2021-06-24 13:05 | 2:40 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV line-2 | 2021-06-25 09:45 | 2021-06-25 13:05 | 3:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-1 | 2021-06-26 05:37 | 2021-06-27 20:32 | 38:55 | S/O | Due to D/W work | 0 | 0 | No interruption
Bogura | Bogura-Naogaon 132 kV line-2 | 2021-06-29 18:02 | 2021-06-29 19:06 | 1:04 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 79:24 |  | Unserved Energy: |  | 0
Others :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 858:46 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:June 2021
| Area | Previous Month (May' 2021) |  |  |  | Current Month (June' 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 36 | 19 | 66 | 121 | 37 | 15 | 115 | 167
2 | Dhaka (South) Grid Circle. | 17 | 6 | 27 | 50 | 10 | 1 | 23 | 34
3 | Chattogram Grid Circle. | 12 | 2 | 31 | 45 | 18 | 7 | 29 | 54
4 | Cumilla Grid Circle. | 44 | 3 | 32 | 79 | 29 | 2 | 26 | 57
5 | Khulna Grid Circle. | 23 | 16 | 29 | 68 | 23 | 7 | 34 | 64
6 | HVDC Grid Circle | 1 | 0 | 2 | 3 | 1 | 0 | 4 | 5
7 | Bogura Grid Circle. | 31 | 16 | 54 | 101 | 19 | 19 | 35 | 73
8 | Others | Total number of Total: 0; Total number of Total: 0
9 | Total | 164 | 62 | 241 | 467 | 137 | 51 | 266 | 454
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:June 2021
| Area | Previous Month (April 2021) |  |  |  | Current Month (May' 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 5769.34 | 183.08 | 3297.68 | 9250.1 | 210.42 | 945.83 | 1686.47 | 2842.72
2 | Dhaka (South) Grid Circle. | 33.67 | 0 | 58.43 | 92.1 | 547.5 | 0 | 0 | 547.5
3 | Chattogram Grid Circle. | 185.26 | 58 | 0 | 243.26 | 258.3 | 57.84 | 1059.3 | 1375.44
4 | Cumilla Grid Circle. | 1205.9 | 51 | 0 | 1256.9 | 230.91 | 0 | 122.71 | 353.62
5 | Khulna Grid Circle. | 69.14 | 193.17 | 89.4 | 351.71 | 188.87 | 111.47 | 472.02 | 772.36
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Bogura Grid Circle. | 38.25 | 126.59 | 616.22 | 781.06 | 152.49 | 362.38 | 200.3 | 715.17
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 7301.56 | 611.84 | 4061.73 | 11975.13 | 1588.49 | 1477.52 | 3540.8 | 6606.81
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:June 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | [6 empty] | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 10 | 20 | 3 | 2 | 15 | 2718.0033
2 | Dhaka (South) | 5031.6 | 1 | - | 1 | - | - | 1 | 506
3 | Chattogram | 2042 | 4 | 1 | 5 | 1 | 2 | 2 | 659.43
4 | Khulna | 2434 | 10 | 13 | 23 | 4 | 6 | 13 | 760.35
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 8 | 3 | 11 | - | 2 | 9 | 562.68
7 | Cumilla | 2981 | 5 | 2 | 7 | 3 | 1 | 3 | 251.84
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 5458.3033
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.85%
3 | Chattogram | 99.97%
4 | Khulna | 99.88%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.74% | [6 empty] | Information Management Division
7 | Cumilla | 99.96% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:June 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 4 | - | 4 | 2 | 2 | - | 124.7167
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | 2 | - | - | 41.5
3 | Chattogram | 917 | - | 3 | 2 | 5 | 1 | 1 | 3 | 716
4 | Khulna | 1238.4 | - | 1 | - | 1 | 1 | - | - | 12 | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 1 | - | 1 | - | - | 1 | 152.5
7 | Cumilla | 1648.16 | - | 4 | - | 4 | 3 | - | 1 | 101.7833
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 1148.5
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.91%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.94%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.99% | [7 empty] | Information Management Division
7 | Cumilla | 99.98% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:June 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-05-18 | 34 | - | 21 | 45hr02 min |  |  | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month:June 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Madanganj | 1 | 0:44 | 25 | 18.3333 | Due to tripping of 132/33 kV Transformers- T2
Bhaluka | 2 | 2:01 | 50 | 100.8333 | Due to red-hot maintenance of 132/33 kV Trasformer T1
|  | 0:17 | 20 | 5.6667 | Due to S/D of 132/33 kV Transformer-T2
Munshiganj | 1 | 2:40 | 60 | 160 | Due to red-hot maint
Uttara | 1 | 0:16 | 22 | 5.8667 | Due to tripping of 132/33 kV Transformers-GT1,G T2
Mymensing | 2 | 0:09 | 60 | 9 | Due to tripping of 132/33 kV Transformers-T1, T2
|  | 1:13 | 20 | 24.3333 | Due to S/D of 132/33 kV Transformer-T1 with 33 kV Bus
Narinda | 1 | 1:30 | 35 | 52.5 | Due to tripping of 132/33 kV Transformers-T1, T2
Kabirpur | 5 | 2:55 | 35 | 102.0833 | Due to red-hot maint
|  | 2:19 | 65 | 150.5833 | Due to clearance for above the work
|  | 1:27 | 60 | 87 | Due to red-hot maint
|  | 3:21 | 17 | 56.95 | Due to S/D of 132/33 kV Transformer-T1 with 33 kV Bus-1
|  | 0:26 | 44 | 19.0667 | Due to tripping of Kabirpur-Manikganj 132 kV lines-1 & 2
Tangail | 1 | 4:56 | 70 | 345.3333 | Due to red-hot maint
Shyampur | 1 | 16:52 | 30 | 506 | Due to tripping of 132/33 kV Transformers- T1
Bakulia | 2 | 0:20 | 20 | 6.6667 | Due to red-hot maint
Bakulia |  | 0:54 | 25 | 22.5 | Due to red-hot maint
Halishahar | 1 | 0:31 | 48 | 24.8 | Due to tripping of 132/33 kV Transformers-T1, T3
Madunaghat | 1 | 1:26 | 20 | 28.6667 | Due to red hot maintenance
Chowmuhoni | 1 | 2:13 | 36 | 79.8 | Due to tripping of Chowmuhoni-Feni 132 kV line
Ramganj | 1 | 1:24 | 40 | 56 | Due to tripping of 132/33 kV Transformer-T2
Sylhet | 3 | 0:58 | 26 | 25.1333 | Due to tripping of 132/33 kV Transformer-T1
|  | 0:16 | 5 | 1.3333 | Due to tripping of 132/33 kV Transformer-T1
|  | 0:11 | 25 | 4.5833 | Due to tripping of Sylhet-Chatak 132 kV line-2
Cumilla(N) | 1 | 0:14 | 100 | 23.3333 | Due to tripping of 132/33 kV Transformer-T4
Cumilla | 1 | 0:23 | 64 | 23.3333 | Due to tripping of 132/33 kV Transformer-T4
Faridpur | 1 | 0:31 | 12 | 6.2 | Due to red-hot maintenance
Mongla | 2 | 0:57 | 36 | 34.2 | Due to tripping of 132/33 kV transformers T-1 & T-2
|  | 1:17 | 15 | 19.25 | Due to S/D of 132/33 kV Transformer-T2
Khulna© | 1 | 0:40 | 24 | 16 | Due to tripping of 132/33 kV Transformer-T1
Barishal(O) | 1 | 1:24 | 20 | 28 | Due to red-hot maintenance
Madaripur | 3 | 0:16 | 62 | 16.5333 | Due to tripping of 132/33 kV Transformer-T1
|  | 0:26 | 58 | 25.1333 | Due to tripping of 132/33 kV Transformer-T1
|  | 1:16 | 20 | 25.3333 | Due to S/D of 132/33 kV Transformer-T2
Jhenaidah | 1 | 1:28 | 45 | 66 | Due to red-hot maint
Gopalganj Old | 2 | 2:00 | 39 | 78 | Due to tripping of 132/33 kV Transformer-T2
|  | 0:07 | 60 | 7 | Due to tripping of 132/33 kV Transformer-T3
Barapukuria | 1 | 1:11 | 32 | 37.8667 | Due to red-hot maint
Mohasthangarh | 1 | 2:11 | 10 | 21.8333 | Due to red-hot maint
Naogaon | 2 | 1:05 | 20 | 21.6667 | Due to red-hot maint
|  | 1:00 | 60 | 60 | Due to 33 kV B-phase CT problem
Rajshahi(O) | 1 | 1:44 | 35 | 60.6667 | Due to red-hot maint
Polashbari | 2 | 1:50 | 22 | 40.3333 | Due to S/D of 132/33 kV Transformer-T3,T4 and 33 kV Bus
|  | 0:50 | 15 | 12.5 | Due to red-hot maint
Rajshahi new | 1 | 1:27 | 6 | 8.7 | Due to red-hot maint
Ghorasal | 1 | 0:03 | 30 | 1.5 | Due to tripping of Ghorasal-Joydevpur 132 kV line-1
Rampura | 2 | 0:41 | 49 | 33.4833 | Due to tripping of Rampura-Ullon 132 kV line-1,2
|  | 0:53 | 80 | 70.6667 | Due to tripping of Rampura-Ullon 132 kV line-1
Siddhirganj | 1 | 0:14 | 60 | 14 | Due to tripping of Siddhirganj-Matuail 132 kV line
Haripur | 1 | 0:15 | 110 | 27.5 | Due to tripping of Haripur-Ullon 132 kV line
Dohazari | 4 | 0:34 | 20 | 11.3333 | Due to tripping of Dohazari-Cox's Bazar 132 kV line-1
|  | 1:32 | 95 | 145.6667 | Due to tripping of Dohazari-Cox'sbazar 132 kV line-2
|  | 12:34 | 30 | 377 | Due to S/D of Dohazari-(Matarbari)-Cox's Bazar 132 kV line
|  | 10:33 | 10 | 105.5 | Due to S/D of Dohazari-Cox's Bazar 132 kV line-1
Sikalbaha | 1 | 0:17 | 270 | 76.5 | Due to tripping of Sikalbaha-Madunaghat 132 kV both lines
Fenchuganj | 1 | 0:26 | 30 | 13 | Due to tripping of Fenchuganj-Kulaura 132 kV line-1,2
Sunamganj | 1 | 0:11 | 24 | 4.4 | Due to tripping of Sunamganj-Chatak 132 kV line
Barisal | 1 | 0:16 | 45 | 12 | Due to tripping of Barisal-Patuakhali 132 kV line
Bogura | 1 | 1:01 | 150 | 152.5 | Due to tripping of Bogura-Naogaon 132 kV line-2
Joydevpur | 1 | 0:53 | 40 | 35.3333 | 132/33 kV Transformer-T2
New Tongi | 1 | 0:00 | 10 | 77.8333 | Due to S/D of 132/33 kV Transformer-T1
Sherpur(Mym.) | 1 | 5:30 | 25 | 137.5 | Due to S/D of 132/33 kV Transformer-T1 with 33 kV Bus
Kodda | 2 | 10:33 | 50 | 527.5 | Due to S/D of 132/33 kV Transformer-T1,T2
|  | 7:48 | 100 | 780 | Due to S/D of 132/33 kV Transformer-T3,T4
Sherpur | 1 | 1:29 | 14 | 20.7667 | Due to S/D of 132/33 kV Transformer-T1 with 33 kV Bus
Narail | 2 | 0:52 | 13 | 11.2667 | Due to red-hot maintenance
|  | 1:35 | 13 | 20.5833 | Due to S/D of 132/33 kV Transformer-T2 with 33 kV bus section-1
Khulshi | 1 | 36:03 | 16 | 576.8 | Due to S/D of 132/33 kv transformers T-2
Biyanibazar | 1 | 3:28 | 30 | 104 | Due to S/D of 33 kV Bus with transformer T-1 & T-2
Feni | 1 | 1:06 | 17 | 18.7 | Due to S/D of 132/33 kV transformer T1 with 33 kV Bus
Barisal(N) | 1 | 1:43 | 18 | 30.9 | Due to S/D of 132/33 kV transformer T4 & T5
Gollamari | 1 | 2:58 | 12 | 35.6 | Due to S/D of 132/33 kV Transformer-T2
Chuadanga | 1 | 9:40 | 10 | 96.6667 | Due to S/D of 132/33 kV Transformer-T2
Barisal(S) | 1 | 1:06 | 20 | 22 | Due to S/D of 132/33 kV Transformer-T1r with 33 kV bus
Satkhira | 3 | 1:49 | 30 | 54.5 | Due to S/D of 132/33 kV Transformer-T1
|  | 2:49 | 26 | 73.2333 | Due to S/D of 132/33 kV Transformer-T1with 33 kV bus
|  | 0:25 | 10 | 4.1667 | Due to S/D of 132/33 kV Transformer-T2
Gopalganj | 2 | 1:14 | 30 | 37 | Due to S/D of 132/33 kV Transformer-T1
|  | 2:33 | 15 | 38.25 | Due to S/D of 132/33 kV Transformer-T2
Noapara | 1 | 0:49 | 19 | 15.5167 | Due to S/D of 132/33 kV Transformer-T1,T2
Bagerhat | 1 | 0:49 | 24 | 19.6 | Due to S/D of 132/33 kV Transformer-T1,T2
Natore | 1 | 2:47 | 50 | 139.1667 | Due to S/D of 33 kV Bus of 132/33 kV Transformer-T1,T2
Shahjadpur | 2 | 1:18 | 16 | 20.8 | Due to S/D of 132/33 kV Transformer-T1
|  | 12:39 | 11 | 139.15 | Due to red-hot maint
| Total Unserved energy : |  |  | 6606.8 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: June'2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 126 | 7 | 2021-06-01 | 15:00
2 | Munsiganj | 108 | 4 | 2021-06-01 | 0:00
3 | Sonargaon | 90 | 28 | 2021-06-01 | 19:30
4 | Shyampur | 216 | 26 | 2021-06-01 | 0:00
5 | Bhulta | 223 | 15 | 2021-06-01 | 23:00
6 | Madanganj | 65 | 14 | 2021-06-01 | 11:00
7 | Shitalakhya | 128 | 10 | 2021-06-01 | 13:00
8 | Rahim steel | 32 | 15 | 2021-06-01 | 12:00
9 | Matuail | 66 | 5 | 2021-06-01 | 12:00
10 | Ghorasal | 82 | 27 | 2021-06-01 | 22:00
11 | Narsingdi | 181 | 13 | 2021-06-01 | 21:00
12 | Haripur (SBU) | 127 | 14 | 2021-06-01 | 21:00
13 | Sreenagar | 44 | 14 | 2021-06-01 | 22:00
14 | Ullon | 79 | 26 | 2021-06-01 | 19:30
15 | Hasnabad | 85 | 27 | 2021-06-01 | 20:00
16 | Magbazar | 102 | 3 | 2021-06-01 | 13:00
17 | Maniknagar | 78 | 28 | 2021-06-01 | 13:00
18 | Bangabhaban | 14 | 7 | 2021-06-01 | 11:00
19 | Narinda | 72 | 26 | 2021-06-01 | 13:00
20 | Dhanmondi | 215 | 14 | 2021-06-01 | 13:00
21 | Lalbag | 97 | 23 | 2021-06-01 | 17:00
22 | Madartek | 84 | 27 | 2021-06-01 | 0:00
23 | Dhaka University | 49 | 13 | 2021-06-01 | 13:00
24 | Aftabnagar | 10 | 2 | 2021-06-01 | 19:30
25 | Fatullah | 66 | 3 | 2021-06-01 | 10:00
26 | Nawabganj | 55 | 4 | 2021-06-01 | 22:00
27 | Keraniganj | 71 | 13 | 2021-06-01 | 19:30
28 | Mirpur | 170 | 6 | 2021-06-01 | 13:00
29 | Kalyanpur | 117 | 27 | 2021-06-01 | 19:30
30 | Gulshan | 146 | 3 | 2021-06-01 | 13:00
31 | Uttara | 111 | 27 | 2021-06-01 | 19:00
32 | Uttara(new) | 36 | 9 | 2021-06-01 | 12:00
33 | Kamrangirchar | 99 | 10 | 2021-06-01 | 14:00
34 | Savar | 193 | 3 | 2021-06-01 | 21:00
35 | Bhasantec | 161 | 6 | 2021-06-01 | 13:
36 | Agargaon | 83 | 6 | 2021-06-01 | 13:00
37 | Satmosjid | 99 | 4 | 2021-06-01 | 19:00
38 | Tongi | 132 | 13 | 2021-06-01 | 11:00
39 | Kabirpur | 261 | 14 | 2021-06-01 | 16:00
40 | Basundhara | 244 | 27 | 2021-06-01 | 14:00
41 | Manikganj | 88 | 25 | 2021-06-01 | 21:00
42 | Joydevpur | 185 | 27 | 2021-06-01 | 19:30
43 | New Tongi | 123 | 5 | 2021-06-01 | 12:00
44 | Kodda | 296 | 28 | 2021-06-01 | 15:00
45 | Dhamrai | 126 | 1 | 2021-06-01 | 0:00
46 | Rajendrapur | 112 | 24 | 2021-06-01 | 20:00
47 | Valuka | 130 | 1 | 2021-06-01 | 19:00
48 | Tangail | 219 | 2 | 2021-06-01 | 21:00
49 | Mymensing | 233 | 26 | 2021-06-01 | 20:00
50 | Kishorganj | 144 | 26 | 2021-06-01 | 24:00
51 | Netrokona | 133 | 10 | 2021-06-01 | 21:00
52 | Jamalpur | 152 | 27 | 2021-06-01 | 21:00
53 | Sherpur | 152 | 4 | 2021-06-01 | 5:00
54 | Srimongal | 61 | 12 | 2021-06-01 | 21:00
55 | Shahjibazar | 125 | 9 | 2021-06-01 | 21:00
56 | Fenchuganj | 49 | 4 | 2021-06-01 | 20:00
57 | Kulawara | 68 | 29 | 2021-06-01 | 23:00
58 | Sylhet | 133 | 15 | 2021-06-01 | 13:00
59 | Chatak | 33 | 13 | 2021-06-01 | 22:00
60 | Sunamganj | 54 | 14 | 2021-06-01 | 21:00
61 | Bianibazar | 77 | 14 | 2021-06-01 | 22:00
62 | Cumilla (S) | 158 | 1 | 2021-06-01 | 1:00
63 | Cumilla(N) | 155 | 11 | 2021-06-01 | 19:00
64 | Chandpur | 83 | 26 | 2021-06-01 | 21:00
65 | Feni | 125 | 13 | 2021-06-01 | 1:00
66 | Chowmuhani | 203 | 27 | 2021-06-01 | 22:00
67 | Ashuganj | 49 | 15 | 2021-06-01 | 11:00
68 | Daudkandi | 158 | 13 | 2021-06-01 | 23:00
69 | B.Baria | 168 | 14 | 2021-06-01 | 22:00
70 | Ramganj | 96 | 27 | 2021-06-01 | 23:00
71 | Chaddagram | 52 | 7 | 2021-06-01 | 21:00
72 | PHP | 12 | 12 | 2021-06-01 | 14:00
73 | Kochua | 68 | 15 | 2021-06-01 | 21:00
74 | Madanhat | 72 | 12 | 2021-06-01 | 14:00
75 | Hathazari | 99 | 12 | 2021-06-01 | 21:00
76 | Khulshi | 226 | 12 | 2021-06-01 | 16:00
77 | Halishahar | 123 | 30 | 2021-06-01 | 14:00
78 | Baraulia | 166 | 24 | 2021-06-01 | 0:00
79 | Sikalbaha | 44 | 29 | 2021-06-01 | 16:00
80 | Dohazari | 112 | 25 | 2021-06-01 | 19:30
81 | Cox'sbazar | 104 | 1 | 2021-06-01 | 1:00
82 | Chandraghona | 30 | 3 | 2021-06-01 | 21:00
83 | Kaptai | 8 | 12 | 2021-06-01 | 10:00
84 | A. Khaer Stl. | 14 | 25 | 2021-06-01 | 8:00
85 | Bakulia | 117 | 26 | 2021-06-01 | 15:00
86 | Julda | 24 | 2 | 2021-06-01 | 12:00
87 | TK chemical | 30.3 | 27 | 2021-06-01 | 22:00
88 | Modern Steel | 0 | 3 | 2021-06-01 | #N/A
89 | Shahmirpur | 35 | 21 | 2021-06-01 | 2:00
90 | Khagrachhari | 28 | 12 | 2021-06-01 | 7:00
91 | Matarbari | 39.5 | 28 | 2021-06-01 | 1:00
92 | Baroiar Hat | 60 | 13 | 2021-06-01 | 19:00
93 | Rangamati | 16 | 28 | 2021-06-01 | 19:00
94 | Abul Khair 230 | 152 | 9 | 2021-06-01 | 13:00
95 | BSRM | 161 | 12 | 2021-06-01 | 20:00
96 | GPH Ispat | 98 | 9 | 2021-06-01 | 11:00
97 | Agrabad | 0 | 0 | 2021-06-01 | 0:00
98 | Goalpara | 29 | 21 | 2021-06-01 | 19:30
99 | Central s/s | 102 | 5 | 2021-06-01 | 20:0
100 | Noapara | 64 | 3 | 2021-06-01 | 20:00
101 | Jashore | 128 | 5 | 2021-06-01 | 19:30
102 | Benapol | 66 | 3 | 2021-06-01 | 22:00
103 | Jhenidah | 126 | 4 | 2021-06-01 | 22:00
104 | Bottail | 142 | 2 | 2021-06-01 | 19:30
105 | G.K Project | 63 | 2 | 2021-06-01 | 21:00
106 | Faridpur | 203 | 2 | 2021-06-01 | 22:00
107 | Rajbari | 52 | 26 | 2021-06-01 | 19:30
108 | Madaripur | 108 | 27 | 2021-06-01 | 22:00
109 | Sariatpur | 70 | 4 | 2021-06-01 | 21:00
110 | Gopalganj | 99 | 9 | 2021-06-01 | 19:30
111 | Bagerhat | 106 | 2 | 2021-06-01 | 21:00
112 | Mongla | 44 | 28 | 2021-06-01 | 19:30
113 | Satkhira | 119 | 4 | 2021-06-01 | 23:00
114 | Gallamari | 44 | 29 | 2021-06-01 | 9:00
115 | Magura | 62 | 4 | 2021-06-01 | 22:00
116 | Norail | 52 | 26 | 2021-06-01 | 20:00
117 | Chuadanga | 97 | 9 | 2021-06-01 | 20:00
118 | Borguna | 20 | 4 | 2021-06-01 | 22:00
119 | Barsal(N) | 50 | 2 | 2021-06-01 | 22:00
120 | Barsal(S) | 112 | 2 | 2021-06-01 | 21:00
121 | Patuakhali | 114 | 27 | 2021-06-01 | 22:00
122 | Bhandaria | 54 | 25 | 2021-06-01 | 22:00
123 | Borhan Uddin | 48 | 27 | 2021-06-01 | 22:00
124 | Ishurdi | 73 | 9 | 2021-06-01 | 21:00
125 | Ruppur Paromanobik | 4 | 2 | 2021-06-01 | 19:00
126 | Natore | 151 | 3 | 2021-06-01 | 21:00
127 | Bogura | 168 | 27 | 2021-06-01 | 21:00
128 | Naogaon | 127 | 8 | 2021-06-01 | 21:00
129 | Rajshahi | 164 | 8 | 2021-06-01 | 21:00
130 | Rajshahi New | 27 | 8 | 2021-06-01 | 20:00
131 | C.Nawabganj | 77 | 24 | 2021-06-01 | 24:00
132 | Amnura | 62 | 27 | 2021-06-01 | 23:00
133 | Pabna | 114 | 10 | 2021-06-01 | 21:00
134 | Shahjadpur | 102 | 2 | 2021-06-01 | 20:00
135 | Serajganj | 109 | 14 | 2021-06-01 | 21:00
136 | Niyamatpur | 76 | 15 | 2021-06-01 | 21:00
137 | Joypurhat | 62 | 2 | 2021-06-01 | 21:00
138 | Sherpur(Bogura) | 59 | 27 | 2021-06-01 | 19:30
139 | Mohastangar | 78 | 27 | 2021-06-01 | 21:00
140 | Bangura | 34 | 2 | 2021-06-01 | 21:00
141 | Rangpur | 144 | 4 | 2021-06-01 | 20:00
142 | Lalmonirhat | 47 | 15 | 2021-06-01 | 19:30
143 | Saidpur | 112 | 23 | 2021-06-01 | 20:00
144 | Purbasadipur | 122 | 10 | 2021-06-01 | 13:00
145 | Thakurgaon | 88 | 3 | 2021-06-01 | 21:00
146 | Palshbari | 121 | 25 | 2021-06-01 | 21:00
147 | Barapukuria | 58 | 5 | 2021-06-01 | 21:00
148 | Panchugar | 57 | 10 | 2021-06-01 | 20:00
149 | Joldhaka | 64 | 13 | 2021-06-01 | 20:00
150 | Kurigram | 64 | 13 | 2021-06-01 | 21:00
151 | Mitha Pukur | 46 | 2 | 2021-06-01 | 19:30

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:June 2021
Area | MW | Date | Hour | Remarks
Dhaka | 4718 | 10.06.21 | 15:00
Chattogram | 1389 | 14.06.21 | 22:00
Khulna | 1592 | 03.06.21 | 21:00
Rajshahi | 1355 | 27.06.21 | 21:00
Cumilla | 1244 | 02.06.21 | 23:00
Mymensingh | 1050 | 26.06.21 | 21:00
Sylhet | 552 | 14.06.21 | 22:00
Barisal | 391 | 27.06.21 | 22:00
Rangpur | 829 | 13.06.21 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: June'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 406 | 30 | 2021-06-01 | 19:00 | 392 | 5 | 2021-06-01 | 11:00
2 | Bheramara | 400 | 410 | 12 | 2021-06-01 | 13:00 | 383 | 5 | 2021-06-01 | 21:00
3 | Ashuganj(N) | 400 | 399 | 9 | 2021-06-01 | 13:00 | 360 | 1 | 2021-06-01 | 15:00
4 | Payra | 400 | 416 | 19 | 2021-06-01 | 20:00 | 0 | 11 | 2021-06-01 | 1:00
5 | Kaliakoir | 400 | 395 | 30 | 2021-06-01 | 6:00 | 366 | 21 | 2021-06-01 | 9:00
6 | Bhulta | 400 | 385 | 9 | 2021-06-01 | 21:00 | 357 | 1 | 2021-06-01 | 15:00
7 | Gopalganj | 400 | 416 | 19 | 2021-06-01 | 15:00 | 0 | 11 | 2021-06-01 | 11:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-06-01 | 20:00 | 227 | 2 | 2021-06-01 | 10:00
2 | Ishurdi | 230 | 237 | 7 | 2021-06-01 | 18:00 | 224 | 1 | 2021-06-01 | 11:00
3 | Ashuganj | 230 | 240 | 1 | 2021-06-01 | 1:00 | 228 | 16 | 2021-06-01 | 24:00
4 | Serajganj | 230 | 235 | 12 | 2021-06-01 | 12:00 | 225 | 1 | 2021-06-01 | 5:00
5 | Baghabari | 230 | 234 | 9 | 2021-06-01 | 17:00 | 224 | 23 | 2021-06-01 | 23:00
6 | Barapukuria | 230 | 238 | 12 | 2021-06-01 | 6:00 | 223 | 23 | 2021-06-01 | 24:00
7 | Bogura | 230 | 230 | 9 | 2021-06-01 | 19:00 | 212 | 23 | 2021-06-01 | 23:00
8 | Rajshahi | 230 | 238 | 21 | 2021-06-01 | 18:00 | 221 | 1 | 2021-06-01 | 11:00
9 | Khulna South | 230 | 246 | 17 | 2021-06-01 | 3:00 | 202 | 6 | 2021-06-01 | 13:00
10 | Rampura | 230 | 229 | 1 | 2021-06-01 | 1:00 | 214 | 2 | 2021-06-01 | 10:00
11 | Haripur | 230 | 227 | 30 | 2021-06-01 | 19:00 | 208 | 18 | 2021-06-01 | 10:00
12 | Hasnabad | 230 | 230 | 14 | 2021-06-01 | 21:00 | 210 | 30 | 2021-06-01 | 11:00
13 | Shyampur | 230 | 229 | 4 | 2021-06-01 | 21:00 | 220 | 1 | 2021-06-01 | 12:00
14 | Aminbazar | 230 | 228 | 1 | 2021-06-01 | 1:00 | 210 | 3 | 2021-06-01 | 2:00
15 | Tongi | 230 | 230 | 30 | 2021-06-01 | 19:00 | 207 | 30 | 2021-06-01 | 11:00
16 | Comilla (N) | 230 | 244 | 12 | 2021-06-01 | 12:00 | 216 | 23 | 2021-06-01 | 10:00
17 | Hathazari | 230 | 226 | 6 | 2021-06-01 | 13:00 | 211 | 9 | 2021-06-01 | 13:00
18 | Megnaghat | 230 | 232 | 1 | 2021-06-01 | 19:30 | 218 | 27 | 2021-06-01 | 13:00
19 | Fenchuganj | 230 | 241 | 25 | 2021-06-01 | 19:30 | 231 | 30 | 2021-06-01 | 11:00
20 | Siddhirganj | 230 | 230 | 1 | 2021-06-01 | 1:00 | 209 | 18 | 2021-06-01 | 10:00
21 | Maniknagar | 230 | 228 | 1 | 2021-06-01 | 1:00 | 213 | 2 | 2021-06-01 | 10:00
22 | Old Airport | 230 | 227 | 1 | 2021-06-01 | 22:00 | 210 | 5 | 2021-06-01 | 14:00
23 | Barisal | 230 | 251 | 23 | 2021-06-01 | 2:00 | 226 | 3 | 2021-06-01 | 22:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-06-01 | 3:00 | 233 | 3 | 2021-06-01 | 22:00
25 | AKSML | 230 | 227 | 1 | 2021-06-01 | 20:00 | 210 | 9 | 2021-06-01 | 10:00
26 | BSRM | 230 | 228 | 1 | 2021-06-01 | 20:00 | 211 | 23 | 2021-06-01 | 10:00
27 | Bibiyana | 230 | 241 | 1 | 2021-06-01 | 20:00 | 232 | 10 | 2021-06-01 | 17:00
28 | Bhulta | 230 | 230 | 1 | 2021-06-01 | 8:00 | 215 | 2 | 2021-06-01 | 10:00
29 | Ashuganj (S) | 230 | 232 | 22 | 2021-06-01 | 20:00 | 219 | 1 | 2021-06-01 | 15:00
30 | Kaliakoir | 230 | 229 | 1 | 2021-06-01 | 21:00 | 209 | 24 | 2021-06-01 | 11:00
31 | GPH | 230 | 227 | 1 | 2021-06-01 | 20:00 | 208 | 23 | 2021-06-01 | 10:00
132 kV Substation
1 | Siddhirganj | 132 | 133 | 30 | 2021-06-01 | 0.79167 | 122 | 27 | 2021-06-01 | 0.5
2 | Munsiganj | 132 | 135 | 30 | 2021-06-01 | 0.8125 | 122 | 2 | 2021-06-01 | 0.41667
3 | Sonargaon | 132 | 133 | 2 | 2021-06-01 | 0.8125 | 119 | 18 | 2021-06-01 | 0.41667
4 | Shyampur | 132 | 134 | 2 | 2021-06-01 | 0.91667 | 129 | 7 | 2021-06-01 | 0.41667
5 | Bhulta | 132 | 131 | 1 | 2021-06-01 | 0.375 | 112 | 1 | 2021-06-01 | 0.70833
6 | Madanganj | 132 | 134 | 30 | 2021-06-01 | 0.8125 | 120 | 18 | 2021-06-01 | 0.41667
7 | Shitalakhya | 132 | 141 | 2 | 2021-06-01 | 0.95833 | 122 | 30 | 2021-06-01 | 0.45833
8 | Rahim Steal | 132 | 133 | 1 | 2021-06-01 | 0.375 | 120 | 18 | 2021-06-01 | 0.41667
9 | Matuail | 132 | 133 | 30 | 2021-06-01 | 0.79167 | 94 | 5 | 2021-06-01 | 0.25
10 | Ghorasal | 132 | 140 | 12 | 2021-06-01 | 0.91667 | 126 | 21 | 2021-06-01 | 0.33333
11 | Narsinghdi | 132 | 136 | 1 | 2021-06-01 | 0.33333 | 118 | 1 | 2021-06-01 | 0.70833
12 | Haripur (SBU) | 132 | 133 | 16 | 2021-06-01 | 0.79167 | 103 | 8 | 2021-06-01 | 0.95833
13 | Sreenagar | 132 | 137 | 25 | 2021-06-01 | 0.75 | 117 | 18 | 2021-06-01 | 0.41667
14 | Ullon | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 120 | 18 | 2021-06-01 | 0.45833
15 | Hasnabad | 132 | 139 | 14 | 2021-06-01 | 1899-12-31 | 124 | 30 | 2021-06-01 | 0.45833
16 | Magbazar | 132 | 136 | 30 | 2021-06-01 | 0.79167 | 122 | 2 | 2021-06-01 | 0.5
17 | Maniknagar | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 126 | 18 | 2021-06-01 | 0.41667
18 | Bangabhaban | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 126 | 18 | 2021-06-01 | 0.41667
19 | Motijheel | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 126 | 18 | 2021-06-01 | 0.41667
20 | Narinda | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 126 | 18 | 2021-06-01 | 0.41667
21 | Kazla | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 126 | 18 | 2021-06-01 | 0.41667
22 | Dhanmondi | 132 | 133 | 1 | 2021-06-01 | 0.20833 | 120 | 18 | 2021-06-01 | 0.45833
23 | Lalbag | 132 | 139 | 3 | 2021-06-01 | 0.083333 | 122 | 21 | 2021-06-01 | 0.41667
24 | Madartek | 132 | 136 | 1 | 2021-06-01 | 0.041667 | 123 | 2 | 2021-06-01 | 0.41667
25 | Dhaka University | 132 | 137 | 1 | 2021-06-01 | 0.33333 | 121 | 18 | 2021-06-01 | 0.41667
26 | Aftabnagar | 132 | 137 | 1 | 2021-06-01 | 0.083333 | 124 | 2 | 2021-06-01 | 0.5
27 | Fatullah | 132 | 135 | 8 | 2021-06-01 | 0.83333 | 122 | 2 | 2021-06-01 | 0.41667
28 | Nawabganj | 132 | 135 | 28 | 2021-06-01 | 0.33333 | 118 | 30 | 2021-06-01 | 0.5
29 | Keraniganj | 132 | 132 | 9 | 2021-06-01 | 0.875 | 119 | 30 | 2021-06-01 | 0.45833
30 | Mirpur | 132 | 137 | 15 | 2021-06-01 | 0.041667 | 124 | 23 | 2021-06-01 | 0.41667
31 | Kalyanpur | 132 | 137 | 1 | 2021-06-01 | 1;00 | 120 | 6 | 2021-06-01 | 0.41667
32 | Gulshan | 132 | 137 | 6 | 2021-06-01 | 0.20833 | 124 | 2 | 2021-06-01 | 0.41667
33 | Uttara | 132 | 137 | 1 | 2021-06-01 | 0.041667 | 122 | 5 | 2021-06-01 | 0.5
34 | Uttara(New) | 132 | 140 | 1 | 2021-06-01 | 0.33333 | 121 | 18 | 2021-06-01 | 0.41667
35 | Kamrangirchar | 132 | 138 | 1 | 2021-06-01 | 0.041667 | 122 | 5 | 2021-06-01 | 0.45833
36 | Savar | 132 | 138 | 3 | 2021-06-01 | 0.083333 | 124 | 2 | 2021-06-01 | 0.375
37 | Bhasantec | 132 | 137 | 1 | 2021-06-01 | 0.58333 | 124 | 30 | 2021-06-01 | 0.45833
38 | Agargaon | 132 | 137 | 15 | 2021-06-01 | 0.041667 | 125 | 1 | 2021-06-01 | 0.5
39 | Satmosjid | 132 | 136 | 1 | 2021-06-01 | 0.041667 | 126 | 2 | 2021-06-01 | 0.41667
40 | Tongi | 132 | 140 | 25 | 2021-06-01 | 0.8125 | 126 | 5 | 2021-06-01 | 0.45833
41 | Kabirpur | 132 | 139 | 1 | 2021-06-01 | 0.20833 | 124 | 28 | 2021-06-01 | 16:00
42 | Basundhara | 132 | 138 | 1 | 2021-06-01 | 0.83333 | 122 | 5 | 2021-06-01 | 0.45833
43 | Manikganj | 132 | 141 | 25 | 2021-06-01 | 0.33333 | 126 | 22 | 2021-06-01 | 0.45833
44 | Joydevpur | 132 | 143 | 30 | 2021-06-01 | 19:30 | 126 | 9 | 2021-06-01 | 0.33333
45 | New Tongi | 132 | 139 | 25 | 2021-06-01 | 0.77083 | 124 | 5 | 2021-06-01 | 0.45833
46 | Kodda | 132 | 138 | 1 | 2021-06-01 | 0.041667 | 121 | 8 | 2021-06-01 | 0.58333
47 | Dhamrai | 132 | 137 | 30 | 2021-06-01 | 19:00 | 122 | 4 | 2021-06-01 | 0.91667
48 | Rajendrapur | 132 | 137 | 25 | 2021-06-01 | 0.75 | 118 | 5 | 2021-06-01 | 0.5
49 | Valuka | 132 | 130 | 29 | 2021-06-01 | 0.5 | 107 | 22 | 2021-06-01 | 0.79167
50 | Tangail | 132 | 138 | 14 | 2021-06-01 | 0.33333 | 119 | 14 | 2021-06-01 | 0.875
51 | Mymensing | 132 | 133 | 29 | 2021-06-01 | 0.45833 | 112 | 9 | 2021-06-01 | 0.79167
52 | Kishorganj | 132 | 135 | 29 | 2021-06-01 | 0.041667 | 117 | 22 | 2021-06-01 | 0.91667
53 | Netrokona | 132 | 133 | 29 | 2021-06-01 | 0.41667 | 106 | 9 | 2021-06-01 | 0.8125
54 | Jamalpur | 132 | 139 | 14 | 2021-06-01 | 0.54167 | 115 | 9 | 2021-06-01 | 0.79167
55 | Sherpur | 132 | 139 | 14 | 2021-06-01 | 0.70833 | 115 | 9 | 2021-06-01 | 0.8125
56 | Srimongal | 132 | 141 | 5 | 2021-06-01 | 0.29167 | 130 | 9 | 2021-06-01 | 0.95833
57 | Shahjibazar | 132 | 139 | 5 | 2021-06-01 | 0.29167 | 127 | 15 | 2021-06-01 | 0.95833
58 | Fenchuganj | 132 | 139 | 2 | 2021-06-01 | 0.25 | 132 | 9 | 2021-06-01 | 0.875
59 | Khulawara | 132 | 138 | 1 | 2021-06-01 | 0.20833 | 131 | 13 | 2021-06-01 | 0.875
60 | Sylhet | 132 | 135 | 1 | 2021-06-01 | 0.25 | 129 | 9 | 2021-06-01 | 1899-12-31
61 | Chattak | 132 | 136 | 2 | 2021-06-01 | 0.29167 | 126 | 13 | 2021-06-01 | 0.91667
62 | Sunamganj | 132 | 135 | 1 | 2021-06-01 | 0.33333 | 124 | 2 | 2021-06-01 | 0.79167
63 | Biani Bazar | 132 | 137 | 5 | 2021-06-01 | 0.16667 | 125 | 13 | 2021-06-01 | 0.875
64 | Comilla(South) | 132 | 131 | 1 | 2021-06-01 | 0.20833 | 123 | 2 | 2021-06-01 | 0.8125
65 | Comilla (North) | 132 | 139 | 1 | 2021-06-01 | 0.8125 | 129 | 23 | 2021-06-01 | 0.41667
66 | Chandpur | 132 | 140 | 1 | 2021-06-01 | 0 | 128 | 4 | 2021-06-01 | 0.41667
67 | Feni | 132 | 140 | 1 | 2021-06-01 | 0.66667 | 125 | 29 | 2021-06-01 | 0.25
68 | Chowmuhani | 132 | 138 | 18 | 2021-06-01 | 0.8125 | 122 | 29 | 2021-06-01 | 0.25
69 | Ashuganj | 132 | 142 | 29 | 2021-06-01 | 0.54167 | 130 | 6 | 2021-06-01 | 0.16667
70 | Daudkandi | 132 | 138 | 14 | 2021-06-01 | 0.8125 | 124 | 2 | 2021-06-01 | 0.375
71 | Brahminbaria | 132 | 138 | 5 | 2021-06-01 | 0.33333 | 124 | 10 | 2021-06-01 | 0.58333
72 | Ramganj | 132 | 141 | 3 | 2021-06-01 | 0.58333 | 117 | 30 | 2021-06-01 | 0.125
73 | Chaddagram | 132 | 138 | 1 | 2021-06-01 | 0.875 | 127 | 30 | 2021-06-01 | 0.083333
74 | PHP | 132 | 138 | 1 | 2021-06-01 | 0.16667 | 123 | 30 | 2021-06-01 | 0.125
75 | Kochua | 132 | 139 | 1 | 2021-06-01 | 0.8125 | 129 | 4 | 2021-06-01 | 0.41667
76 | Madanhat | 132 | 136 | 1 | 2021-06-01 | 0.66667 | 125 | 9 | 2021-06-01 | 0.5
77 | Hathazari | 132 | 135 | 1 | 2021-06-01 | 0.70833 | 126 | 9 | 2021-06-01 | 0.33333
78 | Khulshi | 132 | 132 | 1 | 2021-06-01 | 0.66667 | 120 | 9 | 2021-06-01 | 0.45833
79 | Halishahar | 132 | 133 | 16 | 2021-06-01 | 0.83333 | 118 | 9 | 2021-06-01 | 0.29167
80 | Baraulia | 132 | 134 | 1 | 2021-06-01 | 0.66667 | 121 | 23 | 2021-06-01 | 0.41667
81 | Sikalbaha | 132 | 136 | 6 | 2021-06-01 | 0.5 | 125 | 2 | 2021-06-01 | 0.83333
82 | Dohazari | 132 | 135 | 1 | 2021-06-01 | 0.83333 | 121 | 23 | 2021-06-01 | 0.41667
83 | Cox'sbazar | 132 | 128 | 6 | 2021-06-01 | 0.45833 | 100 | 8 | 2021-06-01 | 0.79167
84 | Chandraghona | 132 | 135 | 6 | 2021-06-01 | 0.5 | 123 | 23 | 2021-06-01 | 0.41667
85 | Kaptai | 132 | 138 | 29 | 2021-06-01 | 0.041667 | 126 | 9 | 2021-06-01 | 0.29167
86 | A. Khaer Stl. | 132 | 133 | 1 | 2021-06-01 | 0.70833 | 122 | 9 | 2021-06-01 | 0.41667
87 | Bakulia | 132 | 135 | 6 | 2021-06-01 | 0.54167 | 123 | 23 | 2021-06-01 | 0.41667
88 | Julda | 132 | 138 | 1 | 2021-06-01 | 0.79167 | 125 | 19 | 2021-06-01 | 0.41667
89 | TK Chemical | 132 | 135 | 1 | 2021-06-01 | 0.83333 | 124 | 9 | 2021-06-01 | 0.45833
90 | Modern Steel | 132 | #N/A | #N/A | 2021-06-01 | #N/A | 0 | 0 | 2021-06-01 | #N/A
91 | Shahmirpur | 132 | 137 | 6 | 2021-06-01 | 0.54167 | 124 | 20 | 2021-06-01 | 0.375
92 | Khagrachhari | 132 | 134 | 6 | 2021-06-01 | 0.5 | 122 | 9 | 2021-06-01 | 0.45833
93 | Matarbari | 132 | 133 | 4 | 2021-06-01 | 0.29167 | 98 | 8 | 2021-06-01 | 0.79167
94 | Baroiar Hat | 132 | 137 | 1 | 2021-06-01 | 0.16667 | 125 | 30 | 2021-06-01 | 0.125
95 | Rangamati | 132 | 134 | 6 | 2021-06-01 | 0.5 | 122 | 23 | 2021-06-01 | 0.41667
96 | Agrabad | 132 | 133 | 6 | 2021-06-01 | 0.54167 | 121 | 9 | 2021-06-01 | 0.5
97 | Goalpara | 132 | 142 | 7 | 2021-06-01 | 0.75 | 120 | 24 | 2021-06-01 | 0.8125
98 | Khulna Central | 132 | 142 | 7 | 2021-06-01 | 0.75 | 117 | 4 | 2021-06-01 | 0.79167
99 | Noapara | 132 | 138 | 20 | 2021-06-01 | 0.25 | 117 | 24 | 2021-06-01 | 0.8125
100 | Jessore | 132 | 137 | 7 | 2021-06-01 | 0.75 | 107 | 4 | 2021-06-01 | 0.79167
101 | Benapol | 132 | 137 | 7 | 2021-06-01 | 0.75 | 111 | 4 | 2021-06-01 | 0.79167
102 | Jhenida | 132 | 136 | 7 | 2021-06-01 | 0.75 | 107 | 2 | 2021-06-01 | 0
103 | Bottail | 132 | 137 | 7 | 2021-06-01 | 0.75 | 119 | 2 | 2021-06-01 | 0
104 | G.K Project | 132 | 141 | 7 | 2021-06-01 | 0.75 | 130 | 13 | 2021-06-01 | 0.33333
105 | Faridpur | 132 | 138 | 6 | 2021-06-01 | 0.75 | 125 | 3 | 2021-06-01 | 0.91667
106 | Rajbari | 132 | 137 | 29 | 2021-06-01 | 0.5 | 125 | 27 | 2021-06-01 | 0.95833
107 | Madaripur | 132 | 144 | 5 | 2021-06-01 | 0.66667 | 127 | 19 | 2021-06-01 | 0.58333
108 | Sariatpur | 132 | 143 | 6 | 2021-06-01 | 0.70833 | 125 | 3 | 2021-06-01 | 0.91667
109 | Gopalganj | 132 | 147 | 5 | 2021-06-01 | 0.66667 | 127 | 3 | 2021-06-01 | 0.91667
110 | Bagerhat | 132 | 140 | 6 | 2021-06-01 | 0.75 | 110 | 4 | 2021-06-01 | 0.5
111 | Mongla | 132 | 139 | 6 | 2021-06-01 | 0.77083 | 114 | 4 | 2021-06-01 | 0.5
112 | Satkhira | 132 | 142 | 6 | 2021-06-01 | 0.75 | 116 | 4 | 2021-06-01 | 0.5
113 | Gallamari | 132 | 141 | 6 | 2021-06-01 | 0.77083 | 121 | 4 | 2021-06-01 | 0.5
114 | Magura | 132 | 136 | 7 | 2021-06-01 | 0.75 | 104 | 27 | 2021-06-01 | 0.91667
115 | Norail | 132 | 132 | 7 | 2021-06-01 | 0.75 | 103 | 27 | 2021-06-01 | 0.91667
116 | Chuadanga | 132 | 133 | 7 | 2021-06-01 | 0.75 | 95 | 4 | 2021-06-01 | 0.79167
117 | Borguna | 132 | 143 | 6 | 2021-06-01 | 0.83333 | 121 | 3 | 2021-06-01 | 0.91667
118 | Barisal(N) | 132 | 144 | 6 | 2021-06-01 | 0.70833 | 128 | 3 | 2021-06-01 | 0.91667
119 | Barisal(S) | 132 | 143 | 5 | 2021-06-01 | 0.66667 | 125 | 3 | 2021-06-01 | 0.91667
120 | Patuakhali | 132 | 144 | 5 | 2021-06-01 | 0.66667 | 120 | 3 | 2021-06-01 | 0.91667
121 | Bhandaria | 132 | 144 | 5 | 2021-06-01 | 0.70833 | 121 | 9 | 2021-06-01 | 0.8125
122 | Ishurdi | 132 | 138 | 7 | 2021-06-01 | 0.75 | 130 | 1 | 2021-06-01 | 0.45833
123 | Ruppur paromanobik | 132 | 137 | 7 | 2021-06-01 | 0.70833 | 121 | 9 | 2021-06-01 | 0.91667
124 | Natore | 132 | 137 | 9 | 2021-06-01 | 0.79167 | 125 | 18 | 2021-06-01 | 0.95833
125 | Bogra | 132 | 138 | 12 | 2021-06-01 | 0.58333 | 124 | 5 | 2021-06-01 | 0.45833
126 | Noagaon | 132 | 134 | 29 | 2021-06-01 | 0.29167 | 115 | 24 | 2021-06-01 | 0.5
127 | Rajshahi | 132 | 134 | 5 | 2021-06-01 | 0.83333 | 124 | 1 | 2021-06-01 | 0.5
128 | Rajshahi New | 132 | 136 | 30 | 2021-06-01 | 0.77083 | 123 | 1 | 2021-06-01 | 0.45833
129 | C.Nawabganj | 132 | 135 | 13 | 2021-06-01 | 0.77083 | 121 | 1 | 2021-06-01 | 0.5
130 | Amnura | 132 | 136 | 2 | 2021-06-01 | 0.77083 | 121 | 1 | 2021-06-01 | 0.5
131 | Pabna | 132 | 138 | 7 | 2021-06-01 | 0.75 | 128 | 1 | 2021-06-01 | 0.45833
132 | Shahjadpur | 132 | 140 | 5 | 2021-06-01 | 0.70833 | 125 | 23 | 2021-06-01 | 0.91667
133 | Serajganj | 132 | 136 | 7 | 2021-06-01 | 0.75 | 125 | 2 | 2021-06-01 | 0.083333
134 | Niyamatpur | 132 | 136 | 29 | 2021-06-01 | 0.29167 | 112 | 24 | 2021-06-01 | 0.5
135 | Joypurhat | 132 | 135 | 29 | 2021-06-01 | 0.29167 | 113 | 26 | 2021-06-01 | 0.875
136 | Sherpur(Bogura) | 132 | 137 | 7 | 2021-06-01 | 0.75 | 123 | 25 | 2021-06-01 | 0.125
137 | Mohastangor | 132 | 137 | 12 | 2021-06-01 | 0.58333 | 122 | 23 | 2021-06-01 | 0.95833
138 | Bangura | 132 | 139 | 7 | 2021-06-01 | 0.75 | 130 | 1 | 2021-06-01 | 0.5
139 | Rangpur | 132 | 133 | 12 | 2021-06-01 | 0.58333 | 113 | 25 | 2021-06-01 | 0.041667
140 | Lalmonirhat | 132 | 133 | 12 | 2021-06-01 | 0.58333 | 114 | 23 | 2021-06-01 | 0.91667
141 | Saidpur | 132 | 135 | 12 | 2021-06-01 | 0.20833 | 111 | 2 | 2021-06-01 | 0.95833
142 | Purbasadipur | 132 | 132 | 12 | 2021-06-01 | 0.25 | 106 | 2 | 2021-06-01 | 0.91667
143 | Thakurgaon | 132 | 132 | 12 | 2021-06-01 | 0.25 | 105 | 2 | 2021-06-01 | 0.91667
144 | Palashbari | 132 | 134 | 12 | 2021-06-01 | 0.58333 | 115 | 2 | 2021-06-01 | 0.91667
145 | Barapukuria | 132 | 138 | 12 | 2021-06-01 | 0.25 | 123 | 23 | 2021-06-01 | 1899-12-31
146 | Panchagar | 132 | 132 | 5 | 2021-06-01 | 0.66667 | 102 | 3 | 2021-06-01 | 0.875
147 | Joldhaka | 132 | 133 | 30 | 2021-06-01 | 0.29167 | 108 | 2 | 2021-06-01 | 0.91667
148 | Kurigram | 132 | 133 | 12 | 2021-06-01 | 0.58333 | 109 | 2 | 2021-06-01 | 0.91667
149 | Mithapukur | 132 | 135 | 12 | 2021-06-01 | 0.54167 | 118 | 2 | 2021-06-01 | 0.91667

## QF-LDC-36
Page: 1/1 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:June' 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 105 | 325
Hasnabad | TR2 | 225 | 100 | 325 | 2021-06-06 | 16:00
| TR3 | 225 | 100 | 325
| TR1 | 225 | 145 | 430
Tongi | TR2 | 225 | 145 | 430 | 13/06/21 | 12:00
| TR3 | 225 | 145 | 430
Haripur | TR1 | 225 | 126 | 375
| TR2 | 225 | 126 | 375 | 27/06/21 | 11:00
| TR3 | 225 | 126 | 375
| TR1 | 225 | 188 | 527
Rampura | TR2 | 225 | 188 | 527 | 15/06/21 | 13:00
| TR3 | 225 | 188 | 527
Keraniganj | ATR1 | 300 | 52 | 148 | 2021-06-04 | 22:00
| ATR2 | 300 | 78 | 218
| ATR3 | 300 | 78 | 218
| TR1 | 225 | 145 | 404
Aminbazar | TR2 | 225 | 145 | 404 | 30/06/21 | 19:30
| TR3 | 225 | 155 | 422
Agargaon | TR1 | 300 | 171 | 498 | 2021-06-06 | 13:00
| TR2 | 300 | 171 | 498 | 2021-06-06 | 13:00
Maniknagar | TR1 | 300 | 128 | 390 | 27/06/21 | 12:00
| TR2 | 300 | 128 | 390
Cumilla (N) | TR1 | 225 | 157 | 446 | 2021-11-06 | 1:00
| TR2 | 225 | 154 | 435
Fenchuganj | AT2 | 300 | 233 | 615 | 2021-09-06 | 21:00
| MT1 | 150 | 73 | 200 | 19/06/21
Hathazari | MT2 | 150 | 73 | 200
| MT3 | 150 | 73 | 200 |  | 12:00
| MT4 | 150 | 73 | 200
| TR1 | 225 | 112 | 285
Ishurdi | TR2 | 225 | 112 | 285 | 25/06/21 | 20:00
| TR3 | 225 | 112 | 285
Khulna(S) | TR1 | 225 | 125 | 392
| TR2 | 225 | 125 | 392 | 04.06.2021 | 19:00
| TR3 | 300 | 160 | 498
Bogura | TR1 | 225 | 115 | 350
| TR2 | 225 | 115 | 350 | 30/06/21 | 21:00
| TR3 | 225 | 157 | 458
Baghabari | TR1 | 300 | 142 | 405 | 2021-02-06 | 20:00
| TR2 | 225 | 107 | 300
Rajshahi | ATR-01 | 300 | 103 | 270 | 2021-10-06 | 4:00
| ATR-02 | 300 | 103 | 270
Barapukuria | TR1 | 225 | 145 | 441 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 161 | 507 | 2021-01-06 | 20:00 | 132 kV current is being provided
| TR6 | 300 | 209 | 651
Bheramara | Transformer-1 | 225 | 119 | 322 | 25/06/21 | 20
| Transformer-2 | 225 | 119 | 322
Shyampur | ATR-01 | 300 | 130 | 401 | 14.06.2021 | 21:00
| ATR-02 | 300 | 130 | 401
QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:June 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 305.6 | 474 | 2021-01-06 | 10:30
| TR2(400/230 kV) | 520 | 308.8 | 482
| TR1(400/132 kV) | 325 | 274.6 | 442 | 26/06/21 | 19:00
| TR2(400/132 kV) | 325 | 277.1 | 441
Bibiyana | ICT1(400/230 kV) | 520 | 176 | 261 | 21/06/21 | 7:00
| ICT2(400/230kV) | 520 | 172 | 254
Bhulta | ATR1(400/230 kV) | 520 | 215 | 425 | 18/06/21 | 10:15
| ATR2(400/230kV) | 520 | 215 | 425
Ashuganj(N) | GSUT1 | 567 | 379 | 618 | 2021-01-06 | 22:15
Gopalganj | ATR1(400/138 kV) | 325 | 287 | 432 | 02.06.2021 | 21:00
| ATR2(400/138kV) | 325 | 287 | 432
Payra | GSUT1 | 270 | 197 | 862 | 2021-02-06 | 21:44
| GSUT2 | 270 | 196 | 854
| GSUT3 | 270 | 198 | 862
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.
270

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:June 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:June 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-06-01 | 11612 | 11612 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-01 | 9351 | 9351 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-02 | 13014 | 13014 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-02 | 10311 | 10311 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-03 | 12754 | 12754 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-03 | 11290 | 11290 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-04 | 12215 | 12215 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-04 | 9954 | 9954 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-05 | 11262 | 11262 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-05 | 9887 | 9887 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-06 | 10227 | 10227 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-06 | 10141 | 10141 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-07 | 10869 | 10869 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-07 | 10513 | 10513 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-08 | 12411 | 12411 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-08 | 9916 | 9916 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-09 | 12803 | 12803 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-09 | 10589 | 10589 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-10 | 12223 | 12223 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-10 | 11218 | 11218 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-11 | 11584 | 11584 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-11 | 9153 | 9153 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-12 | 12668 | 12668 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-12 | 10068 | 10068 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-13 | 12792 | 12792 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-13 | 10836 | 10836 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-14 | 12749 | 12749 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-14 | 10959 | 10959 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-15 | 12352 | 12352 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-15 | 10948 | 10948 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-16 | 11896 | 11896 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-16 | 9945 | 9945 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-17 | 11600 | 11600 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-17 | 9766 | 9766 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-18 | 10628 | 10628 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-18 | 8115 | 8115 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-19 | 10821 | 10821 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-19 | 8530 | 8530 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-20 | 11276 | 11276 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-20 | 9409 | 9409 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-21 | 12356 | 12356 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-21 | 10314 | 10314 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-22 | 12106 | 12106 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-22 | 9884 | 9884 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-23 | 12611 | 12611 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-23 | 10676 | 10676 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-24 | 12604 | 12604 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-24 | 10725 | 10725 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-25 | 12025 | 12025 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-25 | 9590 | 9590 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-26 | 12938 | 12938 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-26 | 10063 | 10063 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-27 | 12792 | 12792 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-27 | 10888 | 10888 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-28 | 12335 | 12335 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-28 | 10694 | 10694 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-29 | 11425 | 11425 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-29 | 9751 | 9751 | - | - | - | - | - | - | - | - | - | - | - | -
2021-06-30 | 10217 | 10217 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-06-30 | 9931 | 9931 | - | - | - | - | - | - | - | - | - | - | - | -
Evening Peak | Max. L/S | 0 | - | -
| Min. L/S | 0 | - | -
| No. of Days | - | [12 empty] | 0 | 0 | 1
[15 empty] | 0 | 0 | 2
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 3
Day Peak | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 4
| No. of Days | - | - | - | [10 empty] | 0 | 0 | 5
[15 empty] | 0 | 0 | 6
| Max. L/S | - | - | - | [10 empty] | 0 | 0 | 7
Full Day | Min. L/S | - | - | - | [10 empty] | 0 | 0 | 8
| No. of Days | - | [12 empty] | 0 | 0 | 9
| Average L/S | #DIV/0! | [12 empty] | 0 | 0 | 10
[15 empty] | 0 | 0 | 11
[15 empty] | 0 | 0 | 12
[15 empty] | 0 | 0 | 13
[15 empty] | 0 | 0 | 14
[15 empty] | 0 | 0 | 15
[15 empty] | 0 | 0 | 16
[15 empty] | 0 | 0 | 17
[15 empty] | 0 | 0 | 18
[15 empty] | 0 | 0 | 19
[15 empty] | 0 | 0 | 20
[15 empty] | 0 | 0 | 21
[15 empty] | 0 | 0 | 22
[15 empty] | 0 | 0 | 23
[15 empty] | 0 | 0 | 24
[15 empty] | 0 | 0 | 25
[15 empty] | 0 | 0 | 26
[15 empty] | 0 | 0 | 27
[15 empty] | 0 | 0 | 28
[15 empty] | 0 | 0 | 29
[15 empty] | 0 | 0 | 30
[15 empty] | #REF! | #REF! | 31

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:June 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13014 | 2021-06-02 | 21:00
2 | Maximum Day Peak Genaration | MW | 9351 | 2021-06-01 | 12:00
3 | Maximum Evening Peak Demand | MW | 13014 | 44349 | 19:00
4 | Minimum Generation | MW | 7369 | 2021-06-18 | 9:00
5 | Average of the daily evening peak Genaration | MW | 11972.1667
6 | Average of the daily day peak Genaration | MW | 10113.8333
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 7570.405
12 | Total Generation by BPDB | MkWh | 1824.666 | % of total Gen. | 24.1%
13 | Total Generation by IPP | MkWh | 2192.5944 | '' | 28.96%
14 | A) Total Generation by Generation Companies | MkWh | 2223.2428 | '' | 29.37%
| B) Total Generation by REB | MkWh | 133.1241 | " | 1.758%
| C) Total Generation by RENTAL | MkWh | 485.0104 | " | 6.407%
| D) Total Imported from India (BIPTC) | MkWh | 631.2368 | " | 8.338%
| E) Total Imported from Tripura, India (A.C) | MkWh | 80.5306 | " | 1.064%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4718.5487 | % of total Gen. | 62.33%
| B) Oil | MkWh | 1686.2176 | '' | 22.27%
| C) Hydro | MkWh | 17.4436 | '' | 0.2304%
| D) Solar | MkWh | 15.602 | '' | 0.2061%
| E) Coal | MkWh | 420.8257 | '' | 5.559%
| F) BIPTC (Import from India) | MkWh | 631.2368 | '' | 8.338%
| G) A.C (Import from Tripura, India) | MkWh | 80.5306 | '' | 1.064%
16 | Maximun of the daily total Generation . | MkWh | 274.8708 | 2021-06-14
17 | Monthly Load factor | % | 78.1871
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 24397.1081
| A) Gas | M.Taka | 4854.5553
| B) Liquid fuel | M.Taka | 13757.7269
| C) Coal | M.Taka | 1961.539
| D) BIPTC (Import from India) | M.Taka | 3219.3076
| E) Tripura(Import from India) | M.Taka | 603.9792
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 935.2007 | 2021-06-07
| A) Gas | M.Taka | 174.4409 | 2021-06-19
| B) Liquid fuel | M.Taka | 710.3224 | 2021-06-07
| C) Coal | M.Taka | 73.1937 | 2021-06-21
| D) BIPTC (Import from India) | M.Taka | 112.8862 | 2021-06-04
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.4656
| B) Excluding Hydro & Solar | Taka/kWhR | 3.4804
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 83.73 | 30/6/2021 | 06:00
b) | Actual | FT (MSL) | 76.12 | 30/6/2021 | 06:00
22 | Peak Genaration of June 2020 | MW | 12070 | 24/06/20 | 22:00
23 | Peak Demand of June 2020 | MW | 12070 | 24/06/20 | 12:00
24 | Maximum peak Generation recorded upto 30/06/2021 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 30/06/2021 | MW | 14097 | 27/04/21 | 20:00
26 | Maximum load shed recorded upto 30/06/2021 | MW | 1459 | 05/04/10 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.