## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-08-16 | Monday
|  |  | Date (day): | 2021-08-16 |  | Monday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 14083.6 | MW |  |  | (b) At Evening Peak Hour : |  | 15036 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-08-15 | 2021-08-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 110 | 110 | 110 | 110 | 80 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 276 | 278 | 280 | 280 |  | 132 | ST Under maint.
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 341 | 347 | 340 | 340 | 20 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 240 | 240 | 240 | 240 | 210 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 270 | 240 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 60 | 85 | 85 |  | 15 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 21 | 20 | 20
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 330 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 24 | 94 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 133 | 133 |  | 16 | Engine problem
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 25 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 0 | 25 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 0 | 173 | 280 | 280 |  | 20 | Engine problem.
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 0 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 49 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 0 | 90 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 33 | 90 | 90 | 90 |  | 14 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 26 | 114 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 26 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 2290 | 3101 | 3698 | 3920 | 787 | 965
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 8 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 11 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 19 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 120 | 119 | 120 | 120 | 110 |  | Low water level
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 88 | 90 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 102 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 31 | 37 | 10 | 25
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 82 | 96 | 95 | 95 |  | 13 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 4 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 16 | 71 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 50 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 96 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 838 | 1168 | 1433 | 1523 | 370 | 486
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 80 | 80 | 80 | 54 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 182 | 215 | 215 | 215 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 260 | 330 | 330 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 330 | 330 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 20 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 35 | 35 | 35 |  | 16 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 80 | 118 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 136 | 134 | 140 | 140
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 28 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 112 | 140 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 0 | 100 | 113 | 113
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 81 | 104 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1525 | 1885 | 2220 | 2347 | 505 | 90
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 157 | 156 | 156 |  | 46 | Machine problem.
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 5 | 6 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 35 | 178 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 109 | 110 | 112 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 24 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 369 | 496 | 545.6 | 522 | 0 | 133
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | GT-4 under S/D
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 266 | 271 | 270 | 270 | 60 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 60 | 59 | 62 | 64
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 84 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 196 | 190 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 402 | 367 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 390 | 400 | 350 | 383
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 2046 | 2025 | 2094 | 2130 | 60 | 174
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 700 | 686 | 469 | 469
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 0 | 0 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 50 | 0 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 390 | 410 | 330 | 400
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 17 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1107 | 1351 | 1054 | 1484 | 0 | 78
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 23 | 34 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 77 | 89 | 89 |  | 105 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 12 | 12 | 83 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 215 | 215 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 735 | 921 | 1236 | 1236 | 83 | 105
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 0 | 0 | 40 |  | 31 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 30 |  | 20 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 164 | 185 | 185 | 185 | 35 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 195 | 206 | 220 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 335 | 385 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 19 | 0 | 20 |  | 30 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 7 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 0 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 2 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 784 | 1272 | 1532 | 1586 | 465 | 96
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 155 | 155 | 150 | 155 | 119 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 35 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 3 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 193 | 268 | 271 | 288 | 119 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 9887 | 12487 | 14083.6 | 15036 | 2389 | 2317
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9310.5816 | 11759 | 13262.5172 | 14159.3917
| A. |  | 2021-08-15 | (Yesterday) |  |  |  |  | Sunday
| 1 | Highest Generation : |  |  | 12584 | MW at | 23:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 9182 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12487 | MW
| 3 | Day peak Generation : |  |  | 9887 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11759 | MW
| 4 | Evening peak Generation : |  |  | 12487 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 261.7463 | MKWHr | By Solar | 0.56122 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 160.354 | MKWHr |  | By Oil: | 62.3948 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.8052 | MKWHr |  | By Hydro: | 2.8607 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2389 | MW | Dhaka | 3771 | 3771 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2317 | MW | Chittagong | 1189 | 1189 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4706 | MW | Khulna | 1632 | 1632 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1214.38 | MMCFD |  |  | Rajshahi | 1325 | 1325 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 165960754.442 | ii) Oil : | Taka | 423587284.93 | Comilla | 1181 | 1181 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 73279876 | Total | Taka | 662827915.372 | Mymensingh | 990 | 990 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 5.7735 | MKWHr. | Sylhet | 506 | 506 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -530 | MW (E to W) at | 21:00 | hrs | Barisal | 370 | 370 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -530 | MW at | 21:00 | hrs | Rangpur | 795 | 795 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.8° C |  |  | Total | 11759 | 11759 |  | 0
| B. |  | 2021-08-16 | (Today) |  |  |  | Monday |  |  | Probable max. temperature in Dhaka |  |  | 34.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 15036 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1836 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 274.5591 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9738 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.7905 | MKWHr. | ii) HVDC Flow at Peak Time |  | 686 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9798 | MKWHr. | iii) Maximum HVDC Flow : |  | 701 | MW at | 1:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 91.17 |  | (b) Today: | 91.42 |  | (c) Rule Curve: |  | 93.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-08-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 279 |  | 0 | 240 | 250 | 0 | 0 | 40 | 330 | 0 | 0 | 0 | 102 | 64 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 24 | 25 | 33 | 16 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 10 | 96 | 19 | 21 | 33 | 0 | 0 | 80 | 260 | 265 | 181 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 140 | 154 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 59 | 81 | 0 | 225 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 277 | 0 | 0 | 191 | 0 | 149 | 0 | 100 | 199 | 135 | 365 | 102 | 105 | 105 | 0 | 107 | 0 | 110 | 114 | 106 | 100 | 330 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 701 | 0 | 365 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 178 | 0 | 388 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 216 | 0 | 17 | 0 |  | 8554 | 3484 | 12038 | 4660 | 701 | 1866 | 3581 | 685 | 120 | 285 | 140 | 0 | 0 | 91.1
2:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 283 |  | 0 | 240 | 275 | 0 | 0 | 40 | 328 | 0 | 0 | 0 | 32 | 16 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 24 | 25 | 33 | 8 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 10 | 96 | 0 | 21 | 35 | 0 | 0 | 80 | 260 | 270 | 185 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 136 | 152 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 59 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 278 | 0 | 0 | 191 | 0 | 120 | 0 | 100 | 200 | 135 | 365 | 102 | 105 | 105 | 0 | 107 | 0 | 110 | 0 | 105 | 100 | 330 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 700 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 52 | 20 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 176 | 0 | 414 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 219 | 0 | 17 | 0 |  | 8226 | 3430 | 11656 | 4670 | 700 | 1904 | 3342 | 675 | 120 | 109 | 136 | 0 | 0 | 91.12
3:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 293 |  | 0 | 240 | 280 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 16 | 16 | 22 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 24 | 25 | 33 | 8 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 93 | 0 | 21 | 35 | 0 | 0 | 80 | 260 | 265 | 181 | 8 | 138 | 23 | 56 | 0 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 134 | 156 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 59 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 95 | 0 | 0 | 191 | 0 | 88 | 0 | 100 | 199 | 133 | 365 | 102 | 105 | 105 | 0 | 107 | 0 | 110 | 0 | 106 | 100 | 330 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 700 | 0 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 170 | 0 | 415 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 520 | 219 | 0 | 17 | 0 |  | 7983 | 3291 | 11274 | 4659 | 700 | 1915 | 3031 | 675 | 121 | 39 | 134 | 0 | 0 | 91.14
4:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 298 |  | 0 | 240 | 265 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 16 | 0 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 24 | 25 | 33 | 8 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 96 | 0 | 21 | 38 | 0 | 0 | 80 | 265 | 270 | 186 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 130 | 154 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 59 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 45 | 0 | 0 | 190 | 0 | 88 | 0 | 100 | 199 | 128 | 366 | 102 | 70 | 105 | 0 | 107 | 0 | 110 | 0 | 105 | 100 | 330 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 699 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 170 | 0 | 410 | 70 | 0 | 113 | 0 | 113 | 0 | 0 | 35 | 520 | 219 | 0 | 0 | 0 |  | 7876 | 3250 | 11126 | 4678 | 699 | 1927 | 2896 | 675 | 121 | 0 | 130 | 0 | 0 | 91.15
5:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 282 | 302 |  | 0 | 240 | 260 | 0 | 0 | 55 | 333 | 0 | 0 | 0 | 7 | 0 | 24 | 0 | 0 | 0 | 54 | 55 | 55 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 93 | 0 | 21 | 38 | 0 | 0 | 80 | 260 | 265 | 182 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 124 | 157 | 8 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 270 | 59 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 15 | 0 | 0 | 120 | 0 | 88 | 0 | 100 | 199 | 132 | 364 | 102 | 50 | 90 | 0 | 107 | 0 | 110 | 0 | 100 | 100 | 330 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 699 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 170 | 0 | 373 | 70 | 0 | 35 | 0 | 113 | 0 | 0 | 0 | 510 | 218 | 0 | 0 | 0 |  | 7675 | 3090 | 10765 | 4670 | 699 | 1882 | 2603 | 666 | 121 | 0 | 124 | 0 | 0 | 91.16
6:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 317 |  | 0 | 240 | 275 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 89 | 0 | 21 | 38 | 0 | 0 | 80 | 260 | 270 | 185 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 116 | 155 | 8 | 21 | 0 | 44 | 42 | 14 | 0 | 110 | 271 | 59 | 84 | 0 | 226 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 73 | 0 | 100 | 68 | 130 | 364 | 111 | 50 | 89 | 0 | 72 | 0 | 110 | 0 | 65 | 100 | 300 | 73 | 0 | 17 | 116 | 0 | 17 | 1 |  | 699 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 170 | 0 | 402 | 17 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 450 | 219 | 0 | 0 | 0 |  | 7008 | 2873 | 9881 | 4599 | 699 | 1884 | 1856 | 605 | 121 | 0 | 116 | 1 | 0 | 91.17
7:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 321 |  | 0 | 240 | 275 | 0 | 0 | 30 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 89 | 0 | 21 | 23 | 0 | 0 | 80 | 265 | 275 | 187 | 8 | 137 | 22 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 104 | 155 | 8 | 21 | 0 | 43 | 42 | 14 | 0 | 110 | 270 | 59 | 84 | 0 | 226 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 71 | 2 | 50 | 17 | 50 | 369 | 111 | 17 | 51 | 0 | 16 | 0 | 110 | 0 | 17 | 50 | 300 | 17 | 4 | 17 | 116 | 0 | 17 | 5 |  | 700 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 165 | 0 | 12 | 0 | 170 | 0 | 400 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 430 | 219 | 0 | 0 | 0 |  | 6516 | 2841 | 9357 | 4619 | 700 | 1869 | 1349 | 585 | 120 | 0 | 104 | 11 | 0 | 91.18
8:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 281 | 322 |  | 0 | 240 | 250 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 89 | 0 | 21 | 38 | 0 | 0 | 80 | 275 | 265 | 182 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 21 | 102 | 154 | 8 | 21 | 0 | 43 | 42 | 14 | 0 | 110 | 271 | 64 | 84 | 0 | 225 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 0 | 0 | 0 | 32 | 0 | 60 | 3 | 50 | 17 | 50 | 366 | 110 | 0 | 51 | 2 | 16 | 0 | 68 | 0 | 17 | 20 | 300 | 17 | 6 | 17 | 116 | 0 | 17 | 8 |  | 700 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 186 | 0 | 368 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 218 | 0 | 0 | 1 |  | 6392 | 2790 | 9182 | 4628 | 700 | 1850 | 1208 | 555 | 118 | 0 | 102 | 21 | 0 | 90.76
9:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 278 | 322 |  | 0 | 240 | 290 | 0 | 0 | 15 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 15 | 25 | 33 | 0 | 0 | 58 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 89 | 0 | 20 | 39 | 0 | 0 | 80 | 310 | 300 | 203 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 18 | 104 | 154 | 8 | 21 | 1 | 43 | 42 | 14 | 0 | 110 | 268 | 62 | 81 | 0 | 225 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 8 | 20 | 17 | 20 | 400 | 110 | 0 | 34 | 3 | 16 | 0 | 68 | 0 | 17 | 20 | 300 | 17 | 12 | 17 | 116 | 0 | 17 | 16 |  | 699 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 186 | 0 | 409 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 217 | 0 | 0 | 2 |  | 6420 | 2822 | 9242 | 4727 | 699 | 1892 | 1106 | 553 | 118 | 0 | 104 | 43 | 0 | 90.78
10:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 280 | 348 |  | 0 | 240 | 250 | 0 | 0 | 20 | 300 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 22 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 25 | 0 | 0 | 0 | 72 | 0 | 20 | 37 | 0 | 0 | 80 | 275 | 300 | 182 | 8 | 137 | 23 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 12 | 108 | 153 | 8 | 21 | 2 | 43 | 42 | 47 | 0 | 163 | 269 | 63 | 81 | 0 | 225 | 18 | 0 | 10 | 295 | 24 | 11 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 11 | 20 | 17 | 40 | 402 | 110 | 0 | 66 | 6 | 16 | 0 | 97 | 0 | 34 | 20 | 350 | 17 | 17 | 17 | 100 | 0 | 17 | 33 |  | 699 | 0 | 375 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 157 | 0 | 11 | 0 | 186 | 0 | 368 | 17 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 400 | 216 | 0 | 0 | 2 |  | 6603 | 2778 | 9381 | 4746 | 699 | 1948 | 1135 | 553 | 120 | 0 | 108 | 72 | 0 | 90.8
11:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 278 | 347 |  | 0 | 240 | 275 | 0 | 0 | 35 | 324 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 18 | 25 | 20 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 77 | 0 | 20 | 30 | 0 | 0 | 80 | 355 | 295 | 184 | 8 | 136 | 23 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 12 | 112 | 153 | 8 | 21 | 1 | 43 | 42 | 50 | 0 | 163 | 269 | 61 | 81 | 0 | 185 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 0 | 0 | 0 | 19 | 0 | 19 | 17 | 35 | 17 | 70 | 401 | 109 | 0 | 88 | 3 | 16 | 0 | 110 | 0 | 65 | 20 | 370 | 17 | 23 | 17 | 116 | 0 | 17 | 19 |  | 700 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 158 | 0 | 11 | 0 | 191 | 0 | 343 | 17 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 400 | 217 | 0 | 0 | 2 |  | 6869 | 2737 | 9606 | 4797 | 700 | 1921 | 1333 | 556 | 120 | 0 | 112 | 67 | 0 | 90.82
12:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 276 | 341 |  | 0 | 240 | 270 | 0 | 0 | 40 | 324 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 25 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 0 | 20 | 31 | 0 | 0 | 80 | 320 | 300 | 182 | 8 | 136 | 23 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 112 | 152 | 5 | 21 | 1 | 43 | 42 | 50 | 0 | 163 | 266 | 60 | 84 | 0 | 196 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 11 | 90 | 28 | 80 | 402 | 109 | 0 | 88 | 4 | 16 | 0 | 110 | 0 | 81 | 50 | 390 | 33 | 24 | 26 | 116 | 0 | 17 | 26 |  | 700 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 195 | 0 | 335 | 17 | 0 | 7 | 0 | 35 | 0 | 3 | 0 | 400 | 215 | 0 | 0 | 2 |  | 7068 | 2819 | 9887 | 4852 | 700 | 1899 | 1578 | 555 | 120 | 0 | 112 | 71 | 0 | 90.84
13:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 276 | 337 |  | 0 | 240 | 275 | 0 | 0 | 40 | 325 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 35 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 87 | 0 | 20 | 28 | 0 | 0 | 80 | 325 | 300 | 184 | 8 | 137 | 23 | 55 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 124 | 152 | 5 | 21 | 1 | 44 | 42 | 50 | 0 | 163 | 268 | 63 | 84 | 0 | 211 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 8 | 0 | 0 | 36 | 0 | 49 | 20 | 90 | 52 | 100 | 404 | 109 | 0 | 88 | 5 | 16 | 0 | 110 | 0 | 104 | 100 | 400 | 53 | 3 | 54 | 116 | 0 | 17 | 17 |  | 700 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 166 | 0 | 11 | 0 | 199 | 0 | 400 | 33 | 0 | 35 | 0 | 42 | 0 | 0 | 0 | 400 | 218 | 0 | 0 | 3 |  | 7324 | 2947 | 10271 | 4904 | 700 | 1978 | 1843 | 553 | 120 | 0 | 124 | 49 | 0 | 90.86
14:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 276 | 322 |  | 0 | 240 | 255 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 85 | 0 | 19 | 27 | 0 | 0 | 80 | 310 | 300 | 183 | 8 | 137 | 23 | 54 | 0 | 35 | 0 | 0 | 1 | 22 | 11 | 25 | 20 | 124 | 153 | 5 | 21 | 1 | 44 | 42 | 53 | 0 | 130 | 271 | 63 | 82 | 0 | 211 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 17 | 0 | 0 | 60 | 0 | 49 | 19 | 90 | 80 | 100 | 402 | 109 | 6 | 88 | 1 | 16 | 0 | 110 | 0 | 103 | 100 | 357 | 53 | 27 | 126 | 116 | 0 | 17 | 18 |  | 699 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 165 | 0 | 11 | 0 | 199 | 0 | 361 | 60 | 0 | 68 | 0 | 99 | 0 | 3 | 0 | 410 | 217 | 0 | 0 | 5 |  | 7324 | 3034 | 10358 | 4797 | 699 | 1884 | 2097 | 563 | 120 | 0 | 124 | 74 | 0 | 91.22
15:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 273 | 321 |  | 0 | 240 | 275 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 64 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 0 | 92 | 0 | 19 | 37 | 0 | 0 | 80 | 260 | 270 | 183 | 8 | 137 | 23 | 54 | 0 | 35 | 0 | 0 | 8 | 22 | 11 | 25 | 20 | 124 | 153 | 6 | 21 | 1 | 44 | 42 | 53 | 0 | 130 | 270 | 63 | 82 | 0 | 211 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 60 | 0 | 0 | 60 | 0 | 49 | 16 | 90 | 100 | 100 | 303 | 109 | 17 | 90 | 2 | 16 | 0 | 110 | 0 | 102 | 100 | 350 | 53 | 21 | 126 | 116 | 0 | 17 | 19 |  | 686 | 0 | 385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 167 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 196 | 0 | 347 | 86 | 0 | 70 | 0 | 107 | 0 | 2 | 0 | 420 | 217 | 0 | 0 | 4 |  | 7259 | 3058 | 10317 | 4598 | 686 | 1891 | 2242 | 587 | 124 | 0 | 124 | 65 | 0 | 91.23
16:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 273 | 322 |  | 0 | 240 | 265 | 0 | 0 | 50 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 35 | 55 | 18 | 25 | 25 | 25 | 33 | 0 | 0 | 65 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 94 | 0 | 19 | 37 | 0 | 0 | 80 | 260 | 270 | 182 | 8 | 137 | 23 | 53 | 0 | 35 | 0 | 0 | 8 | 22 | 11 | 25 | 18 | 116 | 153 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 130 | 271 | 63 | 81 | 0 | 218 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 60 | 0 | 0 | 60 | 0 | 49 | 4 | 100 | 100 | 100 | 305 | 100 | 17 | 90 | 2 | 16 | 0 | 110 | 0 | 99 | 100 | 350 | 53 | 11 | 162 | 96 | 0 | 17 | 8 |  | 686 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 193 | 0 | 336 | 53 | 0 | 70 | 0 | 85 | 0 | 1 | 0 | 420 | 217 | 0 | 0 | 1 |  | 7231 | 2978 | 10209 | 4608 | 686 | 1867 | 2204 | 576 | 125 | 0 | 116 | 27 | 0 | 91.24
17:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 275 | 323 |  | 0 | 240 | 280 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 20 | 25 | 25 | 25 | 33 | 0 | 0 | 64 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 94 | 0 | 19 | 37 | 0 | 0 | 80 | 280 | 285 | 195 | 8 | 137 | 23 | 55 | 0 | 15 | 0 | 0 | 8 | 22 | 11 | 10 | 20 | 112 | 152 | 6 | 21 | 0 | 44 | 42 | 14 | 0 | 130 | 270 | 40 | 20 | 0 | 190 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 30 | 0 | 0 | 40 | 0 | 49 | 3 | 40 | 68 | 108 | 316 | 85 | 17 | 68 | 1 | 16 | 0 | 110 | 0 | 100 | 40 | 350 | 19 | 9 | 90 | 116 | 0 | 17 | 7 |  | 687 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 193 | 0 | 348 | 89 | 0 | 35 | 0 | 35 | 0 | 1 | 0 | 400 | 170 | 0 | 0 | 0 |  | 6750 | 2883 | 9633 | 4618 | 687 | 1715 | 1803 | 553 | 124 | 0 | 112 | 21 | 0 | 91.25
18:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 257 | 302 |  | 0 | 240 | 280 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 24 | 4 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 20 | 25 | 25 | 25 | 33 | 0 | 0 | 62 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 95 | 0 | 20 | 37 | 0 | 0 | 80 | 280 | 285 | 191 | 8 | 137 | 23 | 55 | 0 | 15 | 0 | 0 | 8 | 22 | 11 | 25 | 21 | 112 | 152 | 6 | 21 | 0 | 44 | 42 | 14 | 0 | 130 | 269 | 40 | 20 | 0 | 190 | 18 | 0 | 10 | 295 | 24 | 8 | 0 | 30 | 0 | 0 | 40 | 0 | 49 | 0 | 40 | 68 | 122 | 314 | 85 | 17 | 51 | 0 | 16 | 0 | 68 | 0 | 70 | 40 | 350 | 17 | 2 | 72 | 116 | 0 | 17 | 1 |  | 686 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 172 | 0 | 12 | 0 | 186 | 0 | 347 | 53 | 0 | 35 | 0 | 35 | 0 | 0 | 0 | 370 | 130 | 0 | 0 | 0 |  | 6587 | 2695 | 9282 | 4528 | 686 | 1656 | 1646 | 525 | 122 | 4 | 112 | 3 | 0 | 91.26
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 257 | 343 |  | 0 | 240 | 275 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 64 | 82 | 13 | 0 | 0 | 0 | 54 | 35 | 35 | 20 | 25 | 14 | 25 | 17 | 20 | 0 | 60 | 60 | 100 | 0 | 5 | 0 | 0 | 0 | 0 |  | 24 | 0 | 99 | 36 | 96 | 13 | 20 | 37 | 0 | 0 | 80 | 290 | 300 | 210 | 8 | 136 | 23 | 55 | 0 | 28 | 0 | 0 | 16 | 22 | 11 | 25 | 21 | 136 | 152 | 6 | 21 | 0 | 44 | 42 | 49 | 0 | 130 | 269 | 50 | 84 | 0 | 225 | 18 | 0 | 10 | 300 | 24 | 11 | 0 | 60 | 0 | 0 | 120 | 0 | 66 | 0 | 100 | 121 | 120 | 376 | 110 | 58 | 71 | 0 | 66 | 0 | 106 | 45 | 97 | 100 | 395 | 42 | 0 | 122 | 116 | 0 | 17 | 0 |  | 686 | 0 | 395 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 81 | 0 | 0 | 28 | 30 | 19 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 181 | 0 | 11 | 14 | 161 | 0 | 394 | 70 | 0 | 55 | 0 | 113 | 0 | 0 | 90 | 390 | 217 | 0 | 15 | 0 |  | 7974 | 3310 | 11284 | 4806 | 686 | 1961 | 2671 | 545 | 120 | 359 | 136 | 0 | 0 | 91.29
19:30 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 279 | 336 |  | 0 | 240 | 260 | 0 | 0 | 55 | 328 | 0 | 0 | 0 | 82 | 82 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 14 | 25 | 17 | 30 | 0 | 59 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 50 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 260 | 270 | 213 | 8 | 136 | 23 | 55 | 0 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 134 | 153 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 61 | 84 | 0 | 225 | 18 | 0 | 10 | 285 | 24 | 11 | 0 | 120 | 0 | 0 | 185 | 0 | 136 | 0 | 100 | 200 | 120 | 365 | 110 | 90 | 90 | 0 | 66 | 0 | 110 | 70 | 113 | 100 | 397 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 686 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 95 | 0 | 0 | 29 | 52 | 19 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 100 | 178 | 0 | 402 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 108 | 480 | 217 | 0 | 54 | 0 |  | 8547 | 3716 | 12263 | 4812 | 686 | 1991 | 3509 | 635 | 119 | 377 | 134 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 279 | 346 |  | 0 | 240 | 250 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 82 | 82 | 47 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 26 | 25 | 25 | 40 | 0 | 59 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 50 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 260 | 270 | 215 | 8 | 135 | 23 | 20 | 0 | 35 | 0 | 0 | 47 | 22 | 11 | 25 | 21 | 140 | 154 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 61 | 83 | 0 | 176 | 18 | 0 | 10 | 275 | 24 | 11 | 0 | 130 | 0 | 0 | 187 | 0 | 130 | 0 | 100 | 200 | 115 | 366 | 110 | 90 | 90 | 0 | 68 | 0 | 110 | 70 | 106 | 100 | 400 | 87 | 0 | 162 | 116 | 0 | 17 | 0 |  | 686 | 0 | 410 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 93 | 0 | 0 | 31 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 100 | 195 | 0 | 390 | 105 | 0 | 105 | 0 | 113 | 0 | 0 | 113 | 490 | 217 | 0 | 54 | 0 |  | 8508 | 3780 | 12288 | 4808 | 686 | 1944 | 3518 | 646 | 119 | 427 | 140 | 0 | 0 | 91.28
21:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 278 | 347 |  | 0 | 240 | 240 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 94 | 100 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 25 | 33 | 25 | 0 | 59 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 100 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 260 | 300 | 215 | 8 | 134 | 23 | 20 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 140 | 157 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 59 | 84 | 0 | 190 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 173 | 0 | 0 | 178 | 0 | 149 | 0 | 100 | 200 | 118 | 367 | 110 | 90 | 90 | 0 | 71 | 0 | 110 | 100 | 104 | 100 | 400 | 90 | 0 | 114 | 96 | 0 | 17 | 0 |  | 686 | 0 | 410 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 77 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 30 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 100 | 206 | 0 | 385 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 215 | 0 | 54 | 0 |  | 8675 | 3812 | 12487 | 4863 | 686 | 1954 | 3603 | 685 | 119 | 437 | 140 | 0 | 0 | 91.29
22:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 279 | 346 |  | 0 | 240 | 290 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 102 | 100 | 25 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 8 | 0 | 61 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 295 | 315 | 212 | 8 | 138 | 23 | 35 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 142 | 154 | 7 | 21 | 0 | 43 | 42 | 52 | 0 | 163 | 270 | 56 | 84 | 0 | 191 | 18 | 0 | 10 | 280 | 24 | 11 | 0 | 228 | 0 | 0 | 178 | 0 | 149 | 0 | 100 | 199 | 118 | 332 | 110 | 90 | 90 | 0 | 34 | 0 | 110 | 114 | 106 | 100 | 395 | 90 | 0 | 90 | 115 | 0 | 17 | 0 |  | 686 | 0 | 410 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 30 | 52 | 10 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 100 | 213 | 0 | 412 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 220 | 0 | 54 | 0 |  | 8706 | 3838 | 12544 | 4885 | 686 | 1989 | 3638 | 682 | 121 | 401 | 142 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 278 | 346 |  | 0 | 240 | 295 | 0 | 0 | 55 | 329 | 0 | 0 | 0 | 102 | 100 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 8 | 0 | 61 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 19 | 20 | 40 | 0 | 0 | 80 | 295 | 320 | 212 | 8 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 142 | 154 | 7 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 270 | 56 | 84 | 0 | 191 | 18 | 0 | 10 | 310 | 24 | 11 | 0 | 245 | 0 | 0 | 178 | 0 | 141 | 0 | 100 | 199 | 117 | 336 | 110 | 70 | 90 | 0 | 35 | 0 | 110 | 114 | 110 | 100 | 395 | 90 | 0 | 90 | 115 | 0 | 17 | 0 |  | 694 | 0 | 405 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 100 | 205 | 0 | 410 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 220 | 0 | 54 | 0 |  | 8753 | 3831 | 12584 | 4880 | 694 | 2042 | 3623 | 691 | 121 | 391 | 142 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 279 | 346 |  | 0 | 240 | 275 | 0 | 0 | 55 | 332 | 0 | 0 | 0 | 102 | 100 | 12 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 25 | 33 | 8 | 0 | 60 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 19 | 20 | 38 | 0 | 0 | 80 | 260 | 285 | 213 | 8 | 136 | 23 | 56 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 140 | 155 | 7 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 270 | 56 | 84 | 0 | 190 | 18 | 0 | 10 | 300 | 24 | 5 | 0 | 245 | 0 | 0 | 178 | 0 | 134 | 0 | 100 | 199 | 118 | 305 | 110 | 90 | 90 | 0 | 35 | 0 | 110 | 114 | 105 | 100 | 400 | 90 | 0 | 90 | 90 | 0 | 17 | 0 |  | 694 | 0 | 410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 15 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 187 | 0 | 11 | 100 | 208 | 0 | 411 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 220 | 0 | 54 | 0 |  | 8604 | 3799 | 12403 | 4793 | 694 | 2031 | 3587 | 702 | 120 | 336 | 140 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 2740500 | 7389536 | 0 | 0 | 6768000 | 7712000 |  | 0 | 5622750 | 6462080 | 0 | 0 | 1115059 | 7452840 | 0 | 0 | 0 | 974160 | 646560 | 283706 | 0 | 0 | 0 | 1311120 | 934260 | 1002601 | 439920 | 600000 | 567000 | 614700 | 797600 | 190080 | 0 | 1396669 | 1464000 | 2400000 | 0 | 78112 | 0 | 0 | 0 | 0 |  | 589680 | 0 | 618370 | 489600 | 2188800 | 135360 | 476688 | 909120 | 0 | 0 | 1913438 | 7046500 | 6948000 | 4676000 | 200727 | 3281410 | 512640 | 1283520 | 0 | 776268 | 0 | 12088 | 479669 | 509040 | 254340 | 566400 | 504840 | 2979840 | 3612880 | 169920 | 491652 | 8700 | 1034000 | 990600 | 997800 | 0 | 3466309 | 6173000 | 1396992 | 1856640 | 0 | 5024160 | 403000 | 0 | 248940 | 7207500 | 571824 | 228096 | 0 | 2207999 | 0 | 0 | 2498400 | 0 | 1942272 | 113535 | 1900800 | 2925120 | 2525807 | 8667000 | 2529600 | 1194000 | 2049090 | 29041 | 1139127 | 0 | 2639552 | 695400 | 2133600 | 1893120 | 8438900 | 1397760 | 174020 | 2465280 | 2719855 | 0 | 441720 | 190400 |  | 16790545 | 0 | 9401184 | 0 | 0 | 205440 | 0 | 0 | 1440 | 0 | 0 | 2110507 | 673851 | 0 | 0 | 0 | 0 | 282544 | 22135 | 691936 | 0 | 0 | 145882 | 1193280 | 112130 | 497280 | 0 | 258156 | 0 | 0 | 3781600 | 0 | 0 | 0 | 0 | 4243291 | 0 | 278693 | 523200 | 4805518 | 0 | 9220900 | 1504320 | 0 | 1646615 | 0 | 1755763 | 0 | 18761 | 981216 | 12023600 | 5091573 | 0 | 349200 | 26760 |  | 183109002 | 78637320 | 261746322 | 114310152 | 16790545 | 46043871 | 59656303 | 15805200 | 2860669 | 2738525 | 2979840 | 561217 | 0
Fuel Cost | 0 | 0 | 0 | 4028535 | 8202384.96 | 0 | 0 | 6835680 | 7943360 |  | 0 | 6128797.5 | 7172908.8 | 0 | 0 | 9433399.14 | 7750953.6 | 0 | 0 | 0 | 8884339.2 | 6362150.4 | 2615769.32 | 0 | 0 | 0 | 9571176 | 7221829.8 | 9885645.86 | 329940 | 450000 | 0 | 0 | 0 | 1838073.6 | 0 | 377100.63 | 395280 | 4344000 | 0 | 725660.48 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5998189 | 4675680 | 19042560 | 1072051.2 | 600626.88 | 2700086.4 | 0 | 0 | 2812753.86 | 5214410 | 6948000 | 4301920 | 258937.83 | 3773621.5 | 579283.2 | 1796928 | 0 | 1327418.28 | 0 | 122088.8 | 4580838.95 | 646480.8 | 190755 | 991200 | 378630 | 22348800 | 3829652.8 | 1542873.6 | 624398.04 | 138678 | 1695760 | 1584960 | 1776084 | 0 | 3951592.26 | 6419920 | 2752074.24 | 3546182.4 | 0 | 8691796.8 | 882570 | 0 | 507837.6 | 7279575 | 428868 | 173352.96 | 0 | 16692472.44 | 0 | 0 | 12991680 | 0 | 19111956.48 | 1327224.15 | 15491520 | 31737552 | 17806939.35 | 8060310 | 23069952 | 11283300 | 17847573.9 | 0 | 8611800.12 | 0 | 23201662.08 | 6940092 | 18284952 | 12608179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96713539.2 | 0 | 9871243.2 | 0 | 0 | 2847398.4 | 0 | 0 | 15105.6 | 0 | 0 | 2384872.91 | 1044469.05 | 0 | 0 | 0 | 0 | 2780232.96 | 224891.6 | 6123633.6 | 0 | 0 | 1413596.58 | 11562883.2 | 1087661 | 954777.6 | 0 | 195424.092 | 0 | 0 | 20496272 | 0 | 0 | 0 | 0 | 5601144.12 | 0 | 418039.5 | 8899632 | 5622456.06 | 0 | 9128691 | 15705100.8 | 0 | 15626376.35 | 0 | 13624720.88 | 0 | 207309.05 | 7251186.24 | 52783604 | 0 | 0 | 0 | 0 |  | 491751585.41 | 292584260.992 | 784335846.402 | 117197978.022 | 96713539.2 | 48762776.42 | 396612336.99 | 73279876 | 772380.63 | 26974947.94 | 22348800 | 1673211.2 | 0
Yesterday Day Peak | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 276 | 341 |  | 0 | 240 | 270 | 0 | 0 | 40 | 324 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 25 | 18 | 25 | 24 | 25 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 82 | 0 | 20 | 31 | 0 | 0 | 80 | 320 | 300 | 182 | 8 | 136 | 23 | 55 | 0 | 25 | 0 | 0 | 0 | 22 | 11 | 25 | 20 | 112 | 152 | 5 | 21 | 1 | 43 | 42 | 50 | 0 | 163 | 266 | 60 | 84 | 0 | 196 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 0 | 0 | 0 | 35 | 0 | 49 | 11 | 90 | 28 | 80 | 402 | 109 | 0 | 88 | 4 | 16 | 0 | 110 | 0 | 81 | 50 | 390 | 33 | 24 | 26 | 116 | 0 | 17 | 26 |  | 700 | 0 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 195 | 0 | 335 | 17 | 0 | 7 | 0 | 35 | 0 | 3 | 0 | 400 | 215 | 0 | 0 | 2 |  | 9887 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 278 | 347 | 0 | 0 | 240 | 240 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 94 | 100 | 60 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 28 | 25 | 33 | 25 | 0 | 59 | 60 | 100 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 102 | 100 | 96 | 19 | 20 | 37 | 0 | 0 | 80 | 260 | 300 | 215 | 8 | 134 | 23 | 20 | 0 | 35 | 0 | 0 | 52 | 22 | 11 | 25 | 21 | 140 | 157 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 59 | 84 | 0 | 190 | 18 | 0 | 10 | 290 | 24 | 11 | 0 | 173 | 0 | 0 | 178 | 0 | 149 | 0 | 100 | 200 | 118 | 367 | 110 | 90 | 90 | 0 | 71 | 0 | 110 | 100 | 104 | 100 | 400 | 90 | 0 | 114 | 96 | 0 | 17 | 0 |  | 686 | 0 | 410 | 0 | 0 | 50 | 0 | 0 | 0 | 0 | 0 | 77 | 34 | 0 | 0 | 0 | 0 | 43 | 0 | 93 | 0 | 0 | 30 | 52 | 19 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 185 | 0 | 11 | 100 | 206 | 0 | 385 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 215 | 0 | 54 | 0 |  | 12487 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 280 | 340 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 133 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 25 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 95 | 50 | 21 | 25 | 0 | 0 | 80 | 330 | 330 | 215 | 8 | 140 | 23 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 156 | 8 | 21 | 0 | 44 | 42 | 51 | 0 | 163 | 270 | 64 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 280 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 135 | 400 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 113 | 113 | 100 | 383 | 90 | 0 | 162 | 116 | 0 | 17 |  |  | 469 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 25 | 60 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 95 | 35 | 0 | 30 | 52 | 20 | 22 | 0 | 11 | 0 | 0 | 155 | 10 | 10 | 0 | 0 | 185 | 0 | 12 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 280 | 340 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 100 | 133 | 85 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 30 | 25 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 95 | 50 | 21 | 10 | 0 | 0 | 80 | 330 | 330 | 215 | 8 | 140 | 23 | 55 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 138 | 156 | 8 | 21 | 1.6 | 43 | 42 | 51 | 0 | 163 | 270 | 62 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 24 | 11 | 100 | 280 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 135 | 400 | 112 | 100 | 105 | 5 | 200 | 54 | 110 | 113 | 113 | 100 | 350 | 90 | 50 | 162 | 116 | 0 | 17 | 30 |  | 469 | 0 | 330 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 35 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 150 | 0 | 0 |  | 0 | 185 | 0 | 12 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 110 | 310 | 0 | 0 | 220 | 270 | 0 | 0 | 240 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 28 | 25 |  | 0 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 0 | 90 | 0 | 0 | 8 | 0 | 0 | 80 | 290 | 310 | 197 | 8 | 136 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 0 | 0 | 110 | 154 | 6 | 21 | 0 | 43 | 42 | 53 | 0 | 110 | 269 | 45 | 84 | 0 | 178 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 15 | 0 | 0 | 80 | 0 | 70 | 7 | 100 | 100 | 108 | 333 | 115 | 50 | 105 | 1 | 35 | 0 | 110 | 0 | 107 | 100 | 350 | 17 | 19 | 54 | 95 | 0 | 17 | 6 | 0 | 460 | 0 | 320 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 197 | 0 | 11 | 0 | 212 | 0 | 370 | 105 | 0 | 50 | 0 | 50 | 0 | 1 | 0 | 380 | 221 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9182 | 8:00
| Highest Generation |  | 12584 | 23:00
| Day Peak Generation |  | 9887 | 12:00
| Evening Peak Generation |  | 12487 | 21:00
| HVDC Max Flow |  | 701 | 1:00
| HVDC EvPeak Flow |  | 686 | 21:00
| Load factor L.F |  | 86.67%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-08-16
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-08-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 9887 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9738 | MW
Evening Peak Generation : |  | 12487 | MW Hour : | 21:00 | Available Max Generation : |  | 15036 | MW
E.P. Demand (at gen end) : |  | 12487 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 12584 | MW Hour : | 23:00 | Reserve(Generation end) |  | 1836 | MW
Total Gen. (MKWH) : |  | 261.7463 | System Load Factor : | 86.67% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -530 | MW at | 21:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-08-16
Actual : | 91.42 | Ft.(MSL) , | Rule curve : | 93.8 | Ft.( MSL )
Gas Consumed : | Total = | 1214.38 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 165960754.442
: |  | Coal : | 73279876 | Oil : | 423587284.93 | Total : | 662827915.372
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4620.4455 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1576.0829 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1412.9868 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1277.0612 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1153.8916 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 931.162 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 514.3858 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 239.5831 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 718.1884 |  |  | 0 | 0%
Total | 0 |  | 12443.7873 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-3,4
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Sirajganj unit-1
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sirajganj 132/33 kV T4 transformer was under shutdown from 13:05 to 14:06 due to R/H maintenance.
b) Gollamari 132/33 kV T1 & T2 transformers (33 kV Side) tripped at 15:18 showing O/C due to fire at |  |  |  |  | About 36 MW power interruption occurred under Gollamari S/S
WZPDCL 33/11 kV T2 transformer B-phase CT and were switched on at 15:40. |  |  |  |  | area from 15:18 to 15:40.
c) Sikalbaha 132/33 kV T3 transformer tripped at 14:45 showing R Y B, O/C and was switched on at 15:25.
d) Aminbazar-Manikganj P.P. S/S 132 kV Ckt-1 tripped at 20:23 from both ends showing Dist. R-phase at
Power Plant end & Dist.Z1,3-phase at S/S end and was switched on at 04:22(16/08/2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-08-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 110 | 2740500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7389536 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 278 | 6768000 | ST Under maint.
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 347 | 7712000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 240 | 5622750 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 240 | 6462080 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1115059
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 60 | 283706 | Low demand
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 439920
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 330 | 7452840
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 94 | 974160 | Engine problem
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1311120
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 646560 | Low demand
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 934260
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1002601
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1167000 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614700
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 797600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 25 | 190080 | Low demand
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 173 | 2207999 | Low demand
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 0 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 0 | 0 | Reserve.
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 1942272
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1194000 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1397760 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 114 | 2465280
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 190400
| Dhaka area Total |  |  |  | 5819 | 3101 | 63022183
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 8 | 78112 | Low demand
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 113535
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 19 | 135360 | Low demand
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 119 | 2860669 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 90 | 2049090 | Engine problem
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 618370
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 489600
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1900800
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 476688
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 37 | 909120
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 96 | 2188800 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29041
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 71 | 1139127 | Transformer O/L
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer O/L
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2639552
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1893120
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 96 | 2719855 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1168 | 22640839
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 80 | 1913438 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 215 | 4676000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 260 | 7046500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6948000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 512640 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 1283520 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 200727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 776268 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 118 | 2525807 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 12088 | Reserve.
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 134 | 3281410 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 2925120
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 509040
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 254340
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2979840
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 566400
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 479669
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 504840
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 0 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 100 | 695400
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 104 | 2133600 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 441720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1885 | 40666367
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 157 | 3612880 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 491652
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 6 | 169920 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 8700
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 178 | 2498400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 110 | 2529600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 174020
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 589680
| Mymensingh Area Total |  |  |  | 709 | 496 | 10074852
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1034000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 990600 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3466309
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 271 | 6173000
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 997800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 228096
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 59 | 1396992
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1856640
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 190 | 5024160
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 403000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 571824
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7207500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 367 | 8667000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 248940
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 400 | 8438900
| Sylhet Area Total |  |  |  | 2377 | 2025 | 46704761
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 686 | 16790545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 0 | 1440
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 50 | 205440 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9401184
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 523200
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 1504320
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1351 | 28426129
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 673851
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 77 | 2110507 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 278693 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 12023600
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 215 | 5091573
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 349200 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 921 | 20527424
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 282544 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 0 | 22135
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 145882 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 185 | 4243291 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 206 | 4805518 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 385 | 9220900 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 19 | 112130 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 497280
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 258156
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1193280
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 691936 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 1646615
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 981216
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26760
| Rajshahi Area Total |  |  |  | 2179 | 1272 | 24127643
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 155 | 3781600 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1755763
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 18761
| Rangpur Area Total |  |  |  | 605 | 268 | 5556124
| Total |  |  |  | 21280 | 12487 | 261746322
| Eastern Grid Total |  |  |  | 14321 | 8675 | 183109002
| Western Grid Total |  |  |  | 6959 | 3812 | 78637320
| National Grid Total |  |  |  | 21280 | 12487 | 261746322
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-08-15
(a) ENTIRE EASTERN GRID : |  | 7637 | MW | (b) ENTIRE WESTERN GRID : |  | 4122 | MW
i) Dhaka area |  | 3771 | MW | i) Khulna area |  | 1632 | MW
ii) Chittagong area |  | 1189 | MW | ii) Rajshahi area |  | 1325 | MW
iii) Comilla area |  | 1181 | MW | iii) Barisal area |  | 370 | MW
iv) Mymensingh area |  | 990 | MW | iv) Rangpur area |  | 795 | MW
v) Sylhet area |  | 506 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11759 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 108 | 23:00 | Kishoreganj | 150 | 21:00 | Jessore | 126 | 21:00
Munsiganj | 108 | 0:00 | Netrokona | 111 | 19:30 | Benapol | 64 | 21:00
Sonargaon | 73 | 0:00 | Jamalpur | 151 | 22:00 | Jhenida | 124 | 19:30
Shyampur | 178 | 10:00 | Sherpur | 128 | 23:00 | Bottail | 122 | 19:30
Bhulta | 200 | 23:00 | Srimongal | 58 | 20:00 | G.K Project | 59 | 21:00
Madanganj | 37 | 2:00 | Shahjibazar | 115 | 21:00 | Faridpur | 154 | 21:00
Shitalakhya | 93 | 11:00 | Fenchuganj | 46 | 21:00 | Rajbari | 52 | 19:00
Rahim steel | 16 | 1:00 | Kulawara | 43 | 21:00 | Madaripur | 112 | 22:00
Matuail | 54 | 1:00 | Sylhet | 114 | 20:00 | Sariatpur | 74 | 22:00
Ghorasal | 81 | 23:00 | Chatak | 28 | 21:00 | Gopalganj | 98 | 22:00
Narsingdi | 174 | 21:00 | Sunamganj | 48 | 22:00 | Bagerhat | 109 | 21:00
Haripur (SBU) | 89 | 3:00 | Biani Bazar | 60 | 19:30 | Mongla | 38 | 1:00
Sreenagar | 43 | 21:00 | Comilla (S) | 142 | 22:00 | Satkhira | 113 | 22:00
Ullon | 68 | 0:00 | Comilla(N) | 131 | 22:00 | Gallamari | 42 | 20:00
Hasnabad | 80 | 23:00 | Chandpur | 76 | 0:00 | Magura | 64 | 20:00
Magbazar | 76 | 19:00 | Feni | 129 | 22:00 | Norail | 46 | 20:00
Maniknagar | 54 | 19:00 | Chowmuhani | 202 | 1:00 | Chuadanga | 105 | 20:00
Bangabhaban | 4 | 1:00 | Ashuganj | 46 | 0:00 | Borguna | 20 | 22:00
Motijheel | 16 | 13:00 | Daudkandi | 150 | 22:00 | Barisal(N) | 49 | 22:00
Narinda | 44 | 13:00 | B.Baria | 168 | 22:00 | Barisal (S) | 106 | 21:00
Kazla | 75 | 22:00 | Ramganj | 92 | 23:00 | Patuakhali | 119 | 23:00
Dhanmondi | 113 | 13:00 | Chaddagram | 45 | 21:00 | Bhandaria | 58 | 22:00
Lalbag | 77 | 19:00 | PHP | 6 | 2:00 | Borhan Uddin | 45 | 19:30
Madartek | 72 | 23:00 | Kochua | 74 | 23:00 | Ishurdi | 64 | 21:00
Dhaka University | 19 | 12:00 | Madunaghat | 56 | 19:00 | Ruppur Paromanobik | 3 | 21:00
Aftabnagar | 10 | 19:00 | Hathazari | 92 | 19:30 | Natore | 134 | 20:00
Fatullah | 52 | 1:00 | Khulshi | 156 | 3:00 | Bogra | 159 | 20:00
Nawabganj | 54 | 21:00 | Halishahar | 78 | 19:00 | Noagaon | 114 | 21:00
Keraniganj | 59 | 22:00 | Baraulia | 116 | 1:00 | Rajshahi | 156 | 21:00
Mirpur | 105 | 19:00 | Sikalbaha | 38 | 1:00 | Rajshahi New | 14 | 21:00
Kalyanpur | 102 | 19:00 | Dohazari | 96 | 20:00 | C.Nawabganj | 65 | 19:30
Gulshan | 72 | 19:00 | Cox'sbazar | 111 | 19:00 | Amnura | 50 | 21:00
Uttara | 77 | 20:00 | Chandraghona | 28 | 19:00 | Pabna | 105 | 21:00
Uttara New | 17 | 1:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 100 | 21:00
Kamrangirchar | 75 | 1:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 106 | 21:00
Savar | 127 | 2:00 | Bakulia | 96 | 21:00 | Niyamatpur | 71 | 21:00
Bhasantec | 120 | 19:00 | Julda | 20 | 1:00 | Joypurhat | 58 | 21:00
Agargaon | 72 | 21:00 | TK chemical | 30.5 | 22:00 | Sherpur(Bogura) | 54 | 19:00
Satmosjid | 95 | 19:00 | Modern Steel | 0 | 0.041667 | Mohastangor | 68 | 20:00
Tongi | 102 | 18:30 | Shahmirpur | 27 | 23:00 | Bhangura | 34 | 21:00
Kabirpur | 177 | 1:00 | Khagrachhari | 30 | 1:00 | Rangpur | 120 | 14:00
Basundhara | 200 | 19:00 | Matarbari | 37 | 18:30 | Lalmonirhat | 45 | 19:30
Manikganj | 78 | 22:00 | Baroiar Hat | 48 | 21:00 | Saidpur | 95 | 1:00
Joydevpur | 128 | 23:00 | Rangamati | 13 | 19:00 | Purbasadipur | 109 | 21:00
New Tongi | 86 | 1:00 | Abul Khair 230 | 140 | 16:00 | Thakurgaon | 88 | 20:00
Kodda | 239 | 1:00 | BSRM | 159 | 18:30 | Palashbari | 108 | 19:00
Dhamrai | 92 | 21:00 | GPH Ispat | 93 | 18:00 | Barapukuria | 51 | 1:00
Rajendrapur | 94 | 1:00 | Agrabad | 71 | 20:00 | Panchagar | 52 | 2:00
Valuka | 114 | 1:00 | Goalpara | 23 | 16:00 | Joldhaka | 58 | 21:00
Tangail | 211 | 19:30 | Central S/S | 99 | 20:00 | Kurigram | 55 | 20:00
Mymensing | 202 | 19:00 | Noapara | 113 | 22:00 | Mithapukur | 39 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-08-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 18:30 | 402 | 9:00 | Kaliakoir | 396 | 0.75 | 387 | 0.54167
| Bheramara | 404 | 1:00 | 397 | 21:00 | Bhulta | 388 | 0.041667 | 380 | 0.375
| Ashuganj(N) | 392 | 1:00 | 387 | 10:00 | Gopalganj | 410 | 0.625 | 391 | 0.875
| Payra | 414 | 1:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 18:00 | 230 | 1:00 | Hathazari | 228 | 19:30 | 219 | 9:00
| Ishurdi | 235 | 18:00 | 225 | 1:00 | Megnaghat | 234 | 14:00 | 231 | 9:00
| Ashuganj | 240 | 18:30 | 236 | 10:00 | Fenchuganj | 244 | 1:00 | 241 | 1:00
| Serajganj | 229 | 16:00 | 224 | 13:00 | Siddhirganj | 232 | 1:00 | 228 | 11:00
| Baghabari | 233 | 17:00 | 215 | 21:00 | Maniknagar | 231 | 1:00 | 227 | 10:00
| Barapukuria | 235 | 15:00 | 226 | 21:00 | Agargaon | 230 | 18:00 | 223 | 11:00
| Bogra | 227 | 19:00 | 214 | 13:00 | Barisal | 241 | 1:00 | 232 | 1:00
| Rajshahi | 232 | 18:00 | 219 | 13:00 | Bhola 225 MW | 244 | 18:00 | 237 | 19:00
| Khulna South | 226 | 18:30 | 204 | 2:00 | AKSML | 229 | 1:00 | 220 | 9:00
| Rampura | 230 | 1:00 | 227 | 10:00 | BSRM | 229 | 1:00 | 222 | 17:00
| Haripur | 229 | 1:00 | 226 | 11:00 | Bibiyana | 243 | 20:00 | 240 | 1:00
| Hasnabad | 228 | 1:00 | 224 | 8:00 | Bhulta | 236 | 23:00 | 229 | 9:00
| Shyampur | 229 | 1:00 | 220 | 11:00 | Ashuganj (S) | 236 | 2:00 | 233 | 9:00
| Aminbazar | 231 | 1:00 | 224 | 2:00 | Kaliakoir | 232 | 1:00 | 210 | 11:00
| Tongi | 230 | 1:00 | 221 | 11:00 | GPH | 228 | 1:00 | 220 | 9:00
| Comilla (N) | 231 | 18:30 | 226 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 131 | 9:00 | Madanhat | 138 | 0.83333 | 131 | 0.41667
| Munsiganj | 138 | 21:00 | 130 | 9:00 | Hathazari | 136 | 0.8125 | 130 | 0.45833
| Sonargaon | 134 | 19:30 | 128 | 1:00 | Khulshi | 135 | 0.83333 | 128 | 0.375
| Shyampur | 137 | 1:00 | 133 | 11:00 | Halishahar | 137 | 0.875 | 128 | 0.375
| Bhulta | 128 | 18:30 | 124 | 10:00 | Baraulia | 134 | 0.83333 | 129 | 0.375
| Madanganj | 135 | 9:00 | 129 | 11:00 | Sikalbaha | 138 | 0.83333 | 130 | 0.33333
| Shitalakhya | 137 | 21:00 | 130 | 9:00 | Dohazari | 133 | 0.83333 | 126 | 0.375
| Rahim steal | 134 | 1:00 | 131 | 11:00 | Cox'sbazar | 121 | 0.20833 | 118 | 0.041667
| Matuail | 134 | 1:00 | 131 | 9:00 | Chandraghona | 136 | 0.8125 | 131 | 0.375
| Ghorasal | 138 | 1:00 | 136 | 15:00 | Kaptai | 143 | 0.75 | 132 | 0.58333
| Narsinghdi | 130 | 6:00 | 124 | 22:00 | A. Khaer Stl. | 134 | 0.8125 | 130 | 0.29167
| Haripur (SBU) | 134 | 1:00 | 132 | 9:00 | Bakulia | 137 | 0.875 | 129 | 0.45833
| Sreenagar | 132 | 21:00 | 126 | 11:00 | Julda | 138 | 0.79167 | 130 | 0.375
| Ullon | 134 | 1:00 | 130 | 10:00 | TK Chemical | 137 | 0.875 | 131 | 0.70833
| Hasnabad | 135 | 1:00 | 130 | 10:00 | Modern Steel | 136 | 0.8125 | 131 | 0.375
| Magbazar | 135 | 3:00 | 130 | 21:00 | Shahmirpur | 138 | 0.83333 | 129 | 0.375
| Maniknagar | 135 | 1:00 | 132 | 11:00 | Khagrachhari | 134 | 0.041667 | 130 | 0.375
| Bangabhaban | 135 | 1:00 | 132 | 11:00 | Matarbari | 126 | 0.77083 | 120 | 0.041667
| Motijheel | 135 | 1:00 | 132 | 11:00 | Baroiar Hat | 135 | 0.041667 | 128 | 0.29167
| Narinda | 135 | 1:00 | 132 | 11:00 | Rangamati | 135 | 20:00 | 131 | 10:00
| Kazla | 135 | 1:00 | 132 | 11:00 | Agrabad | 136 | 21:00 | 129 | 9:00
| Dhanmondi | 135 | 1:00 | 131 | 10:00 | Goalpara S/S | 138 | 18:00 | 123 | 0.083333
| Lalbag | 134 | 3:00 | 129 | 11:00 | Khulna Central S/S | 137 | 18:00 | 128 | 0.54167
| Madartek | 134 | 1:00 | 130 | 13:00 | Noapara | 136 | 18:00 | 119 | 0.083333
| Dhaka University | 135 | 5:00 | 131 | 12:00 | Jessore | 131 | 18:00 | 122 | 0.041667
| Aftabnagar | 134 | 1:00 | 131 | 10:00 | Benapol | 132 | 0.75 | 116 | 0.041667
| Fatullah | 138 | 4:00 | 133 | 10:00 | Jhenida | 130 | 18:00 | 118 | 0.79167
| Nawabganj | 131 | 4:00 | 126 | 16:00 | Bottail | 133 | 0.75 | 124 | 0.041667
| Keraniganj | 132 | 1:00 | 127 | 13:00 | G.K Project | 140 | 0.75 | 134 | 0.041667
| Mirpur | 134 | 20:00 | 130 | 7:00 | Faridpur | 136 | 0.75 | 129 | 0.875
| Kalyanpur | 135 | 1:00 | 129 | 11:00 | Rajbari | 137 | 0.75 | 128 | 0.875
| Gulshan | 134 | 3:00 | 130 | 10:00 | Madaripur | 141 | 0.75 | 132 | 0.875
| Uttara | 133 | 1:00 | 126 | 11:00 | Shariyatpur S/S | 140 | 18:00 | 130 | 0.875
| Uttara New | 134 | 1:00 | 127 | 11:00 | Gopalganj | 143 | 0.75 | 134 | 0.875
| Kamrangirchar | 135 | 2:00 | 129 | 11:00 | Bagerhat | 135 | 15:00 | 115 | 0.083333
| Savar | 136 | 1:00 | 128 | 9:00 | Mongla | 135 | 17:00 | 116 | 0.083333
| Bhasantec | 137 | 1:00 | 132 | 11:00 | Satkhira | 136 | 18:00 | 121 | 19:00
| Agargaon | 137 | 1:00 | 133 | 11:00 | Gallamari | 139 | 0.75 | 122 | 2:00
| Satmosjid | 137 | 1:00 | 132 | 13:00 | Magura | 129 | 17:00 | 111 | 0.8125
| Tongi | 135 | 19:30 | 129 | 1:00 | Narail | 127 | 0.75 | 110 | 0.79167
| Kabirpur | 135 | 5.00 | 130 | 22:00 | Chuadanga | 132 | 18:00 | 118 | 0.041667
| Basundhara | 133 | 18:30 | 125 | 11:00 | Borguna | 137 | 18:00 | 129 | 0.77083
| Manikganj | 139 | 8:00 | 134 | 22:00 | Barisal(N) | 140 | 18:00 | 132 | 1:00
| Joydevpur | 138 | 18:30 | 130 | 13:00 | Barisal (S) | 139 | 0.75 | 130 | 0.95833
| New Tongi | 134 | 1:00 | 126 | 12:00 | Patuakhali(S) | 135 | 0.33333 | 127 | 0.083333
| Kodda | 135 | 20:00 | 123 | 9:00 | Bhandaria | 135 | 0.75 | 125 | 0.041667
| Dhamrai | 133 | 1:00 | 130 | 18:00 | Ishurdi | 137 | 18:30 | 130 | 1:00
| Rajendrapur | 138 | 19:00 | 129 | 11:00 | Ruppur Paromanobik | 136 | 18:00 | 130 | 19:30
| Valuka | 123 | 18:30 | 110 | 24:00 | Natore | 135 | 18:00 | 129 | 19:30
| Tangail | 133 | 18:30 | 125 | 19:00 | Bogra | 134 | 18:30 | 125 | 13:00
| Mymensing | 126 | 18:30 | 114 | 24:00 | Noagaon | 132 | 18:30 | 121 | 21:00
| Kishorganj | 128 | 18:30 | 118 | 21:00 | Rajshahi | 134 | 18:00 | 127 | 13:00
| Netrokona | 123 | 16:00 | 110 | 22:00 | Rajshahi New | 136 | 18:30 | 128 | 13:00
| Jamalpur | 134 | 18:30 | 121 | 22:00 | C.Nawabganj | 133 | 18:30 | 125 | 13:00
| Sherpur | 133 | 18:30 | 122 | 23:00 | Amnura | 132 | 18:00 | 124 | 5:00
| Srimongal | 137 | 5:00 | 133 | 22:00 | Pabna | 134 | 18:00 | 128 | 19:00
| Shahjibazar | 136 | 8:00 | 131 | 23:00 | Shahjadpur | 137 | 18:00 | 133 | 21:00
| Fenchuganj | 137 | 10:00 | 133 | 23:00 | Serajganj | 132 | 18:00 | 126 | 20:00
| Khulawara | 135 | 5:00 | 134 | 1:00 | Niyamatpur | 130 | 18:30 | 115 | 19:30
| Sylhet | 134 | 5:00 | 132 | 19:00 | Joypurhat | 131 | 18:30 | 119 | 21:00
| Chatak | 135 | 10:00 | 129 | 20:00 | Sherpur(Bogura) | 134 | 18:00 | 127 | 13:00
| Sunamganj | 133 | 8:00 | 127 | 19:30 | Mohastangor | 133 | 18:30 | 123 | 21:00
| Biani Bazar | 134 | 6:00 | 129 | 19:00 | Bangura | 136 | 17:00 | 131 | 9:00
| Comilla(s) | 129 | 7:00 | 124 | 20:00 | Rangpur | 130 | 17:00 | 117 | 21:00
| Comilla(n) | 139 | 21:00 | 134 | 11:00 | Lalmonirhat | 130 | 17:00 | 118 | 21:00
| Chandpur | 138 | 18:30 | 131 | 8:00 | Saidpur | 130 | 17:00 | 116 | 21:00
| Feni | 135 | 21:00 | 128 | 15:00 | Purbasadipur | 128 | 17:00 | 111 | 21:00
| Chowmuhani | 132 | 19:00 | 127 | 11:00 | Thakurgaon | 128 | 18:00 | 112 | 21:00
| Ashuganj | 137 | 18:30 | 133 | 0:00 | Palashbari | 131 | 18:00 | 118 | 1:00
| Daudkandi | 132 | 6:00 | 128 | 11:00 | Barapukuria | 135 | 18:00 | 126 | 21:00
| B.Baria | 132 | 18:00 | 127 | 22:00 | Panchagar | 128 | 13:00 | 112 | 19:30
| Ramganj | 134 | 21:00 | 127 | 8:00 | Joldhaka | 130 | 0.625 | 111 | 0.875
| Chaddagram | 137 | 21:00 | 130 | 8:00 | Kurigram | 131 | 0.75 | 116 | 0.875
| PHP | 135 | 1:00 | 127 | 15:00 | Mithapukur | 132 | 0.66667 | 121 | 0.875
| Kochua | 136 | 19:30 | 130 | 11:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-08-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 380 | 8604 | 3799 | 12403 |  |  |  | QF-LDC-11
0:30 | 435 | 8579 | 3641.5 | 12220.5 | Date: | 2021-08-15
1:00 | 490 | 8554 | 3484 | 12038
1:30 | 450 | 8390 | 3457 | 11847
2:00 | 410 | 8226 | 3430 | 11656
2:30 | 407 | 8104.5 | 3360.5 | 11465 | [5 empty] | Gen. at Eve. Peak | 12487 | 12487 MW (21:00 )
3:00 | 404 | 7983 | 3291 | 11274 | [6 empty] | 21:00
3:30 | 385 | 7929.5 | 3270.5 | 11200 | [5 empty] | Gen. at Day Peak | 9887 | 9887 MW (12:00 )
4:00 | 366 | 7876 | 3250 | 11126 | [6 empty] | 12:00
4:30 | 389 | 7775.5 | 3170 | 10945.5 | [5 empty] | Highest Generation | 12584
5:00 | 412 | 7675 | 3090 | 10765 | [6 empty] | 23:00
5:30 | 315 | 7341.5 | 2981.5 | 10323
6:00 | 218 | 7008 | 2873 | 9881
6:30 | 199 | 6762 | 2857 | 9619
7:00 | 180 | 6516 | 2841 | 9357
7:30 | 190 | 6454 | 2815.5 | 9269.5
8:00 | 200 | 6392 | 2790 | 9182
8:30 | 168 | 6406 | 2806 | 9212
9:00 | 136 | 6420 | 2822 | 9242
9:30 | 168 | 6511.5 | 2800 | 9311.5
10:00 | 200 | 6603 | 2778 | 9381
10:30 | 235 | 6736 | 2757.5 | 9493.5
11:00 | 270 | 6869 | 2737 | 9606
11:30 | 290 | 6968.5 | 2778 | 9746.5
12:00 | 310 | 7068 | 2819 | 9887
12:30 | 322 | 7196 | 2883 | 10079
13:00 | 334 | 7324 | 2947 | 10271
13:30 | 297 | 7324 | 2990.5 | 10314.5
14:00 | 260 | 7324 | 3034 | 10358
14:30 | 232 | 7291.5 | 3046 | 10337.5
15:00 | 204 | 7259 | 3058 | 10317
15:30 | 160 | 7245 | 3018 | 10263
16:00 | 116 | 7231 | 2978 | 10209
16:30 | 60 | 6990.5 | 2930.5 | 9921
17:00 | 4 | 6750 | 2883 | 9633
17:30 | 34 | 6668.5 | 2789 | 9457.5
18:00 | 64 | 6587 | 2695 | 9282
18:30 | 280 | 7280.5 | 3002.5 | 10283
19:00 | 496 | 7974 | 3310 | 11284
19:30 | 480 | 8547 | 3716 | 12263
20:00 | 508 | 8508 | 3780 | 12288 |  |  |  | Executive Engineer
20:30 | 519 | 8591.5 | 3796 | 12387.5 |  |  |  | Network Operation Division
21:00 | 530 | 8675 | 3812 | 12487
21:30 | 495 | 8690.5 | 3825 | 12515.5
22:00 | 460 | 8706 | 3838 | 12544 |  |  |  |  | Page 6 of 7
22:30 | 444 | 8729.5 | 3834.5 | 12564
23:00 | 428 | 8753 | 3831 | 12584
23:30 | 404 | 8678.5 | 3815 | 12493.5
24:00 | 380 | 8604 | 3799 | 12403
12487 MW (21:00 )
9887 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-08-15 |  | Energy | 261746322
[11 empty] | 2021-08-15 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4793 | 694 | 2031 | 3623 | 702 | 120 | 336 | 0 | 140 | 0
0:30 | 4726.5 | 697.5 | 1948.5 | 3602 | 693.5 | 120 | 310.5 | 0 | 140 | 0 | Date: | 2021-08-15
1:00 | 4660 | 701 | 1866 | 3581 | 685 | 120 | 285 | 0 | 140 | 0
1:30 | 4665 | 700.5 | 1885 | 3461.5 | 680 | 120 | 197 | 0 | 138 | 0 | [7 empty] | Total Energy | 261.7463 | Total Energy Gen 261.746 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.746 MKWHr
2:00 | 4670 | 700 | 1904 | 3342 | 675 | 120 | 109 | 0 | 136 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4664.5 | 700 | 1909.5 | 3186.5 | 675 | 120.5 | 74 | 0 | 135 | 0 | [7 empty] | Energy Requirement | 261.7463
3:00 | 4659 | 700 | 1915 | 3031 | 675 | 121 | 39 | 0 | 134 | 0
3:30 | 4668.5 | 699.5 | 1921 | 2963.5 | 675 | 121 | 19.5 | 0 | 132 | 0 | [6 empty] | Shortage
4:00 | 4678 | 699 | 1927 | 2896 | 675 | 121 | 0 | 0 | 130 | 0
4:30 | 4674 | 699 | 1904.5 | 2749.5 | 670.5 | 121 | 0 | 0 | 127 | 0
5:00 | 4670 | 699 | 1882 | 2603 | 666 | 121 | 0 | 0 | 124 | 0
5:30 | 4634.5 | 699 | 1883 | 2229.5 | 635.5 | 121 | 0 | 0 | 120 | 0.5
6:00 | 4599 | 699 | 1884 | 1856 | 605 | 121 | 0 | 0 | 116 | 1
6:30 | 4609 | 699.5 | 1876.5 | 1602.5 | 595 | 120.5 | 0 | 0 | 110 | 6 |  |  |  |  | Coal
7:00 | 4619 | 700 | 1869 | 1349 | 585 | 120 | 0 | 0 | 104 | 11
7:30 | 4623.5 | 700 | 1859.5 | 1278.5 | 570 | 119 | 0 | 0 | 103 | 16 |  |  |  | Oil |  |  |  | ,
8:00 | 4628 | 700 | 1850 | 1208 | 555 | 118 | 0 | 0 | 102 | 21
8:30 | 4677.5 | 699.5 | 1871 | 1157 | 554 | 118 | 0 | 0 | 103 | 32
9:00 | 4727 | 699 | 1892 | 1106 | 553 | 118 | 0 | 0 | 104 | 43
9:30 | 4736.5 | 699 | 1920 | 1120.5 | 553 | 119 | 0 | 0 | 106 | 57.5
10:00 | 4746 | 699 | 1948 | 1135 | 553 | 120 | 0 | 0 | 108 | 72
10:30 | 4771.5 | 699.5 | 1934.5 | 1234 | 554.5 | 120 | 0 | 0 | 110 | 69.5
11:00 | 4797 | 700 | 1921 | 1333 | 556 | 120 | 0 | 0 | 112 | 67
11:30 | 4824.5 | 700 | 1910 | 1455.5 | 555.5 | 120 | 0 | 0 | 112 | 69
12:00 | 4852 | 700 | 1899 | 1578 | 555 | 120 | 0 | 0 | 112 | 71
12:30 | 4878 | 700 | 1938.5 | 1710.5 | 554 | 120 | 0 | 0 | 118 | 60
13:00 | 4904 | 700 | 1978 | 1843 | 553 | 120 | 0 | 0 | 124 | 49
13:30 | 4904 | 700 | 1978 | 1843 | 553 | 120 | 0 | 0 | 124 | 49
14:00 | 4904 | 700 | 1978 | 1843 | 553 | 120 | 0 | 0 | 124 | 49
14:30 | 4751 | 693 | 1934.5 | 2042.5 | 570 | 122 | 0 | 0 | 124 | 57
15:00 | 4598 | 686 | 1891 | 2242 | 587 | 124 | 0 | 0 | 124 | 65
15:30 | 4603 | 686 | 1879 | 2223 | 581.5 | 124.5 | 0 | 0 | 120 | 46
16:00 | 4608 | 686 | 1867 | 2204 | 576 | 125 | 0 | 0 | 116 | 27
16:30 | 4613 | 686.5 | 1791 | 2003.5 | 564.5 | 124.5 | 0 | 0 | 114 | 24
17:00 | 4618 | 687 | 1715 | 1803 | 553 | 124 | 0 | 0 | 112 | 21
17:30 | 4573 | 686.5 | 1685.5 | 1724.5 | 539 | 123 | 2 | 0 | 112 | 12
18:00 | 4528 | 686 | 1656 | 1646 | 525 | 122 | 4 | 0 | 112 | 3
18:30 | 4667 | 686 | 1808.5 | 2158.5 | 535 | 121 | 181.5 | 0 | 124 | 1.5
19:00 | 4806 | 686 | 1961 | 2671 | 545 | 120 | 359 | 0 | 136 | 0
19:30 | 4812 | 686 | 1991 | 3509 | 635 | 119 | 377 | 0 | 134 | 0
20:00 | 4808 | 686 | 1944 | 3518 | 646 | 119 | 427 | 0 | 140 | 0
20:30 | 4835.5 | 686 | 1949 | 3560.5 | 665.5 | 119 | 432 | 0 | 140 | 0
21:00 | 4863 | 686 | 1954 | 3603 | 685 | 119 | 437 | 0 | 140 | 0
21:30 | 4874 | 686 | 1971.5 | 3620.5 | 683.5 | 120 | 419 | 0 | 141 | 0
22:00 | 4885 | 686 | 1989 | 3638 | 682 | 121 | 401 | 0 | 142 | 0
22:30 | 4882.5 | 690 | 2015.5 | 3630.5 | 686.5 | 121 | 396 | 0 | 142 | 0
23:00 | 4880 | 694 | 2042 | 3623 | 691 | 121 | 391 | 0 | 142 | 0
23:30 | 4836.5 | 694 | 2036.5 | 3623 | 696.5 | 120.5 | 363.5 | 0 | 141 | 0 | Max Temp. in Dhaka |  | 33.8° C
24:00 | 4793 | 694 | 2031 | 3623 | 702 | 120 | 336 | 0 | 140 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 261.746 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 261.746 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-08-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 60 | 60 | 61 | 61 | 61 | 61 | 60 | 58 | 58 | 60 | 60 | 60 | 60 | 60 | 64 | 65 | 64 | 62 |  | 60 | 59 | 59 | 59 | 61 | 61 | 60 | 1396669
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1464000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [18 empty] | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 78112
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 3 | 8 | 11 | 17 | 11 | 20 | 19 | 16 | 4 | 3 | 0 | [8 empty] | 113535
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 68 | 17 | [17 empty] | 99 | 102 | 102 | 102 | 85 | 85 | 85 | 618370
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 90 | 89 | 51 | 51 | 34 | 66 | 88 | 88 | 88 | 88 | 90 | 90 | 68 | 51 |  | 71 | 90 | 90 | 90 | 90 | 90 | 90 | 2049090
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 0
14 | Titas 50 MW Peaking PP | [26 empty] | 12088
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 330 | 328 | 330 | 330 | 333 | 280 | 280 | 280 | 280 | 300 | 324 | 324 | 325 | 280 | 280 | 280 | 280 | 250 |  | 326 | 328 | 330 | 330 | 329 | 329 | 332 | 7452840
18 | Kodda 300 MW PP Unit-2 (Summit) | 277 | 278 | 95 | 45 | 15 | [7 empty] | 8 | 17 | 60 | 60 | 30 | 30 |  | 60 | 120 | 130 | 173 | 228 | 245 | 245 | 2207999
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 200727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2740500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7389536
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 |  | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 1913438
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 22 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 512640
33 | Ashuganj 225 MW CCPP | 181 | 185 | 181 | 186 | 182 | 185 | 187 | 182 | 203 | 182 | 184 | 182 | 184 | 183 | 183 | 182 | 195 | 191 |  | 210 | 213 | 215 | 215 | 212 | 212 | 213 | 4676000
34 | Ashuganj 450 MW CCPP(South) | 265 | 270 | 265 | 270 | 265 | 270 | 275 | 265 | 300 | 300 | 295 | 300 | 300 | 300 | 270 | 270 | 285 | 285 |  | 300 | 270 | 270 | 300 | 315 | 320 | 285 | 6948000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 265 | 260 | 260 | 265 | 275 | 310 | 275 | 355 | 320 | 325 | 310 | 260 | 260 | 280 | 280 |  | 290 | 260 | 260 | 260 | 295 | 295 | 260 | 7046500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 55 | 55 | 55 | 54 | 54 | 53 | 55 | 55 |  | 55 | 55 | 20 | 20 | 35 | 56 | 56 | 1283520
36 | Chandpur 150 MW CCPP | 137 | 137 | 138 | 137 | 137 | 137 | 137 | 137 | 137 | 137 | 136 | 136 | 137 | 137 | 137 | 137 | 137 | 137 |  | 136 | 136 | 135 | 134 | 138 | 137 | 136 | 3281410
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 281 | 281 | 281 | 281 | 282 | 281 | 281 | 281 | 278 | 280 | 278 | 276 | 276 | 276 | 273 | 273 | 275 | 257 |  | 257 | 279 | 279 | 278 | 279 | 278 | 279 | 6768000
40 | Meghnaghat 450 MW CCPP(MPL) | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240 |  | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 5622750
41 | Haripur 360MW CCPP(HPL) | 279 | 283 | 293 | 298 | 302 | 317 | 321 | 322 | 322 | 348 | 347 | 341 | 337 | 322 | 321 | 322 | 323 | 302 |  | 343 | 336 | 346 | 347 | 346 | 346 | 346 | 7712000
42 | RPCL 210MW CCPP | 154 | 152 | 156 | 154 | 157 | 155 | 155 | 154 | 154 | 153 | 153 | 152 | 152 | 153 | 153 | 153 | 152 | 152 |  | 152 | 153 | 154 | 157 | 154 | 154 | 155 | 3612880
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 6 | 12 | 17 | 23 | 24 | 3 | 27 | 21 | 11 | 9 | 2 | [8 empty] | 174020
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 44 | 44 |  | 44 | 43 | 43 | 43 | 43 | 43 | 43 | 1034000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 990600
46 | Shajibazar 330 MW CCPP | 270 | 270 | 270 | 270 | 270 | 271 | 270 | 271 | 268 | 269 | 269 | 266 | 268 | 271 | 270 | 271 | 270 | 269 |  | 269 | 271 | 271 | 271 | 270 | 270 | 270 | 6173000
47 | Shahjibazar GTPP Unit- 8 & 9 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 64 | 62 | 63 | 61 | 60 | 63 | 63 | 63 | 63 | 40 | 40 |  | 50 | 61 | 61 | 59 | 56 | 56 | 56 | 1396992
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 84 | 84 | 84 | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 84 | 84 | 82 | 82 | 81 | 20 | 20 |  | 84 | 84 | 83 | 84 | 84 | 84 | 84 | 1856640
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 225 | 225 | 225 | 225 | 225 | 226 | 226 | 225 | 225 | 225 | 185 | 196 | 211 | 211 | 211 | 218 | 190 | 190 |  | 225 | 225 | 176 | 190 | 191 | 191 | 190 | 5024160
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 403000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 248940
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 5 | 228096
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 14 | 14 | 14 | 14 | 47 | 50 | 50 | 50 | 53 | 53 | 53 | 14 | 14 |  | 49 | 53 | 53 | 53 | 52 | 53 | 53 | 997800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 571824
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 290 | 290 | 300 | 290 | 290 | 290 | 290 | 295 | 295 | 300 | 290 | 295 | 290 | 300 | 290 | 290 | 295 |  | 300 | 285 | 275 | 290 | 280 | 310 | 300 | 7207500
| Bibiyana South 400 MW | 330 | 330 | 330 | 330 | 330 | 300 | 300 | 300 | 300 | 350 | 370 | 390 | 400 | 357 | 350 | 350 | 350 | 350 |  | 395 | 397 | 400 | 400 | 395 | 395 | 400 | 8438900
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 35 | 17 | 17 | 17 | 17 | 17 | 25 | 35 | 55 | 55 | 55 | 17 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 1002601
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 25 | 22 | 22 | 24 | 24 | 23 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 589680
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 | 19 | 19 | 19 | 19 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 476688
61 | Narshingdi 22 MW PP (Doreen) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 20 |  | 20 | 20 | 20 | 21 | 21 | 21 | 21 | 439920
62 | Tangail 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 491652
63 | Impoprt (Tripura) | 140 | 136 | 134 | 130 | 124 | 116 | 104 | 102 | 104 | 108 | 112 | 112 | 124 | 124 | 124 | 116 | 112 | 112 |  | 136 | 134 | 140 | 140 | 142 | 142 | 140 | 2979840
64 | Malancha, Ctg. EPZ (United) | 33 | 35 | 35 | 38 | 38 | 38 | 23 | 38 | 39 | 37 | 30 | 31 | 28 | 27 | 37 | 37 | 37 | 37 |  | 37 | 37 | 37 | 37 | 37 | 40 | 38 | 909120
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 509040
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 254340
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 10 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 566400
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 12 | 12 | 20 | 20 | 20 | 20 | 18 | 20 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 504840
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 15 | 22 | 20 | 24 | 24 | 24 | 24 | 25 | 25 | 25 |  | 14 | 14 | 26 | 28 | 29 | 29 | 29 | 567000
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614700
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 17 | 17 | 25 | 33 | 33 | 33 | 33 | 797600
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | [18 empty] | 45 | 70 | 70 | 100 | 114 | 114 | 114 | 695400
| Chowmuhani 113 MW | 106 | 105 | 106 | 105 | 100 | 65 | 17 | 17 | 17 | 34 | 65 | 81 | 104 | 103 | 102 | 99 | 100 | 70 |  | 97 | 113 | 106 | 104 | 106 | 110 | 105 | 2133600
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 17 | 17 | 17 | 17 | 17 | 17 | 26 | 54 | 126 | 126 | 162 | 90 | 72 |  | 122 | 162 | 162 | 114 | 90 | 90 | 90 | 2465280
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 16 | 8 | 8 | 8 | [15 empty] | 20 | 30 | 40 | 25 | 8 | 8 | 8 | 190080
79 | Kodda 150MW PP | 64 | 16 | 16 | [14 empty] | 4 |  | 82 | 82 | 82 | 100 | 100 | 100 | 100 | 646560
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 5 | 5 | 6 | 6 | 6 | 6 |  | 6 | 6 | 6 | 6 | 7 | 7 | 7 | 169920
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 25 | 8 | [9 empty] | 1 | 8 | 8 | 8 | 8 |  | 16 | 25 | 47 | 52 | 52 | 52 | 52 | 479669
| Gazipur 100 MW PP | 105 | 105 | 105 | 70 | 50 | 50 | 17 | [6 empty] | 6 | 17 | 17 | 17 | 17 |  | 58 | 90 | 90 | 90 | 90 | 70 | 90 | 1194000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 0 | 2 | 3 | 6 | 3 | 4 | 5 | 1 | 2 | 2 | 1 | 0 | [8 empty] | 29041
| Jodiac Power | [26 empty] | 0
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 68 | 68 | 97 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 68 |  | 106 | 110 | 110 | 110 | 110 | 110 | 110 | 2639552
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 12 | 12 | 22 | 25 | 24 | [14 empty] | 13 | 50 | 47 | 60 | 25 | 12 | 12 | 283706
86 | Meghnaghat CCPP ( Summit) | 250 | 275 | 280 | 265 | 260 | 275 | 275 | 250 | 290 | 250 | 275 | 270 | 275 | 255 | 275 | 265 | 280 | 280 |  | 275 | 260 | 250 | 240 | 290 | 295 | 275 | 6462080
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 90 | 73 | 17 | 17 | 17 | 17 | 17 | 33 | 53 | 53 | 53 | 53 | 19 | 17 |  | 42 | 90 | 87 | 90 | 90 | 90 | 90 | 1397760
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 10 | 10 | 10 | 10 | [15 empty] | 36 | 50 | 50 | 100 | 100 | 100 | 100 | 489600
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 25 | 25 | 25 | 35 | 35 | 35 | 35 | 15 | 15 |  | 28 | 35 | 35 | 35 | 35 | 35 | 35 | 776268
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 32 | 16 | 16 | 7 | 7 | 7 | 7 | 7 | 7 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 64 | 82 | 82 | 94 | 102 | 102 | 102 | 974160
95 | Patenga 50MW PP (Baraka) | 19 | [18 empty] | 13 | 19 | 19 | 19 | 19 | 19 | 19 | 135360
96 | Chattogram 108 MW PP (ECPV) | 96 | 96 | 93 | 96 | 93 | 89 | 89 | 89 | 89 | 72 | 77 | 82 | 87 | 85 | 92 | 94 | 94 | 95 |  | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 2188800
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 55 | 55 | 55 | 40 | 30 | 15 | 15 | 20 | 35 | 40 | 40 | 40 | 40 | 50 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1115059
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 17 | 17 |  | 35 | 55 | 55 | 55 | 55 | 55 | 55 | 934260
101 | Kushiara 163 MW CCPP (KP) | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 163 | 163 | 163 | 163 | 130 | 130 | 130 | 130 | 130 |  | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 3466309
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | [9 empty] | 8700
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1311120
104 | Keranigonj 300 MW PP (APR)
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 191 | 191 | 191 | 190 | 120 | 32 | 32 | 32 | 8 | 8 | 19 | 35 | 36 | 60 | 60 | 60 | 40 | 40 |  | 120 | 185 | 187 | 178 | 178 | 178 | 178 | 2498400
112 | Aurahati 100MW PP (Aggreko)
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 120 | 88 | 88 | 88 | 73 | 71 | 60 | 19 | 17 | 19 | 49 | 49 | 49 | 49 | 49 | 49 | 49 |  | 66 | 136 | 130 | 149 | 149 | 141 | 134 | 1942272
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 20 | 20 | 35 | 90 | 90 | 90 | 90 | 100 | 40 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1900800
116 | Chandpur 200MW (Desh energy) | 199 | 200 | 199 | 199 | 199 | 68 | 17 | 17 | 17 | 17 | 17 | 28 | 52 | 80 | 100 | 100 | 68 | 68 |  | 121 | 200 | 200 | 200 | 199 | 199 | 199 | 2925120
117 | Ashuganj 150MW PP (Midland) | 135 | 135 | 133 | 128 | 132 | 130 | 50 | 50 | 20 | 40 | 70 | 80 | 100 | 100 | 100 | 100 | 108 | 122 |  | 120 | 120 | 115 | 118 | 118 | 117 | 118 | 2525807
118 | Bibiyana-III 400 MW CCPP | 365 | 365 | 365 | 366 | 364 | 364 | 369 | 366 | 400 | 402 | 401 | 402 | 404 | 402 | 303 | 305 | 316 | 314 |  | 376 | 365 | 366 | 367 | 332 | 336 | 305 | 8667000
| Jamalpur 115 MW PP (United) | 102 | 102 | 102 | 102 | 102 | 111 | 111 | 110 | 110 | 110 | 109 | 109 | 109 | 109 | 109 | 100 | 85 | 85 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2529600
| Anwara 300 MW PP (United) | 107 | 107 | 107 | 107 | 107 | 72 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 66 | 66 | 68 | 71 | 34 | 35 | 35 | 1139127
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 20 | 20 | 20 | 20 | 50 | 100 | 100 | 100 | 100 | 40 | 40 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1893120
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 100 | 116 | 116 | 116 | 116 | 116 | 96 | 116 | 116 |  | 116 | 116 | 116 | 96 | 115 | 115 | 90 | 2719855
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 441720
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 5 | 8 | 16 | 33 | 19 | 26 | 17 | 18 | 19 | 8 | 7 | 1 | [8 empty] | 190400
120 | Eastern Zone Total | 8554 | 8226 | 7983 | 7876 | 7675 | 7008 | 6516 | 6392 | 6420 | 6603 | 6869 | 7068 | 7324 | 7324 | 7259 | 7231 | 6750 | 6587 |  | 7974 | 8547 | 8508 | 8675 | 8706 | 8753 | 8604 | 183109002
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [26 empty] | 1440
| Khulna 225 MW CCPP | 40 | [20 empty] | 50 | 50 | 40 | 40 |  | 205440
129 | Rupsha 105 MW PP (Orion rupsha) | 70 | 70 | 70 | 70 | 70 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 33 | 60 | 86 | 53 | 89 | 53 |  | 70 | 105 | 105 | 105 | 105 | 105 | 105 | 1504320
130
131
132 | United Payra Power Ltd. | 17 | 17 | 17 | [16 empty] | 15 | 54 | 54 | 54 | 54 | 54 | 54 | 349200
133 | Bhola Nutan Biddut BD LTD (GAS) | 216 | 219 | 219 | 219 | 218 | 219 | 219 | 218 | 217 | 216 | 217 | 215 | 218 | 217 | 217 | 217 | 170 | 130 |  | 217 | 217 | 217 | 215 | 220 | 220 | 220 | 5091573
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 12 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 278693
| Bhola 225 MW CCPP | 87 | 88 | 86 | 87 | 87 | 88 | 88 | 86 | 85 | 86 | 86 | 86 | 90 | 87 | 88 | 89 | 89 | 87 |  | 89 | 89 | 88 | 77 | 87 | 88 | 88 | 2110507
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 33 | 32 | 28 | 25 | 24 | 23 | 22 | 23 | 23 | 23 | 23 | 25 | 23 | 23 | 20 |  | 34 | 34 | 34 | 34 | 34 | 34 | 34 | 673851
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 14 | 100 | 100 | 100 | 100 | 100 | 100 | 523200
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 701 | 700 | 700 | 699 | 699 | 699 | 700 | 700 | 699 | 699 | 700 | 700 | 700 | 699 | 686 | 686 | 687 | 686 |  | 686 | 686 | 686 | 686 | 686 | 694 | 694 | 16790545
147 | Bheramara 410 MW CCPP | 365 | 370 | 370 | 375 | 375 | 375 | 375 | 375 | 375 | 375 | 350 | 390 | 390 | 390 | 385 | 390 | 395 | 350 |  | 395 | 410 | 410 | 410 | 410 | 405 | 410 | 9401184
148 | Payra 1320 MW | 530 | 520 | 520 | 520 | 510 | 450 | 430 | 400 | 400 | 400 | 400 | 400 | 400 | 410 | 420 | 420 | 400 | 370 |  | 390 | 480 | 490 | 530 | 530 | 540 | 550 | 12023600
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 155 | 155 | 155 | 155 | 156 | 155 | 155 | 155 | 153 | 153 | 156 | 155 | 153 | 153 | 167 | 156 | 153 | 155 |  | 155 | 155 | 156 | 155 | 152 | 151 | 152 | 3781600
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [19 empty] | 50 | 50 | 50 | 43 | 43 | 43 | 43 | 282544
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 2 | 2 | 2 | 3 | 5 | 4 | 1 | 0 | 0 | [8 empty] | 26760
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 155 | 156 | 155 | 155 | 156 | 159 | 165 | 163 | 159 | 157 | 158 | 164 | 166 | 165 | 163 | 163 | 170 | 172 |  | 181 | 184 | 185 | 185 | 184 | 184 | 187 | 4243291
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 178 | 176 | 170 | 170 | 170 | 170 | 170 | 186 | 186 | 186 | 191 | 195 | 199 | 199 | 196 | 193 | 193 | 186 |  | 161 | 178 | 195 | 206 | 213 | 205 | 208 | 4805518
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 388 | 414 | 415 | 410 | 373 | 402 | 400 | 368 | 409 | 368 | 343 | 335 | 400 | 361 | 347 | 336 | 348 | 347 |  | 394 | 402 | 390 | 385 | 412 | 410 | 411 | 9220900
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [26 empty] | 22135
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 497280
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 258156
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [26 empty] | 0
167 | Katakhali 50 MW Peaking PP | [19 empty] | 28 | 29 | 31 | 30 | 30 | 30 | 15 | 145882
168 | Santahar 50 MW Peaking PP | 20 | 20 | [17 empty] | 19 | 19 | 19 | 19 | 10 |  |  | 112130
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 25 |  | 30 | 52 | 52 | 52 | 52 | 52 | 52 | 1193280
170 | Chapainawabganj 100 MW Peaking PP | 93 | 56 | 23 | [16 empty] | 81 | 95 | 93 | 93 | 93 | 93 | 93 | 691936
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 35 | [6 empty] | 7 | 35 | 68 | 70 | 70 | 35 | 35 |  | 55 | 113 | 105 | 113 | 113 | 113 | 113 | 1646615
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 35 | 35 | [15 empty] | 90 | 108 | 113 | 113 | 113 | 113 | 113 | 981216
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 15 | [5 empty] | 35 | 42 | 99 | 107 | 85 | 35 | 35 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 1755763
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 3 |  | 3 | 2 | 1 | 1 | 0 | [8 empty] | 18761
178
178