## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-08-24 | Tuesday
|  |  | Date (day): | 2021-08-24 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13741.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14679 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-08-23 | 2021-08-24 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 70 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 300 | 300 | 310 | 310 |  | 55 | Machine problem
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 389 | 394 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 137 | 195 | 250 | 250 | 110 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 260 | 270 | 270 | 270 | 180 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 270 | 300 | 300 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 40 | 40 |  | 15 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Unit transformer problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 17 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 100 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 329 | 335 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 150 | 150
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 47 | 47 | 47 |  | 33 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 42 | 51 | 52 | 52
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 255 | 280 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 103 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 25 | 70 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 27 | 100 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 135 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 105 | 105
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 90 | 90 | 95 |  | 9 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 35 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5819 | 3202 | 3464 | 3604 | 3831 | 957 | 892
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 100 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 180 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 38 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 117 | 120 | 120 | 120 | 110 |  | Low water level
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 85 | 85 | 102 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 60 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 24 | 5 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 81 | 50 | 95 | 96 |  | 12 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 125 | 125 | 200 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 0 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 102 | 115 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1192 | 1229 | 1427 | 1519 | 370 | 485
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 80 | 70 | 70 | 70 | 64 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 183 | 175 | 215 | 215 |  |  | FGMO
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 260 | 265 | 330 | 360 |  |  | FGMO
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 295 | 330 | 360 |  |  | FGMO
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 5 | 5 | 5 |  | 40 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 5 | 5 | 5 | 5 | 50 |  | Gas shortage
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 133 | 133 | 125 | 130 |  | 20 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 43 | 50 | 50 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 137 | 135 | 140 | 140
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 197 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 16 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 134 | 138 | 163
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 52 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 20 | 20
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 25 | 200 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 99 | 114 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1907 | 2104 | 2133 | 2323 | 565 | 113
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 84 | 102 | 120 | 120 |  | 82 | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 6 | 6 |  | 89 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 164 | 140 | 200 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 106 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 32 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 24 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 430 | 402 | 535.6 | 484 | 0 | 171
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 44 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 42 | 42 | 42 | 42 |  | 48 | GT-4 under S/D
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 155 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 264 | 236 | 270 | 270 | 60 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 53 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 0 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 |  |  | Under maint
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 0 | 84 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 0 | 0 | 0 | 0 |  |  | Under maint
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 367 | 401 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 10 | 10 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 217 | 260 | 350 | 400
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1507 | 1606 | 1807 | 1857 | 60 | 175
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 680 | 679 | 707 | 707
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 4 | 24 | 0 | 25 |  | 29 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 0 | 55 | 0 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 250 | 230 | 250 | 250
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 105 | 105 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1039 | 1193 | 1212 | 1572 | 0 | 78
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 34 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 83 | 88 | 88 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 11 | 11 | 12 | 12 | 83 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 360 | 570 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 214 | 216 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 689 | 936 | 1235 | 1235 | 83 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 37 | 0 | 40 |  | 31 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 31 |  | 19 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 175 | 158 | 200 | 200 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 188 | 160 | 220 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 398 | 392 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 0 | 23 |  | 27 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 19 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 43 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 47 | 94 | 95 | 95
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 50 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1107 | 1291 | 1512 | 1570 | 480 | 77
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 153 | 153 | 155 | 155 | 119 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 100 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 254 | 266 | 276 | 288 | 119 | 190
|  | Total |  |  |  |  | 22031 | 21280 | 11327 | 12491 | 13741.6 | 14679 | 2634 | 2287
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10718.5285 | 11820 | 13003.4194 | 13890.4635
| A. |  | 2021-08-23 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12491 | MW at | 21:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 21:00 | hrs.
| 2 | Minimum Generation : |  |  | 10099 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12491 | MW
| 3 | Day peak Generation : |  |  | 11327 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11820 | MW
| 4 | Evening peak Generation : |  |  | 12491 | MW at | 21:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 279.6205 | MKWHr | By Solar | 0.50619 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 146.6865 | MKWHr |  | By Oil: | 94.4254 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.7864 | MKWHr |  | By Hydro: | 2.8312 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2634 | MW | Dhaka | 4297 | 4297 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2287 | MW | Chittagong | 1267 | 1267 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 4921 | MW | Khulna | 1644 | 1644 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1102.813 | MMCFD |  |  | Rajshahi | 1234 | 1234 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146846288.486 | ii) Oil : | Taka | 727975834.72 | Comilla | 1133 | 1133 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 73192297 | Total | Taka | 948014420.206 | Mymensingh | 828 | 828 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 4.9605 | MKWHr. | Sylhet | 313 | 313 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -500 | MW (E to W) at | 21:00 | hrs | Barisal | 380 | 380 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -504 | MW at | 20:00 | hrs | Rangpur | 724 | 724 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.0° C |  |  | Total | 11820 | 11820 |  | 0
| B. |  | 2021-08-24 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13000 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14679 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1679 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 291.0148 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9254 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.4058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 679 | MW at | 21:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9789 | MKWHr. | iii) Maximum HVDC Flow : |  | 681 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 93.34 |  | (b) Today: | 93.35 |  | (c) Rule Curve: |  | 96.04
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-08-23
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 393 | 181 |  | 0 | 250 | 260 | 0 | 0 | 40 | 332 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 51 | 0 | 64 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 78 | 92 | 93 | 50 | 20 | 37 | 0 | 0 | 80 | 260 | 290 | 195 | 8 | 135 | 23 | 40 | 0 | 35 | 0 | 0 | 52 | 11 | 11 | 33 | 21 | 130 | 99 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 163 | 273 | 0 | 84 | 0 | 212 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 275 | 0 | 0 | 166 | 0 | 149 | 0 | 100 | 200 | 122 | 402 | 115 | 105 | 105 | 0 | 107 | 0 | 110 | 114 | 107 | 100 | 351 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 680 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 43 | 25 | 93 | 0 | 0 | 6 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 40 | 204 | 0 | 388 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 218 | 0 | 35 | 0 |  | 8763 | 3581 | 12344 | 4731 | 680 | 1803 | 3783 | 685 | 124 | 408 | 130 | 0 | 0 | 93.34
2:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 393 | 188 |  | 0 | 250 | 250 | 0 | 0 | 40 | 332 | 0 | 0 | 0 | 102 | 115 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 64 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 92 | 96 | 25 | 20 | 37 | 0 | 0 | 80 | 260 | 290 | 190 | 8 | 136 | 23 | 40 | 0 | 35 | 0 | 0 | 52 | 11 | 11 | 33 | 21 | 130 | 100 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 163 | 272 | 0 | 84 | 0 | 205 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 278 | 0 | 0 | 166 | 0 | 149 | 0 | 100 | 200 | 120 | 400 | 115 | 105 | 105 | 0 | 107 | 0 | 104 | 114 | 107 | 100 | 350 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 681 | 0 | 315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 40 | 203 | 0 | 394 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 218 | 0 | 35 | 0 |  | 8582 | 3480 | 12062 | 4716 | 681 | 1826 | 3695 | 695 | 124 | 195 | 130 | 0 | 0 | 93.34
3:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 393 | 195 |  | 0 | 250 | 245 | 0 | 0 | 40 | 332 | 0 | 0 | 0 | 64 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 64 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 96 | 24 | 20 | 38 | 0 | 0 | 80 | 260 | 290 | 207 | 8 | 136 | 23 | 25 | 0 | 35 | 0 | 0 | 52 | 11 | 11 | 33 | 21 | 124 | 100 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 163 | 272 | 0 | 84 | 0 | 205 | 18 | 0 | 10 | 280 | 24 | 8 | 0 | 280 | 0 | 0 | 157 | 0 | 149 | 0 | 100 | 200 | 127 | 402 | 106 | 34 | 105 | 0 | 107 | 0 | 105 | 46 | 107 | 100 | 351 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 681 | 0 | 313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 176 | 0 | 11 | 0 | 203 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 218 | 0 | 17 | 0 |  | 8321 | 3322 | 11643 | 4734 | 681 | 1824 | 3401 | 655 | 124 | 100 | 124 | 0 | 0 | 93.34
4:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 393 | 202 |  | 0 | 250 | 275 | 0 | 0 | 40 | 328 | 0 | 0 | 0 | 50 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 96 | 0 | 20 | 38 | 0 | 0 | 80 | 270 | 295 | 208 | 8 | 137 | 19 | 25 | 0 | 35 | 0 | 0 | 25 | 11 | 11 | 33 | 21 | 24 | 100 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 0 | 84 | 0 | 205 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 156 | 0 | 149 | 0 | 100 | 200 | 128 | 401 | 106 | 17 | 105 | 0 | 107 | 0 | 110 | 17 | 106 | 100 | 350 | 90 | 0 | 162 | 116 | 0 | 17 | 0 |  | 681 | 0 | 310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 174 | 0 | 11 | 0 | 203 | 0 | 400 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 221 | 0 | 0 | 0 |  | 8028 | 3301 | 11329 | 4735 | 681 | 1842 | 3172 | 655 | 120 | 100 | 24 | 0 | 0 | 93.34
5:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 393 | 201 |  | 0 | 250 | 265 | 0 | 0 | 40 | 327 | 0 | 0 | 0 | 50 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 92 | 96 | 0 | 20 | 39 | 0 | 0 | 80 | 265 | 290 | 209 | 8 | 138 | 19 | 25 | 0 | 35 | 0 | 0 | 8 | 11 | 11 | 33 | 21 | 116 | 100 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 163 | 271 | 0 | 84 | 0 | 205 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 145 | 0 | 0 | 157 | 0 | 149 | 0 | 100 | 200 | 127 | 402 | 115 | 17 | 105 | 0 | 107 | 0 | 110 | 0 | 108 | 100 | 350 | 91 | 0 | 162 | 116 | 0 | 17 | 0 |  | 675 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 172 | 0 | 11 | 0 | 200 | 0 | 415 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 70 | 480 | 222 | 0 | 0 | 0 |  | 8082 | 3237 | 11319 | 4716 | 675 | 1858 | 3099 | 635 | 120 | 100 | 116 | 0 | 0 | 93.34
6:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 392 | 202 |  | 0 | 250 | 290 | 0 | 0 | 33 | 331 | 0 | 0 | 0 | 50 | 100 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 60 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 90 | 0 | 20 | 39 | 0 | 0 | 80 | 260 | 290 | 211 | 8 | 137 | 19 | 25 | 0 | 35 | 0 | 0 | 8 | 11 | 11 | 33 | 21 | 110 | 100 | 0 | 16 | 0 | 43 | 42 | 53 | 0 | 163 | 270 | 0 | 0 | 0 | 205 | 18 | 0 | 10 | 275 | 24 | 8 | 0 | 14 | 0 | 0 | 167 | 0 | 149 | 1 | 100 | 120 | 127 | 402 | 115 | 17 | 105 | 0 | 107 | 0 | 110 | 0 | 107 | 100 | 350 | 85 | 0 | 108 | 116 | 0 | 17 | 1 |  | 675 | 0 | 305 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 172 | 0 | 11 | 0 | 198 | 0 | 391 | 70 | 0 | 35 | 0 | 70 | 0 | 0 | 35 | 430 | 223 | 0 | 0 | 0 |  | 7643 | 2964 | 10607 | 4710 | 675 | 1733 | 2576 | 581 | 120 | 100 | 110 | 2 | 0 | 93.34
7:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 396 | 176 |  | 0 | 250 | 290 | 0 | 0 | 40 | 327 | 0 | 0 | 0 | 31 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 88 | 0 | 20 | 30 | 0 | 0 | 80 | 300 | 330 | 197 | 8 | 138 | 0 | 25 | 0 | 0 | 0 | 0 | 8 | 11 | 11 | 33 | 21 | 106 | 99 | 0 | 16 | 0 | 44 | 42 | 14 | 0 | 163 | 269 | 0 | 0 | 0 | 205 | 18 | 0 | 10 | 300 | 24 | 8 | 0 | 14 | 0 | 0 | 166 | 0 | 147 | 3 | 100 | 51 | 128 | 402 | 115 | 17 | 105 | 1 | 53 | 0 | 110 | 0 | 55 | 100 | 350 | 17 | 3 | 54 | 116 | 0 | 17 | 3 |  | 674 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 172 | 0 | 11 | 0 | 194 | 0 | 415 | 35 | 0 | 35 | 0 | 34 | 0 | 0 | 35 | 410 | 220 | 0 | 0 | 0 |  | 7262 | 2881 | 10143 | 4748 | 674 | 1667 | 2192 | 561 | 121 | 64 | 106 | 10 | 0 | 93.34
8:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 397 | 162 |  | 0 | 250 | 240 | 0 | 0 | 40 | 290 | 0 | 0 | 0 | 32 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 22 | 33 | 33 | 0 | 0 | 61 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 50 | 89 | 0 | 20 | 7 | 0 | 0 | 80 | 260 | 295 | 186 | 8 | 135 | 19 | 25 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 21 | 108 | 100 | 0 | 16 | 0 | 44 | 42 | 47 | 0 | 163 | 271 | 0 | 0 | 0 | 167 | 18 | 0 | 10 | 290 | 24 | 8 | 0 | 14 | 0 | 0 | 166 | 0 | 141 | 9 | 100 | 62 | 125 | 401 | 115 | 17 | 105 | 2 | 85 | 0 | 110 | 0 | 77 | 100 | 351 | 32 | 17 | 78 | 116 | 0 | 17 | 3 |  | 680 | 0 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 0 | 191 | 0 | 385 | 50 | 0 | 43 | 0 | 58 | 0 | 0 | 50 | 400 | 185 | 0 | 0 | 1 |  | 7239 | 2860 | 10099 | 4589 | 680 | 1621 | 2330 | 554 | 121 | 64 | 108 | 32 | 0 | 93.34
9:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 358 | 157 |  | 0 | 250 | 275 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 75 | 64 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 21 | 33 | 33 | 9 | 0 | 62 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 50 | 89 | 0 | 18 | 2 | 0 | 0 | 80 | 290 | 320 | 190 | 8 | 139 | 20 | 25 | 0 | 35 | 0 | 0 | 40 | 0 | 11 | 33 | 21 | 98 | 98 | 0 | 16 | 1 | 44 | 42 | 47 | 0 | 110 | 270 | 0 | 0 | 0 | 20 | 18 | 0 | 9 | 280 | 24 | 8 | 0 | 67 | 0 | 0 | 166 | 0 | 142 | 5 | 100 | 174 | 125 | 352 | 115 | 51 | 105 | 0 | 90 | 0 | 110 | 17 | 107 | 100 | 350 | 90 | 23 | 144 | 116 | 0 | 17 | 9 |  | 679 | 0 | 295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 169 | 0 | 11 | 0 | 188 | 0 | 361 | 85 | 0 | 101 | 0 | 100 | 0 | 1 | 50 | 350 | 180 | 0 | 0 | 2 |  | 7441 | 2911 | 10352 | 4365 | 679 | 1517 | 2961 | 505 | 122 | 64 | 98 | 41 | 0 | 93.34
10:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 353 | 145 |  | 0 | 260 | 255 | 0 | 0 | 40 | 328 | 0 | 0 | 0 | 102 | 142 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 20 | 25 | 21 | 33 | 33 | 23 | 0 | 63 | 60 | 100 | 0 | 6 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 50 | 89 | 0 | 18 | 2 | 0 | 0 | 80 | 265 | 290 | 173 | 8 | 136 | 20 | 25 | 0 | 35 | 0 | 0 | 52 | 0 | 11 | 33 | 21 | 114 | 98 | 0 | 16 | 1 | 44 | 42 | 50 | 0 | 163 | 268 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 300 | 24 | 8 | 0 | 127 | 0 | 0 | 165 | 0 | 130 | 6 | 100 | 197 | 123 | 365 | 115 | 85 | 105 | 1 | 122 | 0 | 110 | 50 | 105 | 100 | 351 | 90 | 25 | 144 | 116 | 0 | 17 | 4 |  | 679 | 0 | 275 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 10 | 198 | 0 | 412 | 105 | 0 | 113 | 0 | 100 | 0 | 1 | 90 | 330 | 218 | 0 | 0 | 0 |  | 7804 | 3040 | 10844 | 4338 | 679 | 1676 | 3248 | 486 | 123 | 142 | 114 | 38 | 0 | 93.34
11:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 376 | 137 |  | 0 | 260 | 270 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 21 | 33 | 33 | 42 | 0 | 63 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 30 | 82 | 8 | 18 | 2 | 0 | 0 | 80 | 285 | 315 | 182 | 8 | 137 | 20 | 5 | 0 | 35 | 0 | 0 | 52 | 0 | 11 | 0 | 21 | 114 | 82 | 0 | 16 | 3 | 44 | 42 | 47 | 0 | 130 | 267 | 0 | 0 | 0 | 0 | 18 | 0 | 9 | 295 | 24 | 8 | 0 | 240 | 0 | 0 | 164 | 0 | 127 | 7 | 100 | 197 | 127 | 395 | 106 | 105 | 105 | 3 | 141 | 0 | 110 | 114 | 103 | 100 | 350 | 90 | 36 | 158 | 116 | 0 | 17 | 18 |  | 679 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 194 | 0 | 419 | 105 | 0 | 113 | 0 | 96 | 0 | 1 | 113 | 350 | 218 | 0 | 0 | 0 |  | 8022 | 3003 | 11025 | 4252 | 679 | 1612 | 3510 | 505 | 123 | 162 | 114 | 68 | 0 | 93.34
12:00 | 0 | 0 | 0 | 70 | 300 | 0 | 0 | 389 | 137 |  | 0 | 260 | 275 | 0 | 0 | 40 | 329 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 21 | 33 | 33 | 42 | 0 | 57 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 60 | 81 | 38 | 18 | 2 | 0 | 0 | 80 | 260 | 295 | 183 | 8 | 137 | 23 | 5 | 0 | 35 | 0 | 43 | 52 | 16 | 11 | 33 | 21 | 120 | 84 | 0 | 19 | 1 | 44 | 42 | 50 | 0 | 163 | 264 | 0 | 0 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 8 | 25 | 255 | 0 | 25 | 164 | 27 | 135 | 19 | 100 | 197 | 133 | 367 | 106 | 105 | 105 | 5 | 125 | 0 | 110 | 114 | 99 | 100 | 217 | 90 | 32 | 162 | 102 | 0 | 17 | 35 |  | 680 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 83 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 188 | 0 | 398 | 105 | 0 | 113 | 0 | 100 | 0 | 1 | 113 | 360 | 214 | 0 | 0 | 3 |  | 8238 | 3089 | 11327 | 4185 | 680 | 1633 | 3654 | 513 | 117 | 329 | 120 | 96 | 0 | 93.34
13:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 137 |  | 0 | 260 | 260 | 0 | 0 | 29 | 333 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 21 | 33 | 33 | 42 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 82 | 85 | 44 | 18 | 3 | 0 | 0 | 80 | 260 | 295 | 160 | 8 | 135 | 23 | 5 | 0 | 35 | 0 | 50 | 52 | 16 | 11 | 33 | 21 | 118 | 70 | 0 | 19 | 2 | 44 | 42 | 50 | 0 | 110 | 236 | 0 | 0 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 8 | 100 | 260 | 52 | 100 | 163 | 100 | 148 | 17 | 100 | 197 | 133 | 367 | 115 | 105 | 105 | 2 | 125 | 0 | 110 | 114 | 102 | 100 | 259 | 90 | 25 | 162 | 96 | 0 | 17 | 23 |  | 680 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 9 | 47 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 170 | 0 | 11 | 0 | 184 | 0 | 410 | 105 | 0 | 113 | 0 | 107 | 0 | 2 | 113 | 400 | 214 | 0 | 0 | 4 |  | 8401 | 3163 | 11564 | 4100 | 680 | 1606 | 3965 | 554 | 120 | 346 | 118 | 75 | 0 | 93.34
14:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 170 |  | 0 | 260 | 265 | 0 | 0 | 25 | 321 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 20 | 33 | 33 | 42 | 0 | 57 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 68 | 50 | 20 | 3 | 0 | 0 | 80 | 265 | 295 | 162 | 8 | 132 | 22 | 5 | 0 | 35 | 0 | 50 | 52 | 18 | 11 | 19 | 6 | 124 | 70 | 0 | 19 | 1 | 44 | 42 | 53 | 0 | 110 | 235 | 0 | 0 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 8 | 100 | 278 | 53 | 70 | 163 | 100 | 149 | 17 | 100 | 197 | 133 | 367 | 115 | 105 | 105 | 2 | 125 | 0 | 110 | 114 | 98 | 100 | 260 | 90 | 16 | 162 | 97 | 0 | 29 | 26 |  | 680 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 88 | 24 | 0 | 0 | 0 | 0 | 0 | 9 | 47 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 164 | 0 | 11 | 0 | 180 | 0 | 398 | 105 | 0 | 113 | 0 | 107 | 0 | 2 | 113 | 400 | 215 | 0 | 0 | 5 |  | 8366 | 3142 | 11508 | 4049 | 680 | 1603 | 3964 | 552 | 117 | 350 | 124 | 69 | 0 | 93.34
15:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 397 | 175 |  | 0 | 260 | 275 | 0 | 0 | 40 | 319 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 20 | 33 | 33 | 42 | 0 | 57 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 54 | 50 | 20 | 2 | 0 | 0 | 80 | 300 | 325 | 152 | 8 | 138 | 22 | 5 | 0 | 35 | 0 | 50 | 52 | 18 | 11 | 33 | 21 | 120 | 85 | 0 | 21 | 1 | 44 | 42 | 53 | 0 | 110 | 230 | 0 | 20 | 0 | 0 | 18 | 0 | 10 | 310 | 24 | 3 | 200 | 275 | 175 | 90 | 152 | 100 | 149 | 2 | 100 | 196 | 135 | 383 | 115 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 99 | 100 | 260 | 90 | 22 | 162 | 97 | 0 | 35 | 13 |  | 679 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 88 | 25 | 0 | 0 | 0 | 0 | 0 | 18 | 47 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 174 | 0 | 407 | 105 | 0 | 113 | 0 | 106 | 0 | 1 | 113 | 420 | 215 | 0 | 0 | 1 |  | 8752 | 3171 | 11923 | 4153 | 679 | 1667 | 4210 | 573 | 117 | 364 | 120 | 40 | 0 | 93.34
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 398 | 178 |  | 0 | 260 | 270 | 0 | 0 | 28 | 318 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 42 | 0 | 53 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 50 | 50 | 20 | 2 | 0 | 0 | 70 | 265 | 295 | 164 | 8 | 135 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 18 | 11 | 33 | 21 | 116 | 98 | 0 | 19 | 1 | 43 | 42 | 53 | 0 | 110 | 233 | 0 | 81 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 8 | 200 | 275 | 175 | 60 | 152 | 100 | 149 | 4 | 100 | 187 | 130 | 365 | 115 | 105 | 105 | 1 | 125 | 0 | 110 | 114 | 104 | 100 | 260 | 90 | 10 | 162 | 97 | 0 | 35 | 6 |  | 679 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 89 | 24 | 0 | 0 | 0 | 0 | 0 | 37 | 47 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 156 | 0 | 11 | 0 | 170 | 0 | 410 | 105 | 0 | 113 | 0 | 0 | 0 | 1 | 113 | 430 | 217 | 0 | 0 | 1 |  | 8624 | 3095 | 11719 | 4045 | 679 | 1725 | 4063 | 585 | 113 | 369 | 116 | 24 | 0 | 93.34
17:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 396 | 178 |  | 0 | 260 | 235 | 0 | 0 | 28 | 320 | 0 | 0 | 0 | 98 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 47 | 0 | 48 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 92 | 50 | 50 | 20 | 2 | 0 | 0 | 70 | 265 | 295 | 180 | 8 | 136 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 116 | 99 | 0 | 19 | 0 | 43 | 42 | 53 | 0 | 110 | 234 | 0 | 83 | 0 | 0 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 278 | 0 | 0 | 152 | 50 | 149 | 3 | 100 | 155 | 127 | 367 | 115 | 105 | 105 | 1 | 125 | 0 | 110 | 114 | 104 | 100 | 250 | 90 | 9 | 162 | 96 | 0 | 35 | 1 |  | 680 | 0 | 245 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 75 | 23 | 0 | 0 | 0 | 0 | 0 | 46 | 47 | 0 | 0 | 0 | 43 | 0 | 12 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 155 | 0 | 11 | 0 | 170 | 0 | 376 | 105 | 0 | 113 | 0 | 24 | 0 | 1 | 113 | 410 | 185 | 0 | 0 | 1 |  | 8046 | 3017 | 11063 | 4045 | 680 | 1621 | 3535 | 564 | 108 | 378 | 116 | 16 | 0 | 93.34
18:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 362 | 182 |  | 0 | 260 | 265 | 0 | 0 | 30 | 320 | 0 | 0 | 0 | 102 | 115 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 20 | 33 | 33 | 51 | 0 | 53 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 50 | 50 | 50 | 20 | 6 | 0 | 0 | 70 | 265 | 295 | 189 | 8 | 137 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 122 | 98 | 0 | 21 | 0 | 44 | 42 | 53 | 0 | 110 | 233 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 270 | 24 | 8 | 0 | 278 | 0 | 0 | 100 | 0 | 149 | 0 | 60 | 100 | 132 | 330 | 115 | 105 | 105 | 0 | 68 | 0 | 110 | 52 | 108 | 60 | 260 | 90 | 1 | 162 | 97 | 0 | 35 | 0 |  | 680 | 0 | 240 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 46 | 47 | 0 | 0 | 0 | 43 | 11 | 20 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 159 | 0 | 11 | 0 | 170 | 0 | 307 | 70 | 0 | 35 | 0 | 70 | 0 | 1 | 35 | 410 | 219 | 0 | 0 | 0 |  | 7658 | 2868 | 10526 | 4028 | 680 | 1602 | 3042 | 565 | 113 | 372 | 122 | 2 | 0 | 93.34
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 364 | 184 |  | 0 | 260 | 260 | 0 | 0 | 35 | 332 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 20 | 33 | 33 | 51 | 0 | 58 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 50 | 50 | 20 | 2 | 0 | 0 | 70 | 265 | 295 | 185 | 8 | 136 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 142 | 98 | 0 | 21 | 0 | 44 | 42 | 53 | 0 | 110 | 234 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 8 | 200 | 278 | 207 | 100 | 141 | 100 | 149 | 0 | 100 | 119 | 128 | 400 | 111 | 105 | 105 | 0 | 121 | 0 | 110 | 114 | 112 | 100 | 260 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 679 | 0 | 240 | 0 | 0 | 65 | 0 | 0 | 22 | 0 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 43 | 46 | 95 | 0 | 0 | 30 | 43 | 24 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 167 | 0 | 11 | 33 | 170 | 0 | 397 | 85 | 50 | 48 | 0 | 110 | 0 | 0 | 100 | 470 | 219 | 0 | 12 | 0 |  | 8711 | 3467 | 12178 | 4095 | 679 | 1713 | 4197 | 624 | 118 | 610 | 142 | 0 | 0 | 93.34
19:30 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 383 | 190 |  | 0 | 260 | 265 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 22 | 33 | 33 | 51 | 0 | 58 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 50 | 50 | 20 | 4 | 0 | 0 | 70 | 265 | 295 | 188 | 8 | 138 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 134 | 101 | 0 | 21 | 0 | 44 | 42 | 50 | 0 | 155 | 236 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 8 | 200 | 278 | 155 | 100 | 140 | 101 | 149 | 0 | 100 | 150 | 128 | 402 | 111 | 105 | 105 | 0 | 124 | 0 | 110 | 114 | 114 | 100 | 260 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 679 | 0 | 240 | 0 | 0 | 65 | 0 | 0 | 25 | 0 | 0 | 88 | 33 | 0 | 0 | 0 | 0 | 43 | 38 | 95 | 0 | 0 | 30 | 43 | 25 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 100 | 164 | 0 | 387 | 105 | 50 | 75 | 0 | 113 | 0 | 0 | 113 | 550 | 216 | 0 | 17 | 0 |  | 8783 | 3656 | 12439 | 4121 | 679 | 1750 | 4326 | 705 | 118 | 606 | 134 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 392 | 190 |  | 0 | 260 | 250 | 0 | 0 | 40 | 332 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 0 | 25 | 18 | 33 | 33 | 51 | 0 | 58 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 50 | 50 | 20 | 8 | 0 | 0 | 70 | 265 | 295 | 187 | 8 | 134 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 30 | 21 | 134 | 102 | 0 | 21 | 0 | 44 | 42 | 53 | 0 | 155 | 235 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 265 | 24 | 8 | 200 | 280 | 154 | 100 | 140 | 100 | 149 | 0 | 100 | 185 | 127 | 401 | 112 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 114 | 100 | 260 | 90 | 0 | 162 | 116 | 0 | 35 | 0 |  | 679 | 0 | 235 | 0 | 0 | 55 | 0 | 0 | 25 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 43 | 37 | 95 | 0 | 0 | 32 | 43 | 25 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 100 | 163 | 0 | 378 | 105 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 560 | 201 | 0 | 17 | 0 |  | 8789 | 3663 | 12452 | 4107 | 679 | 1718 | 4385 | 714 | 118 | 597 | 134 | 0 | 0 | 93.34
21:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 394 | 195 |  | 0 | 270 | 270 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 22 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 50 | 50 | 20 | 24 | 0 | 0 | 70 | 265 | 295 | 175 | 8 | 135 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 134 | 102 | 0 | 21 | 0 | 43 | 42 | 53 | 0 | 155 | 236 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 0 | 200 | 280 | 103 | 70 | 140 | 100 | 149 | 0 | 100 | 200 | 133 | 401 | 115 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 114 | 100 | 260 | 90 | 0 | 162 | 115 | 0 | 35 | 0 |  | 679 | 0 | 230 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 43 | 37 | 94 | 0 | 0 | 30 | 43 | 25 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 158 | 0 | 11 | 100 | 160 | 0 | 392 | 105 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 216 | 0 | 17 | 0 |  | 8805 | 3686 | 12491 | 4101 | 679 | 1794 | 4347 | 723 | 120 | 593 | 134 | 0 | 0 | 93.34
22:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 195 |  | 0 | 270 | 290 | 0 | 0 | 40 | 329 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 22 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 51 | 50 | 20 | 34 | 0 | 0 | 70 | 275 | 305 | 170 | 8 | 138 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 17 | 21 | 132 | 102 | 0 | 21 | 0 | 43 | 42 | 53 | 0 | 155 | 236 | 0 | 81 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 0 | 200 | 281 | 56 | 70 | 140 | 101 | 149 | 0 | 100 | 200 | 133 | 401 | 111 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 115 | 100 | 260 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 680 | 0 | 230 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 43 | 37 | 94 | 0 | 0 | 30 | 43 | 25 | 22 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 151 | 0 | 11 | 100 | 155 | 0 | 416 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 218 | 0 | 17 | 0 |  | 8807 | 3652 | 12459 | 4094 | 680 | 1847 | 4269 | 724 | 120 | 593 | 132 | 0 | 0 | 93.34
23:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 195 |  | 0 | 270 | 300 | 0 | 0 | 40 | 325 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 22 | 33 | 33 | 51 | 0 | 61 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 93 | 51 | 50 | 20 | 36 | 0 | 0 | 70 | 295 | 305 | 176 | 8 | 138 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 136 | 102 | 0 | 21 | 0 | 43 | 42 | 53 | 0 | 155 | 234 | 0 | 81 | 0 | 0 | 18 | 0 | 10 | 290 | 24 | 0 | 115 | 281 | 23 | 30 | 140 | 52 | 141 | 0 | 100 | 200 | 134 | 401 | 111 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 107 | 100 | 260 | 91 | 0 | 162 | 114 | 0 | 35 | 0 |  | 679 | 0 | 220 | 0 | 0 | 55 | 0 | 0 | 18 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 37 | 95 | 0 | 0 | 30 | 52 | 25 | 22 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 149 | 0 | 11 | 100 | 151 | 0 | 405 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 219 | 0 | 17 | 0 |  | 8605 | 3625 | 12230 | 4113 | 679 | 1829 | 4060 | 721 | 121 | 571 | 136 | 0 | 0 | 93.34
24:00 | 0 | 0 | 0 | 110 | 300 | 0 | 0 | 397 | 214 |  | 0 | 270 | 288 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 22 | 33 | 33 | 51 | 0 | 61 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 68 | 93 | 44 | 50 | 20 | 36 | 0 | 0 | 70 | 280 | 290 | 152 | 8 | 135 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 132 | 102 | 0 | 21 | 0 | 43 | 42 | 53 | 0 | 140 | 236 | 0 | 81 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 0 | 50 | 281 | 0 | 0 | 146 | 54 | 138 | 0 | 100 | 200 | 135 | 401 | 112 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 96 | 100 | 260 | 94 | 0 | 162 | 114 | 0 | 35 | 0 |  | 679 | 0 | 225 | 0 | 0 | 55 | 0 | 0 | 18 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 37 | 95 | 0 | 0 | 15 | 52 | 25 | 22 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 0 | 0 | 149 | 0 | 11 | 100 | 149 | 0 | 419 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 219 | 0 | 17 | 0 |  | 8544 | 3628 | 12172 | 4183 | 679 | 1857 | 3922 | 722 | 121 | 556 | 132 | 0 | 0 | 93.34
KWH | 0 | 0 | 0 | 1354500 | 7135527 | 0 | 0 | 9440000 | 4296000 |  | 0 | 6052750 | 6371753 | 0 | 0 | 925213 | 7751422 | 0 | 0 | 0 | 2133792 | 3060960 | 0 | 0 | 0 | 0 | 1027440 | 1328124 | 1326092 | 401472 | 600000 | 475560 | 823000 | 811300 | 786240 | 0 | 1371191 | 1460000 | 2400000 | 0 | 417445 | 0 | 0 | 0 | 0 |  | 588480 | 0 | 1130095 | 1798680 | 1745280 | 764160 | 462192 | 423360 | 0 | 0 | 1843312 | 6806500 | 7311000 | 4427000 | 217454 | 3268790 | 336384 | 391200 | 0 | 821736 | 0 | 659992 | 1052333 | 330156 | 255060 | 732800 | 505042 | 2978880 | 2218160 | 0 | 428400 | 10000 | 1035000 | 1004400 | 1197600 | 0 | 3520881 | 5749000 | 0 | 1147200 | 0 | 1822080 | 392000 | 0 | 245700 | 7115000 | 561432 | 161328 | 1598208 | 5356907 | 869224 | 744558 | 3691200 | 1071621 | 3516050 | 96525 | 2346240 | 4276320 | 3102909 | 9337000 | 2684400 | 2070000 | 2535843 | 20760 | 2677200 | 0 | 2724860 | 1922040 | 2493960 | 2358720 | 7257700 | 2042880 | 211020 | 3692160 | 2665909 | 0 | 668880 | 135729 |  | 16405818 | 0 | 6544224 | 0 | 0 | 359040 | 0 | 0 | 229900 | 0 | 0 | 2111253 | 656101 | 0 | 0 | 0 | 0 | 309136 | 421718 | 1062176 | 0 | 0 | 158788 | 1108800 | 192647 | 486000 | 0 | 240968 | 0 | 0 | 3776700 | 0 | 0 | 0 | 0 | 4185127 | 0 | 271174 | 704640 | 4618055 | 0 | 9537891 | 2332320 | 137561 | 2435520 | 0 | 2234361 | 0 | 11757 | 2314656 | 12009700 | 5169355 | 0 | 198000 | 20400 |  | 199376671 | 80243786 | 279620457 | 105137144 | 16405818 | 41549402 | 86840979 | 15786400 | 2831191 | 7584452 | 2978880 | 506191 | 0
Fuel Cost | 0 | 0 | 0 | 1991115 | 7920434.97 | 0 | 0 | 9534400 | 4424880 |  | 0 | 6597497.5 | 7072645.83 | 0 | 0 | 7827301.98 | 8061478.88 | 0 | 0 | 0 | 19460183.04 | 30119846.4 | 0 | 0 | 0 | 0 | 7500312 | 10266398.52 | 13075267.12 | 301104 | 450000 | 0 | 0 | 0 | 7602940.8 | 0 | 370221.57 | 394200 | 4344000 | 0 | 3878064.05 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10961921.5 | 17177394 | 15183936 | 6052147.2 | 582361.92 | 1257379.2 | 0 | 0 | 2709668.64 | 5036810 | 7311000 | 4072840 | 280515.66 | 3759108.5 | 380113.92 | 547680 | 0 | 1405168.56 | 0 | 6665919.2 | 10049780.15 | 419298.12 | 191295 | 1282400 | 378781.5 | 22341600 | 2351249.6 | 0 | 544068 | 159400 | 1697400 | 1607040 | 2131728 | 0 | 4013804.34 | 5978960 | 0 | 2191152 | 0 | 3152198.4 | 858480 | 0 | 501228 | 7186150 | 421074 | 122609.28 | 27185518.08 | 40498216.92 | 14759423.52 | 12449009.76 | 19194240 | 17917503.12 | 34597932 | 1128377.25 | 19121856 | 46398072 | 21875508.45 | 8683410 | 24481728 | 19561500 | 22087192.53 | 0 | 20239632 | 0 | 23951519.4 | 19181959.2 | 21373237.2 | 15709075.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 94497511.68 | 0 | 6871435.2 | 0 | 0 | 4976294.4 | 0 | 0 | 2411651 | 0 | 0 | 2385715.89 | 1016956.55 | 0 | 0 | 0 | 0 | 3041898.24 | 4284654.88 | 9400257.6 | 0 | 0 | 1538655.72 | 10744272 | 1868675.9 | 933120 | 0 | 182412.776 | 0 | 0 | 20469714 | 0 | 0 | 0 | 0 | 5524367.64 | 0 | 406761 | 11985926.4 | 5403124.35 | 0 | 9442512.09 | 24349420.8 | 2339912.61 | 23113084.8 | 0 | 17338641.36 | 0 | 129914.85 | 17105307.84 | 52722583 | 0 | 0 | 0 | 0 |  | 732550862.98 | 334484782.576 | 1067035645.556 | 104509755.586 | 94497511.68 | 42336532.9 | 652706059.88 | 73192297 | 764421.57 | 75269774.84 | 22341600 | 1417692.1 | 0
Yesterday Day Peak | 0 | 0 | 0 | 70 | 300 | 0 | 0 | 389 | 137 |  | 0 | 260 | 275 | 0 | 0 | 40 | 329 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 17 | 25 | 21 | 33 | 33 | 42 | 0 | 57 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 60 | 81 | 38 | 18 | 2 | 0 | 0 | 80 | 260 | 295 | 183 | 8 | 137 | 23 | 5 | 0 | 35 | 0 | 43 | 52 | 16 | 11 | 33 | 21 | 120 | 84 | 0 | 19 | 1 | 44 | 42 | 50 | 0 | 163 | 264 | 0 | 0 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 8 | 25 | 255 | 0 | 25 | 164 | 27 | 135 | 19 | 100 | 197 | 133 | 367 | 106 | 105 | 105 | 5 | 125 | 0 | 110 | 114 | 99 | 100 | 217 | 90 | 32 | 162 | 102 | 0 | 17 | 35 |  | 680 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 83 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 8 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 188 | 0 | 398 | 105 | 0 | 113 | 0 | 100 | 0 | 1 | 113 | 360 | 214 | 0 | 0 | 3 |  | 11327 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 394 | 195 | 0 | 0 | 270 | 270 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 22 | 33 | 33 | 51 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 100 | 50 | 50 | 20 | 24 | 0 | 0 | 70 | 265 | 295 | 175 | 8 | 135 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 25 | 21 | 134 | 102 | 0 | 21 | 0 | 43 | 42 | 53 | 0 | 155 | 236 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 280 | 24 | 0 | 200 | 280 | 103 | 70 | 140 | 100 | 149 | 0 | 100 | 200 | 133 | 401 | 115 | 105 | 105 | 0 | 125 | 0 | 110 | 114 | 114 | 100 | 260 | 90 | 0 | 162 | 115 | 0 | 35 | 0 |  | 679 | 0 | 230 | 0 | 0 | 55 | 0 | 0 | 24 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 43 | 37 | 94 | 0 | 0 | 30 | 43 | 25 | 22 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 158 | 0 | 11 | 100 | 160 | 0 | 392 | 105 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 216 | 0 | 17 | 0 |  | 12491 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 250 | 0 | 0 | 270 | 300 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 102 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 96 | 50 | 21 | 20 | 0 | 0 | 70 | 360 | 360 | 215 | 8 | 140 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 163 | 120 | 6 | 21 | 0 | 43 | 42 | 51 | 0 | 163 | 270 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 130 | 400 | 115 | 105 | 105 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 400 | 95 | 0 | 162 | 116 | 0 | 17 |  |  | 707 | 0 | 250 | 0 | 0 | 225 | 0 | 0 | 25 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 95 | 0 | 0 | 31 | 52 | 23 | 22 | 0 | 11 | 0 | 0 | 155 | 10 | 10 | 0 | 0 | 200 | 0 | 12 | 100 | 220 | 0 | 400 | 105 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 250 | 0 | 0 | 270 | 300 | 0 | 0 | 40 | 335 | 0 | 0 | 0 | 100 | 150 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 22 | 33 | 33 | 52 | 0 | 60 | 60 | 100 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 95 | 50 | 20 | 5 | 0 | 0 | 70 | 330 | 330 | 215 | 8 | 140 | 5 | 5 | 0 | 35 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 138 | 120 | 6 | 21 | 1.6 | 43 | 42 | 51 | 0 | 163 | 270 | 0 | 84 | 0 | 0 | 18 | 0 | 10 | 341 | 24 | 11 | 100 | 300 | 100 | 100 | 200 | 50 | 149 | 20 | 100 | 200 | 125 | 400 | 115 | 105 | 105 | 5 | 200 | 54 | 110 | 114 | 113 | 100 | 350 | 90 | 50 | 162 | 116 | 0 | 17 | 30 |  | 707 | 0 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 0 | 95 | 0 | 0 | 30 | 52 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 |  | 0 | 200 | 0 | 12 | 50 | 220 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 351 | 247 | 0 | 0 | 270 | 285 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 55 | 12 | 25 | 6 | 30 |  | 0 | 0 | 59 | 60 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 40 | 5 | 0 | 20 | 2 | 0 | 0 | 70 | 280 | 280 | 178 | 8 | 137 | 5 | 5 | 0 | 35 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 94 | 102 | 0 | 21 | 0 | 43 | 42 | 50 | 0 | 110 | 236 | 0 | 78 | 0 | 0 | 18 | 0 | 10 | 300 | 24 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 137 | 0 | 100 | 100 | 122 | 352 | 85 | 20 | 105 | 3 | 125 | 0 | 110 | 0 | 98 | 100 | 350 | 54 | 6 | 108 | 115 | 0 | 17 | 4 | 0 | 691 | 0 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 18 | 0 | 8 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 140 | 0 | 11 | 0 | 140 | 0 | 417 | 19 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 420 | 180 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 10099 | 8:00
| Highest Generation |  | 12491 | 21:00
| Day Peak Generation |  | 11327 | 12:00
| Evening Peak Generation |  | 12491 | 21:00
| HVDC Max Flow |  | 681 | 2:00
| HVDC EvPeak Flow |  | 679 | 21:00
| Load factor L.F |  | 93.27%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-08-24
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-08-23 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11327 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9254 | MW
Evening Peak Generation : |  | 12491 | MW Hour : | 21:00 | Available Max Generation : |  | 14679 | MW
E.P. Demand (at gen end) : |  | 12491 | MW Hour : | 21:00 | Max Demand (Evening) : |  | 13000 | MW
Maximum Generation : |  | 12491 | MW Hour : | 21:00 | Reserve(Generation end) |  | 1679 | MW
Total Gen. (MKWH) : |  | 279.6205 | System Load Factor : | 93.27% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -504 | MW at | 20:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-08-24
Actual : | 93.35 | Ft.(MSL) , | Rule curve : | 96.04 | Ft.( MSL )
Gas Consumed : | Total = | 1102.813 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146846288.486
: |  | Coal : | 73192297 | Oil : | 727975834.72 | Total : | 948014420.206
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4572.7129 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1559.5051 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1398.072 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1263.5625 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1141.7051 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 921.3271 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 509.3319 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.0627 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 710.6011 |  |  | 0 | 0%
Total | 0 |  | 12313.8804 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-3,4
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Sirajganj unit-1
7) Raozan #2
8) Sylhet 225 MW
9) Shahjinazar 8 & 9
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet 225 MW CCPP ST was shut down at 08:54.
b) Sylhet 225 MW CCPP GT was shut down at 09:01 due to air filter replacement.
c) Ghorasal unit-5 was shut down at 12:05 due to gas shortage.
d) Bibiyana(S) CCPP ST was shut down at 12:13 due to steam leakage.
e) Ghorasal-Norsingdi 132 kV Ckt-1 was under shut down from 08:57 to 14:43 for D/W.
f) Kishoreganj 132/33 kV T1 & T2 transformers tripped at 12:40 showing O/C relay at 33 kV end and was |  |  |  |  | About 90 MW power interruption occurred under Kishoreganj S/S
switched on at 14:05. |  |  |  |  | area from 12:40 to 14:05.
g) Kishoreganj 132/33 kV T3A & T3B transformers tripped at 12:40 due to 33 kV breakers & CT got
damage.
h) Jaldhaka 132/33 kV T-1 transformer was under shut down from 12:01 to 13:35 for C/M.
i) Jaldhaka 132/33 kV T-2 transformer was under shut down from 11:45 to 12:00 for C/M.
j) Jaldhaka-Saidpur 132 kV Ckt-1 was under shut down from 11:45 to 12:00 for C/M.
k) Jaldhaka-Saidpur 132 kV Ckt-2 was under shut down from 11:31 to 11:45 for C/M.
l) Barapukuria-Saidpur 132 kV Ckt-1 tripped at 15:37 showing Dist. Z1, O/C 3-phase relays at Barapukuria
end and was switched on at 15:53.
m) Noapara 132/33 kV T-4 transformer was under shut down from 14:51 to 15:50 for C/M. |  |  |  |  | About 8 MW power interruption occurred under Noapara S/S
area from 14:51 to 15:50.
n) Siddhirganj 230/132 kV MTR-2 transformer was under shut down from 13:57 to 18:13 for C/M.
o) Khulna 225 MW GT was synchronized at 18:28.
p) Dohazari-Cox'sbazar 132 kV Ckt-2 tripped at 18:40 showing O/C,U/V at 33 kV end and was
switched on at 18:46.
q) Noapara 132/33 kV T-3 transformer was under shut down from 20:50 to 21:15 for C/M.
r) Shahjibazar 132/33 kV T2 & T6 transformers tripped at 20:58 due to 33 kV feeder fault and was
switched on at 21:08.
s) Cumilla(N)-Shahjibazar 230 kV Ckt-2 tripped at 21:31 showing Dist. E/F 3-phase relay at Cumilla(N) end
and was switched on at 21:58.
t) Bhulta 132/33 kV T-2 transformer was shut down at 07:03(24-08-2021) due to red hot maintenance at
33 kV end.
u) Haripur-Bhulta 132 kV Ckt tripped at 04:05(24-08-2021) due to tripping of T1 transformer by PEF
and 33 kV feeder fault and was switched on at 04:24(24-08-20210.
v) Mohasthangarh 132/33 kV T-1 transformer was shut down at 06:58(24-08-2021) due to red hot
maintenance at 33 kV end.
w) Bibiyana(S) CCPP ST was synchronized at 05:21(24-08-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-08-23 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 1354500 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7135527 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 394 | 9440000 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 195 | 4296000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 270 | 6052750 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 270 | 6371753 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 925213 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 0 | 0 | Reserve.
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 401472
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 100 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 335 | 7751422
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2133792
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1027440
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 3060960
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1328124
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 1326092
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 47 | 1075560 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 823000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 811300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 786240
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 280 | 5356907 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 103 | 869224 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 70 | 744558 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1071621
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3516050
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 2070000
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 2042880 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3692160
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 135729
| Dhaka area Total |  |  |  | 5819 | 3464 | 75600274
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 100 | 2400000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 417445
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 96525
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 764160
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 120 | 2831191 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2535843
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1130095 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1798680
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2346240
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 462192
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 24 | 423360
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 50 | 1745280 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 20760
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 125 | 2677200 | Transformer O/L
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 0 | 0 | Transformer O/L
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2724860
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2358720
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 115 | 2665909
| Chattogram area Total |  |  |  | 2382 | 1229 | 27398460
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 70 | 1843312 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 175 | 4427000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 265 | 6806500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7311000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 5 | 336384 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 5 | 391200 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 821736 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 3102909 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 659992
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 135 | 3268790 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4276320
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 330156
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255060
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 2978880
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 732800 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 1052333
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 505042
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1598208
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1922040
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 114 | 2493960
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 668880 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2104 | 45999956
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 102 | 2218160 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 428400
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 140 | 3691200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2684400
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 211020
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 588480
| Mymensingh Area Total |  |  |  | 709 | 402 | 9831660
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1035000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 42 | 1004400 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 155 | 3520881
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 236 | 5749000 | Machine problem
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 53 | 1197600
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 0 | 161328 | Engine problem
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Under maint.
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 84 | 1147200
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 0 | 1822080
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 392000 | Engine problem
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 561432
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7115000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 401 | 9337000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 10 | 245700
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 260 | 7257700 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1606 | 40546321
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 679 | 16405818
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 24 | 229900
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 55 | 359040 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 230 | 6544224 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 704640
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2332320
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1193 | 26575942
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Reserve.
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 656101
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 2111253 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 271174 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 570 | 12009700
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 216 | 5169355
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 198000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 936 | 20415583
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 309136 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 37 | 421718 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 0 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 158788 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 158 | 4185127 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 160 | 4618055 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 392 | 9537891 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 192647 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 486000
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240968
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 1108800
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 1062176 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 137561 | Low demand
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2435520
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2314656
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 20400
| Rajshahi Area Total |  |  |  | 2179 | 1291 | 27229443
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 153 | 3776700 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2234361
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 11757
| Rangpur Area Total |  |  |  | 605 | 266 | 6022818
| Total |  |  |  | 21280 | 12491 | 279620457
| Eastern Grid Total |  |  |  | 14321 | 8805 | 199376671
| Western Grid Total |  |  |  | 6959 | 3686 | 80243786
| National Grid Total |  |  |  | 21280 | 12491 | 279620457
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-08-23
(a) ENTIRE EASTERN GRID : |  | 7838 | MW | (b) ENTIRE WESTERN GRID : |  | 3982 | MW
i) Dhaka area |  | 4297 | MW | i) Khulna area |  | 1644 | MW
ii) Chittagong area |  | 1267 | MW | ii) Rajshahi area |  | 1234 | MW
iii) Comilla area |  | 1133 | MW | iii) Barisal area |  | 380 | MW
iv) Mymensingh area |  | 828 | MW | iv) Rangpur area |  | 724 | MW
v) Sylhet area |  | 313 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11820 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 106 | 0:00 | Netrokona | 108 | 19:00 | Benapol | 56 | 21:00
Munsiganj | 78 | 17:00 | Jamalpur | 136 | 5:00 | Jhenida | 126 | 19:00
Sonargaon | 224 | 11:00 | Sherpur | 114 | 1:00 | Bottail | 136 | 19:00
Shyampur | 218 | 11:00 | Srimongal | 73 | 21:00 | G.K Project | 59 | 19:30
Bhulta | 47 | 23:00 | Shahjibazar | 100 | 20:00 | Faridpur | 148 | 22:00
Madanganj | 112 | 15:00 | Fenchuganj | 48 | 1:00 | Rajbari | 58 | 19:30
Shitalakhya | 30 | 14:00 | Kulawara | 41 | 19:00 | Madaripur | 109 | 22:00
Rahim steel | 66 | 11:00 | Sylhet | 129 | 18:30 | Sariatpur | 70 | 21:00
Matuail | 80 | 1:00 | Chatak | 26 | 1:00 | Gopalganj | 97 | 19:30
Ghorasal | 175 | 1:00 | Sunamganj | 45 | 1:00 | Bagerhat | 104 | 22:00
Narsingdi | 121 | 11:00 | Biani Bazar | 57 | 19:00 | Mongla | 42 | 10:00
Haripur (SBU) | 39 | 21:00 | Comilla (S) | 142 | 19:00 | Satkhira | 122 | 22:00
Sreenagar | 65 | 19:00 | Comilla(N) | 144 | 20:00 | Gallamari | 38 | 1:00
Ullon | 78 | 19:00 | Chandpur | 75 | 23:00 | Magura | 60 | 22:00
Hasnabad | 106 | 15:00 | Feni | 126 | 22:00 | Norail | 46 | 19:00
Magbazar | 76 | 16:00 | Chowmuhani | 216 | 23:00 | Chuadanga | 109 | 21:00
Maniknagar | 13 | 10:00 | Ashuganj | 44 | 3:00 | Borguna | 18 | 19:00
Bangabhaban | 42 | 8:00 | Daudkandi | 151 | 19:00 | Barisal(N) | 48 | 21:00
Motijheel | 68 | 13:00 | B.Baria | 165 | 19:00 | Barisal (S) | 112 | 19:00
Narinda | 83 | 12:00 | Ramganj | 88 | 21:00 | Patuakhali | 116 | 22:00
Kazla | 189 | 13:00 | Chaddagram | 47 | 22:00 | Bhandaria | 54 | 20:00
Dhanmondi | 91 | 13:00 | PHP | 9 | 20:00 | Borhan Uddin | 46 | 21:00
Lalbag | 69 | 1:00 | Kochua | 80 | 20:00 | Ishurdi | 68 | 21:00
Madartek | 36 | 13:00 | Madunaghat | 60 | 19:00 | Ruppur Paromanobik | 4 | 13:00
Dhaka University | 29 | 13:00 | Hathazari | 94 | 19:00 | Natore | 127 | 1:00
Aftabnagar | 61 | 12:00 | Khulshi | 189 | 16:00 | Bogra | 158 | 1:00
Fatullah | 49 | 1:00 | Halishahar | 90 | 9:00 | Noagaon | 118 | 1:00
Nawabganj | 66 | 18:30 | Baraulia | 156 | 1:00 | Rajshahi | 150 | 21:00
Keraniganj | 120 | 15:00 | Sikalbaha | 32 | 19:30 | Rajshahi New | 15 | 1:00
Mirpur | 108 | 19:30 | Dohazari | 106 | 19:00 | C.Nawabganj | 58 | 22:00
Kalyanpur | 70 | 14:00 | Cox'sbazar | 88 | 18:30 | Amnura | 48 | 21:00
Gulshan | 90 | 13:00 | Chandraghona | 26 | 22:00 | Pabna | 118 | 20:00
Uttara | 16 | 15:00 | Kaptai | 4.2 | 19:00 | Shahjadpur | 88 | 20:00
Uttara New | 95 | 17:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 99 | 20:00
Kamrangirchar | 175 | 16:00 | Bakulia | 111 | 19:00 | Niyamatpur | 69 | 1:00
Savar | 138 | 14:00 | Julda | 23 | 12:00 | Joypurhat | 57 | 1:00
Bhasantec | 87 | 14:00 | TK chemical | 28.7 | 21:00 | Sherpur(Bogura) | 55 | 1:00
Agargaon | 96 | 14:00 | Modern Steel | 0 | 1:00 | Mohastangor | 68 | 1:00
Satmosjid | 145 | 12:00 | Shahmirpur | 33 | 23:00 | Bhangura | 32 | 20:00
Tongi | 251 | 15:00 | Khagrachhari | 30 | 13:00 | Rangpur | 116 | 1:00
Kabirpur | 245 | 13:00 | Matarbari | 27 | 1:00 | Lalmonirhat | 42 | 19:30
Basundhara | 78 | 1:00 | Baroiar Hat | 48 | 19:00 | Saidpur | 88 | 15:00
Manikganj | 175 | 15:00 | Rangamati | 12 | 18:30 | Purbasadipur | 95 | 21:00
Joydevpur | 111 | 16:00 | Abul Khair 230 | 149 | 9:00 | Thakurgaon | 80 | 20:00
New Tongi | 286 | 10:00 | BSRM | 133 | 16:00 | Palashbari | 117 | 1:00
Kodda | 114 | 19:30 | GPH Ispat | 93 | 19:00 | Barapukuria | 51 | 19:30
Dhamrai | 106 | 21:00 | Agrabad | 84 | 15:00 | Panchagar | 57 | 20:00
Rajendrapur | 124 | 20:00 | Goalpara | 36 | 24:00 | Joldhaka | 56 | 20:00
Valuka | 206 | 1:00 | Central S/S | 102 | 19:00 | Kurigram | 54 | 2:00
Tangail | 209 | 19:00 | Noapara | 51 | 21:00 | Mithapukur | 45 | 23:00
Mymensing | 179 | 1:00 | Noapara | 50 | 19:30 | Mithapukur | 32 | 19:30
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-08-23 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 6:00 | 401 | 3:00 | Kaliakoir | 395 | 0.375 | 388 | 0.29167
| Bheramara | 403 | 20:00 | 396 | 19:30 | Bhulta | 387 | 0.83333 | 377 | 0.45833
| Ashuganj(N) | 392 | 18:00 | 385 | 10:00 | Gopalganj | 405 | 0.625 | 387 | 0.8125
| Payra | 413 | 7:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 227 | 18:30 | 220 | 6:00
| Ishurdi | 235 | 17:00 | 225 | 22:00 | Megnaghat | 233 | 8:00 | 229 | 10:00
| Ashuganj | 240 | 20:00 | 236 | 11:00 | Fenchuganj | 242 | 2:00 | 238 | 14:00
| Serajganj | 230 | 5:00 | 226 | 21:00 | Siddhirganj | 231 | 20:00 | 227 | 15:00
| Baghabari | 233 | 17:00 | 226 | 21:00 | Maniknagar | 230 | 20:00 | 224 | 10:00
| Barapukuria | 238 | 17:00 | 230 | 1:00 | Agargaon | 230 | 8:00 | 223 | 10:00
| Bogra | 228 | 18:00 | 217 | 1:00 | Barisal | 240 | 14:00 | 229 | 22:00
| Rajshahi | 231 | 17:00 | 220 | 15:00 | Bhola 225 MW | 243 | 8:00 | 234 | 5:00
| Khulna South | 225 | 6:00 | 209 | 15:00 | AKSML | 230 | 14:00 | 220 | 5:00
| Rampura | 230 | 23:00 | 224 | 11:00 | BSRM | 230 | 19:00 | 223 | 5:00
| Haripur | 229 | 20:00 | 223 | 10:00 | Bibiyana | 242 | 20:00 | 236 | 8:00
| Hasnabad | 228 | 19:00 | 222 | 10:00 | Bhulta | 233 | 24:00 | 226 | 11:00
| Shyampur | 233 | 7:00 | 220 | 10:00 | Ashuganj (S) | 236 | 1:00 | 234 | 10:00
| Aminbazar | 231 | 1:00 | 222 | 2:00 | Kaliakoir | 231 | 23:00 | 224 | 7:00
| Tongi | 232 | 19:30 | 222 | 7:00 | GPH | 227 | 8:00 | 222 | 7:00
| Comilla (N) | 232 | 19:30 | 227 | 7:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 19:30 | 130 | 9:00 | Madanhat | 137 | 0.29167 | 134 | 0.083333
| Munsiganj | 138 | 20:00 | 130 | 7:00 | Hathazari | 135 | 0.79167 | 131 | 0.25
| Sonargaon | 133 | 19:30 | 130 | 10:00 | Khulshi | 134 | 0.54167 | 130 | 0.66667
| Shyampur | 137 | 19:30 | 131 | 11:00 | Halishahar | 136 | 0.54167 | 131 | 0.77083
| Bhulta | 127 | 18:30 | 121 | 10:00 | Baraulia | 135 | 0.083333 | 130 | 0.29167
| Madanganj | 137 | 19:30 | 130 | 11:00 | Sikalbaha | 137 | 0.29167 | 133 | 0
| Shitalakhya | 139 | 20:00 | 130 | 10:00 | Dohazari | 132 | 0.5 | 127 | 0.77083
| Rahim steal | 134 | 18:30 | 130 | 10:00 | Cox'sbazar | 117 | 0.5 | 105 | 0.041667
| Matuail | 134 | 19:30 | 130 | 9:00 | Chandraghona | 135 | 0.041667 | 133 | 0.29167
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 134 | 0.54167 | 132 | 0.041667
| Narsinghdi | 130 | 8:00 | 124 | 1:00 | A. Khaer Stl. | 134 | 0.77083 | 130 | 0
| Haripur (SBU) | 135 | 20:00 | 130 | 10:00 | Bakulia | 137 | 0.54167 | 131 | 0.66667
| Sreenagar | 131 | 19:00 | 127 | 9:00 | Julda | 136 | 0.5 | 133 | 0.75
| Ullon | 132 | 1:00 | 126 | 11:00 | TK Chemical | 136 | 0.91667 | 132 | 0.77083
| Hasnabad | 133 | 19:00 | 129 | 10:00 | Modern Steel | 134 | 0.375 | 131 | 0.25
| Magbazar | 133 | 2:00 | 126 | 11:00 | Shahmirpur | 138 | 0.79167 | 134 | 0.20833
| Maniknagar | 134 | 1:00 | 129 | 11:00 | Khagrachhari | 134 | 0.54167 | 130 | 0.77083
| Bangabhaban | 134 | 1:00 | 129 | 11:00 | Matarbari | 114 | 0.45833 | 100 | 0.77083
| Motijheel | 134 | 1:00 | 129 | 11:00 | Baroiar Hat | 135 | 0.45833 | 132 | 0.16667
| Narinda | 134 | 1:00 | 129 | 11:00 | Rangamati | 134 | 6:00 | 132 | 7:00
| Kazla | 134 | 1:00 | 129 | 11:00 | Agrabad | 134 | 1:00 | 130 | 18:00
| Dhanmondi | 134 | 20:00 | 128 | 11:00 | Goalpara S/S | 138 | 18:00 | 126 | 0.625
| Lalbag | 132 | 2:00 | 127 | 10:00 | Khulna Central S/S | 138 | 9:00 | 125 | 0.625
| Madartek | 133 | 6:00 | 126 | 15:00 | Noapara | 135 | 10:00 | 123 | 0.625
| Dhaka University | 133 | 0:00 | 126 | 15:00 | Jessore | 130 | 5:00 | 120 | 0.54167
| Aftabnagar | 133 | 3:00 | 126 | 15:00 | Benapol | 132 | 0.20833 | 119 | 0.625
| Fatullah | 137 | 19:30 | 131 | 10:00 | Jhenida | 129 | 9:00 | 117 | 0.875
| Nawabganj | 132 | 19:30 | 126 | 10:00 | Bottail | 133 | 0.70833 | 125 | 0.8125
| Keraniganj | 133 | 20:00 | 127 | 10:00 | G.K Project | 139 | 0.375 | 134 | 0.083333
| Mirpur | 132 | 2:00 | 128 | 10:00 | Faridpur | 135 | 0.33333 | 128 | 0.875
| Kalyanpur | 133 | 3:00 | 129 | 10:00 | Rajbari | 135 | 0.29167 | 126 | 0.875
| Gulshan | 133 | 5:00 | 125 | 15:00 | Madaripur | 140 | 0.29167 | 130 | 0.875
| Uttara | 131 | 3:00 | 126 | 11:00 | Shariyatpur S/S | 138 | 6:00 | 129 | 0.8125
| Uttara New | 133 | 5:00 | 127 | 15:00 | Gopalganj | 143 | 0.33333 | 130 | 0.875
| Kamrangirchar | 133 | 3:00 | 127 | 10:00 | Bagerhat | 134 | 10:00 | 120 | 0.625
| Savar | 134 | 4:00 | 129 | 10:00 | Mongla | 134 | 18:00 | 120 | 0.625
| Bhasantec | 136 | 3:00 | 130 | 10:00 | Satkhira | 136 | 9:00 | 123 | 13:00
| Agargaon | 136 | 2:00 | 132 | 12:00 | Gallamari | 138 | 0.25 | 127 | 15:00
| Satmosjid | 136 | 20:00 | 131 | 10:00 | Magura | 129 | 17:00 | 114 | 0.875
| Tongi | 141 | 19:30 | 133 | 10:00 | Narail | 118 | 0.041667 | 114 | 0.8125
| Kabirpur | 136 | 18:00 | 132 | 15:00 | Chuadanga | 132 | 8:00 | 115 | 0.875
| Basundhara | 138 | 18:30 | 130 | 9:00 | Borguna | 135 | 10:00 | 125 | 0.83333
| Manikganj | 140 | 20:00 | 135 | 1:00 | Barisal(N) | 140 | 8:00 | 130 | 19:30
| Joydevpur | 139 | 20:00 | 134 | 9:00 | Barisal (S) | 137 | 0.33333 | 127 | 0.95833
| New Tongi | 139 | 20:00 | 131 | 9:00 | Patuakhali(S) | 136 | 0.33333 | 123 | 0.91667
| Kodda | 137 | 20:00 | 125 | 9:00 | Bhandaria | 135 | 0.70833 | 121 | 0.91667
| Dhamrai | 133 | 18:30 | 129 | 21:00 | Ishurdi | 137 | 17:00 | 132 | 13:00
| Rajendrapur | 136 | 18:30 | 124 | 10:00 | Ruppur Paromanobik | 137 | 17:00 | 131 | 21:00
| Valuka | 125 | 21:00 | 107 | 3:00 | Natore | 137 | 17:00 | 130 | 21:00
| Tangail | 141 | 11:00 | 125 | 1:00 | Bogra | 138 | 17:00 | 130 | 1:00
| Mymensing | 129 | 20:00 | 113 | 3:00 | Noagaon | 134 | 17:00 | 123 | 1:00
| Kishorganj | 129 | 13:00 | 118 | 1:00 | Rajshahi | 136 | 17:00 | 129 | 21:00
| Netrokona | 129 | 20:00 | 110 | 2:00 | Rajshahi New | 138 | 17:00 | 129 | 3:00
| Jamalpur | 138 | 19:30 | 122 | 5:00 | C.Nawabganj | 137 | 17:00 | 127 | 15:00
| Sherpur | 137 | 18:30 | 120 | 4:00 | Amnura | 138 | 17:00 | 126 | 3:00
| Srimongal | 134 | 17:00 | 130 | 13:00 | Pabna | 134 | 17:00 | 130 | 13:00
| Shahjibazar | 134 | 18:00 | 127 | 15:00 | Shahjadpur | 140 | 4:00 | 134 | 15:00
| Fenchuganj | 134 | 6:00 | 129 | 18:30 | Serajganj | 134 | 18:00 | 129 | 21:00
| Khulawara | 134 | 7:00 | 130 | 11:00 | Niyamatpur | 133 | 17:00 | 121 | 1:00
| Sylhet | 131 | 7:00 | 126 | 12:00 | Joypurhat | 135 | 17:00 | 121 | 2:00
| Chatak | 130 | 6:00 | 124 | 15:00 | Sherpur(Bogura) | 137 | 18:00 | 128 | 2:00
| Sunamganj | 129 | 8:00 | 123 | 12:00 | Mohastangor | 139 | 17:00 | 127 | 1:00
| Biani Bazar | 130 | 22:00 | 123 | 19:00 | Bangura | 137 | 17:00 | 132 | 2:00
| Comilla(s) | 129 | 6:00 | 124 | 18:30 | Rangpur | 136 | 17:00 | 122 | 1:00
| Comilla(n) | 140 | 19:30 | 136 | 5:00 | Lalmonirhat | 135 | 18:00 | 123 | 1:00
| Chandpur | 143 | 12:00 | 133 | 6:00 | Saidpur | 132 | 16:00 | 125 | 1:00
| Feni | 138 | 10:00 | 130 | 6:00 | Purbasadipur | 133 | 17:00 | 120 | 1:00
| Chowmuhani | 135 | 7:00 | 132 | 23:00 | Thakurgaon | 132 | 17:00 | 119 | 1:00
| Ashuganj | 137 | 20:00 | 134 | 22:00 | Palashbari | 136 | 17:00 | 125 | 21:00
| Daudkandi | 138 | 19:00 | 130 | 10:00 | Barapukuria | 138 | 17:00 | 130 | 1:00
| B.Baria | 131 | 21:00 | 127 | 22:00 | Panchagar | 133 | 17:00 | 118 | 2:00
| Ramganj | 137 | 10:00 | 130 | 7:00 | Joldhaka | 133 | 0.70833 | 118 | 0.041667
| Chaddagram | 137 | 19:30 | 130 | 6:00 | Kurigram | 136 | 0.70833 | 124 | 0.041667
| PHP | 136 | 11:00 | 130 | 5:00 | Mithapukur | 137 | 0.70833 | 125 | 0.083333
| Kochua | 138 | 17:00 | 135 | 19:30
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-08-23
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 302 | 8544 | 3628 | 12172 |  |  |  | QF-LDC-11
0:30 | 368 | 8653.5 | 3604.5 | 12258 | Date: | 2021-08-23
1:00 | 434 | 8763 | 3581 | 12344
1:30 | 423 | 8672.5 | 3530.5 | 12203
2:00 | 412 | 8582 | 3480 | 12062
2:30 | 433 | 8451.5 | 3401 | 11852.5 | [5 empty] | Gen. at Eve. Peak | 12491 | 12491 MW (21:00 )
3:00 | 454 | 8321 | 3322 | 11643 | [6 empty] | 21:00
3:30 | 413 | 8174.5 | 3311.5 | 11486 | [5 empty] | Gen. at Day Peak | 11327 | 11327 MW (12:00 )
4:00 | 372 | 8028 | 3301 | 11329 | [6 empty] | 12:00
4:30 | 357 | 8055 | 3269 | 11324 | [5 empty] | Highest Generation | 12491
5:00 | 342 | 8082 | 3237 | 11319 | [6 empty] | 21:00
5:30 | 283 | 7862.5 | 3100.5 | 10963
6:00 | 224 | 7643 | 2964 | 10607
6:30 | 177 | 7452.5 | 2922.5 | 10375
7:00 | 130 | 7262 | 2881 | 10143
7:30 | 126 | 7250.5 | 2870.5 | 10121
8:00 | 122 | 7239 | 2860 | 10099
8:30 | 78 | 7340 | 2885.5 | 10225.5
9:00 | 34 | 7441 | 2911 | 10352
9:30 | 97 | 7622.5 | 2975.5 | 10598
10:00 | 160 | 7804 | 3040 | 10844
10:30 | 99 | 7913 | 3021.5 | 10934.5
11:00 | 38 | 8022 | 3003 | 11025
11:30 | 47 | 8130 | 3046 | 11176
12:00 | 56 | 8238 | 3089 | 11327
12:30 | 120 | 8319.5 | 3126 | 11445.5
13:00 | 184 | 8401 | 3163 | 11564
13:30 | 191 | 8383.5 | 3152.5 | 11536
14:00 | 198 | 8366 | 3142 | 11508
14:30 | 167 | 8559 | 3156.5 | 11715.5
15:00 | 136 | 8752 | 3171 | 11923
15:30 | 69 | 8688 | 3133 | 11821
16:00 | 2 | 8624 | 3095 | 11719
16:30 | 133 | 8335 | 3056 | 11391
17:00 | 264 | 8046 | 3017 | 11063
17:30 | 225 | 7852 | 2942.5 | 10794.5
18:00 | 186 | 7658 | 2868 | 10526
18:30 | 250 | 8184.5 | 3167.5 | 11352
19:00 | 314 | 8711 | 3467 | 12178
19:30 | 436 | 8783 | 3656 | 12439
20:00 | 504 | 8789 | 3663 | 12452 |  |  |  | Executive Engineer
20:30 | 502 | 8797 | 3674.5 | 12471.5 |  |  |  | Network Operation Division
21:00 | 500 | 8805 | 3686 | 12491
21:30 | 502 | 8806 | 3669 | 12475
22:00 | 504 | 8807 | 3652 | 12459 |  |  |  |  | Page 6 of 7
22:30 | 469 | 8706 | 3638.5 | 12344.5
23:00 | 434 | 8605 | 3625 | 12230
23:30 | 368 | 8574.5 | 3626.5 | 12201
24:00 | 302 | 8544 | 3628 | 12172
12491 MW (21:00 )
11327 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-08-23 |  | Energy | 279620457
[11 empty] | 2021-08-23 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4183 | 679 | 1857 | 4060 | 722 | 121 | 556 | 0 | 132 | 0
0:30 | 4457 | 679.5 | 1830 | 3921.5 | 703.5 | 122.5 | 482 | 0 | 131 | 0 | Date: | 2021-08-23
1:00 | 4731 | 680 | 1803 | 3783 | 685 | 124 | 408 | 0 | 130 | 0
1:30 | 4723.5 | 680.5 | 1814.5 | 3739 | 690 | 124 | 301.5 | 0 | 130 | 0 | [7 empty] | Total Energy | 279.6205 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4716 | 681 | 1826 | 3695 | 695 | 124 | 195 | 0 | 130 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4725 | 681 | 1825 | 3548 | 675 | 124 | 147.5 | 0 | 127 | 0 | [7 empty] | Energy Requirement | 279.6205
3:00 | 4734 | 681 | 1824 | 3401 | 655 | 124 | 100 | 0 | 124 | 0
3:30 | 4734.5 | 681 | 1833 | 3286.5 | 655 | 122 | 100 | 0 | 74 | 0 | [6 empty] | Shortage
4:00 | 4735 | 681 | 1842 | 3172 | 655 | 120 | 100 | 0 | 24 | 0
4:30 | 4725.5 | 678 | 1850 | 3135.5 | 645 | 120 | 100 | 0 | 70 | 0
5:00 | 4716 | 675 | 1858 | 3099 | 635 | 120 | 100 | 0 | 116 | 0
5:30 | 4713 | 675 | 1795.5 | 2837.5 | 608 | 120 | 100 | 0 | 113 | 1
6:00 | 4710 | 675 | 1733 | 2576 | 581 | 120 | 100 | 0 | 110 | 2
6:30 | 4729 | 674.5 | 1700 | 2384 | 571 | 120.5 | 82 | 0 | 108 | 6 |  |  |  |  | Coal
7:00 | 4748 | 674 | 1667 | 2192 | 561 | 121 | 64 | 0 | 106 | 10
7:30 | 4668.5 | 677 | 1644 | 2261 | 557.5 | 121 | 64 | 0 | 107 | 21 |  |  |  | Oil |  |  |  | ,
8:00 | 4589 | 680 | 1621 | 2330 | 554 | 121 | 64 | 0 | 108 | 32
8:30 | 4477 | 679.5 | 1569 | 2645.5 | 529.5 | 121.5 | 64 | 0 | 103 | 36.5
9:00 | 4365 | 679 | 1517 | 2961 | 505 | 122 | 64 | 0 | 98 | 41
9:30 | 4351.5 | 679 | 1596.5 | 3104.5 | 495.5 | 122.5 | 103 | 0 | 106 | 39.5
10:00 | 4338 | 679 | 1676 | 3248 | 486 | 123 | 142 | 0 | 114 | 38
10:30 | 4295 | 679 | 1644 | 3379 | 495.5 | 123 | 152 | 0 | 114 | 53
11:00 | 4252 | 679 | 1612 | 3510 | 505 | 123 | 162 | 0 | 114 | 68
11:30 | 4218.5 | 679.5 | 1622.5 | 3582 | 509 | 120 | 245.5 | 0 | 117 | 82
12:00 | 4185 | 680 | 1633 | 3654 | 513 | 117 | 329 | 0 | 120 | 96
12:30 | 4142.5 | 680 | 1619.5 | 3809.5 | 533.5 | 118.5 | 337.5 | 0 | 119 | 85.5
13:00 | 4100 | 680 | 1606 | 3965 | 554 | 120 | 346 | 0 | 118 | 75
13:30 | 4100 | 680 | 1606 | 3965 | 554 | 120 | 346 | 0 | 118 | 75
14:00 | 4100 | 680 | 1606 | 3965 | 554 | 120 | 346 | 0 | 118 | 75
14:30 | 4126.5 | 679.5 | 1636.5 | 4087.5 | 563.5 | 118.5 | 355 | 0 | 119 | 57.5
15:00 | 4153 | 679 | 1667 | 4210 | 573 | 117 | 364 | 0 | 120 | 40
15:30 | 4099 | 679 | 1696 | 4136.5 | 579 | 115 | 366.5 | 0 | 118 | 32
16:00 | 4045 | 679 | 1725 | 4063 | 585 | 113 | 369 | 0 | 116 | 24
16:30 | 4045 | 679.5 | 1673 | 3799 | 574.5 | 110.5 | 373.5 | 0 | 116 | 20
17:00 | 4045 | 680 | 1621 | 3535 | 564 | 108 | 378 | 0 | 116 | 16
17:30 | 4036.5 | 680 | 1611.5 | 3288.5 | 564.5 | 110.5 | 375 | 0 | 119 | 9
18:00 | 4028 | 680 | 1602 | 3042 | 565 | 113 | 372 | 0 | 122 | 2
18:30 | 4061.5 | 679.5 | 1657.5 | 3619.5 | 594.5 | 115.5 | 491 | 0 | 132 | 1
19:00 | 4095 | 679 | 1713 | 4197 | 624 | 118 | 610 | 0 | 142 | 0
19:30 | 4121 | 679 | 1750 | 4326 | 705 | 118 | 606 | 0 | 134 | 0
20:00 | 4107 | 679 | 1718 | 4385 | 714 | 118 | 597 | 0 | 134 | 0
20:30 | 4104 | 679 | 1756 | 4366 | 718.5 | 119 | 595 | 0 | 134 | 0
21:00 | 4101 | 679 | 1794 | 4347 | 723 | 120 | 593 | 0 | 134 | 0
21:30 | 4097.5 | 679.5 | 1820.5 | 4308 | 723.5 | 120 | 593 | 0 | 133 | 0
22:00 | 4094 | 680 | 1847 | 4269 | 724 | 120 | 593 | 0 | 132 | 0
22:30 | 4103.5 | 679.5 | 1838 | 4164.5 | 722.5 | 120.5 | 582 | 0 | 134 | 0
23:00 | 4113 | 679 | 1829 | 4060 | 721 | 121 | 571 | 0 | 136 | 0
23:30 | 4148 | 679 | 1843 | 4060 | 721.5 | 121 | 563.5 | 0 | 134 | 0 | Max Temp. in Dhaka |  | 33.0° C
24:00 | 4183 | 679 | 1857 | 4060 | 722 | 121 | 556 | 0 | 132 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-08-23
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 64 | 64 | 64 | 60 | 60 | 60 | 61 | 61 | 62 | 63 | 63 | 57 | 60 | 57 | 57 | 53 | 48 | 53 |  | 58 | 58 | 58 | 60 | 60 | 61 | 61 | 1371191
2 | Karnaphuli Hydro PP Unit-4 & 5 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 |  | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 1460000
3 | Chattogram TPP-1 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2400000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 25 | [7 empty] | 6 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 417445
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 9 | 5 | 6 | 7 | 19 | 17 | 17 | 2 | 4 | 3 | 0 | [8 empty] | 96525
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 78 | 17 | [9 empty] | 85 | 85 | 85 | 85 | 68 | 68 | 85 |  | 85 | 85 | 85 | 85 | 85 | 68 | 68 | 1130095
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2535843
| Daudkandi 200 MW PP (B.Trac) | [11 empty] | 25 | 100 | 100 | 200 | 200 |  |  |  | 200 | 200 | 200 | 200 | 200 | 115 | 50 | 1598208
14 | Titas 50 MW Peaking PP | [11 empty] | 43 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 659992
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 332 | 332 | 332 | 328 | 327 | 331 | 327 | 290 | 250 | 328 | 270 | 329 | 333 | 321 | 319 | 318 | 320 | 320 |  | 332 | 335 | 332 | 335 | 329 | 325 | 335 | 7751422
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 278 | 280 | 145 | 145 | 14 | 14 | 14 | 67 | 127 | 240 | 255 | 260 | 278 | 275 | 275 | 278 | 278 |  | 278 | 278 | 280 | 280 | 281 | 281 | 281 | 5356907
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 70 | [13 empty] | 110 | 1354500
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7135527
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 70 | 70 | 70 |  | 70 | 70 | 70 | 70 | 70 | 70 | 70 | 1843312
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 19 | 19 | 19 |  | 19 | 20 | 20 | 20 | 23 | 23 | 22 | 22 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 336384
33 | Ashuganj 225 MW CCPP | 195 | 190 | 207 | 208 | 209 | 211 | 197 | 186 | 190 | 173 | 182 | 183 | 160 | 162 | 152 | 164 | 180 | 189 |  | 185 | 188 | 187 | 175 | 170 | 176 | 152 | 4427000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 295 | 290 | 290 | 330 | 295 | 320 | 290 | 315 | 295 | 295 | 295 | 325 | 295 | 295 | 295 |  | 295 | 295 | 295 | 295 | 305 | 305 | 290 | 7311000
| Ashuganj 450 MW CCPP(North) | 260 | 260 | 260 | 270 | 265 | 260 | 300 | 260 | 290 | 265 | 285 | 260 | 260 | 265 | 300 | 265 | 265 | 265 |  | 265 | 265 | 265 | 265 | 275 | 295 | 280 | 6806500
35 | Ashuganj 55 MW PP (Precision) | 40 | 40 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 391200
36 | Chandpur 150 MW CCPP | 135 | 136 | 136 | 137 | 138 | 137 | 138 | 135 | 139 | 136 | 137 | 137 | 135 | 132 | 138 | 135 | 136 | 137 |  | 136 | 138 | 134 | 135 | 138 | 138 | 135 | 3268790
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 393 | 393 | 393 | 393 | 393 | 392 | 396 | 397 | 358 | 353 | 376 | 389 | 396 | 395 | 397 | 398 | 396 | 362 |  | 364 | 383 | 392 | 394 | 395 | 395 | 397 | 9440000
40 | Meghnaghat 450 MW CCPP(MPL) | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 260 | 260 | 260 | 270 | 270 | 270 | 270 | 6052750
41 | Haripur 360MW CCPP(HPL) | 181 | 188 | 195 | 202 | 201 | 202 | 176 | 162 | 157 | 145 | 137 | 137 | 137 | 170 | 175 | 178 | 178 | 182 |  | 184 | 190 | 190 | 195 | 195 | 195 | 214 | 4296000
42 | RPCL 210MW CCPP | 99 | 100 | 100 | 100 | 100 | 100 | 99 | 100 | 98 | 98 | 82 | 84 | 70 | 70 | 85 | 98 | 99 | 98 |  | 98 | 101 | 102 | 102 | 102 | 102 | 102 | 2218160
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 3 | 17 | 23 | 25 | 36 | 32 | 25 | 16 | 22 | 10 | 9 | 1 | [8 empty] | 211020
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 44 |  | 44 | 44 | 44 | 43 | 43 | 43 | 43 | 1035000
45 | Fenchugonj CCPP Phase-2 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 42 |  | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 1004400
46 | Shajibazar 330 MW CCPP | 273 | 272 | 272 | 271 | 271 | 270 | 269 | 271 | 270 | 268 | 267 | 264 | 236 | 235 | 230 | 233 | 234 | 233 |  | 234 | 236 | 235 | 236 | 236 | 234 | 236 | 5749000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 84 | 84 | 84 | 84 | 84 | [9 empty] | 20 | 81 | 83 | 84 |  | 84 | 84 | 84 | 84 | 81 | 81 | 81 | 1147200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 212 | 205 | 205 | 205 | 205 | 205 | 205 | 167 | 20 | [16 empty] | 0 | 1822080
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 392000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9 | 9 | 10 | 10 | 10 | 10 | 10 | 10 | 10 |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 245700
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 3 | 8 | 8 | 8 |  | 8 | 8 | 8 |  |  |  | 0 | 161328
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 14 | 47 | 47 | 50 | 47 | 50 | 50 | 53 | 53 | 53 | 53 | 53 |  | 53 | 50 | 53 | 53 | 53 | 53 | 53 | 1197600
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 561432
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 280 | 290 | 290 | 275 | 300 | 290 | 280 | 300 | 295 | 300 | 310 | 280 | 310 | 300 | 270 | 270 |  | 280 | 280 | 265 | 280 | 300 | 290 | 300 | 7115000
| Bibiyana South 400 MW | 351 | 350 | 351 | 350 | 350 | 350 | 350 | 351 | 350 | 351 | 350 | 217 | 259 | 260 | 260 | 260 | 250 | 260 |  | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 7257700
58 | Nababganj 55 MW PP (Southern power ) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1326092
59 | Tangail Palli Power Gen 22 MW | 24 | 24 | 22 | 22 | 24 | 24 | 24 | 22 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 588480
60 | Barabkunda 22 MW PP (Regent) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 462192
61 | Narshingdi 22 MW PP (Doreen) | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 17 | 17 | 17 | 17 | 17 |  |  | 21 |  |  |  |  | 21 | 21 | 21 | 21 | 401472
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 16 | 16 | 16 | 16 | 16 | 16 | 19 | 19 | 19 | 21 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 428400
63 | Impoprt (Tripura) | 130 | 130 | 124 | 24 | 116 | 110 | 106 | 108 | 98 | 114 | 114 | 120 | 118 | 124 | 120 | 116 | 116 | 122 |  | 142 | 134 | 134 | 134 | 132 | 136 | 132 | 2978880
64 | Malancha, Ctg. EPZ (United) | 37 | 37 | 38 | 38 | 39 | 39 | 30 | 7 | 2 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 2 | 6 |  | 2 | 4 | 8 | 24 | 34 | 36 | 36 | 423360
65 | Feni 22MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  |  |  | 16 | 16 | 18 | 18 | 18 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 330156
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255060
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 19 | 33 | 33 | 33 | 33 |  | 33 | 33 | 30 | 25 | 17 | 33 | 33 | 732800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 6 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 505042
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 21 | 21 | 21 | 20 | 20 | 20 | 20 | 20 |  | 20 | 22 | 18 | 22 | 22 | 22 | 22 | 475560
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 823000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 811300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 46 | 17 |  |  |  |  | 17 | 50 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 52 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1922040
| Chowmuhani 113 MW | 107 | 107 | 107 | 106 | 108 | 107 | 55 | 77 | 107 | 105 | 103 | 99 | 102 | 98 | 99 | 104 | 104 | 108 |  | 112 | 114 | 114 | 114 | 115 | 107 | 96 | 2493960
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 108 | 54 | 78 | 144 | 144 | 158 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3692160
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 51 | [7 empty] | 9 | 23 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 51 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 786240
79 | Kodda 150MW PP | 150 | 115 | 100 | 100 | 100 | 100 | 64 | 64 | 64 | 142 | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 115 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 3060960
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 52 | 25 | 8 | 8 | 8 | 8 | 40 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1052333
| Gazipur 100 MW PP | 105 | 105 | 34 | 17 | 17 | 17 | 17 | 17 | 51 | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2070000
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 0 | 1 | 3 | 5 | 2 | 2 | 0 | 1 | 1 | [9 empty] | 20760
| Jodiac Power | [25 empty] | 0 | 0
| Karnaphuli Power Ltd. | 110 | 104 | 105 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2724860
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [25 empty] | 0 | 0
86 | Meghnaghat CCPP ( Summit) | 260 | 250 | 245 | 275 | 265 | 290 | 290 | 240 | 275 | 255 | 270 | 275 | 260 | 265 | 275 | 270 | 235 | 265 |  | 260 | 265 | 250 | 270 | 290 | 300 | 288 | 6371753
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 90 | 90 | 90 | 90 | 91 | 85 | 17 | 32 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 91 | 94 | 2042880
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 92 | 92 | 10 | 10 | 50 | 50 | 50 | 30 | 60 | 82 | 92 | 92 | 92 | 92 | 50 |  | 100 | 100 | 100 | 100 | 100 | 93 | 93 | 1798680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 821736
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 64 | 50 | 50 | 50 | 31 | 32 | 75 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 98 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2133792
95 | Patenga 50MW PP (Baraka) | 50 | 25 | 24 | [7 empty] | 8 | 38 | 44 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 764160
96 | Chattogram 108 MW PP (ECPV) | 93 | 96 | 96 | 96 | 96 | 90 | 88 | 89 | 89 | 89 | 82 | 81 | 85 | 68 | 54 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 51 | 51 | 44 | 1745280
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 33 | 40 | 40 | 40 | 40 | 40 | 40 | 29 | 25 | 40 | 28 | 28 | 30 |  | 35 | 40 | 40 | 40 | 40 | 40 | 40 | 925213
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1328124
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 | 163 | 130 | 163 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 155 | 155 | 155 | 155 | 155 | 140 | 3520881
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 0 | 1 | 1 | 3 | 1 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 10000
103 | Kamalaghat 54 MW PP(Banco Energy) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1027440
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 52 | 53 | 175 | 175 |  |  |  | 207 | 155 | 154 | 103 | 56 | 23 | 0 | 869224
105 | Bramhangoan 100 MW PP (Aggreko) | [11 empty] | 25 | 100 | 70 | 90 | 60 |  |  |  | 100 | 100 | 100 | 70 | 70 | 30 | 0 | 744558
106 | Mymensingh 200 MW PP (United) | 166 | 166 | 157 | 156 | 157 | 167 | 166 | 166 | 166 | 165 | 164 | 164 | 163 | 163 | 152 | 152 | 152 | 100 |  | 141 | 140 | 140 | 140 | 140 | 140 | 146 | 3691200
112 | Aurahati 100MW PP (Aggreko) | [11 empty] | 27 | 100 | 100 | 100 | 100 | 50 |  |  | 100 | 101 | 100 | 100 | 101 | 52 | 54 | 1071621
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 149 | 149 | 149 | 149 | 147 | 141 | 142 | 130 | 127 | 135 | 148 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 141 | 138 | 3516050
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2346240
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 120 | 51 | 62 | 174 | 197 | 197 | 197 | 197 | 197 | 196 | 187 | 155 | 100 |  | 119 | 150 | 185 | 200 | 200 | 200 | 200 | 4276320
117 | Ashuganj 150MW PP (Midland) | 122 | 120 | 127 | 128 | 127 | 127 | 128 | 125 | 125 | 123 | 127 | 133 | 133 | 133 | 135 | 130 | 127 | 132 |  | 128 | 128 | 127 | 133 | 133 | 134 | 135 | 3102909
118 | Bibiyana-III 400 MW CCPP | 402 | 400 | 402 | 401 | 402 | 402 | 402 | 401 | 352 | 365 | 395 | 367 | 367 | 367 | 383 | 365 | 367 | 330 |  | 400 | 402 | 401 | 401 | 401 | 401 | 401 | 9337000
| Jamalpur 115 MW PP (United) | 115 | 115 | 106 | 106 | 115 | 115 | 115 | 115 | 115 | 115 | 106 | 106 | 115 | 115 | 115 | 115 | 115 | 115 |  | 111 | 111 | 112 | 115 | 111 | 111 | 112 | 2684400
| Anwara 300 MW PP (United) | 107 | 107 | 107 | 107 | 107 | 107 | 53 | 85 | 90 | 122 | 141 | 125 | 125 | 125 | 125 | 125 | 125 | 68 |  | 121 | 124 | 125 | 125 | 125 | 125 | 125 | 2677200
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2358720
| Anlima Energy Ltd. | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 102 | 96 | 97 | 97 | 97 | 96 | 97 |  | 116 | 116 | 116 | 115 | 114 | 114 | 114 | 2665909
| Bhairob 54.5 MW | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 29 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 668880
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 3 | 3 | 9 | 4 | 18 | 35 | 23 | 26 | 13 | 6 | 1 | 0 | [8 empty] | 135729
120 | Eastern Zone Total | 8763 | 8582 | 8321 | 8028 | 8082 | 7643 | 7262 | 7239 | 7441 | 7804 | 8022 | 8238 | 8401 | 8366 | 8752 | 8624 | 8046 | 7658 |  | 8711 | 8783 | 8789 | 8805 | 8807 | 8605 | 8544 | 199376671
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 13 | [9 empty] | 2 | 4 | 5 | 9 | 14 | 17 | 17 | 18 |  | 22 | 25 | 25 | 24 | 24 | 18 | 18 | 229900
| Khulna 225 MW CCPP | [19 empty] | 65 | 65 | 55 | 55 | 55 | 55 | 55 | 359040
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 70 | 35 | 50 | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 70 |  | 85 | 105 | 105 | 105 | 105 | 105 | 105 | 2332320
130
131
132 | United Payra Power Ltd. | 35 | 35 | 17 | [16 empty] | 12 | 17 | 17 | 17 | 17 | 17 | 17 | 198000
133 | Bhola Nutan Biddut BD LTD (GAS) | 218 | 218 | 218 | 221 | 222 | 223 | 220 | 185 | 180 | 218 | 218 | 214 | 214 | 215 | 215 | 217 | 185 | 219 |  | 219 | 216 | 201 | 216 | 218 | 219 | 219 | 5169355
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 271174
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 86 | 87 | 87 | 88 | 88 | 87 | 87 | 83 | 88 | 88 | 88 | 89 | 75 | 88 |  | 88 | 88 | 87 | 88 | 88 | 87 | 87 | 2111253
140 | Bhola 33 MW PP (Venture) | 33 | 33 | 32 | 30 | 30 | 26 | 23 | 21 | 20 | 20 | 18 | 21 | 22 | 24 | 25 | 24 | 23 | 22 |  | 33 | 33 | 33 | 34 | 34 | 34 | 34 | 656101
141 | Noapara 100 MW PP (Bangla Trac) | 40 | 40 | [7 empty] | 10 | [9 empty] | 33 | 100 | 100 | 100 | 100 | 100 | 100 | 704640
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 680 | 681 | 681 | 681 | 675 | 675 | 674 | 680 | 679 | 679 | 679 | 680 | 680 | 680 | 679 | 679 | 680 | 680 |  | 679 | 679 | 679 | 679 | 680 | 679 | 679 | 16405818
147 | Bheramara 410 MW CCPP | 315 | 315 | 313 | 310 | 305 | 305 | 300 | 300 | 295 | 275 | 200 | 250 | 250 | 245 | 245 | 245 | 245 | 240 |  | 240 | 240 | 235 | 230 | 230 | 220 | 225 | 6544224
148 | Payra 1320 MW | 530 | 540 | 500 | 500 | 480 | 430 | 410 | 400 | 350 | 330 | 350 | 360 | 400 | 400 | 420 | 430 | 410 | 410 |  | 470 | 550 | 560 | 570 | 570 | 570 | 570 | 12009700
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 155 | 155 | 155 | 155 | 155 | 151 | 151 | 154 | 155 | 156 | 155 | 153 | 154 | 152 | 153 | 155 | 154 | 155 |  | 154 | 155 | 154 | 153 | 154 | 151 | 152 | 3776700
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | [18 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 309136
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 1 | 2 | 0 | 0 | 3 | 4 | 5 | 1 | 1 | 1 | 0 | [8 empty] | 20400
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 176 | 176 | 176 | 174 | 172 | 172 | 172 | 167 | 169 | 163 | 163 | 175 | 170 | 164 | 161 | 156 | 155 | 159 |  | 167 | 163 | 163 | 158 | 151 | 149 | 149 | 4185127
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 204 | 203 | 203 | 203 | 200 | 198 | 194 | 191 | 188 | 198 | 194 | 188 | 184 | 180 | 174 | 170 | 170 | 170 |  | 170 | 164 | 163 | 160 | 155 | 151 | 149 | 4618055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 388 | 394 | 400 | 400 | 415 | 391 | 415 | 385 | 361 | 412 | 419 | 398 | 410 | 398 | 407 | 410 | 376 | 307 |  | 397 | 387 | 378 | 392 | 416 | 405 | 419 | 9537891
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 25 | [11 empty] | 9 | 9 | 18 | 37 | 46 | 46 |  | 46 | 38 | 37 | 37 | 37 | 37 | 37 | 421718
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 18 | 18 | 19 | 21 | 21 | 21 | 21 | 12 | 20 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 486000
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240968
165 | Amnura 50 MW PP(Sinha) | [25 empty] | 0 | 0
166 | Katakhali 50 MW PP (Northern) | [25 empty] | 0 | 0
167 | Katakhali 50 MW Peaking PP | 6 | [18 empty] | 30 | 30 | 32 | 30 | 30 | 30 | 15 | 158788
168 | Santahar 50 MW Peaking PP | [17 empty] | 11 |  | 24 | 25 | 25 | 25 | 25 | 25 | 25 | 192647
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 52 | 52 | 1108800
170 | Chapainawabganj 100 MW Peaking PP | 93 | 63 | [8 empty] | 10 | 47 | 47 | 47 | 47 | 47 | 47 | 47 |  | 95 | 95 | 95 | 94 | 94 | 95 | 95 | 1062176
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 50 | 50 | 50 | 50 |  |  |  | 137561
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 43 | 101 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 35 |  | 48 | 75 | 113 | 113 | 113 | 113 | 113 | 2435520
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 50 | 50 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 35 |  | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 2314656
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 70 | 34 | 58 | 100 | 100 | 96 | 100 | 107 | 107 | 106 |  | 24 | 70 |  | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 2234361
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 2 | 1 | 1 | 1 | 1 | [8 empty] | 11757
178
178