## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-07 | Tuesday
|  |  | Date (day): | 2021-09-07 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13380.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14395 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-06 | 2021-09-07 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint. |  | 2021-08-16
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 203 | 203 | 203 | 203 |  | 162 | ST under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 365 | 363 | 360 | 360 | 52 |  | Gas shortage |  | 2021-09-02
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 204 | 180 | 220 | 220 | 140 |  | Dirty Gas
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 320 | 320 | 320 | 320 | 130 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 295 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 40 | 41 | 41 |  | 14 | Engine problem
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 39 | 60 | 65 | 65 |  | 35 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 18 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 260 | 270 | 335 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 64 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 133 | 32 | 133 | 16 |  | Fuel shortage
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 37 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 53 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 17 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 300 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 200 | 230 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 92 | 94 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 99 | 100 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 132 | 116 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 53 | 90 | 90 | 90 |  |  | Engine problem |  | 2021-08-31
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 74 | 75 | 95 | 95 |  | 9 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 36 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 3266 | 3484 | 3346 | 3738 | 1005 | 925
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 25 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 48 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 105 | 145 | 145 | 145 | 85 |  | Low water level & Unit-3 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint |  | 2021-08-11
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 71 | 71 | 89 | 89
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 80 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 10 | 9 | 5 | 10
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 6 | 90 | 50 | 95 | 13 |  | Fuel shortage
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 0 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 285 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 104 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 80 | 100 | 80 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 116 | 114 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1218 | 1458 | 1474 | 1519 | 238 | 490
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 181 | 207 | 210 | 210 | 11 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 300 | 330 | 30 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 300 | 300 | 330 | 30 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem |  | 2021-10-15
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 20 | 20 | 5 | 5 | 50 |  | Gas shortage
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem |  | 2021-09-06
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 132 | 138 | 142 | 145 |  | 5 | Engine problem |  | 2021-08-31
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 141 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 190 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 122 | 148 | 138 | 163
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 43 | 43 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 18 | 19 | 20 | 20
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 200 | 150 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 98 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 98 | 98 | 98 |  | 15 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 18 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1984 | 2035 | 1951 | 2207 | 706 | 117
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 108 | 119 | 135 | 135 | 67 |  | Gas shortage |  | 2021-09-01
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 0 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 37 | 184 | 175 | 190 |  | 10 | Engine problem |  | 2021-09-13
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 38 | 115 | 115 | 115 |  |  |  |  | 2021-09-13
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 23 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 18 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 253 | 471 | 527.6 | 491 | 67 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 44 | 44 |  | 26 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 41 | 41 | 42 | 42 |  | 48 | GT-4 under S/D
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 158 | 160 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 50 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 5 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 44 | 81 | 84 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 2021-11-03
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 228 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 320 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 315 | 315 | 315
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 10 | 10
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 325 | 325 | 325 | 325
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1644 | 1761 | 1813 | 1813 | 236 | 174
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 718 | 717 | 729 | 729
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 26 |  | 28 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 40 | 158 | 0 | 158
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 60 |  | 49 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 335 | 260 | 260 | 260 | 150 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 41 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 88 | 88 | 88 | 88 |  | 17 | Engine problem |  | 2021-08-31
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1222 | 1349 | 1227 | 1521 | 150 | 94
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 20 | 29 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 88 | 88 | 88 |  | 106 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 61 | 11 | 11 | 11 | 84 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 380 | 520 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 200 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 676 | 919 | 1234 | 1234 | 84 | 106
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 43 | 50 |  | 2
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 39 | 40 | 42 |  | 29 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 35 | 35 | 35 |  | 15 | Engine problem
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 0 | 0 | 0 | 50 |  | Fuel shortage
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 30 | 30 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 120 | 0 | 0 | 0 | 210 |  | Gas shortage & ST Under maint.
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 181 | 163 | 200 | 200 | 20 |  | Gas shortage |  | 30-08-21
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 177 | 182 | 200 | 200 | 20 |  | Gas shortage
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 6 | 410 | 410 | 410 |  | 4 | Under maint. |  | 2021-06-09
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 18 | 0 | 33 |  | 17 | Engine problem |  | 15-09-2021
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 18 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 25 | 25 | 25 | 25 | 27 |  | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 85 | 84 | 85 |  |  | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 100 | 50 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 110 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 4 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 900 | 1342 | 1532 | 1579 | 497 | 77
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint. |  | 2021-05-11
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 152 | 150 | 155 | 155 | 119 |  | Coal Shortage
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 99 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 258 | 263 | 276 | 293 | 119 | 185
|  | Total |  |  |  |  | 22031 | 21180 | 11421 | 13082 | 13380.6 | 14395 | 3102 | 2255
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10833.4497 | 12409 | 12692.2386 | 13654.4531
| A. |  | 2021-09-06 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 13082 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9847 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13082 | MW
| 3 | Day peak Generation : |  |  | 11421 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12409 | MW
| 4 | Evening peak Generation : |  |  | 13082 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 278.8316 | MKWHr | By Solar | 0.74498 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 137.6218 | MKWHr |  | By Oil: | 101.7799 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 15.7086 | MKWHr |  | By Hydro: | 2.9091 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3102 | MW | Dhaka | 4547 | 4547 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2255 | MW | Chittagong | 1236 | 1236 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5357 | MW | Khulna | 1534 | 1534 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1094.94 | MMCFD |  |  | Rajshahi | 1337 | 1337 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 138869673.618 | ii) Oil : | Taka | 839449674.68 | Comilla | 1203 | 1203 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 72844060 | Total | Taka | 1051163408.298 | Mymensingh | 962 | 962 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.1725 | MKWHr. | Sylhet | 475 | 475 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -332 | MW (E to W) at | 19:30 | hrs | Barisal | 345 | 345 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -482 | MW at | 1:00 | hrs | Rangpur | 770 | 770 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 34.8° C |  |  | Total | 12409 | 12409 |  | 0
| B. |  | 2021-09-07 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 34.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14395 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1095 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 283.478 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9634 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.336 | MKWHr. | ii) HVDC Flow at Peak Time |  | 717 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.7312 | MKWHr. | iii) Maximum HVDC Flow : |  | 718 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 103.2 |  | (b) Today: | 103.93 |  | (c) Rule Curve: |  | 100.38
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-06
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 339 | 192 |  | 0 | 280 | 285 | 0 | 0 | 41 | 250 | 0 | 0 | 0 | 50 | 82 | 29 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 24 | 33 | 0 | 17 | 0 | 40 | 65 | 0 | 120 | 26 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 80 | 97 | 50 | 19 | 36 | 0 | 0 | 0 | 270 | 260 | 215 | 8 | 140 | 23 | 30 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 25 | 0 | 90 | 135 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 162 | 0 | 44 | 0 | 213 | 0 | 0 | 0 | 270 | 24 | 0 | 0 | 300 | 12 | 0 | 111 | 0 | 132 | 0 | 76 | 200 | 137 | 316 | 77 | 52 | 71 | 0 | 111 | 54 | 110 | 114 | 97 | 80 | 320 | 95 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 350 | 0 | 0 | 60 | 0 | 0 | 20 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 30 | 84 | 35 | 0 | 15 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 151 | 12 | 0 | 140 | 0 | 190 | 0 | 12 | 100 | 186 | 0 | 0 | 88 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 223 | 0 | 63 | 0 |  | 7666 | 3719 | 11385 | 4193 | 717 | 1359 | 3751 | 721 | 105 | 449 | 90 | 0 | 0 | 103
2:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 359 | 200 |  | 0 | 280 | 275 | 0 | 0 | 41 | 280 | 0 | 0 | 0 | 48 | 82 | 0 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 25 | 24 | 33 | 17 | 16 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 15 | 0 | 85 | 80 | 92 | 32 | 19 | 38 | 0 | 0 | 0 | 270 | 260 | 215 | 8 | 140 | 23 | 30 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 17 | 0 | 86 | 141 | 8 | 0 | 0 | 43 | 41 | 47 | 0 | 130 | 161 | 0 | 44 | 0 | 213 | 0 | 0 | 0 | 280 | 8 | 5 | 0 | 300 | 158 | 0 | 112 | 0 | 132 | 0 | 76 | 200 | 135 | 316 | 77 | 53 | 71 | 0 | 107 | 54 | 104 | 114 | 92 | 80 | 320 | 95 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 350 | 0 | 0 | 100 | 0 | 0 | 20 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 30 | 84 | 35 | 0 | 15 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 141 | 0 | 190 | 0 | 12 | 100 | 184 | 0 | 0 | 88 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 222 | 0 | 63 | 0 |  | 7772 | 3726 | 11498 | 4224 | 717 | 1378 | 3809 | 702 | 105 | 477 | 86 | 0 | 0 | 103.04
3:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 357 | 202 |  | 0 | 280 | 235 | 0 | 0 | 41 | 280 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 0 | 54 | 37 | 0 | 0 | 25 | 24 | 33 | 33 | 17 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 20 | 0 | 60 | 80 | 25 | 32 | 19 | 38 | 0 | 0 | 0 | 270 | 260 | 216 | 8 | 138 | 23 | 40 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 7 | 0 | 88 | 142 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 161 | 0 | 44 | 0 | 213 | 0 | 0 | 0 | 290 | 16 | 5 | 0 | 300 | 252 | 0 | 114 | 0 | 132 | 0 | 76 | 200 | 138 | 316 | 77 | 53 | 71 | 0 | 106 | 54 | 104 | 114 | 93 | 80 | 320 | 95 | 0 | 162 | 104 | 0 | 17 | 0 |  | 716 | 0 | 350 | 0 | 0 | 158 | 0 | 0 | 20 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 24 | 84 | 35 | 0 | 16 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 141 | 0 | 190 | 0 | 12 | 100 | 186 | 0 | 0 | 88 | 173 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 222 | 0 | 35 | 0 |  | 7722 | 3798 | 11520 | 4259 | 716 | 1400 | 3802 | 695 | 105 | 455 | 88 | 0 | 0 | 103.08
4:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 212 |  | 0 | 225 | 245 | 0 | 0 | 41 | 250 | 0 | 0 | 0 | 48 | 32 | 27 | 0 | 0 | 0 | 54 | 0 | 0 | 0 | 25 | 28 | 33 | 33 | 17 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 51 | 80 | 6 | 32 | 19 | 38 | 0 | 0 | 0 | 270 | 260 | 216 | 8 | 141 | 23 | 40 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 0 | 0 | 90 | 142 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 161 | 0 | 44 | 0 | 213 | 0 | 0 | 0 | 270 | 24 | 8 | 0 | 300 | 208 | 0 | 96 | 0 | 132 | 0 | 76 | 200 | 137 | 316 | 57 | 53 | 71 | 0 | 105 | 54 | 110 | 114 | 91 | 80 | 320 | 95 | 0 | 162 | 116 | 0 | 17 | 0 |  | 717 | 0 | 360 | 0 | 0 | 40 | 0 | 0 | 20 | 0 | 0 | 65 | 35 | 0 | 0 | 0 | 0 | 43 | 24 | 84 | 35 | 0 | 16 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 157 | 0 | 0 | 143 | 0 | 193 | 0 | 12 | 100 | 184 | 0 | 0 | 88 | 171 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 219 | 0 | 17 | 0 |  | 7552 | 3664 | 11216 | 4257 | 717 | 1333 | 3699 | 687 | 105 | 328 | 90 | 0 | 0 | 103.12
5:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 355 | 226 |  | 0 | 225 | 270 | 0 | 0 | 41 | 250 | 0 | 0 | 0 | 48 | 16 | 39 | 0 | 0 | 0 | 54 | 17 | 0 | 0 | 25 | 28 | 33 | 33 | 17 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 60 | 80 | 5 | 32 | 19 | 38 | 0 | 0 | 0 | 270 | 260 | 214 | 8 | 140 | 23 | 40 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 0 | 0 | 92 | 139 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 161 | 0 | 44 | 0 | 213 | 0 | 0 | 0 | 290 | 24 | 8 | 0 | 300 | 108 | 0 | 96 | 0 | 130 | 0 | 76 | 200 | 142 | 316 | 57 | 53 | 71 | 0 | 106 | 54 | 110 | 114 | 99 | 80 | 320 | 75 | 0 | 162 | 116 | 0 | 17 | 0 |  | 718 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 24 | 84 | 35 | 0 | 16 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 144 | 0 | 193 | 0 | 12 | 50 | 187 | 0 | 0 | 88 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 223 | 0 | 0 | 0 |  | 7514 | 3380 | 10894 | 4249 | 718 | 1370 | 3406 | 673 | 105 | 281 | 92 | 0 | 0 | 103.16
6:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 226 |  | 0 | 225 | 235 | 0 | 0 | 41 | 250 | 0 | 0 | 0 | 48 | 16 | 10 | 0 | 0 | 0 | 54 | 37 | 0 | 21 | 25 | 28 | 33 | 33 | 17 | 0 | 38 | 65 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 6 | 28 | 20 | 38 | 0 | 0 | 0 | 270 | 260 | 216 | 8 | 138 | 23 | 40 | 0 | 35 | 0 | 0 | 43 | 19 | 11 | 0 | 0 | 86 | 160 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 163 | 160 | 0 | 44 | 0 | 179 | 0 | 0 | 0 | 260 | 8 | 8 | 0 | 300 | 0 | 0 | 38 | 0 | 127 | 0 | 76 | 200 | 148 | 316 | 38 | 53 | 71 | 0 | 106 | 54 | 110 | 114 | 97 | 80 | 320 | 75 | 3 | 162 | 116 | 0 | 17 | 1 |  | 718 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 65 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 144 | 0 | 193 | 0 | 12 | 0 | 191 | 0 | 0 | 88 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 450 | 220 | 0 | 0 | 0 |  | 7195 | 3068 | 10263 | 4256 | 718 | 1368 | 3058 | 604 | 103 | 66 | 86 | 4 | 0 | 103.2
7:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 360 | 226 |  | 0 | 225 | 250 | 0 | 0 | 30 | 250 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 37 | 0 | 21 | 25 | 28 | 33 | 33 | 17 | 0 | 37 | 65 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 6 | 0 | 20 | 37 | 0 | 0 | 0 | 270 | 260 | 214 | 8 | 139 | 23 | 40 | 0 | 35 | 0 | 0 | 16 | 19 | 11 | 0 | 0 | 86 | 132 | 8 | 0 | 1 | 43 | 41 | 47 | 0 | 130 | 162 | 0 | 44 | 0 | 179 | 0 | 0 | 0 | 280 | 24 | 8 | 0 | 245 | 0 | 0 | 38 | 0 | 87 | 5 | 76 | 200 | 142 | 315 | 38 | 52 | 71 | 1 | 106 | 54 | 110 | 114 | 97 | 80 | 320 | 75 | 6 | 162 | 116 | 0 | 17 | 9 |  | 718 | 0 | 365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 156 | 0 | 0 | 144 | 0 | 194 | 0 | 12 | 0 | 193 | 0 | 0 | 88 | 0 | 113 | 0 | 70 | 0 | 1 | 113 | 440 | 183 | 0 | 0 | 1 |  | 6915 | 2932 | 9847 | 4225 | 718 | 1307 | 2773 | 596 | 102 | 16 | 86 | 24 | 0 | 103.24
8:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 362 | 216 |  | 0 | 225 | 290 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 32 | 16 | 0 | 0 | 0 | 0 | 54 | 37 | 0 | 21 | 25 | 9 | 33 | 33 | 17 | 0 | 40 | 65 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 20 | 6 | 0 | 20 | 3 | 0 | 0 | 0 | 270 | 260 | 211 | 8 | 142 | 23 | 40 | 0 | 35 | 0 | 0 | 16 | 19 | 11 | 25 | 0 | 90 | 136 | 5 | 0 | 1 | 43 | 41 | 47 | 0 | 130 | 161 | 0 | 44 | 0 | 179 | 0 | 0 | 0 | 290 | 24 | 0 | 0 | 250 | 0 | 0 | 38 | 0 | 89 | 12 | 76 | 200 | 133 | 315 | 38 | 53 | 71 | 3 | 106 | 54 | 110 | 114 | 97 | 80 | 320 | 75 | 35 | 162 | 116 | 0 | 17 | 15 |  | 718 | 0 | 360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 115 | 0 | 195 | 0 | 12 | 0 | 189 | 0 | 0 | 88 | 0 | 113 | 0 | 70 | 0 | 2 | 113 | 420 | 183 | 0 | 0 | 2 |  | 7015 | 2872 | 9887 | 4221 | 718 | 1270 | 2823 | 574 | 105 | 16 | 90 | 70 | 0 | 103.27
9:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 212 |  | 0 | 225 | 270 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 64 | 16 | 31 | 0 | 0 | 0 | 54 | 37 | 0 | 21 | 25 | 9 | 33 | 33 | 17 | 0 | 40 | 65 | 0 | 120 | 10 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 15 | 20 | 5 | 0 | 0 | 0 | 270 | 320 | 196 | 8 | 142 | 23 | 40 | 0 | 35 | 0 | 0 | 36 | 19 | 11 | 25 | 0 | 100 | 121 | 8 | 0 | 2 | 43 | 41 | 47 | 0 | 130 | 159 | 0 | 44 | 0 | 200 | 0 | 0 | 0 | 290 | 24 | 0 | 60 | 285 | 23 | 25 | 38 | 96 | 106 | 15 | 76 | 200 | 128 | 316 | 38 | 55 | 71 | 0 | 106 | 54 | 110 | 114 | 99 | 80 | 321 | 75 | 21 | 162 | 116 | 0 | 17 | 12 |  | 718 | 0 | 355 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 129 | 0 | 186 | 0 | 40 | 0 | 187 | 0 | 0 | 88 | 0 | 113 | 0 | 85 | 0 | 3 | 113 | 420 | 183 | 0 | 0 | 3 |  | 7463 | 2890 | 10353 | 4219 | 718 | 1295 | 3269 | 575 | 105 | 16 | 100 | 56 | 0 | 103.3
10:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 212 |  | 0 | 250 | 270 | 0 | 0 | 40 | 280 | 0 | 0 | 0 | 102 | 32 | 41 | 0 | 0 | 0 | 54 | 37 | 0 | 18 | 25 | 9 | 33 | 33 | 25 | 0 | 41 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 43 | 18 | 4 | 0 | 0 | 0 | 280 | 320 | 190 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 0 | 110 | 106 | 8 | 21 | 1 | 44 | 41 | 47 | 0 | 130 | 160 | 0 | 44 | 0 | 200 | 0 | 0 | 0 | 310 | 24 | 0 | 180 | 300 | 107 | 65 | 37 | 98 | 123 | 13 | 76 | 200 | 135 | 316 | 38 | 55 | 71 | 0 | 273 | 54 | 110 | 114 | 92 | 80 | 320 | 75 | 52 | 162 | 116 | 0 | 17 | 29 |  | 718 | 0 | 350 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 126 | 0 | 180 | 0 | 52 | 1 | 186 | 0 | 0 | 88 | 0 | 113 | 0 | 94 | 0 | 4 | 113 | 400 | 183 | 0 | 0 | 5 |  | 8112 | 2890 | 11002 | 4207 | 718 | 1332 | 3839 | 554 | 106 | 32 | 110 | 104 | 0 | 103.33
11:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 206 |  | 0 | 320 | 240 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 39 | 0 | 0 | 0 | 54 | 37 | 35 | 18 | 25 | 9 | 33 | 33 | 25 | 0 | 41 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 44 | 18 | 4 | 0 | 0 | 0 | 280 | 320 | 184 | 8 | 141 | 23 | 20 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 18 | 108 | 108 | 8 | 21 | 1 | 43 | 41 | 47 | 0 | 130 | 159 | 0 | 44 | 0 | 221 | 0 | 0 | 0 | 280 | 24 | 5 | 200 | 300 | 109 | 92 | 37 | 98 | 132 | 12 | 76 | 200 | 137 | 316 | 38 | 53 | 71 | 0 | 300 | 54 | 110 | 114 | 98 | 80 | 325 | 75 | 53 | 162 | 116 | 0 | 17 | 35 |  | 718 | 0 | 345 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 118 | 0 | 184 | 0 | 52 | 10 | 183 | 0 | 0 | 88 | 0 | 90 | 0 | 100 | 0 | 7 | 113 | 380 | 183 | 0 | 0 | 5 |  | 8285 | 2852 | 11137 | 4219 | 718 | 1367 | 3926 | 532 | 106 | 48 | 108 | 113 | 0 | 103.36
12:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 365 | 204 |  | 0 | 320 | 265 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 39 | 0 | 0 | 0 | 54 | 37 | 35 | 18 | 25 | 28 | 33 | 17 | 25 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 48 | 18 | 10 | 0 | 0 | 0 | 280 | 300 | 181 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 18 | 122 | 108 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 158 | 0 | 44 | 0 | 221 | 0 | 0 | 0 | 290 | 24 | 5 | 200 | 300 | 200 | 92 | 37 | 99 | 132 | 0 | 76 | 200 | 132 | 316 | 38 | 53 | 71 | 0 | 305 | 54 | 104 | 114 | 98 | 80 | 325 | 74 | 23 | 162 | 116 | 0 | 18 | 36 |  | 718 | 0 | 335 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 120 | 0 | 181 | 0 | 61 | 41 | 177 | 0 | 6 | 88 | 100 | 110 | 0 | 99 | 0 | 7 | 113 | 380 | 200 | 0 | 0 | 4 |  | 8365 | 3056 | 11421 | 4182 | 718 | 1413 | 4191 | 532 | 105 | 88 | 122 | 70 | 0 | 103.39
13:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 364 | 160 |  | 0 | 320 | 290 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 36 | 0 | 0 | 0 | 54 | 37 | 35 | 18 | 25 | 28 | 33 | 25 | 25 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 50 | 20 | 10 | 0 | 0 | 0 | 280 | 300 | 182 | 8 | 139 | 23 | 20 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 18 | 124 | 105 | 8 | 21 | 2 | 43 | 41 | 47 | 0 | 130 | 155 | 0 | 43 | 0 | 222 | 0 | 0 | 0 | 280 | 24 | 5 | 200 | 300 | 157 | 93 | 36 | 96 | 120 | 0 | 76 | 200 | 137 | 316 | 38 | 53 | 71 | 0 | 305 | 54 | 103 | 114 | 99 | 80 | 325 | 74 | 49 | 162 | 116 | 0 | 35 | 32 |  | 718 | 0 | 320 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 152 | 0 | 0 | 116 | 0 | 173 | 0 | 78 | 70 | 170 | 0 | 65 | 88 | 50 | 113 | 0 | 104 | 0 | 7 | 113 | 400 | 179 | 0 | 0 | 4 |  | 8368 | 3155 | 11523 | 4221 | 718 | 1415 | 4166 | 552 | 145 | 88 | 124 | 94 | 0 | 103.42
14:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 365 | 147 |  | 0 | 320 | 255 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 37 | 0 | 0 | 0 | 54 | 37 | 35 | 18 | 25 | 28 | 33 | 33 | 25 | 0 | 78 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 49 | 20 | 5 | 0 | 0 | 0 | 280 | 300 | 177 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 41 | 43 | 19 | 8 | 25 | 18 | 126 | 104 | 8 | 21 | 2 | 44 | 41 | 47 | 0 | 130 | 151 | 0 | 43 | 0 | 222 | 0 | 0 | 0 | 300 | 24 | 5 | 200 | 300 | 206 | 94 | 36 | 99 | 121 | 0 | 76 | 200 | 137 | 314 | 38 | 53 | 71 | 5 | 160 | 54 | 110 | 114 | 96 | 80 | 326 | 75 | 43 | 162 | 116 | 0 | 29 | 32 |  | 718 | 0 | 305 | 0 | 0 | 70 | 0 | 0 | 3 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 39 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 112 | 0 | 165 | 0 | 76 | 50 | 155 | 0 | 69 | 88 | 25 | 113 | 0 | 99 | 0 | 7 | 113 | 360 | 162 | 0 | 0 | 4 |  | 8283 | 3124 | 11407 | 4182 | 718 | 1402 | 3989 | 512 | 143 | 242 | 126 | 93 | 0 | 103.45
15:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 147 |  | 0 | 320 | 275 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 36 | 0 | 0 | 0 | 54 | 55 | 35 | 18 | 25 | 28 | 33 | 33 | 25 | 0 | 76 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 50 | 20 | 7 | 0 | 0 | 0 | 280 | 300 | 185 | 8 | 141 | 23 | 20 | 0 | 35 | 0 | 46 | 43 | 19 | 8 | 25 | 19 | 134 | 106 | 8 | 21 | 1 | 43 | 41 | 47 | 0 | 130 | 158 | 0 | 69 | 0 | 221 | 0 | 0 | 0 | 300 | 24 | 5 | 200 | 290 | 207 | 94 | 36 | 96 | 114 | 0 | 76 | 200 | 138 | 315 | 38 | 53 | 71 | 1 | 160 | 54 | 110 | 114 | 98 | 80 | 325 | 75 | 31 | 162 | 116 | 0 | 35 | 20 |  | 718 | 0 | 300 | 0 | 0 | 100 | 0 | 0 | 5 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 50 | 10 | 46 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 110 | 0 | 155 | 0 | 82 | 89 | 149 | 0 | 175 | 88 | 179 | 113 | 0 | 99 | 0 | 5 | 113 | 350 | 162 | 0 | 0 | 4 |  | 8336 | 3453 | 11789 | 4174 | 718 | 1543 | 4210 | 502 | 141 | 305 | 134 | 62 | 0 | 103.48
16:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 148 |  | 0 | 320 | 280 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 37 | 0 | 0 | 0 | 54 | 37 | 35 | 20 | 25 | 28 | 33 | 33 | 25 | 0 | 76 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 19 | 0 | 39 | 80 | 6 | 50 | 20 | 2 | 0 | 0 | 0 | 280 | 300 | 193 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 19 | 0 | 25 | 19 | 130 | 106 | 8 | 21 | 1 | 43 | 41 | 50 | 0 | 130 | 161 | 0 | 78 | 0 | 221 | 0 | 0 | 0 | 300 | 24 | 5 | 200 | 281 | 108 | 60 | 38 | 96 | 113 | 2 | 76 | 200 | 133 | 314 | 38 | 53 | 71 | 0 | 160 | 54 | 110 | 114 | 100 | 80 | 326 | 75 | 19 | 162 | 114 | 0 | 35 | 16 |  | 718 | 0 | 280 | 0 | 0 | 150 | 0 | 0 | 5 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 50 | 20 | 46 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 109 | 0 | 158 | 0 | 12 | 50 | 158 | 0 | 241 | 88 | 0 | 113 | 0 | 99 | 0 | 3 | 113 | 330 | 216 | 0 | 0 | 1 |  | 8213 | 3308 | 11521 | 4169 | 718 | 1598 | 3835 | 482 | 141 | 406 | 130 | 42 | 0 | 103.51
17:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 150 |  | 0 | 320 | 250 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 39 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 78 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 80 | 18 | 20 | 20 | 7 | 0 | 0 | 0 | 280 | 300 | 199 | 8 | 138 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 11 | 25 | 19 | 122 | 124 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 161 | 0 | 81 | 0 | 209 | 0 | 0 | 0 | 310 | 24 | 0 | 10 | 281 | 0 | 0 | 45 | 56 | 114 | 1 | 76 | 200 | 133 | 314 | 64 | 53 | 71 | 0 | 160 | 54 | 110 | 114 | 99 | 100 | 325 | 75 | 8 | 162 | 114 | 0 | 35 | 8 |  | 718 | 0 | 275 | 0 | 0 | 40 | 0 | 0 | 10 | 0 | 0 | 87 | 17 | 0 | 0 | 0 | 0 | 50 | 36 | 46 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 157 | 0 | 11 | 0 | 170 | 0 | 355 | 88 | 0 | 113 | 0 | 99 | 0 | 2 | 113 | 340 | 218 | 0 | 0 | 1 |  | 7935 | 3186 | 11121 | 4084 | 718 | 1763 | 3417 | 491 | 143 | 363 | 122 | 20 | 0 | 103.54
18:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 362 | 150 |  | 0 | 320 | 245 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 133 | 51 | 0 | 0 | 0 | 54 | 55 | 35 | 0 | 25 | 28 | 33 | 33 | 25 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 10 | 79 | 39 | 20 | 4 | 0 | 0 | 0 | 280 | 300 | 209 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 8 | 21 | 11 | 25 | 19 | 118 | 125 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 110 | 162 | 0 | 55 | 0 | 193 | 0 | 0 | 0 | 280 | 24 | 0 | 0 | 288 | 11 | 26 | 182 | 26 | 131 | 0 | 76 | 150 | 138 | 316 | 115 | 53 | 71 | 0 | 214 | 41 | 110 | 51 | 98 | 100 | 325 | 75 | 0 | 162 | 114 | 0 | 35 | 2 |  | 717 | 0 | 260 | 0 | 0 | 40 | 0 | 0 | 16 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 50 | 39 | 54 | 35 | 0 | 13 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 145 | 0 | 11 | 0 | 130 | 0 | 302 | 53 | 0 | 113 | 0 | 70 | 0 | 1 | 113 | 330 | 152 | 0 | 0 | 0 |  | 7992 | 2956 | 10948 | 3995 | 717 | 1535 | 3476 | 481 | 145 | 478 | 118 | 3 | 0 | 103.57
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 360 | 180 |  | 0 | 320 | 275 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 133 | 50 | 0 | 0 | 0 | 54 | 55 | 35 | 15 | 25 | 20 | 33 | 33 | 47 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 80 | 90 | 50 | 20 | 4 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 25 | 21 | 11 | 25 | 19 | 140 | 118 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 160 | 0 | 80 | 0 | 228 | 0 | 0 | 0 | 285 | 24 | 5 | 100 | 300 | 200 | 94 | 184 | 100 | 132 | 0 | 100 | 168 | 138 | 315 | 115 | 90 | 71 | 0 | 285 | 45 | 110 | 100 | 105 | 100 | 325 | 75 | 0 | 162 | 114 | 0 | 35 | 0 |  | 717 | 0 | 265 | 0 | 0 | 158 | 0 | 0 | 22 | 0 | 0 | 87 | 31 | 16 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 0 | 28 | 25 | 15 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 153 | 0 | 11 | 56 | 164 | 0 | 401 | 80 | 120 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 220 | 0 | 24 | 0 |  | 8984 | 3750 | 12734 | 4085 | 717 | 1826 | 4578 | 580 | 145 | 663 | 140 | 0 | 0 | 103.66
19:30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 180 |  | 0 | 320 | 295 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 133 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 80 | 90 | 50 | 20 | 9 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 141 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 8 | 25 | 19 | 148 | 119 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 160 | 0 | 81 | 0 | 228 | 0 | 0 | 0 | 320 | 24 | 11 | 150 | 300 | 230 | 94 | 184 | 100 | 132 | 0 | 100 | 190 | 138 | 315 | 115 | 90 | 71 | 0 | 285 | 54 | 110 | 98 | 98 | 100 | 325 | 75 | 0 | 162 | 114 | 0 | 35 | 0 |  | 717 | 0 | 260 | 0 | 0 | 158 | 0 | 0 | 26 | 0 | 0 | 88 | 29 | 16 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 0 | 30 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 100 | 182 | 0 | 410 | 88 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 220 | 0 | 35 | 0 |  | 9209 | 3873 | 13082 | 4131 | 717 | 1874 | 4725 | 670 | 145 | 672 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 362 | 192 |  | 0 | 320 | 250 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 102 | 133 | 60 | 0 | 0 | 0 | 51 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 82 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 80 | 95 | 50 | 20 | 9 | 0 | 0 | 0 | 280 | 300 | 206 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 11 | 25 | 19 | 136 | 118 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 162 | 0 | 81 | 0 | 228 | 0 | 0 | 0 | 310 | 24 | 11 | 197 | 300 | 214 | 94 | 183 | 99 | 131 | 0 | 100 | 200 | 138 | 316 | 115 | 90 | 71 | 0 | 305 | 54 | 110 | 114 | 97 | 100 | 325 | 75 | 0 | 162 | 96 | 0 | 35 | 0 |  | 717 | 0 | 250 | 0 | 0 | 158 | 0 | 0 | 25 | 0 | 0 | 88 | 32 | 16 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 0 | 33 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 151 | 0 | 0 | 0 | 0 | 159 | 0 | 22 | 100 | 182 | 0 | 407 | 88 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 530 | 220 | 0 | 17 | 0 |  | 9175 | 3865 | 13040 | 4119 | 717 | 1887 | 4679 | 681 | 147 | 674 | 136 | 0 | 0 | 103.63
21:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 194 |  | 0 | 320 | 312 | 0 | 0 | 0 | 270 | 0 | 0 | 0 | 102 | 133 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 82 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 70 | 100 | 95 | 50 | 20 | 17 | 0 | 0 | 0 | 280 | 300 | 205 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 11 | 25 | 21 | 134 | 118 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 162 | 0 | 81 | 0 | 228 | 0 | 0 | 0 | 300 | 24 | 0 | 174 | 300 | 110 | 97 | 184 | 100 | 132 | 0 | 100 | 200 | 138 | 316 | 115 | 90 | 71 | 0 | 286 | 54 | 110 | 114 | 98 | 100 | 325 | 75 | 0 | 162 | 112 | 0 | 35 | 0 |  | 718 | 0 | 240 | 0 | 0 | 158 | 0 | 0 | 25 | 0 | 0 | 88 | 32 | 0 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 8 | 31 | 25 | 17 | 18 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 146 | 0 | 22 | 97 | 179 | 0 | 411 | 88 | 25 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 222 | 0 | 0 | 0 |  | 9110 | 3854 | 12964 | 4082 | 718 | 1893 | 4589 | 745 | 147 | 656 | 134 | 0 | 0 | 103.66
22:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 362 | 193 |  | 0 | 320 | 280 | 0 | 0 | 20 | 270 | 0 | 0 | 0 | 102 | 133 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 83 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 50 | 20 | 26 | 0 | 0 | 0 | 280 | 300 | 212 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 11 | 25 | 21 | 140 | 117 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 163 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 305 | 24 | 0 | 100 | 300 | 100 | 50 | 188 | 98 | 136 | 0 | 100 | 200 | 140 | 316 | 115 | 90 | 71 | 0 | 303 | 54 | 110 | 114 | 97 | 100 | 325 | 95 | 0 | 159 | 114 | 0 | 35 | 0 |  | 718 | 0 | 230 | 0 | 0 | 158 | 0 | 0 | 25 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 8 | 31 | 25 | 16 | 18 | 0 | 11 | 0 | 0 | 159 | 0 | 0 | 0 | 0 | 138 | 0 | 22 | 100 | 174 | 0 | 407 | 88 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 221 | 0 | 0 | 0 |  | 9046 | 3769 | 12815 | 4059 | 718 | 1903 | 4468 | 709 | 148 | 670 | 140 | 0 | 0 | 103.69
23:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 193 |  | 0 | 320 | 275 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 133 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 83 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 40 | 20 | 27 | 0 | 0 | 0 | 280 | 300 | 213 | 8 | 141 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 22 | 11 | 25 | 21 | 140 | 123 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 162 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 0 | 100 | 300 | 100 | 50 | 188 | 99 | 149 | 0 | 100 | 200 | 140 | 315 | 115 | 90 | 71 | 0 | 305 | 54 | 110 | 114 | 98 | 100 | 326 | 95 | 0 | 144 | 114 | 0 | 35 | 0 |  | 717 | 0 | 225 | 0 | 0 | 158 | 0 | 0 | 25 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 50 | 36 | 85 | 35 | 8 | 31 | 25 | 16 | 18 | 0 | 11 | 0 | 0 | 154 | 0 | 0 | 0 | 0 | 130 | 0 | 22 | 100 | 168 | 0 | 414 | 88 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 550 | 221 | 0 | 0 | 0 |  | 9045 | 3741 | 12786 | 4047 | 717 | 1895 | 4468 | 704 | 148 | 667 | 140 | 0 | 0 | 103.72
24:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 206 |  | 0 | 320 | 250 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 115 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 22 | 25 | 29 | 33 | 33 | 34 | 0 | 83 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 96 | 39 | 20 | 27 | 0 | 0 | 0 | 280 | 300 | 214 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 22 | 11 | 25 | 21 | 132 | 127 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 160 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 0 | 100 | 300 | 150 | 80 | 115 | 99 | 149 | 0 | 76 | 200 | 143 | 316 | 77 | 34 | 73 | 0 | 305 | 54 | 110 | 114 | 98 | 80 | 325 | 95 | 0 | 144 | 114 | 0 | 35 | 0 |  | 718 | 0 | 225 | 0 | 0 | 158 | 0 | 0 | 25 | 0 | 0 | 88 | 34 | 0 | 0 | 0 | 0 | 50 | 37 | 85 | 35 | 0 | 16 | 25 | 16 | 18 | 0 | 11 | 0 | 0 | 153 | 0 | 0 | 0 | 0 | 128 | 0 | 22 | 100 | 167 | 0 | 404 | 88 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 550 | 221 | 0 | 0 | 0 |  | 8877 | 3713 | 12590 | 4048 | 718 | 1908 | 4298 | 703 | 148 | 635 | 132 | 0 | 0 | 103.75
KWH | 0 | 0 | 0 | 0 | 4814400 | 0 | 0 | 8796160 | 4594000 |  | 0 | 6540250 | 6462749 | 0 | 0 | 899363 | 6470948 | 0 | 0 | 0 | 2021760 | 1572960 | 912648 | 0 | 0 | 0 | 1299600 | 983568 | 513500 | 325296 | 600000 | 562680 | 821300 | 706600 | 667680 | 0 | 1325073 | 1584000 | 0 | 3000000 | 545722 | 0 | 0 | 0 | 0 |  | 525360 | 0 | 1051660 | 1811640 | 960960 | 920160 | 463536 | 477600 | 0 | 0 | 0 | 6922000 | 6995000 | 4915000 | 217454 | 3344140 | 513936 | 687840 | 0 | 815964 | 0 | 540016 | 940070 | 470412 | 217440 | 468100 | 275100 | 2731200 | 2870960 | 187200 | 426888 | 10950 | 1029000 | 949920 | 1160400 | 0 | 3336464 | 3719000 | 0 | 1315200 | 0 | 5118890 | 0 | 0 | 0 | 7175500 | 523584 | 78432 | 2225856 | 7080652 | 3011124 | 1112570 | 2145600 | 1437121 | 3026880 | 59535 | 1918080 | 4686720 | 3305309 | 7612000 | 1552800 | 1453200 | 1729599 | 13561 | 4712073 | 1277290 | 2673006 | 2714340 | 2344440 | 2070720 | 7754000 | 1956480 | 324340 | 3889440 | 2746200 | 0 | 658080 | 253938 |  | 17336000 | 0 | 7655040 | 0 | 0 | 1870080 | 0 | 0 | 286680 | 0 | 0 | 1602209 | 637571 | 28800 | 0 | 0 | 0 | 749040 | 453743 | 1142360 | 722860 | 26469 | 236481 | 602400 | 189218 | 406560 | 0 | 255474 | 0 | 0 | 3770200 | 0 | 0 | 2148500 | 0 | 4304373 | 0 | 688561 | 1444800 | 4471573 | 0 | 3522763 | 2077920 | 1223140 | 2721888 | 0 | 2441088 | 0 | 47014 | 2745120 | 11938400 | 4843800 | 0 | 273600 | 35640 |  | 195932187 | 82899365 | 278831552 | 101201891 | 17336000 | 36419927 | 93687645 | 15708600 | 2909073 | 8092238 | 2731200 | 744978 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5343984 | 0 | 0 | 8884121.6 | 4731820 |  | 0 | 7128872.5 | 7173651.39 | 0 | 0 | 7608610.98 | 6729785.92 | 0 | 0 | 0 | 18438451.2 | 15477926.4 | 8414614.56 | 0 | 0 | 0 | 9487080 | 7602980.64 | 5063110 | 243972 | 450000 | 0 | 0 | 0 | 6456465.6 | 0 | 357769.71 | 427680 | 0 | 5430000 | 5069757.38 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10201102 | 17301162 | 8360352 | 7287667.2 | 584055.36 | 1418472 | 0 | 0 | 0 | 5122280 | 6995000 | 4521800 | 280515.66 | 3845761 | 580747.68 | 962976 | 0 | 1395298.44 | 0 | 5454161.6 | 8977668.5 | 597423.24 | 163080 | 819175 | 206325 | 20484000 | 3043217.6 | 1699776 | 542147.76 | 174543 | 1687560 | 1519872 | 2065512 | 0 | 3803568.96 | 3867760 | 0 | 2512032 | 0 | 8855679.7 | 0 | 0 | 0 | 7247255 | 392688 | 59608.32 | 37861810.56 | 53529729.12 | 51128885.52 | 18602170.4 | 11157120 | 24028663.12 | 29784499.2 | 695964.15 | 15632352 | 50850912 | 23302428.45 | 7079160 | 14161536 | 13732740 | 15064807.29 | 0 | 35623271.88 | 11125195.9 | 23495722.74 | 27089113.2 | 20091850.8 | 13790995.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99855360 | 0 | 8037792 | 0 | 0 | 25919308.8 | 0 | 0 | 3007273.2 | 0 | 0 | 1810496.17 | 988235.05 | 281088 | 0 | 0 | 0 | 7370553.6 | 4610028.88 | 10109886 | 5566022 | 357860.88 | 2291500.89 | 5837256 | 1835414.6 | 780595.2 | 0 | 193393.818 | 0 | 0 | 20434484 | 0 | 0 | 2513745 | 0 | 5681772.36 | 0 | 1032841.5 | 24576048 | 5231740.41 | 0 | 3487535.37 | 21693484.8 | 20805611.4 | 25830717.12 | 0 | 18942842.88 | 0 | 519504.7 | 20286436.8 | 52409576 | 0 | 0 | 0 | 0 |  | 771379824.43 | 402298405.428 | 1173678229.858 | 101034143.938 | 99855360 | 37835529.68 | 753172518.71 | 72844060 | 785449.71 | 86277155.97 | 20484000 | 1390011.85 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 365 | 204 |  | 0 | 320 | 265 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 39 | 0 | 0 | 0 | 54 | 37 | 35 | 18 | 25 | 28 | 33 | 17 | 25 | 0 | 40 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 80 | 6 | 48 | 18 | 10 | 0 | 0 | 0 | 280 | 300 | 181 | 8 | 140 | 23 | 20 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 18 | 122 | 108 | 8 | 21 | 0 | 43 | 41 | 47 | 0 | 130 | 158 | 0 | 44 | 0 | 221 | 0 | 0 | 0 | 290 | 24 | 5 | 200 | 300 | 200 | 92 | 37 | 99 | 132 | 0 | 76 | 200 | 132 | 316 | 38 | 53 | 71 | 0 | 305 | 54 | 104 | 114 | 98 | 80 | 325 | 74 | 23 | 162 | 116 | 0 | 18 | 36 |  | 718 | 0 | 335 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 15 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 25 | 0 | 18 | 0 | 11 | 0 | 0 | 152 | 0 | 0 | 120 | 0 | 181 | 0 | 61 | 41 | 177 | 0 | 6 | 88 | 100 | 110 | 0 | 99 | 0 | 7 | 113 | 380 | 200 | 0 | 0 | 4 |  | 11421 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 363 | 180 | 0 | 0 | 320 | 295 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 102 | 133 | 60 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 28 | 33 | 33 | 51 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 80 | 90 | 50 | 20 | 9 | 0 | 0 | 0 | 280 | 300 | 207 | 8 | 141 | 23 | 20 | 0 | 35 | 0 | 48 | 43 | 21 | 8 | 25 | 19 | 148 | 119 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 163 | 160 | 0 | 81 | 0 | 228 | 0 | 0 | 0 | 320 | 24 | 11 | 150 | 300 | 230 | 94 | 184 | 100 | 132 | 0 | 100 | 190 | 138 | 315 | 115 | 90 | 71 | 0 | 285 | 54 | 110 | 98 | 98 | 100 | 325 | 75 | 0 | 162 | 114 | 0 | 35 | 0 |  | 717 | 0 | 260 | 0 | 0 | 158 | 0 | 0 | 26 | 0 | 0 | 88 | 29 | 16 | 0 | 0 | 0 | 50 | 39 | 85 | 35 | 0 | 30 | 25 | 18 | 18 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 100 | 182 | 0 | 410 | 88 | 50 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 220 | 0 | 35 | 0 |  | 13082 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 360 | 220 | 0 | 0 | 320 | 305 | 0 | 0 | 41 | 335 | 0 | 0 | 0 | 102 | 133 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 95 | 50 | 20 | 10 | 0 | 0 | 0 | 330 | 330 | 210 | 8 | 140 | 23 | 5 | 0 | 35 | 0 | 50 | 43 | 22 | 11 | 25 | 20 | 163 | 135 | 8 | 21 | 0 | 44 | 42 | 51 | 0 | 163 | 160 | 0 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 190 | 100 | 149 | 0 | 100 | 200 | 145 | 315 | 115 | 90 | 89 | 0 | 300 | 54 | 110 | 114 | 98 | 100 | 325 | 95 | 0 | 162 | 116 | 0 | 35 |  |  | 729 | 0 | 260 | 0 | 0 | 158 | 0 | 0 | 26 | 60 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 50 | 42 | 85 | 35 | 0 | 40 | 25 | 33 | 22 | 0 | 11 | 0 | 0 | 155 | 15 | 10 | 0 | 0 | 200 | 0 | 11 | 100 | 200 | 0 | 410 | 88 | 200 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 360 | 220 | 0 | 0 | 320 | 305 | 0 | 0 | 41 | 335 | 0 | 0 | 0 | 64 | 32 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 80 | 65 | 0 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 50 | 50 | 20 | 5 | 0 | 0 | 0 | 300 | 300 | 210 | 8 | 140 | 23 | 5 | 0 | 35 | 0 | 0 | 43 | 22 | 11 | 25 | 20 | 138 | 135 | 8 | 21 | 1.6 | 44 | 42 | 51 | 0 | 163 | 160 | 0 | 84 | 0 | 225 | 18 | 0 | 10 | 341 | 24 | 11 | 100 | 300 | 100 | 100 | 175 | 50 | 116 | 20 | 100 | 200 | 142 | 315 | 115 | 90 | 89 | 5 | 300 | 54 | 110 | 114 | 98 | 80 | 325 | 95 | 50 | 162 | 116 | 0 | 17 | 30 |  | 729 | 0 | 260 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 33 | 110 | 0 | 0 | 0 | 43 | 40 | 84 | 35 | 0 | 30 | 25 | 0 | 22 | 0 | 11 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 200 | 0 | 11 | 50 | 200 | 0 | 410 | 88 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 361 | 212 | 0 | 0 | 320 | 305 | 0 | 0 | 40 | 270 | 0 | 0 | 0 | 7 | 32 | 12 | 0 | 0 | 0 | 54 | 55 | 35 | 21 | 25 | 29 | 33 |  | 0 | 0 | 82 | 65 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 0 | 0 | 10 | 6 | 19 | 20 | 9 | 0 | 0 | 0 | 280 | 300 | 203 | 8 | 142 | 23 | 30 | 0 | 35 | 0 | 0 | 8 | 22 | 11 | 25 | 12 | 84 | 135 | 8 | 21 | 0 | 43 | 41 | 50 | 0 | 110 | 159 | 0 | 81 | 0 | 193 | 0 | 0 | 0 | 285 | 24 | 2 | 0 | 145 | 0 | 0 | 38 | 0 | 79 | 11 | 80 | 50 | 145 | 316 | 38 | 17 | 76 | 1 | 141 | 17 | 110 | 34 | 98 | 40 | 326 | 95 | 21 | 144 | 114 | 0 | 17 | 10 | 0 | 716 | 0 | 245 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 89 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 18 | 0 | 8 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 134 | 0 | 12 | 0 | 184 | 0 | 366 | 53 | 0 | 35 | 0 | 34 | 0 | 1 | 113 | 340 | 180 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9847 | 7:00
| Highest Generation |  | 13082 | 19:30
| Day Peak Generation |  | 11421 | 12:00
| Evening Peak Generation |  | 13082 | 19:30
| HVDC Max Flow |  | 718 | 5:00
| HVDC EvPeak Flow |  | 717 | 19:30
| Load factor L.F |  | 88.81%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-07
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-06 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11421 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9634 | MW
Evening Peak Generation : |  | 13082 | MW Hour : | 19:30 | Available Max Generation : |  | 14395 | MW
E.P. Demand (at gen end) : |  | 13082 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13300 | MW
Maximum Generation : |  | 13082 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1095 | MW
Total Gen. (MKWH) : |  | 278.8316 | System Load Factor : | 88.81% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -482 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-07
Actual : | 103.93 | Ft.(MSL) , | Rule curve : | 100.38 | Ft.( MSL )
Gas Consumed : | Total = | 1094.94 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 138869673.618
: |  | Coal : | 72844060 | Oil : | 839449674.68 | Total : | 1051163408.298
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4687.9146 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1599.5153 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1434.0686 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1296.1413 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1171.117 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 945.0635 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 521.5293 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 243.1457 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 728.9129 |  |  | 0 | 0%
Total | 0 |  | 12627.4084 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-1,2
2) Ghorasal-3,4
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Rangpur 132/33 kV T-2 transformer was under shutdown from 09:20 to 14:50 for A/M.
b) Aminbazar-Mirpur 132 kV Ckt-1 was under shutdown from 10:28 to 12:12 for A/M.
c) Amnura 132/33 kV T-1 transformer was under shutdown from 10:38 to 13:40 for C/M.
d) Khulna 225 MW GTS was synchronized at 11:12.
e) Sirajganj 410 MW GT was synchronized at 11:22.
f) Meghnaghat 450 MW GT-2 was synchronized at 09:33.
g) Bhola 225 MW ST was synchronized at 12:30.
h) Kaptai unit-3 was synchronized at 12:20.
i) Sirajganj 410 MW ST was synchronized at 13:59.
j) Aminbazar-Mirpur 132 kV Ckt-2 was under shutdown from 12:15 to 13:19 for A/M.
k) Khulna(S)-Mongla 230 kV Ckt-1 & 2 were under shutdown from 09:54 to 13:19 for D/W.
l) 33 kV side of Satkhira 132/33 kV T-1 & T2 transformers tripped at 13:40 due to 33 kV feeder CT blast |  |  |  |  | About 50 MW power interruption occurred under Satkhira S/S area
and was switched on at 13:55. |  |  |  |  | from 14:40 to 13:55.
m) Kaliakoir-Bibiyana 132 kV Ckt-2 was switched on at 14:45.
n) B.Baria-Shahjibazar 132 kV Ckt-1 was switched on at 16:51.
o) Sirajganj 210 MW unit-1 GT was shut down at 16:26 due to gas shortage.
p) 33 kV side of Bottail 132/33 kV T-2 transformers tripped at 20:10 due to 33 kV feeder fault and was |  |  |  |  | About 56 MW power interruption occurred under Bottail S/S area
switched on at 20:16. |  |  |  |  | from 20:10 to 20:16.
q) Comilla(N) 230/132 kV T-2 transformer tripped at 20:25 showing buchholz relay at 230 kV end &
Diff .at 132 kV end.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-06 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 203 | 4814400 | ST Under maint
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 363 | 8796160 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 180 | 4594000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 320 | 6540250 | Gas shortage
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 295 | 6462749 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 40 | 899363 | Engine problem
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 60 | 912648 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 325296
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 270 | 6470948 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 2021760
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1299600
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 133 | 1572960 | Fuel shortage
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 983568
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 513500 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1162680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 821300
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 706600
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 667680 | Fuel shortage
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 7080652
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 230 | 3011124 | Load increasing.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 94 | 1112570
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 100 | 1437121
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 132 | 3026880 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1453200 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 75 | 1956480 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3889440
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 253938
| Dhaka area Total |  |  |  | 5719 | 3484 | 72786867
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 120 | 3000000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 545722
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 59535
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 920160
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 145 | 2909073 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 71 | 1729599 | Engine problem
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 1051660 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 80 | 1811640 | Engine problem
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 1918080
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 463536
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 9 | 477600
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 90 | 960960 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 13561
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 285 | 4712073
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1277290
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2673006
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2070720
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 114 | 2746200
| Chattogram area Total |  |  |  | 2382 | 1458 | 29340415
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 4915000 | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 6922000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 300 | 6995000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 513936 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 20 | 687840 | Gas shortage
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 815964 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 138 | 3305309 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 540016
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 141 | 3344140 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 190 | 4686720
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 470412
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 217440
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 148 | 2731200
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 468100 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 43 | 940070 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 19 | 275100
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 2225856 | Load increasing.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 2714340
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 98 | 2344440 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 658080 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2035 | 45988417
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 119 | 2870960 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 426888
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 187200 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 10950
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 184 | 2145600 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1552800
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 324340
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 525360
| Mymensingh Area Total |  |  |  | 709 | 471 | 8044098
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 41 | 949920 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3336464
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3719000 | Gas shortage
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1160400
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 78432
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1315200
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 228 | 5118890
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Machine problem
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 523584 | Engine problem
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 320 | 7175500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 315 | 7612000
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 325 | 7754000
| Sylhet Area Total |  |  |  | 2377 | 1761 | 39772390
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 717 | 17336000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 286680 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 158 | 1870080
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Reserve.
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 260 | 7655040 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 1444800
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 88 | 2077920 | Engine problem
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1349 | 30670520
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 28800 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 637571
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 88 | 1602209 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 688561 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 520 | 11938400 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4843800
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 273600 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 919 | 20012941
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 749040
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 39 | 453743 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 722860 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 0 | 26469 | Fuel shortage
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 30 | 236481 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 2148500 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 163 | 4304373
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 182 | 4471573 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 410 | 3522763
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 18 | 189218 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 18 | 406560 | Engine problem
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 255474
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 25 | 602400 | Fuel shortage
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 85 | 1142360 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 50 | 1223140 | Engine problem
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2721888
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2745120
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35640
| Rajshahi Area Total |  |  |  | 2179 | 1342 | 25957602
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 150 | 3770200 | Coal shortage
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Engine problem
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2441088
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47014
| Rangpur Area Total |  |  |  | 605 | 263 | 6258302
| Total |  |  |  | 21180 | 13082 | 278831552
| Eastern Grid Total |  |  |  | 14221 | 9209 | 195932187
| Western Grid Total |  |  |  | 6959 | 3873 | 82899365
| National Grid Total |  |  |  | 21180 | 13082 | 278831552
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-06
(a) ENTIRE EASTERN GRID : |  | 8423 | MW | (b) ENTIRE WESTERN GRID : |  | 3986 | MW
i) Dhaka area |  | 4547 | MW | i) Khulna area |  | 1534 | MW
ii) Chittagong area |  | 1236 | MW | ii) Rajshahi area |  | 1337 | MW
iii) Comilla area |  | 1203 | MW | iii) Barisal area |  | 345 | MW
iv) Mymensingh area |  | 962 | MW | iv) Rangpur area |  | 770 | MW
v) Sylhet area |  | 475 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12409 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 10:00 | Kishoreganj | 124 | 3:00 | Jessore | 115 | 19:30
Munsiganj | 96 | 21:00 | Netrokona | 122 | 20:00 | Benapol | 58 | 20:00
Sonargaon | 76 | 18:30 | Jamalpur | 139 | 19:30 | Jhenida | 119 | 19:00
Shyampur | 194 | 12:00 | Sherpur | 132 | 2:00 | Bottail | 127 | 22:00
Bhulta | 213 | 19:30 | Srimongal | 59 | 2:00 | G.K Project | 59 | 1:00
Madanganj | 48 | 21:00 | Shahjibazar | 116 | 20:00 | Faridpur | 152 | 20:00
Shitalakhya | 94 | 15:00 | Fenchuganj | 49 | 19:00 | Rajbari | 54 | 22:00
Rahim steel | 27 | 16:00 | Kulawara | 46 | 19:30 | Madaripur | 103 | 22:00
Matuail | 69 | 10:00 | Sylhet | 144 | 15:00 | Sariatpur | 70 | 22:00
Ghorasal | 82 | 22:00 | Chatak | 32 | 19:30 | Gopalganj | 93 | 22:00
Narsingdi | 183 | 21:00 | Sunamganj | 52 | 19:30 | Bagerhat | 100 | 22:00
Haripur (SBU) | 124 | 16:00 | Biani Bazar | 67 | 1:00 | Mongla | 50 | 12:00
Sreenagar | 44 | 20:00 | Comilla (S) | 150 | 18:30 | Satkhira | 112 | 1:00
Ullon | 65 | 20:00 | Comilla(N) | 135 | 19:30 | Gallamari | 33 | 12:00
Hasnabad | 80 | 19:00 | Chandpur | 71 | 21:00 | Magura | 56 | 21:00
Magbazar | 114 | 15:00 | Feni | 121 | 19:30 | Norail | 47 | 18:30
Maniknagar | 76 | 13:00 | Chowmuhani | 194 | 23:00 | Chuadanga | 103 | 1:00
Bangabhaban | 13 | 10:00 | Ashuganj | 43 | 1:00 | Borguna | 14 | 1:00
Motijheel | 30 | 11:00 | Daudkandi | 151 | 20:00 | Barisal(N) | 42 | 1:00
Narinda | 74 | 13:00 | B.Baria | 170 | 20:00 | Barisal (S) | 106 | 19:00
Kazla | 83 | 12:00 | Ramganj | 98 | 22:00 | Patuakhali | 120 | 1:00
Dhanmondi | 187 | 14:00 | Chaddagram | 49 | 19:00 | Bhandaria | 52 | 1:00
Lalbag | 90 | 13:00 | PHP | 10 | 5:00 | Borhan Uddin | 45 | 1:00
Madartek | 73 | 23:00 | Kochua | 72 | 20:00 | Ishurdi | 69 | 22:00
Dhaka University | 35 | 13:00 | Madunaghat | 58 | 16:00 | Ruppur Paromanobik | 3 | 19:00
Aftabnagar | 16 | 13:00 | Hathazari | 91 | 19:00 | Natore | 129 | 20:00
Fatullah | 59 | 0:00 | Khulshi | 193 | 16:00 | Bogra | 169 | 24:00
Nawabganj | 53 | 21:00 | Halishahar | 92 | 9:00 | Noagaon | 115 | 20:00
Keraniganj | 72 | 18:30 | Baraulia | 149 | 16:00 | Rajshahi | 154 | 22:00
Mirpur | 124 | 18:30 | Sikalbaha | 41 | 13:00 | Rajshahi New | 16 | 0:00
Kalyanpur | 108 | 19:00 | Dohazari | 104 | 19:00 | C.Nawabganj | 62 | 21:00
Gulshan | 114 | 11:00 | Cox'sbazar | 86 | 22:00 | Amnura | 53 | 22:00
Uttara | 86 | 16:00 | Chandraghona | 30 | 18:30 | Pabna | 113 | 20:00
Uttara New | 31 | 15:00 | Kaptai | 4.5 | 18:30 | Shahjadpur | 94 | 20:00
Kamrangirchar | 97 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 114 | 21:00
Savar | 167 | 19:00 | Bakulia | 118 | 19:00 | Niyamatpur | 75 | 22:00
Bhasantec | 133 | 13:00 | Julda | 24 | 1:00 | Joypurhat | 61 | 22:00
Agargaon | 92 | 13:00 | TK chemical | 27.5 | 19:30 | Sherpur(Bogura) | 59 | 19:30
Satmosjid | 101 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 68 | 20:00
Tongi | 122 | 15:00 | Shahmirpur | 30 | 1:00 | Bhangura | 33 | 21:00
Kabirpur | 267 | 12:00 | Khagrachhari | 28 | 18:00 | Rangpur | 136 | 22:00
Basundhara | 246 | 14:00 | Matarbari | 32.5 | 18:00 | Lalmonirhat | 48 | 21:00
Manikganj | 74 | 20:00 | Baroiar Hat | 48 | 18:30 | Saidpur | 102 | 19:00
Joydevpur | 188 | 12:00 | Rangamati | 14 | 20:00 | Purbasadipur | 109 | 23:00
New Tongi | 92 | 10:00 | Abul Khair 230 | 135 | 10:00 | Thakurgaon | 88 | 24:00
Kodda | 259 | 19:00 | BSRM | 148 | 18:00 | Palashbari | 116 | 1:00
Dhamrai | 118 | 19:00 | GPH Ispat | 95 | 16:00 | Barapukuria | 56 | 20:00
Rajendrapur | 112 | 19:00 | Agrabad | 84 | 14:00 | Panchagar | 58 | 24:00
Valuka | 114 | 11:00 | Goalpara | 29 | 1:00 | Joldhaka | 63 | 21:00
Tangail | 192 | 20:00 | Central S/S | 99 | 1:00 | Kurigram | 62 | 21:00
Mymensing | 232 | 21:00 | Noapara | 49 | 19:30 | Mithapukur | 37 | 15:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-06 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 6:00 | 401 | 15:00 | Kaliakoir | 396 | 0.75 | 383 | 0.5
| Bheramara | 401 | 4:00 | 394 | 21:00 | Bhulta | 390 | 0.25 | 376 | 0.625
| Ashuganj(N) | 397 | 4:00 | 382 | 16:00 | Gopalganj | 408 | 0.625 | 386 | 0.875
| Payra | 412 | 1:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 238 | 20:00 | 230 | 6:00
| Ishurdi | 235 | 18:00 | 223 | 19:30 | Megnaghat | 236 | 6:00 | 231 | 14:00
| Ashuganj | 243 | 6:00 | 236 | 13:00 | Fenchuganj | 243 | 1:00 | 240 | 1:00
| Serajganj | 231 | 6:00 | 225 | 1:00 | Siddhirganj | 235 | 6:00 | 227 | 16:00
| Baghabari | 234 | 5:00 | 224 | 20:00 | Maniknagar | 233 | 6:00 | 225 | 16:00
| Barapukuria | 239 | 6:00 | 224 | 21:00 | Agargaon | 232 | 9:00 | 223 | 16:00
| Bogra | 229 | 6:00 | 212 | 21:00 | Barisal | 245 | 12:00 | 230 | 21:00
| Rajshahi | 231 | 4:00 | 218 | 19:30 | Bhola 225 MW | 244 | 14:00 | 238 | 21:00
| Khulna South | 227 | 3:00 | 215 | 20:00 | AKSML | 237 | 12:00 | 230 | 7:00
| Rampura | 229 | 1:00 | 222 | 15:00 | BSRM | 236 | 2:00 | 230 | 15:00
| Haripur | 233 | 3:00 | 225 | 12:00 | Bibiyana | 244 | 6:00 | 236 | 20:00
| Hasnabad | 230 | 2:00 | 226 | 10:00 | Bhulta | 234 | 2:00 | 226 | 12:00
| Shyampur | 231 | 1:00 | 224 | 10:00 | Ashuganj (S) | 239 | 7:00 | 233 | 13:00
| Aminbazar | 233 | 1:00 | 226 | 2:00 | Kaliakoir | 233 | 5:00 | 223 | 15:00
| Tongi | 230 | 4:00 | 220 | 13:00 | GPH | 237 | 20:00 | 229 | 15:00
| Comilla (N) | 236 | 6:00 | 230 | 11:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 131 | 15:00 | Madanhat | 140 | 0.75 | 135 | 0.041667
| Munsiganj | 139 | 1:00 | 133 | 16:00 | Hathazari | 138 | 0.83333 | 134 | 0.16667
| Sonargaon | 136 | 1:00 | 132 | 9:00 | Khulshi | 136 | 0.75 | 130 | 0.625
| Shyampur | 139 | 1:00 | 134 | 16:00 | Halishahar | 138 | 0.83333 | 132 | 0.33333
| Bhulta | 131 | 1:00 | 120 | 13:00 | Baraulia | 138 | 0.041667 | 132 | 0.45833
| Madanganj | 139 | 1:00 | 132 | 15:00 | Sikalbaha | 139 | 0.75 | 132 | 0.625
| Shitalakhya | 139 | 1:00 | 134 | 13:00 | Dohazari | 133 | 0.70833 | 127 | 0.625
| Rahim steal | 136 | 1:00 | 131 | 14:00 | Cox'sbazar | 121 | 0.5 | 109 | 0.91667
| Matuail | 135 | 1:00 | 131 | 15:00 | Chandraghona | 138 | 0.75 | 134 | 0.33333
| Ghorasal | 140 | 1:00 | 138 | 10:00 | Kaptai | 137 | 0.75 | 132 | 0.29167
| Narsinghdi | 131 | 6:00 | 125 | 19:30 | A. Khaer Stl. | 136 | 0.75 | 132 | 0.20833
| Haripur (SBU) | 137 | 1:00 | 131 | 15:00 | Bakulia | 137 | 0.75 | 131 | 0.25
| Sreenagar | 132 | 1:00 | 126 | 13:00 | Julda | 138 | 0.041667 | 131 | 0.25
| Ullon | 133 | 6:00 | 126 | 15:00 | TK Chemical | 139 | 0.83333 | 133 | 0.20833
| Hasnabad | 138 | 1:00 | 133 | 16:00 | Modern Steel | 137 | 0.79167 | 133 | 0.45833
| Magbazar | 135 | 4:00 | 126 | 15:00 | Shahmirpur | 139 | 0.875 | 133 | 0.625
| Maniknagar | 137 | 3:00 | 129 | 13:00 | Khagrachhari | 138 | 0.75 | 133 | 0.625
| Bangabhaban | 137 | 3:00 | 129 | 13:00 | Matarbari | 128 | 0.54167 | 115 | 0.25
| Motijheel | 137 | 3:00 | 129 | 13:00 | Baroiar Hat | 138 | 0.41667 | 134 | 0.58333
| Narinda | 137 | 3:00 | 129 | 13:00 | Rangamati | 138 | 18:00 | 133 | 7:00
| Kazla | 137 | 3:00 | 129 | 13:00 | Agrabad | 138 | 20:00 | 131 | 16:00
| Dhanmondi | 136 | 1:00 | 130 | 12:00 | Goalpara S/S | 140 | 12:00 | 133 | 0.8125
| Lalbag | 132 | 1:00 | 127 | 16:00 | Khulna Central S/S | 139 | 12:00 | 132 | 0.8125
| Madartek | 134 | 4:00 | 126 | 13:00 | Noapara | 137 | 12:00 | 129 | 0.8125
| Dhaka University | 134 | 3:00 | 126 | 14:00 | Jessore | 131 | 12:00 | 121 | 0.8125
| Aftabnagar | 134 | 1:00 | 127 | 11:00 | Benapol | 132 | 0.75 | 121 | 0.77083
| Fatullah | 139 | 1:00 | 134 | 12:00 | Jhenida | 129 | 12:00 | 117 | 0.875
| Nawabganj | 132 | 1:00 | 127 | 16:00 | Bottail | 133 | 0.75 | 124 | 0.8125
| Keraniganj | 132 | 1:00 | 127 | 16:00 | G.K Project | 138 | 0.41667 | 132 | 0.8125
| Mirpur | 134 | 3:00 | 127 | 16:00 | Faridpur | 137 | 0.75 | 127 | 0.875
| Kalyanpur | 135 | 1:00 | 130 | 10:00 | Rajbari | 134 | 0.25 | 125 | 0.875
| Gulshan | 133 | 3:00 | 125 | 16:00 | Madaripur | 139 | 0.29167 | 132 | 0.83333
| Uttara | 133 | 1:00 | 126 | 14:00 | Shariyatpur S/S | 141 | 18:00 | 130 | 0.875
| Uttara New | 134 | 2:00 | 126 | 17:00 | Gopalganj | 142 | 0.25 | 132 | 0.875
| Kamrangirchar | 132 | 3:00 | 126 | 16:00 | Bagerhat | 136 | 17:00 | 129 | 0.20833
| Savar | 137 | 6:00 | 129 | 16:00 | Mongla | 135 | 10:00 | 124 | 0.083333
| Bhasantec | 138 | 1:00 | 131 | 15:00 | Satkhira | 137 | 12:00 | 128 | 4:00
| Agargaon | 139 | 3:00 | 132 | 15:00 | Gallamari | 140 | 0.125 | 133 | 5:00
| Satmosjid | 138 | 1:00 | 131 | 16:00 | Magura | 130 | 18:00 | 115 | 0.95833
| Tongi | 140 | 4.00 | 131 | 16:00 | Narail | 127 | 0.5 | 115 | 0.875
| Kabirpur | 137 | 3:00 | 131 | 12:00 | Chuadanga | 133 | 15:00 | 119 | 0.8125
| Basundhara | 140 | 18:30 | 126 | 15:00 | Borguna | 138 | 10:00 | 126 | 0.875
| Manikganj | 142 | 6.00 | 134 | 20:00 | Barisal(N) | 140 | 14:00 | 130 | 21:00
| Joydevpur | 140 | 1:00 | 135 | 15:00 | Barisal (S) | 138 | 0.41667 | 128 | 0.875
| New Tongi | 140 | 3:00 | 127 | 14:00 | Patuakhali(S) | 136 | 0.58333 | 122 | 0.875
| Kodda | 138 | 1:00 | 120 | 15:00 | Bhandaria | 137 | 0.58333 | 124 | 0.875
| Dhamrai | 135 | 6.00 | 126 | 19:00 | Ishurdi | 137 | 18:00 | 130 | 19:30
| Rajendrapur | 136 | 2:00 | 117 | 15:00 | Ruppur Paromanobik | 135 | 4:00 | 130 | 19:30
| Valuka | 120 | 18:00 | 108 | 14:00 | Natore | 137 | 18:00 | 127 | 21:00
| Tangail | 133 | 18:00 | 125 | 12:00 | Bogra | 137 | 6:00 | 125 | 1:00
| Mymensing | 124 | 18:00 | 112 | 13:00 | Noagaon | 132 | 6:00 | 117 | 21:00
| Kishorganj | 126 | 7:00 | 119 | 12:00 | Rajshahi | 135 | 18:00 | 127 | 19:30
| Netrokona | 120 | 2:00 | 109 | 12:00 | Rajshahi New | 136 | 13:00 | 128 | 19:30
| Jamalpur | 134 | 18:00 | 111 | 14:00 | C.Nawabganj | 137 | 18:00 | 128 | 19:30
| Sherpur | 132 | 18:00 | 109 | 13:00 | Amnura | 138 | 18:00 | 129 | 19:30
| Srimongal | 135 | 6:00 | 131 | 1:00 | Pabna | 134 | 18:00 | 127 | 19:30
| Shahjibazar | 133 | 5:00 | 129 | 1:00 | Shahjadpur | 138 | 10:00 | 133 | 20:00
| Fenchuganj | 137 | 9:00 | 132 | 3:00 | Serajganj | 134 | 6:00 | 133 | 20:00
| Khulawara | 135 | 9:00 | 131 | 1:00 | Niyamatpur | 131 | 5:00 | 113 | 21:00
| Sylhet | 133 | 8:00 | 130 | 12:00 | Joypurhat | 134 | 6:00 | 115 | 21:00
| Chatak | 133 | 7:00 | 129 | 1:00 | Sherpur(Bogura) | 136 | 6:00 | 125 | 21:00
| Sunamganj | 131 | 8:00 | 126 | 1:00 | Mohastangor | 137 | 6:00 | 123 | 21:00
| Biani Bazar | 133 | 18:30 | 127 | 1:00 | Bangura | 136 | 16:00 | 129 | 19:00
| Comilla(s) | 129 | 2:00 | 124 | 12:00 | Rangpur | 132 | 7:00 | 115 | 21:00
| Comilla(n) | 142 | 6:00 | 137 | 21:00 | Lalmonirhat | 133 | 7:00 | 114 | 21:00
| Chandpur | 141 | 13:00 | 137 | 18:00 | Saidpur | 132 | 6:00 | 113 | 21:00
| Feni | 138 | 9:00 | 134 | 1:00 | Purbasadipur | 130 | 7:00 | 110 | 21:00
| Chowmuhani | 135 | 7:00 | 132 | 1:00 | Thakurgaon | 130 | 6:00 | 107 | 21:00
| Ashuganj | 138 | 7:00 | 134 | 15:00 | Palashbari | 135 | 6:00 | 116 | 1:00
| Daudkandi | 138 | 9:00 | 134 | 8:00 | Barapukuria | 139 | 6:00 | 124 | 21:00
| B.Baria | 133 | 6:00 | 127 | 19:30 | Panchagar | 134 | 6:00 | 106 | 21:00
| Ramganj | 138 | 10:00 | 132 | 22:00 | Joldhaka | 130 | 0.25 | 109 | 0.875
| Chaddagram | 138 | 1:00 | 137 | 7:00 | Kurigram | 136 | 0.25 | 113 | 0.875
| PHP | 138 | 1:00 | 133 | 15:00 | Mithapukur | 136 | 0.25 | 119 | 0.041667
| Kochua | 139 | 3:00 | 135 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-06
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 442 | 8877 | 3713 | 12590 |  |  |  | QF-LDC-11
0:30 | 462 | 8271.5 | 3716 | 11987.5 | Date: | 2021-09-06
1:00 | 482 | 7666 | 3719 | 11385
1:30 | 423 | 7719 | 3722.5 | 11441.5
2:00 | 364 | 7772 | 3726 | 11498
2:30 | 290 | 7747 | 3762 | 11509 | [5 empty] | Gen. at Eve. Peak | 13082 | 13082 MW (19:30 )
3:00 | 216 | 7722 | 3798 | 11520 | [6 empty] | 19:30
3:30 | 201 | 7637 | 3731 | 11368 | [5 empty] | Gen. at Day Peak | 11421 | 11421 MW (12:00 )
4:00 | 186 | 7552 | 3664 | 11216 | [6 empty] | 12:00
4:30 | 170 | 7533 | 3522 | 11055 | [5 empty] | Highest Generation | 13082
5:00 | 154 | 7514 | 3380 | 10894 | [6 empty] | 19:30
5:30 | 146 | 7354.5 | 3224 | 10578.5
6:00 | 138 | 7195 | 3068 | 10263
6:30 | 114 | 7055 | 3000 | 10055
7:00 | 90 | 6915 | 2932 | 9847
7:30 | 75 | 6965 | 2902 | 9867
8:00 | 60 | 7015 | 2872 | 9887
8:30 | 59 | 7239 | 2881 | 10120
9:00 | 58 | 7463 | 2890 | 10353
9:30 | 31 | 7787.5 | 2890 | 10677.5
10:00 | 4 | 8112 | 2890 | 11002
10:30 | 64 | 8198.5 | 2871 | 11069.5
11:00 | 124 | 8285 | 2852 | 11137
11:30 | 75 | 8325 | 2954 | 11279
12:00 | 26 | 8365 | 3056 | 11421
12:30 | 42 | 8366.5 | 3105.5 | 11472
13:00 | 58 | 8368 | 3155 | 11523
13:30 | 46 | 8325.5 | 3139.5 | 11465
14:00 | 34 | 8283 | 3124 | 11407
14:30 | 125 | 8309.5 | 3288.5 | 11598
15:00 | 216 | 8336 | 3453 | 11789
15:30 | 178 | 8274.5 | 3380.5 | 11655
16:00 | 140 | 8213 | 3308 | 11521
16:30 | 178 | 8074 | 3247 | 11321
17:00 | 216 | 7935 | 3186 | 11121
17:30 | 136 | 7963.5 | 3071 | 11034.5
18:00 | 56 | 7992 | 2956 | 10948
18:30 | 120 | 8488 | 3353 | 11841
19:00 | 184 | 8984 | 3750 | 12734
19:30 | 332 | 9209 | 3873 | 13082
20:00 | 394 | 9175 | 3865 | 13040 |  |  |  | Executive Engineer
20:30 | 395 | 9142.5 | 3859.5 | 13002 |  |  |  | Network Operation Division
21:00 | 396 | 9110 | 3854 | 12964
21:30 | 435 | 9078 | 3811.5 | 12889.5
22:00 | 474 | 9046 | 3769 | 12815 |  |  |  |  | Page 6 of 7
22:30 | 471 | 9045.5 | 3755 | 12800.5
23:00 | 468 | 9045 | 3741 | 12786
23:30 | 455 | 8961 | 3727 | 12688
24:00 | 442 | 8877 | 3713 | 12590
13082 MW (19:30 )
11421 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-06 |  | Energy | 278831552
[11 empty] | 2021-09-06 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4048 | 718 | 1908 | 4468 | 703 | 148 | 635 | 0 | 132 | 0
0:30 | 4120.5 | 717.5 | 1633.5 | 4109.5 | 712 | 126.5 | 542 | 0 | 111 | 0 | Date: | 2021-09-06
1:00 | 4193 | 717 | 1359 | 3751 | 721 | 105 | 449 | 0 | 90 | 0
1:30 | 4208.5 | 717 | 1368.5 | 3780 | 711.5 | 105 | 463 | 0 | 88 | 0 | [7 empty] | Total Energy | 278.8316 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4224 | 717 | 1378 | 3809 | 702 | 105 | 477 | 0 | 86 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4241.5 | 716.5 | 1389 | 3805.5 | 698.5 | 105 | 466 | 0 | 87 | 0 | [7 empty] | Energy Requirement | 278.8316
3:00 | 4259 | 716 | 1400 | 3802 | 695 | 105 | 455 | 0 | 88 | 0
3:30 | 4258 | 716.5 | 1366.5 | 3750.5 | 691 | 105 | 391.5 | 0 | 89 | 0 | [6 empty] | Shortage
4:00 | 4257 | 717 | 1333 | 3699 | 687 | 105 | 328 | 0 | 90 | 0
4:30 | 4253 | 717.5 | 1351.5 | 3552.5 | 680 | 105 | 304.5 | 0 | 91 | 0
5:00 | 4249 | 718 | 1370 | 3406 | 673 | 105 | 281 | 0 | 92 | 0
5:30 | 4252.5 | 718 | 1369 | 3232 | 638.5 | 104 | 173.5 | 0 | 89 | 2
6:00 | 4256 | 718 | 1368 | 3058 | 604 | 103 | 66 | 0 | 86 | 4
6:30 | 4240.5 | 718 | 1337.5 | 2915.5 | 600 | 102.5 | 41 | 0 | 86 | 14 |  |  |  |  | Coal
7:00 | 4225 | 718 | 1307 | 2773 | 596 | 102 | 16 | 0 | 86 | 24
7:30 | 4223 | 718 | 1288.5 | 2798 | 585 | 103.5 | 16 | 0 | 88 | 47 |  |  |  | Oil |  |  |  | ,
8:00 | 4221 | 718 | 1270 | 2823 | 574 | 105 | 16 | 0 | 90 | 70
8:30 | 4220 | 718 | 1282.5 | 3046 | 574.5 | 105 | 16 | 0 | 95 | 63
9:00 | 4219 | 718 | 1295 | 3269 | 575 | 105 | 16 | 0 | 100 | 56
9:30 | 4213 | 718 | 1313.5 | 3554 | 564.5 | 105.5 | 24 | 0 | 105 | 80
10:00 | 4207 | 718 | 1332 | 3839 | 554 | 106 | 32 | 0 | 110 | 104
10:30 | 4213 | 718 | 1349.5 | 3882.5 | 543 | 106 | 40 | 0 | 109 | 108.5
11:00 | 4219 | 718 | 1367 | 3926 | 532 | 106 | 48 | 0 | 108 | 113
11:30 | 4200.5 | 718 | 1390 | 4058.5 | 532 | 105.5 | 68 | 0 | 115 | 91.5
12:00 | 4182 | 718 | 1413 | 4191 | 532 | 105 | 88 | 0 | 122 | 70
12:30 | 4201.5 | 718 | 1414 | 4178.5 | 542 | 125 | 88 | 0 | 123 | 82
13:00 | 4221 | 718 | 1415 | 4166 | 552 | 145 | 88 | 0 | 124 | 94
13:30 | 4221 | 718 | 1415 | 4166 | 552 | 145 | 88 | 0 | 124 | 94
14:00 | 4221 | 718 | 1415 | 4166 | 552 | 145 | 88 | 0 | 124 | 94
14:30 | 4197.5 | 718 | 1479 | 4188 | 527 | 143 | 196.5 | 0 | 129 | 78
15:00 | 4174 | 718 | 1543 | 4210 | 502 | 141 | 305 | 0 | 134 | 62
15:30 | 4171.5 | 718 | 1570.5 | 4022.5 | 492 | 141 | 355.5 | 0 | 132 | 52
16:00 | 4169 | 718 | 1598 | 3835 | 482 | 141 | 406 | 0 | 130 | 42
16:30 | 4126.5 | 718 | 1680.5 | 3626 | 486.5 | 142 | 384.5 | 0 | 126 | 31
17:00 | 4084 | 718 | 1763 | 3417 | 491 | 143 | 363 | 0 | 122 | 20
17:30 | 4039.5 | 717.5 | 1649 | 3446.5 | 486 | 144 | 420.5 | 0 | 120 | 11.5
18:00 | 3995 | 717 | 1535 | 3476 | 481 | 145 | 478 | 0 | 118 | 3
18:30 | 4040 | 717 | 1680.5 | 4027 | 530.5 | 145 | 570.5 | 0 | 129 | 1.5
19:00 | 4085 | 717 | 1826 | 4578 | 580 | 145 | 663 | 0 | 140 | 0
19:30 | 4131 | 717 | 1874 | 4725 | 670 | 145 | 672 | 0 | 148 | 0
20:00 | 4119 | 717 | 1887 | 4679 | 681 | 147 | 674 | 0 | 136 | 0
20:30 | 4100.5 | 717.5 | 1890 | 4634 | 713 | 147 | 665 | 0 | 135 | 0
21:00 | 4082 | 718 | 1893 | 4589 | 745 | 147 | 656 | 0 | 134 | 0
21:30 | 4070.5 | 718 | 1898 | 4528.5 | 727 | 147.5 | 663 | 0 | 137 | 0
22:00 | 4059 | 718 | 1903 | 4468 | 709 | 148 | 670 | 0 | 140 | 0
22:30 | 4053 | 717.5 | 1899 | 4468 | 706.5 | 148 | 668.5 | 0 | 140 | 0
23:00 | 4047 | 717 | 1895 | 4468 | 704 | 148 | 667 | 0 | 140 | 0
23:30 | 4047.5 | 717.5 | 1901.5 | 4468 | 703.5 | 148 | 651 | 0 | 136 | 0 | Max Temp. in Dhaka |  | 34.8° C
24:00 | 4048 | 718 | 1908 | 4468 | 703 | 148 | 635 | 0 | 132 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-06
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 40 | 40 | 40 | 40 | 40 | 38 | 37 | 40 | 40 | 41 | 41 | 40 | 80 | 78 | 76 | 76 | 78 | 80 |  | 80 | 80 | 82 | 82 | 83 | 83 | 83 | 1325073
2 | Karnaphuli Hydro PP Unit-4 & 5 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 1584000
3 | Chattogram TPP-1
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 3000000
5 | Raozan 25 MW PP | 26 | 25 | 25 | 25 | 25 | 0 |  |  | 10 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 545722
| Teknaf 20MW PP (Solartech) | [6 empty] | 5 | 12 | 15 | 13 | 12 |  |  |  |  | 2 | 1 | [9 empty] | 59535
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | 60 | 51 | 60 | 0 | [9 empty] | 39 | 85 | 85 |  | 85 | 85 | 85 | 70 | 85 | 85 | 85 | 1051660
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 |  | 71 | 71 | 71 | 71 | 71 | 71 | 73 | 1729599
| Daudkandi 200 MW PP (B.Trac) | [8 empty] | 60 | 180 | 200 | 200 | 200 | 200 | 200 | 200 | 10 |  |  | 100 | 150 | 197 | 174 | 100 | 100 | 100 | 2225856
14 | Titas 50 MW Peaking PP | [13 empty] | 41 | 46 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 540016
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 250 | 280 | 280 | 250 | 250 | 250 | 250 | 280 | 280 | 280 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 |  | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 6470948
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 300 | 300 | 300 | 300 | 245 | 250 | 285 | 300 | 300 | 300 | 300 | 300 | 290 | 281 | 281 | 288 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7080652
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4814400
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 513936
33 | Ashuganj 225 MW CCPP | 215 | 215 | 216 | 216 | 214 | 216 | 214 | 211 | 196 | 190 | 184 | 181 | 182 | 177 | 185 | 193 | 199 | 209 |  | 207 | 207 | 206 | 205 | 212 | 213 | 214 | 4915000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 320 | 320 | 320 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 6995000
| Ashuganj 450 MW CCPP(North) | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 270 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6922000
35 | Ashuganj 55 MW PP (Precision) | 30 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 687840
36 | Chandpur 150 MW CCPP | 140 | 140 | 138 | 141 | 140 | 138 | 139 | 142 | 142 | 140 | 141 | 140 | 139 | 140 | 141 | 140 | 138 | 140 |  | 140 | 141 | 140 | 140 | 140 | 141 | 140 | 3344140
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 339 | 359 | 357 | 361 | 355 | 361 | 360 | 362 | 361 | 363 | 363 | 365 | 364 | 365 | 363 | 363 | 363 | 362 |  | 360 | 363 | 362 | 361 | 362 | 361 | 361 | 8796160
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 225 | 225 | 225 | 225 | 225 | 225 | 250 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 6540250
41 | Haripur 360MW CCPP(HPL) | 192 | 200 | 202 | 212 | 226 | 226 | 226 | 216 | 212 | 212 | 206 | 204 | 160 | 147 | 147 | 148 | 150 | 150 |  | 180 | 180 | 192 | 194 | 193 | 193 | 206 | 4594000
42 | RPCL 210MW CCPP | 135 | 141 | 142 | 142 | 139 | 160 | 132 | 136 | 121 | 106 | 108 | 108 | 105 | 104 | 106 | 106 | 124 | 125 |  | 118 | 119 | 118 | 118 | 117 | 123 | 127 | 2870960
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 3 | 6 | 35 | 21 | 52 | 53 | 23 | 49 | 43 | 31 | 19 | 8 | 0 | [8 empty] | 324340
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 44 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1029000
45 | Fenchugonj CCPP Phase-2 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 41 |  | 41 | 41 | 41 | 41 | 41 | 41 | 41 | 949920
46 | Shajibazar 330 MW CCPP | 162 | 161 | 161 | 161 | 161 | 160 | 162 | 161 | 159 | 160 | 159 | 158 | 155 | 151 | 158 | 161 | 161 | 162 |  | 160 | 160 | 162 | 162 | 163 | 162 | 160 | 3719000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 43 | 43 | 69 | 78 | 81 | 55 |  | 80 | 81 | 81 | 81 | 81 | 80 | 80 | 1315200
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 213 | 213 | 213 | 213 | 213 | 179 | 179 | 179 | 200 | 200 | 221 | 221 | 222 | 222 | 221 | 221 | 209 | 193 |  | 228 | 228 | 228 | 228 | 220 | 220 | 220 | 5118890
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 0 | 5 | 5 | 8 | 8 | 8 | 8 |  |  |  | 5 | 5 | 5 | 5 | 5 | 5 |  |  |  | 5 | 11 | 11 |  |  |  |  | 78432
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1160400
56 | Shahjahanulla 25 MW PP | 24 | 8 | 16 | 24 | 24 | 8 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 523584
57 | Bibiana-II 341 MW CCPP (Summit) | 270 | 280 | 290 | 270 | 290 | 260 | 280 | 290 | 290 | 310 | 280 | 290 | 280 | 300 | 300 | 300 | 310 | 280 |  | 285 | 320 | 310 | 300 | 305 | 290 | 300 | 7175500
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 325 | 325 | 325 | 326 | 325 | 326 | 325 | 325 |  | 325 | 325 | 325 | 325 | 325 | 326 | 325 | 7754000
58 | Nababganj 55 MW PP (Southern power ) | [10 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 513500
59 | Tangail Palli Power Gen 22 MW | 22 | 15 | 20 | 24 | 24 | 24 | 24 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 19 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 525360
60 | Barabkunda 22 MW PP (Regent) | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 | 18 | 18 | 18 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 463536
61 | Narshingdi 22 MW PP (Doreen) |  |  |  |  | 0 | 21 | 21 | 21 | 21 | 18 | 18 | 18 | 18 | 18 | 18 | 20 | 21 |  |  | 15 | 21 | 21 | 21 | 21 | 21 | 22 | 325296
62 | Tangail 22 MW PP (Doreen) | 21 | 0 | 21 | 21 | 21 | 21 |  |  |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 426888
63 | Impoprt (Tripura) | 90 | 86 | 88 | 90 | 92 | 86 | 86 | 90 | 100 | 110 | 108 | 122 | 124 | 126 | 134 | 130 | 122 | 118 |  | 140 | 148 | 136 | 134 | 140 | 140 | 132 | 2731200
64 | Malancha, Ctg. EPZ (United) | 36 | 38 | 38 | 38 | 38 | 38 | 37 | 3 | 5 | 4 | 4 | 10 | 10 | 5 | 7 | 2 | 7 | 4 |  | 4 | 9 | 9 | 17 | 26 | 27 | 27 | 477600
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 22 | 22 | 470412
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 |  | 11 | 8 | 11 | 11 | 11 | 11 | 11 | 217440
67 | Jangalia 33MW PP (Summit) | 25 | 17 | 7 | 0 |  |  |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 468100
68 | Cumilla 25 MW PP (Summit) | [10 empty] | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 21 | 21 | 21 | 21 | 275100
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 9 | 9 | 9 | 9 | 28 | 28 | 28 | 28 | 28 | 28 | 28 |  | 20 | 28 | 28 | 28 | 28 | 28 | 29 | 562680
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 821300
72 | Rupganj 33 MW PP(Summit) | 0 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 17 | 25 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 706600
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 51 |  | 100 | 98 | 114 | 114 | 114 | 114 | 114 | 2714340
| Chowmuhani 113 MW | 97 | 92 | 93 | 91 | 99 | 97 | 97 | 97 | 99 | 92 | 98 | 98 | 99 | 96 | 98 | 100 | 99 | 98 |  | 105 | 98 | 97 | 98 | 97 | 98 | 98 | 2344440
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 159 | 144 | 144 | 3889440
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 17 | 16 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 47 | 51 | 51 | 51 | 51 | 51 | 34 | 667680
79 | Kodda 150MW PP | 82 | 82 | 32 | 32 | 16 | 16 | 16 | 16 | 16 | 32 | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 133 |  | 133 | 133 | 133 | 133 | 133 | 133 | 115 | 1572960
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 187200
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 43 | 43 | 16 | 16 | 36 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 8 |  | 25 | 43 | 43 | 43 | 43 | 43 | 43 | 940070
| Gazipur 100 MW PP | 52 | 53 | 53 | 53 | 53 | 53 | 52 | 53 | 55 | 55 | 53 | 53 | 53 | 53 | 53 | 53 | 53 | 53 |  | 90 | 90 | 90 | 90 | 90 | 90 | 34 | 1453200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | [5 empty] | 5 | 1 | 0 | 0 | [9 empty] | 13561
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 41 |  | 45 | 54 | 54 | 54 | 54 | 54 | 54 | 1277290
| Karnaphuli Power Ltd. | 110 | 104 | 104 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 104 | 103 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2673006
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 29 | 0 | 0 | 27 | 39 | 10 |  |  | 31 | 41 | 39 | 39 | 36 | 37 | 36 | 37 | 39 | 51 |  | 50 | 60 | 60 | 61 | 61 | 61 | 61 | 912648
86 | Meghnaghat CCPP ( Summit) | 285 | 275 | 235 | 245 | 270 | 235 | 250 | 290 | 270 | 270 | 240 | 265 | 290 | 255 | 275 | 280 | 250 | 245 |  | 275 | 295 | 250 | 312 | 280 | 275 | 250 | 6462749
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 95 | 95 | 95 | 95 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 95 | 95 | 95 | 1956480
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 10 | 20 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 10 |  | 80 | 80 | 80 | 100 | 100 | 100 | 100 | 1811640
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 815964
94 | Gagnagar 102 MW PP (Digital Power) | 50 | 48 | 48 | 48 | 48 | 48 | 32 | 32 | 64 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 2021760
95 | Patenga 50MW PP (Baraka) | 50 | 32 | 32 | 32 | 32 | 28 |  |  | 15 | 43 | 44 | 48 | 50 | 49 | 50 | 50 | 20 | 39 |  | 50 | 50 | 50 | 50 | 50 | 40 | 39 | 920160
96 | Chattogram 108 MW PP (ECPV) | 97 | 92 | 25 | 6 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 18 | 79 |  | 90 | 90 | 95 | 95 | 96 | 96 | 96 | 960960
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 41 | 41 | 41 | 41 | 41 | 41 | 30 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 | 40 |  | 40 | 40 |  |  | 20 | 40 | 40 | 899363
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 37 | 0 | 17 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 55 | 37 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 983568
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3336464
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 1 | 1 | 2 | 1 | 1 |  | 2 | 2 | 1 | 1 | 0 | 0 | [8 empty] | 10950
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 51 | 54 | 54 | 54 | 54 | 1299600
104 | Keranigonj 300 MW PP (APR) | 12 | 158 | 252 | 208 | 108 | 0 |  |  | 23 | 107 | 109 | 200 | 157 | 206 | 207 | 108 |  | 11 |  | 200 | 230 | 214 | 110 | 100 | 100 | 150 | 3011124
105 | Bramhangoan 100 MW PP (Aggreko) | [8 empty] | 25 | 65 | 92 | 92 | 93 | 94 | 94 | 60 |  | 26 |  | 94 | 94 | 94 | 97 | 50 | 50 | 80 | 1112570
106 | Mymensingh 200 MW PP (United) | 111 | 112 | 114 | 96 | 96 | 38 | 38 | 38 | 38 | 37 | 37 | 37 | 36 | 36 | 36 | 38 | 45 | 182 |  | 184 | 184 | 183 | 184 | 188 | 188 | 115 | 2145600
112 | Aurahati 100MW PP (Aggreko) | [8 empty] | 96 | 98 | 98 | 99 | 96 | 99 | 96 | 96 | 56 | 26 |  | 100 | 100 | 99 | 100 | 98 | 99 | 99 | 1437121
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 132 | 132 | 132 | 130 | 127 | 87 | 89 | 106 | 123 | 132 | 132 | 120 | 121 | 114 | 113 | 114 | 131 |  | 132 | 132 | 131 | 132 | 136 | 149 | 149 | 3026880
115 | Juldah 100 MW PP Unit-3 (Acorn) | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 |  | 100 | 100 | 100 | 100 | 100 | 100 | 76 | 1918080
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 150 |  | 168 | 190 | 200 | 200 | 200 | 200 | 200 | 4686720
117 | Ashuganj 150MW PP (Midland) | 137 | 135 | 138 | 137 | 142 | 148 | 142 | 133 | 128 | 135 | 137 | 132 | 137 | 137 | 138 | 133 | 133 | 138 |  | 138 | 138 | 138 | 138 | 140 | 140 | 143 | 3305309
118 | Bibiyana-III 400 MW CCPP | 316 | 316 | 316 | 316 | 316 | 316 | 315 | 315 | 316 | 316 | 316 | 316 | 316 | 314 | 315 | 314 | 314 | 316 |  | 315 | 315 | 316 | 316 | 316 | 315 | 316 | 7612000
| Jamalpur 115 MW PP (United) | 77 | 77 | 77 | 57 | 57 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 64 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 77 | 1552800
| Anwara 300 MW PP (United) | 111 | 107 | 106 | 105 | 106 | 106 | 106 | 106 | 106 | 273 | 300 | 305 | 305 | 160 | 160 | 160 | 160 | 214 |  | 285 | 285 | 305 | 286 | 303 | 305 | 305 | 4712073
| Juldah unit-2 (Acorn) | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 80 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 80 | 2070720
| Anlima Energy Ltd. | 116 | 116 | 104 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 114 | 114 | 114 |  | 114 | 114 | 96 | 112 | 114 | 114 | 114 | 2746200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 18 | 35 | 29 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 658080
| Spectra Solar Plant Ltd. | [5 empty] | 1 | 9 | 15 | 12 | 29 | 35 | 36 | 32 | 32 | 20 | 16 | 8 | 2 | [8 empty] | 253938
120 | Eastern Zone Total | 7666 | 7772 | 7722 | 7552 | 7514 | 7195 | 6915 | 7015 | 7463 | 8112 | 8285 | 8365 | 8368 | 8283 | 8336 | 8213 | 7935 | 7992 |  | 8984 | 9209 | 9175 | 9110 | 9046 | 9045 | 8877 | 195932187
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 20 | 20 | 20 | 20 | 20 | 4 | [7 empty] | 3 | 5 | 5 | 10 | 16 |  | 22 | 26 | 25 | 25 | 25 | 25 | 25 | 286680
| Khulna 225 MW CCPP | 60 | 100 | 158 | 40 | 0 | [6 empty] | 40 | 40 | 70 | 100 | 150 | 40 | 40 |  | 158 | 158 | 158 | 158 | 158 | 158 | 158 | 1870080
129 | Rupsha 105 MW PP (Orion rupsha) | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 53 |  | 80 | 88 | 88 | 88 | 88 | 88 | 88 | 2077920
130
131
132 | United Payra Power Ltd. | 63 | 63 | 35 | 17 | 0 | [14 empty] | 24 | 35 | 17 |  |  |  |  | 273600
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 222 | 222 | 219 | 223 | 220 | 183 | 183 | 183 | 183 | 183 | 200 | 179 | 162 | 162 | 216 | 218 | 152 |  | 220 | 220 | 220 | 222 | 221 | 221 | 221 | 4843800
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [19 empty] | 16 | 16 | 16 |  |  |  |  | 28800
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 40 | 52 | 52 | 61 | 78 | 76 | 82 | 12 | 11 | 11 |  | 11 | 11 | 22 | 22 | 22 | 22 | 22 | 688561
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 15 | 15 | 15 | 15 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 88 | 88 | 88 | 88 | 88 | 88 | 1602209
140 | Bhola 33 MW PP (Venture) | 34 | 34 | 34 | 35 | 34 | 32 | 22 | 19 | 18 | 19 | 20 | 20 | 22 | 22 | 23 | 20 | 17 | 20 |  | 31 | 29 | 32 | 32 | 34 | 34 | 34 | 637571
141 | Noapara 100 MW PP (Bangla Trac) | 100 | 100 | 100 | 100 | 50 | 0 |  |  |  | 1 | 10 | 41 | 70 | 50 | 89 | 50 |  |  |  | 56 | 100 | 100 | 97 | 100 | 100 | 100 | 1444800
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 717 | 717 | 716 | 717 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 718 | 717 |  | 717 | 717 | 717 | 718 | 718 | 717 | 718 | 17336000
147 | Bheramara 410 MW CCPP | 350 | 350 | 350 | 360 | 360 | 365 | 365 | 360 | 355 | 350 | 345 | 335 | 320 | 305 | 300 | 280 | 275 | 260 |  | 265 | 260 | 250 | 240 | 230 | 225 | 225 | 7655040
148 | Payra 1320 MW | 570 | 550 | 540 | 530 | 520 | 450 | 440 | 420 | 420 | 400 | 380 | 380 | 400 | 360 | 350 | 330 | 340 | 330 |  | 430 | 520 | 530 | 590 | 550 | 550 | 550 | 11938400
149
150 | Barapukuria TPP Unit-1
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 151 | 152 | 155 | 157 | 153 | 154 | 156 | 154 | 155 | 154 | 152 | 152 | 152 | 152 | 152 | 152 | 151 | 151 |  | 150 | 150 | 151 | 155 | 159 | 154 | 153 | 3770200
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | 43 | 43 | 43 | 0 | [7 empty] | 41 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 749040
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 2 | 3 | 5 | 5 | 4 | 4 | 4 | 4 | 1 | 1 | 0 | [8 empty] | 35640
157 | Sirajgonj 225MW CCPP Unit-1 (Gas) | 140 | 141 | 141 | 143 | 144 | 144 | 144 | 115 | 129 | 126 | 118 | 120 | 116 | 112 | 110 | 109 | [10 empty] | 2148500
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 190 | 190 | 190 | 193 | 193 | 193 | 194 | 195 | 186 | 180 | 184 | 181 | 173 | 165 | 155 | 158 | 157 | 145 |  | 153 | 163 | 159 | 146 | 138 | 130 | 128 | 4304373
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 186 | 184 | 186 | 184 | 187 | 191 | 193 | 189 | 187 | 186 | 183 | 177 | 170 | 155 | 149 | 158 | 170 | 130 |  | 164 | 182 | 182 | 179 | 174 | 168 | 167 | 4471573
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | [11 empty] | 6 | 65 | 69 | 175 | 241 | 355 | 302 |  | 401 | 410 | 407 | 411 | 407 | 414 | 404 | 3522763
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 30 | 30 | 24 | 24 | 24 | 0 | [8 empty] | 10 | 20 | 36 | 39 |  | 39 | 39 | 39 | 39 | 39 | 36 | 37 | 453743
162 | Bogra 22 MW PP (GBB) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 406560
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 255474
165 | Amnura 50 MW PP(Sinha) | 35 | 35 | 35 | 35 | 35 | 0 |  |  | 25 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 722860
166 | Katakhali 50 MW PP (Northern) | [22 empty] | 8 | 8 | 8 |  | 26469
167 | Katakhali 50 MW Peaking PP | 15 | 15 | 16 | 16 | 16 | 0 | [11 empty] | 13 |  | 28 | 30 | 33 | 31 | 31 | 31 | 16 | 236481
168 | Santahar 50 MW Peaking PP | 18 | 18 | 18 | 18 | 18 | 0 | [13 empty] | 15 | 18 | 18 | 17 | 16 | 16 | 16 | 189218
169 | Natore 52 MW PP (Rajlanka) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 602400
170 | Chapainawabganj 100 MW Peaking PP | 84 | 84 | 84 | 84 | 84 | 46 | [7 empty] | 39 | 46 | 46 | 46 | 54 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 1142360
171 | Baghabari 200 MW PP (Paramount) | 120 | 120 | 173 | 171 | 0 | [6 empty] | 100 | 50 | 25 | 179 |  |  |  |  | 120 | 50 | 50 | 25 |  |  |  | 1223140
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 90 | 110 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2721888
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2745120
173 | Rangpur 20 MW GTPP | 12 | 0 | 0 | 0 | 0 | [16 empty] | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 106 | 70 | 70 | 85 | 94 | 100 | 99 | 104 | 99 | 99 | 99 | 99 | 70 |  | 113 | 113 | 113 | 113 | 113 | 106 | 113 | 2441088
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 3 | 4 | 7 | 7 | 7 | 7 | 5 | 3 | 2 | 1 | [8 empty] | 47014
178
178