## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-12 | Sunday
|  |  | Date (day): | 2021-09-12 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13922.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14720 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-11 | 2021-09-12 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint. |  | 2021-08-16
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 203 | 203 | 203 | 203 |  | 162 | ST under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 332 | 396 | 390 | 390 | 22 |  | Gas shortage
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 291 | 214 | 250 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 280 | 300 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 45 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 34 | 65 | 77 | 77 |  | 23 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 0 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 300 | 320 | 326 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 54 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 82 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 28 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 25 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 240 | 300 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 26 | 305 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 30 | 100 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 72 | 80 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 143 | 144 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 70 | 70 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 71 | 90 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 162 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 36 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2960 | 3682 | 3524 | 3849 | 919 | 915
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 90 | 100 | 100 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 100 | 90 | 120 | 120 | 60 |  | Gas shortage
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 14 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 17 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 43 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 162 | 163 | 158 | 158 | 72 |  | Low water level & Unit-3 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint |  | 2021-08-11
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 89 | 88 | 88 | 88 |  | 17 | Engine problem
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 85 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 80 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 20 | 20 | 20 | 20
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 7 | 15 | 30
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 107 | 306 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 36 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 95 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 114 | 114 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1082 | 1502 | 1566 | 1556 | 320 | 507
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 186 | 207 | 210 | 210
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 345 | 330 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 350 | 310 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem |  | 2021-10-15
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 48 | 47 | 48 | 48 |  | 7 | Engine problem
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 45 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 25 | 35 | 35 | 35 |  | 16 | Engine problem |  | 2021-09-06
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 128 | 140 | 130 | 140 |  | 10 | Engine problem |  | 2021-08-31
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 140 | 140 | 141 | 141 |  | 22 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 160 | 160 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 100 | 150 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 28 | 33 | 33 |  | 0 | Engine problem
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 34 | 34 | 43 | 43 |  | 9 | Engine problem
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 20 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 80 | 200 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 98 | 98 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 98 | 108 | 113 | 113
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 35 | 17 | 35 |  | 19 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1915 | 2189 | 2009 | 2229 | 687 | 105
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 155 | 142 | 130 | 160 | 42 |  | Gas shortage |  | 2021-09-01
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 0 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 38 | 177 | 175 | 200 |  |  |  |  | 2021-09-13
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 28 | 106 | 115 | 115 |  |  |  |  | 2021-09-13
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 13 | 24 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 317 | 471 | 523.6 | 527 | 42 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 30 | 30 | 41 | 41 |  | 49 | Machine problem.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 153 | 157 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 25 | 25 |  | 26 | Engine problem
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 79 | 79 | 80 | 84
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 2021-11-03
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 220 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 317 | 402 | 402
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 325 | 325 | 383 | 383 | 0
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1669 | 1671 | 1903 | 1907 | 246 | 215
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 699 | 701 | 721 | 721
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 0 | 22 |  | 32 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 225 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 240 | 220 | 245 | 245 | 165 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 88 | 105 | 105 | 105 |  | 0 | Engine problem |  | 2021-08-31
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 15 | 15 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1162 | 1391 | 1446 | 1558 | 165 | 101
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 25 | 34 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 65 | 65 | 65 | 65 |  | 129 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 12 | 21 | 40 | 40
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 400 | 622 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 218 | 220 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 54 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 720 | 1016 | 1240 | 1240 | 0 | 129
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 32 | 40 | 40 |  | 31 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 35 | 35 | 35 | 35 | 50 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 50 | 50
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 159 | 139 | 160 | 200 | 20 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 185 | 152 | 185 | 200 | 20 |  | Gas shortage
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 413 | 414 | 400 | 410
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 20 |  | 30 | Engine problem |  | 15-09-2021
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 19 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 0 | 43 | 43 | 43 | 9 |  | Fuel shortage
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 85 | 92 |  | 12 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 185 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1033 | 1474 | 1513 | 1639 | 479 | 83
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 77 | 77 |  | 85
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 274 |  | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 120 | 113 | 198 | 215 | 274 | 185
|  | Total |  |  |  |  | 22031 | 21180 | 10978 | 13509 | 13922.6 | 14720 | 3132 | 2327
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10375.8312 | 12768 | 13158.9131 | 13912.5738
| A. |  | 2021-09-11 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13509 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9207 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13509 | MW
| 3 | Day peak Generation : |  |  | 10978 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12768 | MW
| 4 | Evening peak Generation : |  |  | 13509 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 277.6807 | MKWHr | By Solar | 0.83565 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.3741 | MKWHr |  | By Oil: | 95.5113 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.5711 | MKWHr |  | By Hydro: | 3.8134 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 3132 | MW | Dhaka | 4637 | 4637 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2327 | MW | Chittagong | 1273 | 1273 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5459 | MW | Khulna | 1613 | 1613 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1137.03 | MMCFD |  |  | Rajshahi | 1359 | 1359 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 144295001.408 | ii) Oil : | Taka | 776006860.98 | Comilla | 1280 | 1280 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 60955110.19 | Total | Taka | 981256972.578 | Mymensingh | 967 | 967 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 3.315 | MKWHr. | Sylhet | 591 | 591 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -246 | MW (E to W) at | 20:00 | hrs | Barisal | 391 | 391 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -464 | MW at | 1:00 | hrs | Rangpur | 657 | 657 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 36.8° C |  |  | Total | 12768 | 12768 |  | 0
| B. |  | 2021-09-12 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 35.2° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13800 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14720 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11200 | MW
| 4 | Reserve(Generation end) |  |  |  | 920 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 283.6623 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10254 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 16.9265 | MKWHr. | ii) HVDC Flow at Peak Time |  | 701 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.6486 | MKWHr. | iii) Maximum HVDC Flow : |  | 709 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.25 |  | (b) Today: | 105.39 |  | (c) Rule Curve: |  | 101.53
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-11
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 337 | 293 |  | 0 | 280 | 240 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 76 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 29 | 25 | 33 | 25 | 0 | 88 | 75 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 92 | 0 | 50 | 18 | 40 | 0 | 0 | 0 | 280 | 260 | 214 | 8 | 139 | 23 | 47 | 0 | 35 | 0 | 49 | 43 | 19 | 8 | 25 | 0 | 94 | 186 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 163 | 160 | 0 | 74 | 0 | 220 | 0 | 0 | 0 | 295 | 23 | 11 | 75 | 270 | 25 | 40 | 97 | 75 | 143 | 0 | 100 | 200 | 125 | 316 | 68 | 52 | 89 | 0 | 103 | 54 | 103 | 114 | 108 | 100 | 325 | 91 | 0 | 162 | 114 | 0 | 35 | 0 |  | 700 | 0 | 235 | 0 | 0 | 60 | 0 | 0 | 24 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 28 | 92 | 0 | 0 | 15 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 135 | 0 | 12 | 50 | 175 | 0 | 420 | 105 | 0 | 94 | 80 | 113 | 0 | 0 | 113 | 470 | 222 | 0 | 35 | 0 |  | 8384 | 3508 | 11892 | 4011 | 700 | 1967 | 3791 | 620 | 163 | 546 | 94 | 0 | 0 | 105.21
2:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 336 | 292 |  | 0 | 280 | 235 | 0 | 0 | 40 | 300 | 0 | 0 | 0 | 102 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 29 | 25 | 33 | 25 | 0 | 86 | 75 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 85 | 92 | 0 | 32 | 18 | 42 | 0 | 0 | 0 | 280 | 260 | 217 | 8 | 138 | 23 | 47 | 0 | 35 | 0 | 42 | 43 | 19 | 8 | 25 | 0 | 92 | 199 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 163 | 160 | 0 | 74 | 0 | 220 | 0 | 0 | 0 | 280 | 23 | 11 | 0 | 263 | 0 | 0 | 97 | 0 | 142 | 0 | 100 | 200 | 132 | 316 | 68 | 52 | 89 | 0 | 106 | 54 | 110 | 114 | 108 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 701 | 0 | 235 | 0 | 0 | 90 | 0 | 0 | 24 | 0 | 0 | 65 | 33 | 0 | 0 | 0 | 0 | 43 | 21 | 92 | 0 | 0 | 15 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 136 | 0 | 12 | 0 | 175 | 0 | 423 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 480 | 210 | 0 | 17 | 0 |  | 8123 | 3400 | 11523 | 4007 | 701 | 1943 | 3427 | 630 | 161 | 562 | 92 | 0 | 0 | 105.21
3:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 336 | 293 |  | 0 | 280 | 245 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 102 | 48 | 74 | 0 | 0 | 0 | 54 | 55 | 17 | 0 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 0 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 92 | 0 | 32 | 18 | 42 | 0 | 0 | 0 | 280 | 260 | 215 | 8 | 141 | 23 | 47 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 0 | 92 | 202 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 130 | 161 | 0 | 74 | 0 | 220 | 0 | 0 | 0 | 280 | 23 | 11 | 0 | 265 | 0 | 0 | 101 | 0 | 142 | 0 | 100 | 200 | 130 | 316 | 69 | 52 | 89 | 0 | 106 | 54 | 110 | 114 | 108 | 100 | 325 | 89 | 0 | 162 | 114 | 0 | 17 | 0 |  | 701 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 142 | 0 | 12 | 0 | 175 | 0 | 415 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 520 | 222 | 0 | 0 | 0 |  | 7797 | 3369 | 11166 | 3988 | 701 | 1914 | 3381 | 670 | 160 | 260 | 92 | 0 | 0 | 105.22
4:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 336 | 292 |  | 0 | 280 | 270 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 84 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 88 | 0 | 25 | 18 | 42 | 0 | 0 | 0 | 280 | 260 | 214 | 8 | 141 | 23 | 47 | 0 | 35 | 0 | 0 | 43 | 19 | 8 | 25 | 20 | 90 | 208 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 130 | 162 | 0 | 75 | 0 | 220 | 0 | 0 | 0 | 290 | 23 | 11 | 0 | 265 | 0 | 0 | 103 | 0 | 135 | 0 | 100 | 200 | 122 | 316 | 68 | 17 | 89 | 0 | 106 | 54 | 110 | 114 | 107 | 100 | 325 | 91 | 0 | 162 | 114 | 0 | 17 | 0 |  | 701 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 149 | 0 | 12 | 0 | 186 | 0 | 418 | 105 | 0 | 94 | 15 | 113 | 0 | 0 | 113 | 510 | 223 | 0 | 0 | 0 |  | 7624 | 3288 | 10912 | 4051 | 701 | 1927 | 3204 | 660 | 159 | 120 | 90 | 0 | 0 | 105.23
5:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 334 | 292 |  | 0 | 280 | 245 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 54 | 55 | 17 | 19 | 25 | 30 | 25 | 33 | 0 | 0 | 81 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 10 | 0 | 19 | 18 | 42 | 0 | 0 | 0 | 280 | 260 | 215 | 8 | 140 | 23 | 48 | 0 | 35 | 0 | 0 | 25 | 19 | 8 | 25 | 15 | 90 | 211 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 163 | 162 | 0 | 75 | 0 | 220 | 0 | 0 | 0 | 290 | 23 | 11 | 0 | 195 | 0 | 0 | 97 | 0 | 126 | 0 | 100 | 200 | 125 | 316 | 69 | 17 | 89 | 0 | 107 | 54 | 110 | 114 | 108 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 17 | 0 |  | 701 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 154 | 0 | 12 | 0 | 192 | 0 | 360 | 105 | 0 | 94 | 15 | 50 | 0 | 0 | 113 | 490 | 223 | 0 | 0 | 0 |  | 7408 | 3163 | 10571 | 4064 | 701 | 1903 | 2897 | 640 | 156 | 120 | 90 | 0 | 0 | 105.24
6:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 341 | 291 |  | 0 | 280 | 280 | 0 | 0 | 40 | 260 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 30 | 25 | 33 | 0 | 0 | 80 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 32 | 0 | 0 | 0 | 280 | 260 | 213 | 8 | 141 | 20 | 47 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 25 | 15 | 84 | 210 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 130 | 161 | 0 | 75 | 0 | 220 | 0 | 0 | 0 | 280 | 23 | 11 | 0 | 15 | 0 | 0 | 38 | 0 | 117 | 0 | 60 | 200 | 120 | 316 | 38 | 17 | 89 | 0 | 107 | 0 | 104 | 70 | 107 | 60 | 325 | 75 | 0 | 162 | 114 | 0 | 17 | 0 |  | 701 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 149 | 0 | 0 | 0 | 0 | 159 | 0 | 12 | 0 | 195 | 0 | 305 | 35 | 0 | 35 | 15 | 0 | 0 | 0 | 70 | 480 | 223 | 0 | 0 | 0 |  | 6766 | 2883 | 9649 | 4064 | 701 | 1791 | 2105 | 629 | 155 | 120 | 84 | 0 | 0 | 105.25
7:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 315 | 292 |  | 0 | 280 | 270 | 0 | 0 | 55 | 260 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 29 | 25 | 33 | 0 | 0 | 81 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 29 | 0 | 0 | 0 | 295 | 260 | 188 | 8 | 139 | 23 | 49 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 15 | 80 | 212 | 8 | 22 | 0 | 30 | 20 | 25 | 0 | 130 | 162 | 0 | 75 | 0 | 220 | 0 | 0 | 0 | 300 | 23 | 11 | 0 | 15 | 0 | 0 | 38 | 0 | 116 | 4 | 60 | 155 | 120 | 316 | 38 | 17 | 89 | 1 | 107 | 0 | 110 | 70 | 108 | 20 | 325 | 53 | 4 | 162 | 114 | 0 | 17 | 4 |  | 699 | 0 | 260 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 168 | 0 | 12 | 0 | 160 | 0 | 306 | 35 | 0 | 35 | 15 | 0 | 0 | 0 | 35 | 400 | 222 | 0 | 0 | 0 |  | 6670 | 2738 | 9408 | 4008 | 699 | 1808 | 1974 | 550 | 156 | 120 | 80 | 13 | 0 | 105.15
8:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 305 | 291 |  | 0 | 280 | 270 | 0 | 0 | 55 | 260 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 17 | 19 | 25 | 29 | 25 | 33 | 0 | 0 | 81 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 270 | 265 | 180 | 8 | 139 | 20 | 47 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 0 | 86 | 210 | 8 | 19 | 0 | 30 | 20 | 25 | 0 | 130 | 160 | 0 | 75 | 0 | 192 | 0 | 0 | 0 | 260 | 23 | 11 | 0 | 15 | 0 | 0 | 38 | 0 | 121 | 12 | 10 | 120 | 122 | 316 | 38 | 17 | 89 | 2 | 107 | 0 | 110 | 50 | 99 | 10 | 325 | 53 | 12 | 162 | 114 | 0 | 17 | 7 |  | 699 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 150 | 0 | 0 | 0 | 0 | 172 | 0 | 12 | 0 | 176 | 0 | 360 | 35 | 0 | 35 | 15 | 0 | 0 | 0 | 35 | 390 | 184 | 0 | 0 | 1 |  | 6434 | 2773 | 9207 | 3963 | 699 | 1752 | 1857 | 540 | 156 | 120 | 86 | 34 | 0 | 105.28
9:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 333 | 291 |  | 0 | 280 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 9 | 25 | 33 | 12 | 0 | 85 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 15 | 2 | 0 | 0 | 0 | 305 | 350 | 201 | 8 | 139 | 20 | 48 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 2 | 10 | 86 | 188 | 8 | 19 | 1 | 36 | 20 | 25 | 0 | 163 | 157 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 310 | 0 | 11 | 0 | 15 | 0 | 0 | 38 | 0 | 125 | 7 | 73 | 134 | 118 | 316 | 38 | 17 | 89 | 4 | 107 | 1 | 110 | 65 | 99 | 90 | 325 | 53 | 27 | 162 | 114 | 0 | 17 | 20 |  | 698 | 0 | 265 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 12 | 0 | 197 | 0 | 417 | 35 | 0 | 35 | 15 | 4 | 0 | 1 | 90 | 400 | 180 | 0 | 0 | 2 |  | 6925 | 2760 | 9685 | 4140 | 698 | 1890 | 2129 | 400 | 160 | 120 | 86 | 62 | 0 | 105.29
10:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 328 | 291 |  | 0 | 280 | 300 | 0 | 0 | 51 | 300 | 0 | 0 | 0 | 24 | 0 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 9 | 25 | 33 | 25 | 0 | 85 | 75 | 0 | 120 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 0 | 18 | 2 | 0 | 0 | 0 | 340 | 345 | 209 | 8 | 140 | 20 | 49 | 0 | 25 | 0 | 0 | 4 | 19 | 11 | 25 | 20 | 96 | 156 | 8 | 19 | 2 | 30 | 30 | 25 | 0 | 163 | 153 | 0 | 80 | 0 | 221 | 0 | 0 | 0 | 300 | 0 | 11 | 0 | 58 | 0 | 0 | 39 | 0 | 124 | 19 | 100 | 174 | 115 | 316 | 38 | 17 | 89 | 3 | 107 | 17 | 110 | 89 | 98 | 100 | 325 | 68 | 46 | 162 | 114 | 0 | 17 | 27 |  | 698 | 0 | 255 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 166 | 0 | 12 | 0 | 200 | 0 | 410 | 35 | 0 | 80 | 15 | 42 | 0 | 3 | 113 | 400 | 180 | 0 | 0 | 3 |  | 7210 | 2848 | 10058 | 4167 | 698 | 1865 | 2449 | 400 | 160 | 120 | 96 | 103 | 0 | 105.29
11:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 328 | 291 |  | 0 | 280 | 270 | 0 | 0 | 45 | 300 | 0 | 0 | 0 | 0 | 48 | 32 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 9 | 25 | 33 | 25 | 0 | 85 | 75 | 0 | 100 | 1 | 0 | 0 | 0 | 0 |  | 3 | 0 | 0 | 80 | 0 | 22 | 20 | 2 | 0 | 0 | 0 | 330 | 345 | 207 | 8 | 140 | 23 | 48 | 0 | 25 | 0 | 0 | 21 | 19 | 11 | 25 | 20 | 92 | 157 | 8 | 19 | 2 | 30 | 30 | 25 | 0 | 163 | 153 | 0 | 76 | 0 | 220 | 0 | 0 | 0 | 320 | 8 | 11 | 0 | 158 | 25 | 0 | 48 | 0 | 127 | 18 | 100 | 170 | 118 | 316 | 38 | 35 | 89 | 2 | 107 | 20 | 110 | 97 | 98 | 100 | 325 | 71 | 57 | 162 | 114 | 0 | 17 | 26 |  | 698 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 12 | 0 | 191 | 0 | 410 | 70 | 0 | 94 | 15 | 107 | 0 | 5 | 113 | 400 | 180 | 0 | 0 | 5 |  | 7492 | 2953 | 10445 | 4112 | 698 | 1884 | 2816 | 400 | 160 | 168 | 92 | 115 | 0 | 105.18
12:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 332 | 291 |  | 0 | 280 | 280 | 0 | 0 | 45 | 300 | 0 | 0 | 0 | 64 | 82 | 34 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 3 | 25 | 33 | 25 | 0 | 87 | 75 | 0 | 100 | 14 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 80 | 0 | 43 | 20 | 2 | 0 | 0 | 0 | 345 | 350 | 186 | 8 | 140 | 23 | 48 | 0 | 25 | 0 | 0 | 34 | 19 | 11 | 25 | 20 | 100 | 155 | 8 | 19 | 2 | 30 | 30 | 25 | 0 | 163 | 153 | 0 | 79 | 0 | 221 | 0 | 0 | 0 | 300 | 16 | 11 | 80 | 240 | 26 | 30 | 38 | 72 | 143 | 17 | 90 | 160 | 128 | 316 | 28 | 52 | 89 | 3 | 107 | 36 | 110 | 98 | 98 | 95 | 325 | 71 | 54 | 162 | 114 | 0 | 17 | 36 |  | 699 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 12 | 0 | 185 | 0 | 413 | 88 | 0 | 94 | 15 | 113 | 0 | 7 | 113 | 400 | 218 | 0 | 0 | 5 |  | 7943 | 3035 | 10978 | 4096 | 699 | 1907 | 3288 | 400 | 162 | 202 | 100 | 124 | 0 | 105.18
13:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 334 | 291 |  | 0 | 280 | 270 | 0 | 0 | 45 | 300 | 0 | 0 | 0 | 80 | 133 | 37 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 9 | 25 | 33 | 25 | 0 | 87 | 75 | 0 | 100 | 25 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 80 | 0 | 50 | 18 | 2 | 0 | 0 | 0 | 315 | 350 | 181 | 8 | 141 | 23 | 48 | 0 | 25 | 0 | 0 | 34 | 19 | 11 | 25 | 20 | 104 | 143 | 0 | 19 | 2 | 30 | 30 | 25 | 0 | 163 | 154 | 0 | 79 | 0 | 221 | 0 | 0 | 0 | 300 | 16 | 11 | 200 | 273 | 205 | 97 | 38 | 95 | 141 | 18 | 90 | 160 | 133 | 316 | 38 | 52 | 89 | 2 | 107 | 36 | 102 | 97 | 97 | 95 | 325 | 77 | 54 | 162 | 114 | 0 | 17 | 32 |  | 700 | 0 | 230 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 35 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 0 | 12 | 13 | 176 | 0 | 405 | 88 | 0 | 94 | 15 | 113 | 0 | 7 | 113 | 400 | 215 | 0 | 0 | 4 |  | 8428 | 3016 | 11444 | 4049 | 700 | 1897 | 3755 | 400 | 162 | 258 | 104 | 119 | 0 | 105.19
14:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 332 | 282 |  | 0 | 280 | 300 | 0 | 0 | 54 | 300 | 0 | 0 | 0 | 95 | 133 | 37 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 28 | 25 | 33 | 25 | 0 | 87 | 75 | 0 | 100 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 80 | 0 | 50 | 20 | 8 | 0 | 0 | 0 | 350 | 340 | 204 | 8 | 144 | 23 | 47 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 25 | 20 | 116 | 128 | 0 | 22 | 2 | 30 | 30 | 25 | 0 | 163 | 152 | 0 | 78 | 0 | 221 | 0 | 0 | 0 | 290 | 0 | 11 | 150 | 273 | 26 | 50 | 38 | 55 | 143 | 14 | 100 | 160 | 132 | 316 | 38 | 52 | 89 | 4 | 107 | 51 | 110 | 98 | 98 | 100 | 325 | 90 | 53 | 162 | 114 | 0 | 17 | 31 |  | 700 | 0 | 225 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 29 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 35 | 0 | 0 | 5 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 0 | 12 | 0 | 172 | 0 | 404 | 88 | 0 | 94 | 15 | 113 | 0 | 7 | 113 | 410 | 213 | 0 | 0 | 4 |  | 8316 | 3010 | 11326 | 4077 | 700 | 1892 | 3544 | 410 | 162 | 310 | 116 | 115 | 0 | 105.31
15:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 358 | 257 |  | 0 | 280 | 280 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 150 | 36 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 25 | 33 | 25 | 0 | 88 | 75 | 0 | 100 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 80 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 320 | 295 | 181 | 8 | 141 | 23 | 48 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 25 | 20 | 118 | 129 | 0 | 22 | 1 | 30 | 30 | 25 | 0 | 163 | 152 | 0 | 76 | 0 | 221 | 0 | 0 | 0 | 300 | 0 | 11 | 200 | 275 | 262 | 98 | 38 | 89 | 143 | 12 | 100 | 160 | 132 | 316 | 38 | 52 | 89 | 2 | 107 | 54 | 110 | 98 | 101 | 100 | 325 | 90 | 43 | 162 | 114 | 0 | 17 | 22 |  | 699 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 26 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 35 | 0 | 0 | 34 | 0 | 12 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 12 | 35 | 164 | 0 | 407 | 95 | 0 | 94 | 15 | 113 | 0 | 6 | 113 | 420 | 214 | 0 | 0 | 4 |  | 8619 | 3065 | 11684 | 3982 | 699 | 1865 | 4018 | 420 | 163 | 329 | 118 | 90 | 0 | 105.32
16:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 399 | 257 |  | 0 | 280 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 150 | 45 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 25 | 33 | 25 | 0 | 83 | 75 | 0 | 100 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 80 | 0 | 50 | 20 | 2 | 0 | 0 | 0 | 320 | 300 | 180 | 8 | 140 | 23 | 48 | 0 | 35 | 0 | 48 | 43 | 19 | 11 | 16 | 20 | 120 | 129 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 153 | 0 | 76 | 0 | 221 | 0 | 0 | 0 | 300 | 0 | 11 | 200 | 278 | 131 | 60 | 38 | 91 | 142 | 2 | 90 | 160 | 132 | 317 | 38 | 52 | 89 | 1 | 123 | 54 | 110 | 98 | 102 | 90 | 325 | 90 | 28 | 162 | 114 | 0 | 17 | 9 |  | 699 | 0 | 220 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 20 | 7 | 0 | 35 | 0 | 0 | 34 | 0 | 13 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 11 | 20 | 162 | 0 | 414 | 105 | 0 | 108 | 15 | 113 | 0 | 4 | 113 | 420 | 216 | 0 | 0 | 2 |  | 8536 | 3098 | 11634 | 4017 | 699 | 1875 | 3865 | 420 | 158 | 434 | 120 | 46 | 0 | 105.32
17:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 401 | 254 |  | 0 | 280 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 25 | 33 | 25 | 0 | 86 | 75 | 10 | 100 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 90 | 0 | 50 | 20 | 4 | 0 | 0 | 0 | 320 | 300 | 180 | 8 | 138 | 23 | 47 | 0 | 35 | 0 | 48 | 43 | 19 | 11 | 24 | 20 | 128 | 150 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 155 | 0 | 76 | 0 | 220 | 0 | 0 | 0 | 290 | 0 | 11 | 18 | 293 | 0 | 0 | 47 | 50 | 135 | 2 | 90 | 160 | 132 | 316 | 38 | 52 | 71 | 1 | 164 | 54 | 110 | 98 | 109 | 100 | 325 | 90 | 11 | 162 | 114 | 0 | 17 | 5 |  | 700 | 0 | 215 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 43 | 26 | 0 | 35 | 0 | 0 | 43 | 0 | 13 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 12 | 0 | 157 | 0 | 414 | 105 | 0 | 113 | 15 | 113 | 0 | 3 | 113 | 420 | 180 | 0 | 0 | 0 |  | 8213 | 3085 | 11298 | 4046 | 700 | 1826 | 3519 | 420 | 161 | 476 | 128 | 22 | 0 | 105.33
18:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 364 | 238 |  | 0 | 280 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 56 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 25 | 0 | 86 | 75 | 15 | 100 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 65 | 0 | 50 | 20 | 8 | 0 | 0 | 0 | 315 | 305 | 200 | 8 | 140 | 23 | 48 | 0 | 35 | 0 | 48 | 25 | 19 | 11 | 25 | 20 | 126 | 145 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 110 | 154 | 0 | 77 | 0 | 208 | 0 | 0 | 0 | 240 | 24 | 11 | 0 | 298 | 0 | 0 | 104 | 25 | 125 | 0 | 100 | 161 | 132 | 316 | 84 | 52 | 82 | 0 | 300 | 54 | 110 | 98 | 108 | 60 | 325 | 90 | 0 | 162 | 114 | 0 | 17 | 0 |  | 702 | 0 | 215 | 0 | 0 | 120 | 0 | 0 | 20 | 0 | 0 | 65 | 27 | 0 | 0 | 0 | 0 | 43 | 32 | 30 | 35 | 0 | 10 | 34 | 0 | 16 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 16 | 0 | 152 | 0 | 306 | 105 | 0 | 113 | 15 | 113 | 0 | 2 | 113 | 420 | 150 | 0 | 2 | 0 |  | 8211 | 3007 | 11218 | 3988 | 702 | 1584 | 3697 | 420 | 161 | 538 | 126 | 2 | 0 | 105.33
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 375 | 233 |  | 0 | 280 | 270 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 102 | 150 | 64 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 25 | 33 | 51 | 0 | 88 | 75 | 20 | 100 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 6 | 0 | 0 | 0 | 350 | 330 | 206 | 26 | 140 | 23 | 47 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 25 | 20 | 146 | 143 | 0 | 22 | 0 | 30 | 29 | 25 | 0 | 163 | 156 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 200 | 300 | 306 | 100 | 177 | 80 | 132 | 0 | 100 | 160 | 135 | 316 | 105 | 70 | 88 | 0 | 304 | 54 | 110 | 98 | 108 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 23 | 0 |  | 701 | 0 | 220 | 0 | 0 | 190 | 0 | 0 | 22 | 0 | 0 | 64 | 34 | 0 | 0 | 0 | 0 | 43 | 32 | 92 | 35 | 43 | 37 | 43 | 13 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140 | 0 | 21 | 70 | 152 | 0 | 414 | 105 | 184 | 113 | 15 | 113 | 0 | 0 | 113 | 570 | 220 | 0 | 54 | 0 |  | 9400 | 3882 | 13282 | 4147 | 701 | 1900 | 4943 | 570 | 163 | 712 | 146 | 0 | 0 | 105.35
19:30 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 395 | 220 |  | 0 | 280 | 300 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 102 | 150 | 64 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 88 | 75 | 40 | 90 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 3 | 0 | 0 | 0 | 315 | 295 | 209 | 45 | 140 | 23 | 47 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 25 | 21 | 148 | 143 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 156 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 200 | 300 | 308 | 100 | 177 | 78 | 143 | 0 | 100 | 160 | 140 | 316 | 107 | 70 | 88 | 0 | 306 | 54 | 110 | 98 | 109 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 701 | 0 | 225 | 0 | 0 | 225 | 0 | 0 | 27 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 32 | 92 | 35 | 43 | 38 | 43 | 13 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 151 | 0 | 415 | 105 | 185 | 113 | 15 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 54 | 0 |  | 9434 | 4011 | 13445 | 4127 | 701 | 1894 | 5037 | 622 | 163 | 753 | 148 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 396 | 214 |  | 0 | 280 | 300 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 102 | 150 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 88 | 75 | 90 | 90 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 7 | 0 | 0 | 0 | 330 | 310 | 207 | 45 | 140 | 23 | 47 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 28 | 21 | 150 | 142 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 157 | 0 | 79 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 200 | 300 | 305 | 100 | 177 | 80 | 144 | 0 | 100 | 160 | 140 | 317 | 106 | 70 | 88 | 0 | 306 | 54 | 110 | 98 | 108 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 701 | 0 | 220 | 0 | 0 | 225 | 0 | 0 | 25 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 32 | 92 | 35 | 43 | 40 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 152 | 0 | 414 | 105 | 185 | 113 | 15 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 54 | 0 |  | 9515 | 3994 | 13509 | 4204 | 701 | 1893 | 5036 | 622 | 163 | 740 | 150 | 0 | 0 | 105.34
21:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 396 | 214 |  | 0 | 280 | 265 | 0 | 0 | 55 | 323 | 0 | 0 | 0 | 102 | 150 | 59 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 88 | 75 | 30 | 90 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 6 | 0 | 0 | 0 | 325 | 305 | 208 | 45 | 142 | 23 | 48 | 0 | 35 | 0 | 48 | 36 | 19 | 11 | 28 | 21 | 142 | 141 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 158 | 0 | 79 | 0 | 220 | 0 | 0 | 0 | 310 | 24 | 11 | 200 | 298 | 300 | 100 | 177 | 95 | 142 | 0 | 100 | 160 | 135 | 337 | 106 | 70 | 88 | 0 | 306 | 54 | 110 | 98 | 107 | 100 | 353 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 702 | 0 | 215 | 0 | 0 | 225 | 0 | 0 | 24 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 32 | 92 | 35 | 43 | 37 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 152 | 0 | 414 | 105 | 185 | 113 | 15 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 54 | 0 |  | 9472 | 3986 | 13458 | 4183 | 702 | 1913 | 4997 | 622 | 163 | 736 | 142 | 0 | 0 | 105.35
22:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 391 | 214 |  | 0 | 280 | 260 | 0 | 0 | 55 | 322 | 0 | 0 | 0 | 102 | 150 | 73 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 88 | 75 | 10 | 90 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 27 | 0 | 0 | 0 | 315 | 295 | 210 | 45 | 138 | 23 | 48 | 0 | 35 | 0 | 48 | 43 | 19 | 11 | 30 | 21 | 144 | 139 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 160 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 200 | 300 | 252 | 99 | 177 | 95 | 142 | 0 | 100 | 160 | 132 | 403 | 107 | 70 | 88 | 0 | 306 | 54 | 110 | 114 | 108 | 100 | 370 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 702 | 0 | 210 | 0 | 0 | 225 | 0 | 0 | 24 | 0 | 0 | 65 | 35 | 0 | 0 | 0 | 0 | 43 | 30 | 92 | 35 | 43 | 37 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 152 | 0 | 414 | 105 | 120 | 113 | 15 | 113 | 0 | 0 | 113 | 600 | 219 | 0 | 35 | 0 |  | 9477 | 3873 | 13350 | 4215 | 702 | 1915 | 4877 | 600 | 163 | 734 | 144 | 0 | 0 | 0
23:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 387 | 224 |  | 0 | 280 | 265 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 102 | 150 | 75 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 89 | 75 | 0 | 80 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 50 | 20 | 30 | 0 | 0 | 0 | 325 | 295 | 209 | 45 | 141 | 23 | 48 | 0 | 35 | 0 | 48 | 43 | 19 | 11 | 26 | 21 | 140 | 143 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 158 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 150 | 300 | 221 | 75 | 177 | 93 | 145 | 0 | 100 | 170 | 140 | 403 | 107 | 70 | 88 | 0 | 306 | 54 | 110 | 114 | 107 | 100 | 370 | 73 | 0 | 162 | 114 | 0 | 35 | 0 |  | 709 | 0 | 215 | 0 | 0 | 225 | 0 | 0 | 24 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 26 | 92 | 35 | 0 | 37 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 152 | 0 | 414 | 105 | 70 | 113 | 15 | 113 | 0 | 0 | 113 | 580 | 220 | 0 | 72 | 0 |  | 9361 | 3805 | 13166 | 4209 | 709 | 1918 | 4716 | 580 | 164 | 730 | 140 | 0 | 0 | 0
24:00 | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 388 | 252 |  | 0 | 280 | 245 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 102 | 150 | 76 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 29 | 25 | 33 | 25 | 0 | 89 | 75 | 100 | 120 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 85 | 92 | 0 | 50 | 0 | 30 | 0 | 0 | 0 | 325 | 295 | 210 | 45 | 140 | 23 | 47 | 0 | 35 | 0 | 48 | 43 | 19 | 11 | 30 | 21 | 142 | 146 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 161 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 150 | 300 | 212 | 75 | 96 | 94 | 149 | 0 | 100 | 180 | 140 | 402 | 69 | 52 | 88 | 0 | 305 | 54 | 110 | 114 | 108 | 100 | 370 | 72 | 0 | 162 | 114 | 0 | 35 | 0 |  | 708 | 0 | 215 | 0 | 0 | 225 | 0 | 0 | 24 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 26 | 92 | 35 | 0 | 30 | 43 | 0 | 19 | 0 | 11 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 0 | 21 | 100 | 147 | 0 | 414 | 105 | 70 | 113 | 15 | 113 | 0 | 0 | 113 | 540 | 220 | 0 | 72 | 0 |  | 9353 | 3764 | 13117 | 4331 | 708 | 1955 | 4539 | 555 | 164 | 723 | 142 | 0 | 0 | 0
KWH | 0 | 0 | 0 | 0 | 4834000 | 0 | 0 | 8607740 | 6470000 |  | 0 | 6842250 | 6553745 | 0 | 0 | 1278258 | 7173912 | 0 | 0 | 0 | 1896480 | 2194080 | 995437 | 0 | 0 | 0 | 1302840 | 1000984 | 791619 | 323064 | 600000 | 552240 | 615600 | 808000 | 576960 | 0 | 2005396 | 1808000 | 300000 | 2600000 | 398946 | 0 | 0 | 0 | 0 |  | 413760 | 0 | 901564 | 1599720 | 0 | 868800 | 423312 | 429120 | 0 | 0 | 0 | 7549700 | 7282000 | 4856000 | 384727 | 3355890 | 507744 | 1142880 | 0 | 783036 | 0 | 611816 | 738158 | 448956 | 240120 | 603100 | 431960 | 2648640 | 3883360 | 95040 | 468216 | 9750 | 715000 | 606960 | 597000 | 0 | 3695890 | 3678000 | 0 | 1841280 | 0 | 5244750 | 0 | 0 | 0 | 7198000 | 396888 | 264000 | 2115072 | 5419634 | 2337770 | 998276 | 1980000 | 1097834 | 3266350 | 134325 | 2145600 | 4077120 | 3101236 | 7860000 | 1447200 | 1105200 | 2131054 | 29160 | 3999491 | 1006785 | 2680543 | 2399700 | 2515800 | 2149448 | 8044900 | 1939200 | 373770 | 3938400 | 2747455 | 0 | 585720 | 216231 |  | 16926545 | 0 | 5851872 | 0 | 0 | 3441600 | 0 | 0 | 208320 | 0 | 0 | 1549000 | 688370 | 0 | 0 | 0 | 0 | 433920 | 300623 | 815264 | 430970 | 163339 | 239944 | 456960 | 13851 | 410880 | 0 | 244944 | 20073 | 0 | 1306000 | 0 | 0 | 0 | 0 | 3788818 | 0 | 348169 | 792000 | 4353136 | 0 | 9486873 | 2151840 | 805335 | 2251296 | 537984 | 2149084 | 0 | 40076 | 2518656 | 12245000 | 4992460 | 0 | 397200 | 32340 |  | 197287962 | 80392742 | 277680704 | 99063182 | 16926545 | 45310935 | 86350299 | 13571073 | 3813396 | 9160982 | 2648640 | 835652 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5365740 | 0 | 0 | 8693817.4 | 6664100 |  | 0 | 7458052.5 | 7274656.95 | 0 | 0 | 10814062.68 | 7460868.48 | 0 | 0 | 0 | 17295897.6 | 21589747.2 | 9177929.14 | 0 | 0 | 0 | 9510732 | 7737606.32 | 7805363.34 | 242298 | 450000 | 0 | 0 | 0 | 5579203.2 | 0 | 541456.92 | 488160 | 543000 | 4706000 | 3706208.34 | 0 | 0 | 0 | 0 |  | 0 | 0 | 8745170.8 | 15277326 | 0 | 6880896 | 533373.12 | 1274486.4 | 0 | 0 | 0 | 5586778 | 7282000 | 4467520 | 496297.83 | 3859273.5 | 573750.72 | 1600032 | 0 | 1338991.56 | 0 | 6179341.6 | 7049408.9 | 570174.12 | 180090 | 1055425 | 323970 | 19864800 | 4116361.6 | 862963.2 | 594634.32 | 155415 | 1172600 | 971136 | 1062660 | 0 | 4213314.6 | 3825120 | 0 | 3516844.8 | 0 | 9073417.5 | 0 | 0 | 0 | 7269980 | 297666 | 200640 | 35977374.72 | 40972433.04 | 39695334.6 | 16691174.72 | 10296000 | 18355784.48 | 32140884 | 1570259.25 | 17486640 | 44236752 | 21863713.8 | 7309800 | 13198464 | 10444140 | 18561480.34 | 0 | 30236151.96 | 8769097.35 | 23561972.97 | 23949006 | 21560406 | 14315323.68 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97496899.2 | 0 | 6144465.6 | 0 | 0 | 47700576 | 0 | 0 | 2185276.8 | 0 | 0 | 1750370 | 1066973.5 | 0 | 0 | 0 | 0 | 4269772.8 | 3054329.68 | 7215086.4 | 3318469 | 2208343.28 | 2325057.36 | 4427942.4 | 134354.7 | 788889.6 | 0 | 185422.608 | 121040.19 | 0 | 7078520 | 0 | 0 | 0 | 0 | 5001239.76 | 0 | 522253.5 | 13471920 | 5093169.12 | 0 | 9392004.27 | 22465209.6 | 13698748.35 | 21364799.04 | 5078568.96 | 16676891.84 | 0 | 442839.8 | 18612867.84 | 53755550 | 0 | 0 | 0 | 0 |  | 724768951.55 | 377047851.198 | 1101816802.748 | 97630120.848 | 97496899.2 | 46664880.56 | 672608147.64 | 60955110.19 | 1029616.92 | 103398713.34 | 19864800 | 2168514.05 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 332 | 291 |  | 0 | 280 | 280 | 0 | 0 | 45 | 300 | 0 | 0 | 0 | 64 | 82 | 34 | 0 | 0 | 0 | 54 | 17 | 35 | 0 | 25 | 3 | 25 | 33 | 25 | 0 | 87 | 75 | 0 | 100 | 14 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 80 | 0 | 43 | 20 | 2 | 0 | 0 | 0 | 345 | 350 | 186 | 8 | 140 | 23 | 48 | 0 | 25 | 0 | 0 | 34 | 19 | 11 | 25 | 20 | 100 | 155 | 8 | 19 | 2 | 30 | 30 | 25 | 0 | 163 | 153 | 0 | 79 | 0 | 221 | 0 | 0 | 0 | 300 | 16 | 11 | 80 | 240 | 26 | 30 | 38 | 72 | 143 | 17 | 90 | 160 | 128 | 316 | 28 | 52 | 89 | 3 | 107 | 36 | 110 | 98 | 98 | 95 | 325 | 71 | 54 | 162 | 114 | 0 | 17 | 36 |  | 699 | 0 | 240 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 0 | 0 | 0 | 0 | 18 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 159 | 0 | 12 | 0 | 185 | 0 | 413 | 88 | 0 | 94 | 15 | 113 | 0 | 7 | 113 | 400 | 218 | 0 | 0 | 5 |  | 10978 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 396 | 214 | 0 | 0 | 280 | 300 | 0 | 0 | 55 | 320 | 0 | 0 | 0 | 102 | 150 | 65 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 51 | 0 | 88 | 75 | 90 | 90 | 25 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 85 | 100 | 0 | 50 | 20 | 7 | 0 | 0 | 0 | 330 | 310 | 207 | 45 | 140 | 23 | 47 | 0 | 35 | 0 | 48 | 34 | 19 | 11 | 28 | 21 | 150 | 142 | 0 | 22 | 0 | 30 | 30 | 25 | 0 | 163 | 157 | 0 | 79 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 200 | 300 | 305 | 100 | 177 | 80 | 144 | 0 | 100 | 160 | 140 | 317 | 106 | 70 | 88 | 0 | 306 | 54 | 110 | 98 | 108 | 100 | 325 | 90 | 0 | 162 | 114 | 0 | 35 | 0 |  | 701 | 0 | 220 | 0 | 0 | 225 | 0 | 0 | 25 | 0 | 0 | 65 | 34 | 0 | 0 | 0 | 0 | 43 | 32 | 92 | 35 | 43 | 40 | 43 | 0 | 19 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 0 | 21 | 100 | 152 | 0 | 414 | 105 | 185 | 113 | 15 | 113 | 0 | 0 | 113 | 622 | 220 | 0 | 54 | 0 |  | 13509 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 390 | 300 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 102 | 149 | 77 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 83 | 75 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 20 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 26 | 141 | 23 | 48 | 0 | 35 | 0 | 50 | 43 | 22 | 11 | 33 | 21 | 164 | 160 | 8 | 22 | 0 | 30 | 41 | 25 | 0 | 163 | 160 | 0 | 84 | 0 | 225 | 18 | 0 | 0 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 140 | 402 | 115 | 90 | 88 | 0 | 300 | 54 | 110 | 114 | 113 | 100 | 383 | 94 | 0 | 162 | 116 | 0 | 35 |  |  | 721 | 0 | 245 | 0 | 0 | 225 | 0 | 0 | 22 | 40 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 92 | 35 | 50 | 40 | 43 | 20 | 22 | 0 | 11 | 77 | 0 | 0 | 15 | 10 | 0 | 0 | 200 | 0 | 40 | 100 | 200 | 0 | 410 | 105 | 184 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 390 | 250 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 102 | 149 | 77 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 83 | 75 | 100 | 120 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 20 | 15 | 0 | 0 | 0 | 300 | 300 | 210 | 26 | 141 | 23 | 48 | 0 | 35 | 0 | 0 | 43 | 22 | 11 | 33 | 21 | 138 | 130 | 8 | 22 | 1.6 | 30 | 41 | 25 | 0 | 163 | 160 | 0 | 80 | 0 | 225 | 18 | 0 | 0 | 341 | 24 | 11 | 100 | 300 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 130 | 402 | 115 | 70 | 88 | 5 | 300 | 54 | 110 | 98 | 113 | 100 | 383 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 721 | 0 | 245 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 65 | 33 | 110 | 0 | 0 | 0 | 50 | 40 | 85 | 35 | 50 | 0 | 43 | 0 | 22 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 40 | 50 | 185 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 203 | 0 | 0 | 384 | 232 | 0 | 0 | 280 | 285 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 40 | 16 | 0 | 0 | 0 | 0 | 54 | 17 | 35 | 19 | 25 | 14 | 25 |  | 0 | 0 | 84 | 75 | 100 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 0 | 0 | 30 | 0 | 19 | 20 | 10 | 0 | 0 | 0 | 290 | 280 | 211 | 26 | 140 | 17 | 48 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 112 | 136 | 7 | 20 | 0 | 30 | 30 | 25 | 0 | 120 | 157 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 285 | 24 | 8 | 0 | 180 | 0 | 0 | 38 | 0 | 105 | 12 | 64 | 136 | 127 | 402 | 38 | 52 | 75 | 2 | 105 | 17 | 110 | 70 | 108 | 100 | 392 | 88 | 9 | 94 | 114 | 0 | 17 | 6 | 0 | 709 | 0 | 245 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 65 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 19 | 0 | 8 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 0 | 12 | 0 | 188 | 0 | 377 | 53 | 0 | 70 | 105 | 70 | 0 | 2 | 70 | 350 | 152 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 9207 | 8:00
| Highest Generation |  | 13509 | 20:00
| Day Peak Generation |  | 10978 | 12:00
| Evening Peak Generation |  | 13509 | 20:00
| HVDC Max Flow |  | 709 | 23:00
| HVDC EvPeak Flow |  | 701 | 20:00
| Load factor L.F |  | 85.65%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-12
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-11 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10978 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 10254 | MW
Evening Peak Generation : |  | 13509 | MW Hour : | 20:00 | Available Max Generation : |  | 14720 | MW
E.P. Demand (at gen end) : |  | 13509 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13800 | MW
Maximum Generation : |  | 13509 | MW Hour : | 20:00 | Reserve(Generation end) |  | 920 | MW
Total Gen. (MKWH) : |  | 277.6807 | System Load Factor : | 85.65% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -464 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-12
Actual : | 105.39 | Ft.(MSL) , | Rule curve : | 101.53 | Ft.( MSL )
Gas Consumed : | Total = | 1137.03 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 144295001.408
: |  | Coal : | 60955110.19 | Oil : | 776006860.98 | Total : | 981256972.578
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4845.2003 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1654.1414 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1483.215 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1340.6214 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1211.2732 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 977.4711 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 538.1826 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 251.451 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 753.9143 |  |  | 0 | 0%
Total | 0 |  | 13055.4704 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Sylhet 132/33 kV T-2 transformer was under shut down from 09:06 to 10:01 for C/M. |  |  |  |  | About 70 MW power interruption occurred under Sylhet S/S area
b) Barapukuria #03 tripped at 08:27 due to excitation problem. |  |  |  |  | from 09:06 to 10:01.
c) Aminbazar-Manikganj P/P 132 kV Ckt-2 was under shut down from 10:14 to 16:13 for A/M.
d) Rajshahi-Natore 132 kV Ckt-1 was under shut down from 10:11 to 18:11 for C/M.
e) Pabna 132/33 kV T-3 transformer was under shut down from 10:09 to 12:32 for C/M.
f) Haripur-Bhulta 230 kV Ckt-2 tripped at 10:49 from Haripur end showing Directional E/F relay and was
switched on at 11:07.
g) Haripur-Siddhirganj 132 kV Ckt-1,2 tripped at 10:49 from both end showing dist E/F,instentenious
E/F & O/C relay and were switched on at 03:04,03:05(12-09-21) respectively.
h) Haripur-Bhulta 230 kV Ckt-2 tripped at 12:35 from Haripur end showing Directional E/F relay and was
switched on at 12:50.
i) Barisal 132/33 kV T-4 transformer was under shut down from 10:12 to 13:41 for C/M by PGCB & NESCO.
j) Tongi-Bashundhara 132 kV Ckt-1 tripped at 18:05 showing dist B-phase,Z2 at Tongi end and was
switched on at 18:11.
k) Sylhet 132/33 kV T-2 transformer was under shut down from 14:20 to 15:18 for C/M. |  |  |  |  | About 70 MW power interruption occurred under Sylhet S/S area
from 14:20 to 15:18.
l) Sonargaon-Daudkandi 132 kV Ckt-2 was under shut down from 15:35 to 16:02 for replacement of spring
charge motor.
m) Raozan #01 was synchronized at 17:00 the unit tripped several times.
n) Chattak 132/33 kV T2 transformer was shut down form 11:35 to 00:37(12-09-2021) for red hot maint
33 kV side B-phase CT.
o) Polashbari 132 kV main bus was under shut down from 06:55 to 08:30 due to red hot maintenance
at R-phase T-connector.
p) Barapukuria #01 was synchronized at 23:43.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-11 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 203 | 4834000 | ST Under maint
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 396 | 8607740
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 214 | 6470000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6842250 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 300 | 6553745 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1278258
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 65 | 995437 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 323064
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 320 | 7173912
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1896480
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 1302840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2194080
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 1000984
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 791619
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1152240 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 615600 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 808000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 576960
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 300 | 5419634
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 305 | 2337770
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 100 | 998276
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 80 | 1097834 | Engine problem
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 144 | 3266350
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 70 | 1105200 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 90 | 1939200 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3938400
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 216231
| Dhaka area Total |  |  |  | 5719 | 3682 | 73736104
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 90 | 300000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 90 | 2600000 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 398946
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 134325
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 868800
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 163 | 3813396 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 88 | 2131054 | Engine problem
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 901564 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1599720
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2145600
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 20 | 423312
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 429120
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 29160
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 306 | 3999491
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1006785
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2680543
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2149448
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 114 | 2747455
| Chattogram area Total |  |  |  | 2382 | 1502 | 28358719
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 207 | 4856000
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 330 | 7549700 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 310 | 7282000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 507744 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 47 | 1142880 | Engine problem
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 45 | 384727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 783036 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3101236 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 611816
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3355890 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 160 | 4077120 | Engine problem
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 448956
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 240120
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 150 | 2648640
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 28 | 603100 | Engine problem
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 34 | 738158 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 431960 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 2115072
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 98 | 2399700 | Engine problem
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 108 | 2515800
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 35 | 585720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2189 | 46379375
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 142 | 3883360 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 468216
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 95040 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9750
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 177 | 1980000 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 106 | 1447200 | Engine problem
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 373770
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 24 | 413760
| Mymensingh Area Total |  |  |  | 709 | 471 | 8671096
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 30 | 606960 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3695890
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 157 | 3678000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 597000 | Machine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 79 | 1841280
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5244750
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 396888
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7198000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 317 | 7860000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 325 | 8044900 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1671 | 40142668
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 701 | 16926545
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 208320 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 225 | 3441600
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 220 | 5851872 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 792000
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 105 | 2151840
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 15 | 537984 | On Test
| Khulna Area Total |  |  |  | 2129 | 1391 | 29910161
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 34 | 688370
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 65 | 1549000 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 21 | 348169 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 622 | 12245000
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 220 | 4992460
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 54 | 397200 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 1016 | 20220199
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 433920 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 32 | 300623 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 35 | 430970 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 163339 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 239944 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 139 | 3788818 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 152 | 4353136 | Gas shortage
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9486873
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 13851 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 19 | 410880 | Engine problem
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 244944
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 456960 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 815264 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 185 | 805335
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2251296
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2518656
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 32340
| Rajshahi Area Total |  |  |  | 2179 | 1474 | 26747149
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 0 | 20073 | Under maint.
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 1306000 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2149084
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 40076
| Rangpur Area Total |  |  |  | 605 | 113 | 3515233
| Total |  |  |  | 21180 | 13509 | 277680704
| Eastern Grid Total |  |  |  | 14221 | 9515 | 197287962
| Western Grid Total |  |  |  | 6959 | 3994 | 80392742
| National Grid Total |  |  |  | 21180 | 13509 | 277680704
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-11
(a) ENTIRE EASTERN GRID : |  | 8748 | MW | (b) ENTIRE WESTERN GRID : |  | 4020 | MW
i) Dhaka area |  | 4637 | MW | i) Khulna area |  | 1613 | MW
ii) Chittagong area |  | 1273 | MW | ii) Rajshahi area |  | 1359 | MW
iii) Comilla area |  | 1280 | MW | iii) Barisal area |  | 391 | MW
iv) Mymensingh area |  | 967 | MW | iv) Rangpur area |  | 657 | MW
v) Sylhet area |  | 591 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12768 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 16:00 | Kishoreganj | 120 | 4:00 | Jessore | 118 | 22:00
Munsiganj | 108 | 0:00 | Netrokona | 113 | 1:00 | Benapol | 62 | 22:00
Sonargaon | 87 | 0:00 | Jamalpur | 143 | 19:00 | Jhenida | 118 | 21:00
Shyampur | 198 | 9:00 | Sherpur | 122 | 3:00 | Bottail | 139 | 19:00
Bhulta | 214 | 23:00 | Srimongal | 63 | 19:30 | G.K Project | 60 | 20:00
Madanganj | 49 | 16:00 | Shahjibazar | 125 | 23:00 | Faridpur | 157 | 23:00
Shitalakhya | 118 | 16:00 | Fenchuganj | 53 | 20:00 | Rajbari | 56 | 18:30
Rahim steel | 25 | 10:00 | Kulawara | 54 | 20:00 | Madaripur | 111 | 23:00
Matuail | 60 | 7:00 | Sylhet | 156 | 19:00 | Sariatpur | 72 | 21:00
Ghorasal | 82 | 22:00 | Chatak | 34 | 22:00 | Gopalganj | 95 | 19:00
Narsingdi | 192 | 22:00 | Sunamganj | 56 | 22:00 | Bagerhat | 104 | 20:00
Haripur (SBU) | 121 | 19:00 | Biani Bazar | 75 | 19:30 | Mongla | 38 | 13:00
Sreenagar | 46 | 21:00 | Comilla (S) | 150 | 20:00 | Satkhira | 104 | 21:00
Ullon | 62 | 1:00 | Comilla(N) | 146 | 21:00 | Gallamari | 45 | 13:00
Hasnabad | 87 | 12:00 | Chandpur | 74 | 22:00 | Magura | 56 | 22:00
Magbazar | 116 | 15:00 | Feni | 135 | 19:00 | Norail | 47 | 19:30
Maniknagar | 64 | 15:00 | Chowmuhani | 218 | 22:00 | Chuadanga | 106 | 19:30
Bangabhaban | 6 | 10:00 | Ashuganj | 46 | 18:30 | Borguna | 20 | 23:00
Motijheel | 24 | 11:00 | Daudkandi | 160 | 20:00 | Barisal(N) | 48 | 22:00
Narinda | 72 | 13:00 | B.Baria | 179 | 20:00 | Barisal (S) | 114 | 20:00
Kazla | 85 | 12:00 | Ramganj | 90 | 22:00 | Patuakhali | 125 | 23:00
Dhanmondi | 152 | 11:00 | Chaddagram | 54 | 3:00 | Bhandaria | 56 | 21:00
Lalbag | 90 | 18:30 | PHP | 11 | 9:00 | Borhan Uddin | 45 | 1:00
Madartek | 80 | 0:00 | Kochua | 74 | 23:00 | Ishurdi | 73 | 19:30
Dhaka University | 35 | 13:00 | Madunaghat | 61 | 18:30 | Ruppur Paromanobik | 3 | 18:00
Aftabnagar | 17 | 18:00 | Hathazari | 103 | 18:30 | Natore | 136 | 21:00
Fatullah | 60 | 15:00 | Khulshi | 172 | 11:00 | Bogra | 170 | 21:00
Nawabganj | 54 | 21:00 | Halishahar | 100 | 10:00 | Noagaon | 115 | 24:00
Keraniganj | 73 | 19:30 | Baraulia | 144 | 23:00 | Rajshahi | 159 | 21:00
Mirpur | 131 | 18:30 | Sikalbaha | 32 | 19:30 | Rajshahi New | 21 | 22:00
Kalyanpur | 114 | 18:00 | Dohazari | 102 | 20:00 | C.Nawabganj | 62 | 21:00
Gulshan | 124 | 15:00 | Cox'sbazar | 102 | 19:30 | Amnura | 53 | 22:00
Uttara | 87 | 18:30 | Chandraghona | 28 | 19:30 | Pabna | 117 | 21:00
Uttara New | 30 | 16:00 | Kaptai | 4.8 | 19:00 | Shahjadpur | 96 | 19:00
Kamrangirchar | 100 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 109 | 19:30
Savar | 173 | 15:00 | Bakulia | 119 | 19:30 | Niyamatpur | 75 | 1:00
Bhasantec | 134 | 18:30 | Julda | 23 | 13:00 | Joypurhat | 60 | 22:00
Agargaon | 81 | 18:30 | TK chemical | 31 | 19:00 | Sherpur(Bogura) | 58 | 19:30
Satmosjid | 105 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 70 | 24:00
Tongi | 123 | 21:00 | Shahmirpur | 32 | 17:00 | Bhangura | 34 | 19:30
Kabirpur | 253 | 16:00 | Khagrachhari | 26 | 2:00 | Rangpur | 135 | 1:00
Basundhara | 202 | 18:30 | Matarbari | 39 | 1:00 | Lalmonirhat | 43 | 24:00
Manikganj | 76 | 18:30 | Baroiar Hat | 50 | 18:30 | Saidpur | 94 | 1:00
Joydevpur | 180 | 19:00 | Rangamati | 14 | 18:30 | Purbasadipur | 104 | 1:00
New Tongi | 91 | 15:00 | Abul Khair 230 | 10 | 14:00 | Thakurgaon | 82 | 1:00
Kodda | 269 | 11:00 | BSRM | 148 | 9:00 | Palashbari | 117 | 24:00
Dhamrai | 122 | 19:30 | GPH Ispat | 96 | 17:00 | Barapukuria | 47 | 19:30
Rajendrapur | 112 | 24:00 | Agrabad | 85 | 18:30 | Panchagar | 45 | 24:00
Valuka | 124 | 11:00 | Goalpara | 28 | 23:00 | Joldhaka | 54 | 1:00
Tangail | 215 | 22:00 | Central S/S | 114 | 19:00 | Kurigram | 61 | 2:00
Mymensing | 224 | 19:30 | Noapara | 49 | 20:00 | Mithapukur | 33 | 3:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-11 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 409 | 3:00 | 403 | 9:00 | Kaliakoir | 399 | 0.20833 | 386 | 0.625
| Bheramara | 403 | 5:00 | 396 | 19:00 | Bhulta | 392 | 0.20833 | 379 | 0.41667
| Ashuganj(N) | 398 | 3:00 | 387 | 10:00 | Gopalganj | 405 | 0.625 | 385 | 0.77083
| Payra | 410 | 2:00 | 398 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 235 | 19:30 | 228 | 5:00
| Ishurdi | 234 | 5:00 | 223 | 23:00 | Megnaghat | 236 | 2:00 | 231 | 9:00
| Ashuganj | 245 | 5:00 | 237 | 15:00 | Fenchuganj | 243 | 3:00 | 238 | 19:00
| Serajganj | 231 | 6:00 | 225 | 13:00 | Siddhirganj | 234 | 2:00 | 229 | 9:00
| Baghabari | 237 | 7:00 | 224 | 21:00 | Maniknagar | 233 | 2:00 | 225 | 10:00
| Barapukuria | 237 | 6:00 | 217 | 23:00 | Agargaon | 233 | 7:00 | 222 | 10:00
| Bogra | 229 | 7:00 | 207 | 23:00 | Barisal | 238 | 2:00 | 229 | 22:00
| Rajshahi | 230 | 18:30 | 218 | 23:00 | Bhola 225 MW | 240 | 10:00 | 234 | 3:00
| Khulna South | 237 | 18:00 | 225 | 1:00 | AKSML | 233 | 2:00 | 228 | 8:00
| Rampura | 232 | 4:00 | 226 | 12:00 | BSRM | 234 | 4:00 | 229 | 9:00
| Haripur | 232 | 1:00 | 225 | 10:00 | Bibiyana | 243 | 2:00 | 236 | 18:30
| Hasnabad | 232 | 18:30 | 224 | 11:00 | Bhulta | 235 | 2:00 | 227 | 10:00
| Shyampur | 232 | 2:00 | 222 | 10:00 | Ashuganj (S) | 240 | 4:00 | 233 | 10:00
| Aminbazar | 232 | 1:00 | 224 | 2:00 | Kaliakoir | 233 | 2:00 | 223 | 10:00
| Tongi | 237 | 13:00 | 221 | 9:00 | GPH | 235 | 20:00 | 228 | 9:00
| Comilla (N) | 234 | 1:00 | 230 | 10:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 135 | 1:00 | 129 | 15:00 | Madanhat | 138 | 0.77083 | 133 | 0.20833
| Munsiganj | 138 | 1:00 | 130 | 11:00 | Hathazari | 138 | 0.91667 | 135 | 0.16667
| Sonargaon | 135 | 14:00 | 130 | 10:00 | Khulshi | 134 | 0.041667 | 129 | 0.33333
| Shyampur | 138 | 1:00 | 132 | 10:00 | Halishahar | 136 | 0.83333 | 129 | 0.33333
| Bhulta | 129 | 5:00 | 125 | 10:00 | Baraulia | 135 | 0.58333 | 124 | 0.041667
| Madanganj | 137 | 1:00 | 130 | 10:00 | Sikalbaha | 137 | 0.77083 | 131 | 0.33333
| Shitalakhya | 139 | 1:00 | 130 | 11:00 | Dohazari | 134 | 0.83333 | 126 | 0.25
| Rahim steal | 136 | 1:00 | 131 | 10:00 | Cox'sbazar | 127 | 0.83333 | 105 | 0.5
| Matuail | 135 | 1:00 | 129 | 15:00 | Chandraghona | 137 | 0.70833 | 133 | 0.29167
| Ghorasal | 140 | 1:00 | 136 | 10:00 | Kaptai | 135 | 0.041667 | 135 | 0.041667
| Narsinghdi | 133 | 1:00 | 126 | 19:30 | A. Khaer Stl. | 135 | 0.041667 | 130 | 0.29167
| Haripur (SBU) | 136 | 1:00 | 132 | 10:00 | Bakulia | 136 | 0.70833 | 130 | 0.33333
| Sreenagar | 134 | 1:00 | 127 | 10:00 | Julda | 137 | 0.70833 | 132 | 0.16667
| Ullon | 136 | 2:00 | 129 | 10:00 | TK Chemical | 137 | 0.83333 | 131 | 0.25
| Hasnabad | 137 | 23:00 | 130 | 11:00 | Modern Steel | 136 | 0.83333 | 132 | 0.33333
| Magbazar | 136 | 3:00 | 129 | 11:00 | Shahmirpur | 137 | 0.70833 | 132 | 0.41667
| Maniknagar | 135 | 1:00 | 130 | 10:00 | Khagrachhari | 135 | 0.083333 | 132 | 0.375
| Bangabhaban | 135 | 1:00 | 130 | 10:00 | Matarbari | 132 | 0.75 | 120 | 0.041667
| Motijheel | 135 | 1:00 | 130 | 10:00 | Baroiar Hat | 135 | 0.45833 | 132 | 0.875
| Narinda | 135 | 1:00 | 130 | 10:00 | Rangamati | 136 | 18:00 | 133 | 6:00
| Kazla | 135 | 1:00 | 130 | 10:00 | Agrabad | 135 | 2:00 | 130 | 8:00
| Dhanmondi | 136 | 2:00 | 130 | 10:00 | Goalpara S/S | 137 | 3:00 | 133 | 0.83333
| Lalbag | 134 | 3:00 | 126 | 10:00 | Khulna Central S/S | 137 | 16:00 | 132 | 0.041667
| Madartek | 137 | 5:00 | 127 | 12:00 | Noapara | 134 | 15:00 | 129 | 0.041667
| Dhaka University | 137 | 6:00 | 129 | 15:00 | Jessore | 131 | 16:00 | 124 | 0.79167
| Aftabnagar | 136 | 2:00 | 130 | 10:00 | Benapol | 133 | 0.70833 | 123 | 0.041667
| Fatullah | 138 | 1:00 | 132 | 11:00 | Jhenida | 129 | 17:00 | 118 | 0.79167
| Nawabganj | 132 | 6:00 | 126 | 10:00 | Bottail | 132 | 0.75 | 124 | 0.83333
| Keraniganj | 134 | 1:00 | 127 | 10:00 | G.K Project | 137 | 0.20833 | 131 | 0.79167
| Mirpur | 134 | 2:00 | 126 | 10:00 | Faridpur | 135 | 0.29167 | 126 | 0.875
| Kalyanpur | 135 | 1:00 | 128 | 10:00 | Rajbari | 133 | 0.29167 | 125 | 0.79167
| Gulshan | 135 | 3:00 | 128 | 14:00 | Madaripur | 140 | 0.29167 | 132 | 0.91667
| Uttara | 134 | 3:00 | 126 | 10:00 | Shariyatpur S/S | 140 | 8:00 | 130 | 0.875
| Uttara New | 135 | 2:00 | 126 | 10:00 | Gopalganj | 141 | 0.70833 | 133 | 0.875
| Kamrangirchar | 133 | 1:00 | 126 | 10:00 | Bagerhat | 135 | 4:00 | 127 | 0.79167
| Savar | 136 | 1:00 | 128 | 10:00 | Mongla | 135 | 17:00 | 127 | 0.83333
| Bhasantec | 139 | 3:00 | 131 | 10:00 | Satkhira | 135 | 16:00 | 127 | 20:00
| Agargaon | 139 | 2:00 | 132 | 10:00 | Gallamari | 138 | 0.66667 | 132 | 1:00
| Satmosjid | 139 | 2:00 | 132 | 10:00 | Magura | 129 | 7:00 | 116 | 0.79167
| Tongi | 141 | 1:00 | 132 | 8:00 | Narail | 128 | 0.70833 | 115 | 0.83333
| Kabirpur | 139 | 5:00 | 132 | 15:00 | Chuadanga | 133 | 7:00 | 120 | 0.875
| Basundhara | 139 | 18:30 | 129 | 15:00 | Borguna | 136 | 7:00 | 126 | 0.91667
| Manikganj | 142 | 5:00 | 136 | 23:00 | Barisal(N) | 138 | 7:00 | 130 | 22:00
| Joydevpur | 140 | 1:00 | 132 | 10:00 | Barisal (S) | 137 | 0.29167 | 128 | 0.77083
| New Tongi | 138 | 1:00 | 129 | 10:00 | Patuakhali(S) | 134 | 0.29167 | 125 | 0.083333
| Kodda | 136 | 1:00 | 123 | 10:00 | Bhandaria | 134 | 0.29167 | 121 | 0.91667
| Dhamrai | 135 | 2:00 | 128 | 21:00 | Ishurdi | 136 | 5:00 | 130 | 19:00
| Rajendrapur | 136 | 3:00 | 122 | 13:00 | Ruppur Paromanobik | 135 | 6:00 | 130 | 21:00
| Valuka | 126 | 5:00 | 106 | 22:00 | Natore | 135 | 17:00 | 126 | 23:00
| Tangail | 137 | 4:00 | 124 | 23:00 | Bogra | 134 | 5:00 | 122 | 22:00
| Mymensing | 130 | 4:00 | 112 | 0:00 | Noagaon | 130 | 17:00 | 115 | 20:00
| Kishorganj | 131 | 3:00 | 118 | 22:00 | Rajshahi | 133 | 7:00 | 127 | 13:00
| Netrokona | 127 | 7:00 | 108 | 0:00 | Rajshahi New | 135 | 18:00 | 128 | 23:00
| Jamalpur | 137 | 5:00 | 111 | 16:00 | C.Nawabganj | 134 | 18:30 | 126 | 13:00
| Sherpur | 137 | 5:00 | 109 | 13:00 | Amnura | 135 | 18:30 | 127 | 10:00
| Srimongal | 138 | 8:00 | 129 | 22:00 | Pabna | 133 | 18:00 | 127 | 21:00
| Shahjibazar | 135 | 6:00 | 128 | 20:00 | Shahjadpur | 138 | 17:00 | 132 | 20:00
| Fenchuganj | 136 | 7:00 | 130 | 21:00 | Serajganj | 132 | 17:00 | 125 | 20:00
| Khulawara | 134 | 7:00 | 130 | 18:30 | Niyamatpur | 129 | 8:00 | 110 | 22:00
| Sylhet | 132 | 7:00 | 128 | 20:00 | Joypurhat | 130 | 10:00 | 113 | 22:00
| Chatak | 130 | 4:00 | 125 | 18:30 | Sherpur(Bogura) | 134 | 18:00 | 122 | 22:00
| Sunamganj | 129 | 7:00 | 121 | 22:00 | Mohastangor | 135 | 5:00 | 120 | 23:00
| Biani Bazar | 130 | 6:00 | 123 | 21:00 | Bangura | 136 | 18:00 | 130 | 14:00
| Comilla(s) | 126 | 4:00 | 124 | 19:30 | Rangpur | 131 | 4:00 | 111 | 23:00
| Comilla(n) | 138 | 15:00 | 135 | 21:00 | Lalmonirhat | 132 | 5:00 | 113 | 23:00
| Chandpur | 140 | 17:00 | 136 | 21:00 | Saidpur | 132 | 7:00 | 112 | 23:00
| Feni | 137 | 16:00 | 132 | 22:00 | Purbasadipur | 130 | 7:00 | 106 | 23:00
| Chowmuhani | 135 | 17:00 | 130 | 18:30 | Thakurgaon | 131 | 5:00 | 106 | 23:00
| Ashuganj | 140 | 7:00 | 134 | 23:00 | Palashbari | 130 | 5:00 | 117 | 1:00
| Daudkandi | 139 | 14:00 | 130 | 9:00 | Barapukuria | 137 | 6:00 | 117 | 23:00
| B.Baria | 134 | 7:00 | 126 | 21:00 | Panchagar | 134 | 5:00 | 107 | 23:00
| Ramganj | 137 | 17:00 | 133 | 23:00 | Joldhaka | 131 | 0.20833 | 105 | 0.95833
| Chaddagram | 138 | 17:00 | 133 | 23:00 | Kurigram | 132 | 0.20833 | 112 | 0.95833
| PHP | 137 | 17:00 | 132 | 23:00 | Mithapukur | 134 | 0.20833 | 116 | 0.95833
| Kochua | 137 | 14:00 | 133 | 21:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-11
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 450 | 9353 | 3764 | 13117 |  |  |  | QF-LDC-11
0:30 | 457 | 8868.5 | 3636 | 12504.5 | Date: | 2021-09-11
1:00 | 464 | 8384 | 3508 | 11892
1:30 | 451 | 8253.5 | 3454 | 11707.5
2:00 | 438 | 8123 | 3400 | 11523
2:30 | 410 | 7960 | 3384.5 | 11344.5 | [5 empty] | Gen. at Eve. Peak | 13509 | 13509 MW (20:00 )
3:00 | 382 | 7797 | 3369 | 11166 | [6 empty] | 20:00
3:30 | 354 | 7710.5 | 3328.5 | 11039 | [5 empty] | Gen. at Day Peak | 10978 | 10978 MW (12:00 )
4:00 | 326 | 7624 | 3288 | 10912 | [6 empty] | 12:00
4:30 | 290 | 7516 | 3225.5 | 10741.5 | [5 empty] | Highest Generation | 13509
5:00 | 254 | 7408 | 3163 | 10571 | [6 empty] | 20:00
5:30 | 129 | 7087 | 3023 | 10110
6:00 | 4 | 6766 | 2883 | 9649
6:30 | 7 | 6718 | 2810.5 | 9528.5
7:00 | 10 | 6670 | 2738 | 9408
7:30 | 62 | 6552 | 2755.5 | 9307.5
8:00 | 114 | 6434 | 2773 | 9207
8:30 | 121 | 6679.5 | 2766.5 | 9446
9:00 | 128 | 6925 | 2760 | 9685
9:30 | 124 | 7067.5 | 2804 | 9871.5
10:00 | 120 | 7210 | 2848 | 10058
10:30 | 125 | 7351 | 2900.5 | 10251.5
11:00 | 130 | 7492 | 2953 | 10445
11:30 | 87 | 7717.5 | 2994 | 10711.5
12:00 | 44 | 7943 | 3035 | 10978
12:30 | 140 | 8185.5 | 3025.5 | 11211
13:00 | 236 | 8428 | 3016 | 11444
13:30 | 239 | 8372 | 3013 | 11385
14:00 | 242 | 8316 | 3010 | 11326
14:30 | 234 | 8467.5 | 3037.5 | 11505
15:00 | 226 | 8619 | 3065 | 11684
15:30 | 184 | 8577.5 | 3081.5 | 11659
16:00 | 142 | 8536 | 3098 | 11634
16:30 | 75 | 8374.5 | 3091.5 | 11466
17:00 | 8 | 8213 | 3085 | 11298
17:30 | 20 | 8212 | 3046 | 11258
18:00 | 32 | 8211 | 3007 | 11218
18:30 | 142 | 8805.5 | 3444.5 | 12250
19:00 | 252 | 9400 | 3882 | 13282
19:30 | 218 | 9434 | 4011 | 13445
20:00 | 246 | 9515 | 3994 | 13509 |  |  |  | Executive Engineer
20:30 | 276 | 9493.5 | 3990 | 13483.5 |  |  |  | Network Operation Division
21:00 | 306 | 9472 | 3986 | 13458
21:30 | 331 | 9474.5 | 3929.5 | 13404
22:00 | 356 | 9477 | 3873 | 13350 |  |  |  |  | Page 6 of 7
22:30 | 380 | 9419 | 3839 | 13258
23:00 | 404 | 9361 | 3805 | 13166
23:30 | 427 | 9357 | 3784.5 | 13141.5
24:00 | 450 | 9353 | 3764 | 13117
13509 MW (20:00 )
10978 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-11 |  | Energy | 277680704
[11 empty] | 2021-09-11 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4331 | 708 | 1955 | 4716 | 555 | 164 | 723 | 0 | 142 | 0
0:30 | 4171 | 704 | 1961 | 4253.5 | 587.5 | 163.5 | 634.5 | 0 | 118 | 0 | Date: | 2021-09-11
1:00 | 4011 | 700 | 1967 | 3791 | 620 | 163 | 546 | 0 | 94 | 0
1:30 | 4009 | 700.5 | 1955 | 3609 | 625 | 162 | 554 | 0 | 93 | 0 | [7 empty] | Total Energy | 277.6807 | Total Energy Gen 277.681 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 277.681 MKWHr
2:00 | 4007 | 701 | 1943 | 3427 | 630 | 161 | 562 | 0 | 92 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3997.5 | 701 | 1928.5 | 3404 | 650 | 160.5 | 411 | 0 | 92 | 0 | [7 empty] | Energy Requirement | 277.6807
3:00 | 3988 | 701 | 1914 | 3381 | 670 | 160 | 260 | 0 | 92 | 0
3:30 | 4019.5 | 701 | 1920.5 | 3292.5 | 665 | 159.5 | 190 | 0 | 91 | 0 | [6 empty] | Shortage
4:00 | 4051 | 701 | 1927 | 3204 | 660 | 159 | 120 | 0 | 90 | 0
4:30 | 4057.5 | 701 | 1915 | 3050.5 | 650 | 157.5 | 120 | 0 | 90 | 0
5:00 | 4064 | 701 | 1903 | 2897 | 640 | 156 | 120 | 0 | 90 | 0
5:30 | 4064 | 701 | 1847 | 2501 | 634.5 | 155.5 | 120 | 0 | 87 | 0
6:00 | 4064 | 701 | 1791 | 2105 | 629 | 155 | 120 | 0 | 84 | 0
6:30 | 4036 | 700 | 1799.5 | 2039.5 | 589.5 | 155.5 | 120 | 0 | 82 | 6.5 |  |  |  |  | Coal
7:00 | 4008 | 699 | 1808 | 1974 | 550 | 156 | 120 | 0 | 80 | 13
7:30 | 3985.5 | 699 | 1780 | 1915.5 | 545 | 156 | 120 | 0 | 83 | 23.5 |  |  |  | Oil |  |  |  | ,
8:00 | 3963 | 699 | 1752 | 1857 | 540 | 156 | 120 | 0 | 86 | 34
8:30 | 4051.5 | 698.5 | 1821 | 1993 | 470 | 158 | 120 | 0 | 86 | 48
9:00 | 4140 | 698 | 1890 | 2129 | 400 | 160 | 120 | 0 | 86 | 62
9:30 | 4153.5 | 698 | 1877.5 | 2289 | 400 | 160 | 120 | 0 | 91 | 82.5
10:00 | 4167 | 698 | 1865 | 2449 | 400 | 160 | 120 | 0 | 96 | 103
10:30 | 4139.5 | 698 | 1874.5 | 2632.5 | 400 | 160 | 144 | 0 | 94 | 109
11:00 | 4112 | 698 | 1884 | 2816 | 400 | 160 | 168 | 0 | 92 | 115
11:30 | 4104 | 698.5 | 1895.5 | 3052 | 400 | 161 | 185 | 0 | 96 | 119.5
12:00 | 4096 | 699 | 1907 | 3288 | 400 | 162 | 202 | 0 | 100 | 124
12:30 | 4072.5 | 699.5 | 1902 | 3521.5 | 400 | 162 | 230 | 0 | 102 | 121.5
13:00 | 4049 | 700 | 1897 | 3755 | 400 | 162 | 258 | 0 | 104 | 119
13:30 | 4049 | 700 | 1897 | 3755 | 400 | 162 | 258 | 0 | 104 | 119
14:00 | 4049 | 700 | 1897 | 3755 | 400 | 162 | 258 | 0 | 104 | 119
14:30 | 4015.5 | 699.5 | 1881 | 3886.5 | 410 | 162.5 | 293.5 | 0 | 111 | 104.5
15:00 | 3982 | 699 | 1865 | 4018 | 420 | 163 | 329 | 0 | 118 | 90
15:30 | 3999.5 | 699 | 1870 | 3941.5 | 420 | 160.5 | 381.5 | 0 | 119 | 68
16:00 | 4017 | 699 | 1875 | 3865 | 420 | 158 | 434 | 0 | 120 | 46
16:30 | 4031.5 | 699.5 | 1850.5 | 3692 | 420 | 159.5 | 455 | 0 | 124 | 34
17:00 | 4046 | 700 | 1826 | 3519 | 420 | 161 | 476 | 0 | 128 | 22
17:30 | 4017 | 701 | 1705 | 3608 | 420 | 161 | 507 | 0 | 127 | 12
18:00 | 3988 | 702 | 1584 | 3697 | 420 | 161 | 538 | 0 | 126 | 2
18:30 | 4067.5 | 701.5 | 1742 | 4320 | 495 | 162 | 625 | 0 | 136 | 1
19:00 | 4147 | 701 | 1900 | 4943 | 570 | 163 | 712 | 0 | 146 | 0
19:30 | 4127 | 701 | 1894 | 5037 | 622 | 163 | 753 | 0 | 148 | 0
20:00 | 4204 | 701 | 1893 | 5036 | 622 | 163 | 740 | 0 | 150 | 0
20:30 | 4193.5 | 701.5 | 1903 | 5016.5 | 622 | 163 | 738 | 0 | 146 | 0
21:00 | 4183 | 702 | 1913 | 4997 | 622 | 163 | 736 | 0 | 142 | 0
21:30 | 4199 | 702 | 1914 | 4937 | 611 | 163 | 735 | 0 | 143 | 0
22:00 | 4215 | 702 | 1915 | 4877 | 600 | 163 | 734 | 0 | 144 | 0
22:30 | 4212 | 705.5 | 1916.5 | 4796.5 | 590 | 163.5 | 732 | 0 | 142 | 0
23:00 | 4209 | 709 | 1918 | 4716 | 580 | 164 | 730 | 0 | 140 | 0
23:30 | 4270 | 708.5 | 1936.5 | 4716 | 567.5 | 164 | 726.5 | 0 | 141 | 0 | Max Temp. in Dhaka |  | 36.8° C
24:00 | 4331 | 708 | 1955 | 4716 | 555 | 164 | 723 | 0 | 142 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 277.681 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 277.681 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-11
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 88 | 86 | 85 | 84 | 81 | 80 | 81 | 81 | 85 | 85 | 85 | 87 | 87 | 87 | 88 | 83 | 86 | 86 |  | 88 | 88 | 88 | 88 | 88 | 89 | 89 | 2005396
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1808000
3 | Chattogram TPP-1 | [16 empty] | 10 | 15 |  | 20 | 40 | 90 | 30 | 10 |  | 100 | 300000
4 | Chattogram TPP-2 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 90 | 90 | 90 | 90 | 80 | 120 | 2600000
5 | Raozan 25 MW PP | 25 | 25 | 25 | [7 empty] | 1 | 14 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 398946
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 4 | 12 | 7 | 19 | 18 | 17 | 18 | 14 | 12 | 2 | 2 | [9 empty] | 134325
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 85 | [13 empty] | 85 | 85 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 901564
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 89 | 71 | 82 |  | 88 | 88 | 88 | 88 | 88 | 88 | 88 | 2131054
| Daudkandi 200 MW PP (B.Trac) | 75 | [10 empty] | 80 | 200 | 150 | 200 | 200 | 18 |  |  | 200 | 200 | 200 | 200 | 200 | 150 | 150 | 2115072
14 | Titas 50 MW Peaking PP | 49 | 42 | [11 empty] | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 611816
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 260 | 260 | 260 | 260 | 260 | 260 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 250 |  | 320 | 322 | 320 | 323 | 322 | 325 | 325 | 7173912
18 | Kodda 300 MW PP Unit-2 (Summit) | 270 | 263 | 265 | 265 | 195 | 15 | 15 | 15 | 15 | 58 | 158 | 240 | 273 | 273 | 275 | 278 | 293 | 298 |  | 300 | 300 | 300 | 298 | 300 | 300 | 300 | 5419634
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 26 | 45 | 45 | 45 | 45 | 45 | 45 | 384727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 203 |  | 203 | 203 | 203 | 203 | 203 | 203 | 203 | 4834000
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 507744
33 | Ashuganj 225 MW CCPP | 214 | 217 | 215 | 214 | 215 | 213 | 188 | 180 | 201 | 209 | 207 | 186 | 181 | 204 | 181 | 180 | 180 | 200 |  | 206 | 209 | 207 | 208 | 210 | 209 | 210 | 4856000
34 | Ashuganj 450 MW CCPP(South) | 260 | 260 | 260 | 260 | 260 | 260 | 260 | 265 | 350 | 345 | 345 | 350 | 350 | 340 | 295 | 300 | 300 | 305 |  | 330 | 295 | 310 | 305 | 295 | 295 | 295 | 7282000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 295 | 270 | 305 | 340 | 330 | 345 | 315 | 350 | 320 | 320 | 320 | 315 |  | 350 | 315 | 330 | 325 | 315 | 325 | 325 | 7549700
35 | Ashuganj 55 MW PP (Precision) | 47 | 47 | 47 | 47 | 48 | 47 | 49 | 47 | 48 | 49 | 48 | 48 | 48 | 47 | 48 | 48 | 47 | 48 |  | 47 | 47 | 47 | 48 | 48 | 48 | 47 | 1142880
36 | Chandpur 150 MW CCPP | 139 | 138 | 141 | 141 | 140 | 141 | 139 | 139 | 139 | 140 | 140 | 140 | 141 | 144 | 141 | 140 | 138 | 140 |  | 140 | 140 | 140 | 142 | 138 | 141 | 140 | 3355890
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 337 | 336 | 336 | 336 | 334 | 341 | 315 | 305 | 333 | 328 | 328 | 332 | 334 | 332 | 358 | 399 | 401 | 364 |  | 375 | 395 | 396 | 396 | 391 | 387 | 388 | 8607740
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6842250
41 | Haripur 360MW CCPP(HPL) | 293 | 292 | 293 | 292 | 292 | 291 | 292 | 291 | 291 | 291 | 291 | 291 | 291 | 282 | 257 | 257 | 254 | 238 |  | 233 | 220 | 214 | 214 | 214 | 224 | 252 | 6470000
42 | RPCL 210MW CCPP | 186 | 199 | 202 | 208 | 211 | 210 | 212 | 210 | 188 | 156 | 157 | 155 | 143 | 128 | 129 | 129 | 150 | 145 |  | 143 | 143 | 142 | 141 | 139 | 143 | 146 | 3883360
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 4 | 12 | 27 | 46 | 57 | 54 | 54 | 53 | 43 | 28 | 11 | 0 | [8 empty] | 373770
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 36 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 606960
46 | Shajibazar 330 MW CCPP | 160 | 160 | 161 | 162 | 162 | 161 | 162 | 160 | 157 | 153 | 153 | 153 | 154 | 152 | 152 | 153 | 155 | 154 |  | 156 | 156 | 157 | 158 | 160 | 158 | 161 | 3678000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 74 | 74 | 74 | 75 | 75 | 75 | 75 | 75 | 77 | 80 | 76 | 79 | 79 | 78 | 76 | 76 | 76 | 77 |  | 78 | 78 | 79 | 79 | 80 | 80 | 80 | 1841280
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 192 | 220 | 221 | 220 | 221 | 221 | 221 | 221 | 221 | 220 | 208 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5244750
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 597000
56 | Shahjahanulla 25 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  |  | 8 | 16 | 16 |  |  |  |  | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 396888
57 | Bibiana-II 341 MW CCPP (Summit) | 295 | 280 | 280 | 290 | 290 | 280 | 300 | 260 | 310 | 300 | 320 | 300 | 300 | 290 | 300 | 300 | 290 | 240 |  | 300 | 290 | 290 | 310 | 290 | 280 | 290 | 7198000
| Bibiyana South 400 MW | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 |  | 325 | 325 | 325 | 353 | 370 | 370 | 370 | 8044900
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 35 | 35 | 35 | 791619
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 5 | [5 empty] | 3 | 13 | 17 | 22 | 24 | 22 | 24 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 413760
60 | Barabkunda 22 MW PP (Regent) | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 15 | 15 | 18 | 20 | 20 | 18 | 20 | 20 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 |  | 423312
61 | Narshingdi 22 MW PP (Doreen) | 19 |  |  | 19 | 19 |  |  | 19 | 19 | 19 |  |  | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 323064
62 | Tangail 22 MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 468216
63 | Impoprt (Tripura) | 94 | 92 | 92 | 90 | 90 | 84 | 80 | 86 | 86 | 96 | 92 | 100 | 104 | 116 | 118 | 120 | 128 | 126 |  | 146 | 148 | 150 | 142 | 144 | 140 | 142 | 2648640
64 | Malancha, Ctg. EPZ (United) | 40 | 42 | 42 | 42 | 42 | 32 | 29 | 2 | 2 | 2 | 2 | 2 | 2 | 8 | 2 | 2 | 4 | 8 |  | 6 | 3 | 7 | 6 | 27 | 30 | 30 | 429120
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 448956
66 | Feni 11 MW PP (Doreen) | 8 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 240120
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 2 | 25 | 25 | 25 | 25 | 25 | 25 | 16 | 24 | 25 |  | 25 | 25 | 28 | 28 | 30 | 26 | 30 | 603100
68 | Cumilla 25 MW PP (Summit) |  |  |  | 20 | 15 | 15 | 15 |  | 10 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 |  | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 431960
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 29 | 30 | 30 | 29 | 29 | 9 | 9 | 9 | 3 | 9 | 28 | 28 | 28 | 28 | 28 |  | 20 | 29 | 29 | 29 | 29 | 29 | 29 | 552240
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 615600
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 808000
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 114 | 114 | 114 | 70 | 70 | 50 | 65 | 89 | 97 | 98 | 97 | 98 | 98 | 98 | 98 | 98 |  | 98 | 98 | 98 | 98 | 114 | 114 | 114 | 2399700
| Chowmuhani 113 MW | 108 | 108 | 108 | 107 | 108 | 107 | 108 | 99 | 99 | 98 | 98 | 98 | 97 | 98 | 101 | 102 | 109 | 108 |  | 108 | 109 | 108 | 107 | 108 | 107 | 108 | 2515800
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3938400
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 25 | 25 | [6 empty] | 12 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 51 | 51 | 51 | 51 | 51 | 51 | 25 | 576960
79 | Kodda 150MW PP | 150 | 150 | 48 | [7 empty] | 48 | 82 | 133 | 133 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2194080
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | [14 empty] | 95040
81 | Jangalia 52 MW PP (Lakdanavi) | 43 | 43 | 43 | 43 | 25 |  |  |  |  | 4 | 21 | 34 | 34 | 34 | 34 | 43 | 43 | 25 |  | 34 | 34 | 34 | 36 | 43 | 43 | 43 | 738158
| Gazipur 100 MW PP | 52 | 52 | 52 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 |  | 70 | 70 | 70 | 70 | 70 | 70 | 52 | 1105200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 3 | 2 | 3 | 2 | 4 | 2 | 1 | 1 | [9 empty] | 29160
| Jodiac Power | 54 | 54 | 54 | 54 | 54 |  |  |  | 1 | 17 | 20 | 36 | 36 | 51 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1006785
| Karnaphuli Power Ltd. | 103 | 110 | 110 | 110 | 110 | 104 | 110 | 110 | 110 | 110 | 110 | 110 | 102 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2680543
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 76 | 75 | 74 | [7 empty] | 32 | 34 | 37 | 37 | 36 | 45 | 50 | 56 |  | 64 | 64 | 65 | 59 | 73 | 75 | 76 | 995437
86 | Meghnaghat CCPP ( Summit) | 240 | 235 | 245 | 270 | 245 | 280 | 270 | 270 | 270 | 300 | 270 | 280 | 270 | 300 | 280 | 270 | 270 | 300 |  | 270 | 300 | 300 | 265 | 260 | 265 | 245 | 6553745
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 91 | 90 | 89 | 91 | 90 | 75 | 53 | 53 | 53 | 68 | 71 | 71 | 77 | 90 | 90 | 90 | 90 | 90 |  | 90 | 90 | 90 | 90 | 90 | 73 | 72 | 1939200
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 88 | 10 |  |  |  | 10 | 10 | 80 | 80 | 80 | 80 | 80 | 80 | 90 | 65 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1599720
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 25 | 25 | 25 | 25 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 783036
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 58 | 40 | 24 | 24 | 24 | 24 | 24 |  | 64 | 80 | 95 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1896480
95 | Patenga 50MW PP (Baraka) | 50 | 32 | 32 | 25 | 19 | [5 empty] | 22 | 43 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 868800
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | [6 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 40 | 40 | 40 | 40 | 40 | 40 | 55 | 55 | 55 | 51 | 45 | 45 | 45 | 54 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1278258
100 | Manikganj 55 MW PP (Northern) | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1000984
101 | Kushiara 163 MW CCPP (KP) | 163 | 163 | 130 | 130 | 163 | 130 | 130 | 130 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3695890
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 1 | 2 | 2 | 2 | 2 | 2 | 1 | 0 | 0 | 0 | [8 empty] | 9750
103 | Kamalaghat 54 MW PP(Banco Energy) | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1302840
104 | Keranigonj 300 MW PP (APR) | 25 | [9 empty] | 25 | 26 | 205 | 26 | 262 | 131 |  |  |  | 306 | 308 | 305 | 300 | 252 | 221 | 212 | 2337770
105 | Bramhangoan 100 MW PP (Aggreko) | 40 | [10 empty] | 30 | 97 | 50 | 98 | 60 |  |  |  | 100 | 100 | 100 | 100 | 99 | 75 | 75 | 998276
106 | Mymensingh 200 MW PP (United) | 97 | 97 | 101 | 103 | 97 | 38 | 38 | 38 | 38 | 39 | 48 | 38 | 38 | 38 | 38 | 38 | 47 | 104 |  | 177 | 177 | 177 | 177 | 177 | 177 | 96 | 1980000
112 | Aurahati 100MW PP (Aggreko) | 75 | [10 empty] | 72 | 95 | 55 | 89 | 91 | 50 | 25 |  | 80 | 78 | 80 | 95 | 95 | 93 | 94 | 1097834
114 | Kodda 149 MW PP Unit-1 (Summit) | 143 | 142 | 142 | 135 | 126 | 117 | 116 | 121 | 125 | 124 | 127 | 143 | 141 | 143 | 143 | 142 | 135 | 125 |  | 132 | 143 | 144 | 142 | 142 | 145 | 149 | 3266350
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 10 | 73 | 100 | 100 | 90 | 90 | 100 | 100 | 90 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2145600
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 200 | 155 | 120 | 134 | 174 | 170 | 160 | 160 | 160 | 160 | 160 | 160 | 161 |  | 160 | 160 | 160 | 160 | 160 | 170 | 180 | 4077120
117 | Ashuganj 150MW PP (Midland) | 125 | 132 | 130 | 122 | 125 | 120 | 120 | 122 | 118 | 115 | 118 | 128 | 133 | 132 | 132 | 132 | 132 | 132 |  | 135 | 140 | 140 | 135 | 132 | 140 | 140 | 3101236
118 | Bibiyana-III 400 MW CCPP | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 317 | 316 | 316 |  | 316 | 316 | 317 | 337 | 403 | 403 | 402 | 7860000
| Jamalpur 115 MW PP (United) | 68 | 68 | 69 | 68 | 69 | 38 | 38 | 38 | 38 | 38 | 38 | 28 | 38 | 38 | 38 | 38 | 38 | 84 |  | 105 | 107 | 106 | 106 | 107 | 107 | 69 | 1447200
| Anwara 300 MW PP (United) | 103 | 106 | 106 | 106 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 107 | 123 | 164 | 300 |  | 304 | 306 | 306 | 306 | 306 | 306 | 305 | 3999491
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 20 | 10 | 90 | 100 | 100 | 95 | 95 | 100 | 100 | 90 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2149448
| Anlima Energy Ltd. | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2747455
| Bhairob 54.5 MW | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 23 | 35 | 35 | 35 | 35 | 35 | 35 | 585720
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 7 | 20 | 27 | 26 | 36 | 32 | 31 | 22 | 9 | 5 | 0 | [8 empty] | 216231
120 | Eastern Zone Total | 8384 | 8123 | 7797 | 7624 | 7408 | 6766 | 6670 | 6434 | 6925 | 7210 | 7492 | 7943 | 8428 | 8316 | 8619 | 8536 | 8213 | 8211 |  | 9400 | 9434 | 9515 | 9472 | 9477 | 9361 | 9353 | 197287962
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 24 | 24 | [11 empty] | 4 | 4 | 4 | 4 | 20 |  | 22 | 27 | 25 | 24 | 24 | 24 | 24 | 208320
| Khulna 225 MW CCPP | 60 | 90 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 190 | 225 | 225 | 225 | 225 | 225 | 225 | 3441600
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 105 | 105 | 35 | 35 | 35 | 35 | 35 | 70 | 88 | 88 | 88 | 95 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2151840
130
131
132 | United Payra Power Ltd. | 35 | 17 | [15 empty] | 2 |  | 54 | 54 | 54 | 54 | 35 | 72 | 72 | 397200
133 | Bhola Nutan Biddut BD LTD (GAS) | 222 | 210 | 222 | 223 | 223 | 223 | 222 | 184 | 180 | 180 | 180 | 218 | 215 | 213 | 214 | 216 | 180 | 150 |  | 220 | 220 | 220 | 220 | 219 | 220 | 220 | 4992460
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 11 | 12 | 16 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 348169
| Bhola 225 MW CCPP | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 |  | 64 | 65 | 65 | 65 | 65 | 65 | 65 | 1549000
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 32 | 31 | 31 | 29 | 26 | 24 | 23 | 22 | 26 | 25 | 26 | 29 | 26 | 27 | 25 | 27 |  | 34 | 34 | 34 | 34 | 35 | 34 | 34 | 688370
141 | Noapara 100 MW PP (Bangla Trac) | 50 | [11 empty] | 13 |  | 35 | 20 |  |  |  | 70 | 100 | 100 | 100 | 100 | 100 | 100 | 792000
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP | 80 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 |  | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 537984
146 | Bheramara HVDC | 700 | 701 | 701 | 701 | 701 | 701 | 699 | 699 | 698 | 698 | 698 | 699 | 700 | 700 | 699 | 699 | 700 | 702 |  | 701 | 701 | 701 | 702 | 702 | 709 | 708 | 16926545
147 | Bheramara 410 MW CCPP | 235 | 235 | 245 | 245 | 250 | 260 | 260 | 270 | 265 | 255 | 250 | 240 | 230 | 225 | 220 | 220 | 215 | 215 |  | 220 | 225 | 220 | 215 | 210 | 215 | 215 | 5851872
148 | Payra 1320 MW | 470 | 480 | 520 | 510 | 490 | 480 | 400 | 390 | 400 | 400 | 400 | 400 | 400 | 410 | 420 | 420 | 420 | 420 |  | 570 | 622 | 622 | 622 | 600 | 580 | 540 | 12245000
149
150 | Barapukuria TPP Unit-1 | [25 empty] | 15 | 20073
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3 | 150 | 150 | 150 | 150 | 150 | 149 | 150 | 150 | [18 empty] | 1306000
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 43 | [13 empty] | 20 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 433920
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 2 | 3 | 5 | 5 | 4 | 4 | 4 | 2 | 0 | [9 empty] | 32340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 135 | 136 | 142 | 149 | 154 | 159 | 168 | 172 | 171 | 166 | 163 | 159 | 151 | 148 | 140 | 140 | 140 | 140 |  | 140 | 139 | 139 | 139 | 139 | 139 | 136 | 3788818
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 175 | 175 | 186 | 192 | 195 | 160 | 176 | 197 | 200 | 191 | 185 | 176 | 172 | 164 | 162 | 157 | 152 |  | 152 | 151 | 152 | 152 | 152 | 152 | 147 | 4353136
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 420 | 423 | 415 | 418 | 360 | 305 | 306 | 360 | 417 | 410 | 410 | 413 | 405 | 404 | 407 | 414 | 414 | 306 |  | 414 | 415 | 414 | 414 | 414 | 414 | 414 | 9486873
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 28 | 21 | [10 empty] | 5 | 5 | 7 | 7 | 26 | 32 |  | 32 | 32 | 32 | 32 | 30 | 26 | 26 | 300623
162 | Bogra 22 MW PP (GBB) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 | 12 | 13 | 13 | 16 |  | 18 | 18 | 19 | 19 | 19 | 19 | 19 | 410880
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 244944
165 | Amnura 50 MW PP(Sinha) | [11 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 430970
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 43 | 43 | 43 | 43 | 43 |  |  | 163339
167 | Katakhali 50 MW Peaking PP | 15 | 15 | [15 empty] | 10 |  | 37 | 38 | 40 | 37 | 37 | 37 | 30 | 239944
168 | Santahar 50 MW Peaking PP | [19 empty] | 13 | 13 | [5 empty] | 13851
169 | Natore 52 MW PP (Rajlanka) | 8 | 8 | 8 | 8 | 8 | [8 empty] | 5 | 34 | 34 | 43 | 34 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 456960
170 | Chapainawabganj 100 MW Peaking PP | 92 | 92 | 92 | [14 empty] | 30 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 815264
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 184 | 185 | 185 | 185 | 120 | 70 | 70 | 805335
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 35 | 35 | 35 | 35 | 80 | 94 | 94 | 94 | 94 | 94 | 108 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2251296
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 70 | 35 | 35 | 90 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2518656
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 50 |  |  |  | 4 | 42 | 107 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2149084
177 | Sympa Solar Power 8MW | [7 empty] | 0 | 1 | 3 | 5 | 7 | 7 | 7 | 6 | 4 | 3 | 2 | [8 empty] | 40076
178
178