## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-16 | Thursday
|  |  | Date (day): | 2021-09-16 |  | Thursday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13841.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14619 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-15 | 2021-09-16 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint. |  | 2021-08-16
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 205 | 205 | 300 | 300 |  | 65 | ST under maint
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 113 | 119 | 120 | 120 |  | 292 | GBC problem
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 172 | 171 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 280 | 300 | 300 | 150 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 285 | 260 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 13 | 36 | 10 | 13 |  | 87 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 15 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 92 | 87 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 324 | 328 | 326 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 40 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 150 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 47 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 42 | 25 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 263 | 284 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 164 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 96 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 98 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 52 | 90 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 104 | 100 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 160 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 32 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2747 | 3276 | 3470 | 3734 | 777 | 1172
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 12 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 21 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 166 | 168 | 168 | 168 | 62 |  | Low water level & Unit-3 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint |  | 2021-08-11
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 82 | 82 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 100 | 100 | 100 |  | 0 | Engine problem
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 4 | 15 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 114 | 114 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1297 | 1437 | 1403 | 1469 | 250 | 670
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 208 | 210 | 210 | 210
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 280 | 300 | 320 | 40 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 290 | 280 | 300 | 310 | 50 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem |  | 2021-10-15
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 55 | 54 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 8 | 8 | 8 | 187 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 35 | 35 |  | 16 | Engine problem |  | 2021-09-06
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 124 | 138 | 138 |  | 12 | Engine problem |  | 2021-08-31
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 142 | 138 | 142 | 142 |  | 21 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 120 | 140 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 25 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 51 | 52 | 50 | 51
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 16 | 21 | 20 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 200 | 100 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 95 | 94 | 100 | 100
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1882 | 2095 | 2016 | 2224 | 675 | 108
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 109 | 118 | 152 | 152 | 50 |  | Gas shortage |  | 2021-09-01
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 8 | 8 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 3 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 37 | 191 | 175 | 200 |  |  |  |  | 2021-09-13
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 37 | 115 | 115 | 115 |  |  |  |  | 2021-09-13
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 289 | 473 | 545.6 | 519 | 50 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 156 | 158 | 160 | 162 | 168 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 25 | 25 |  | 26 | Engine problem
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 78 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint |  | 2021-11-03
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 221 | 220 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 18 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 295 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 315 | 316 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 383 | 383
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1596 | 1625 | 1842 | 1844 | 262 | 256
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 707 | 708 | 727 | 727
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 27 |  | 27 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 155 | 230 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 320 | 355 | 400 | 10 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 99 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 85 | 102 | 105 | 105 |  |  |  |  | 2021-08-31
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1277 | 1486 | 1562 | 1724 | 10 | 96
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 86 | 87 | 87 |  | 107 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 22 | 22 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 219 | 216 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 45 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 720 | 931 | 1244 | 1244 | 73 | 107
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 41 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 27 | 27 | 27 | 27 | 23 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 8 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 204 | 195 | 206 | 206 | 14 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 202 | 211 | 200 | 220 | 0 |  | Gas shortage
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 413 | 414 | 400 | 400
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 25 | 0 | 25 |  | 25 | Engine problem |  | 15-09-2021
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 20 | 22 |  | 0 | Engine problem
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 34 | 52 | 52 | 52 |  | 0 | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 93 | 90 | 93 |  | 11 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 185 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 94 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1162 | 1572 | 1561 | 1645 | 417 | 94
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 81 | 77 | 77 | 77
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 274 |  | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 16 |  | 4 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 110 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 198 | 190 | 198 | 216 | 274 | 99
|  | Total |  |  |  |  | 22031 | 21180 | 11168 | 13085 | 13841.6 | 14619 | 2788 | 2689
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10591.0365 | 12409 | 13126.5124 | 13863.7502
| A. |  | 2021-09-15 | (Yesterday) |  |  |  |  | Wednesday
| 1 | Highest Generation : |  |  | 13085 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9339 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13085 | MW
| 3 | Day peak Generation : |  |  | 11168 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12409 | MW
| 4 | Evening peak Generation : |  |  | 13085 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 275.4 | MKWHr | By Solar | 3.4933 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 142.3274 | MKWHr |  | By Oil: | 92.6488 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13 | MKWHr |  | By Hydro: | 3.9181 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2788 | MW | Dhaka | 4636 | 4636 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2689 | MW | Chittagong | 1327 | 1327 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5477 | MW | Khulna | 1444 | 1444 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1114.5 | MMCFD |  |  | Rajshahi | 1330 | 1330 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 143816748.338 | ii) Oil : | Taka | 721010542.41 | Comilla | 1207 | 1207 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 60246788.54 | Total | Taka | 925074079.288 | Mymensingh | 962 | 962 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.138 | MKWHr. | Sylhet | 425 | 425 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 90 | MW (E to W) at | 19:30 | hrs | Barisal | 358 | 358 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -78 | MW at | 23:00 | hrs | Rangpur | 720 | 720 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.3° C |  |  | Total | 12409 | 12409 |  | 0
| B. |  | 2021-09-16 | (Today) |  |  |  | Thursday |  |  | Probable max. temperature in Dhaka |  |  | 33.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13500 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14619 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10700 | MW
| 4 | Reserve(Generation end) |  |  |  | 1119 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 284.1345 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9348 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.0575 | MKWHr. | ii) HVDC Flow at Peak Time |  | 708 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.9549 | MKWHr. | iii) Maximum HVDC Flow : |  | 708 | MW at | 10:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.48 |  | (b) Today: | 105.5 |  | (c) Rule Curve: |  | 102.45
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-15
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 296 |  | 0 | 300 | 250 | 0 | 0 | 50 | 335 | 0 | 37 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 29 | 25 | 33 | 25 | 0 | 83 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 23 | 0 | 34 | 92 | 0 | 50 | 21 | 31 | 0 | 0 | 0 | 265 | 265 | 216 | 36 | 138 | 23 | 56 | 0 | 35 | 0 | 0 | 51 | 22 | 11 | 33 | 21 | 128 | 142 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 162 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 300 | 0 | 0 | 115 | 0 | 133 | 0 | 90 | 200 | 142 | 328 | 76 | 52 | 105 | 0 | 106 | 54 | 94 | 107 | 97 | 100 | 330 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 703 | 0 | 320 | 0 | 0 | 175 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 27 | 0 | 0 | 43 | 25 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 22 | 0 | 216 | 0 | 310 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 223 | 0 | 0 | 0 |  | 7881 | 3478 | 11359 | 4037 | 703 | 1880 | 3437 | 538 | 158 | 478 | 128 | 0 | 0 | 105.48
2:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 316 |  | 0 | 300 | 280 | 0 | 0 | 55 | 335 | 0 | 37 | 0 | 40 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 23 | 0 | 0 | 92 | 0 | 12 | 21 | 31 | 0 | 0 | 0 | 265 | 265 | 213 | 36 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 51 | 22 | 11 | 33 | 21 | 124 | 142 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 162 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 300 | 0 | 0 | 116 | 0 | 129 | 0 | 90 | 200 | 137 | 328 | 77 | 35 | 105 | 0 | 106 | 54 | 105 | 107 | 97 | 100 | 330 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 702 | 0 | 335 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 22 | 0 | 216 | 0 | 350 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 450 | 223 | 0 | 0 | 0 |  | 7646 | 3326 | 10972 | 4059 | 702 | 1947 | 3269 | 529 | 158 | 184 | 124 | 0 | 0 | 105.48
3:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 324 |  | 0 | 300 | 270 | 0 | 0 | 55 | 335 | 0 | 37 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 22 | 25 | 29 | 25 | 33 | 0 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 31 | 0 | 0 | 0 | 265 | 265 | 213 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 25 | 22 | 11 | 33 | 21 | 122 | 142 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 250 | 0 | 0 | 116 | 0 | 115 | 0 | 90 | 200 | 138 | 329 | 77 | 52 | 105 | 0 | 106 | 54 | 105 | 108 | 98 | 100 | 330 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 702 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 0 | 216 | 0 | 340 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 440 | 223 | 0 | 0 | 0 |  | 7433 | 3313 | 10746 | 4065 | 702 | 1950 | 3046 | 519 | 158 | 184 | 122 | 0 | 0 | 105.48
4:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 324 |  | 0 | 300 | 270 | 0 | 0 | 40 | 334 | 0 | 37 | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 22 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 32 | 0 | 0 | 0 | 270 | 270 | 213 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 142 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 160 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 95 | 0 | 0 | 115 | 0 | 90 | 0 | 90 | 200 | 132 | 328 | 77 | 52 | 105 | 0 | 106 | 54 | 105 | 108 | 94 | 100 | 330 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 703 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 0 | 216 | 0 | 352 | 102 | 0 | 113 | 0 | 99 | 0 | 0 | 113 | 410 | 223 | 0 | 0 | 0 |  | 7191 | 3278 | 10469 | 4064 | 703 | 1965 | 2801 | 488 | 160 | 168 | 120 | 0 | 0 | 105.48
5:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 330 |  | 0 | 300 | 270 | 0 | 0 | 15 | 335 | 0 | 37 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 29 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 40 | 0 | 0 | 0 | 265 | 265 | 213 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 150 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 160 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 30 | 0 | 0 | 115 | 0 | 86 | 0 | 90 | 200 | 128 | 328 | 77 | 52 | 105 | 0 | 106 | 54 | 110 | 108 | 94 | 100 | 330 | 92 | 0 | 162 | 114 | 0 | 17 | 0 |  | 703 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 0 | 216 | 0 | 340 | 102 | 0 | 113 | 0 | 44 | 0 | 0 | 113 | 390 | 222 | 0 | 0 | 0 |  | 7084 | 3200 | 10284 | 4080 | 703 | 1966 | 2641 | 468 | 160 | 152 | 114 | 0 | 0 | 105.48
6:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 327 |  | 0 | 300 | 270 | 0 | 0 | 15 | 280 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 22 | 25 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 30 | 0 | 0 | 0 | 265 | 265 | 213 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 108 | 157 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 162 | 0 | 81 | 0 | 180 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 15 | 0 | 0 | 37 | 0 | 86 | 1 | 90 | 170 | 133 | 328 | 37 | 52 | 105 | 0 | 106 | 17 | 110 | 52 | 98 | 50 | 330 | 89 | 1 | 162 | 114 | 0 | 17 | 0 |  | 703 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 22 | 0 | 217 | 0 | 352 | 17 | 0 | 35 | 0 | 0 | 0 | 0 | 113 | 370 | 222 | 0 | 0 | 0 |  | 6630 | 2980 | 9610 | 3987 | 703 | 1949 | 2116 | 449 | 160 | 136 | 108 | 2 | 0 | 105.48
7:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 323 |  | 0 | 300 | 285 | 0 | 0 | 15 | 250 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 22 | 25 | 16 | 0 | 0 | 87 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 30 | 0 | 0 | 0 | 280 | 280 | 214 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 22 | 2 | 33 | 18 | 102 | 154 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 81 | 0 | 180 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 15 | 0 | 0 | 37 | 0 | 85 | 5 | 50 | 155 | 130 | 328 | 37 | 52 | 105 | 1 | 106 | 0 | 110 | 17 | 99 | 20 | 330 | 92 | 18 | 162 | 114 | 0 | 17 | 5 |  | 703 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 22 | 0 | 216 | 0 | 348 | 0 | 0 | 35 | 0 | 0 | 0 | 1 | 70 | 350 | 223 | 0 | 0 | 0 |  | 6460 | 2879 | 9339 | 3930 | 703 | 1947 | 1900 | 429 | 162 | 136 | 102 | 30 | 0 | 105.49
8:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 298 |  | 0 | 300 | 285 | 0 | 0 | 25 | 250 | 0 | 37 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 15 | 25 | 22 | 25 | 16 | 0 | 0 | 84 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 0 | 0 | 300 | 280 | 212 | 36 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 5 | 33 | 17 | 104 | 145 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 160 | 0 | 81 | 0 | 221 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 15 | 0 | 0 | 37 | 0 | 98 | 10 | 76 | 155 | 123 | 328 | 37 | 52 | 105 | 3 | 157 | 0 | 110 | 17 | 91 | 25 | 331 | 90 | 27 | 162 | 114 | 0 | 17 | 15 |  | 704 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 22 | 0 | 212 | 0 | 348 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 80 | 310 | 223 | 0 | 0 | 2 |  | 6585 | 2877 | 9462 | 4004 | 704 | 1908 | 1998 | 389 | 159 | 136 | 104 | 60 | 0 | 105.49
9:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 232 |  | 0 | 300 | 280 | 0 | 0 | 55 | 334 | 0 | 90 | 0 | 7 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 25 | 22 | 25 | 33 | 16 | 0 | 83 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 10 | 0 | 7 | 21 | 2 | 0 | 0 | 0 | 290 | 300 | 214 | 36 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 4 | 19 | 8 | 33 | 17 | 104 | 130 | 8 | 19 | 2 | 30 | 0 | 25 | 0 | 130 | 159 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 30 | 0 | 0 | 37 | 0 | 147 | 14 | 76 | 155 | 115 | 328 | 38 | 52 | 105 | 4 | 214 | 12 | 110 | 51 | 91 | 90 | 330 | 89 | 43 | 162 | 114 | 0 | 17 | 11 |  | 704 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 0 | 22 | 0 | 206 | 0 | 315 | 11 | 0 | 49 | 0 | 34 | 0 | 5 | 113 | 310 | 221 | 0 | 0 | 4 |  | 7020 | 2938 | 9958 | 4159 | 704 | 1793 | 2435 | 386 | 158 | 136 | 104 | 83 | 0 | 105.49
10:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 116 | 191 |  | 0 | 300 | 290 | 0 | 0 | 55 | 330 | 0 | 92 | 0 | 16 | 16 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 15 | 25 | 22 | 25 | 33 | 16 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 0 | 26 | 0 | 19 | 21 | 2 | 0 | 0 | 0 | 320 | 350 | 213 | 36 | 141 | 23 | 55 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 16 | 108 | 118 | 8 | 17 | 2 | 30 | 0 | 25 | 0 | 130 | 157 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 305 | 16 | 11 | 0 | 117 | 0 | 0 | 37 | 0 | 149 | 18 | 76 | 155 | 115 | 328 | 38 | 52 | 105 | 4 | 305 | 24 | 98 | 52 | 96 | 90 | 330 | 90 | 53 | 162 | 114 | 0 | 17 | 32 |  | 708 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 213 | 0 | 22 | 0 | 202 | 0 | 408 | 17 | 0 | 84 | 0 | 39 | 0 | 5 | 113 | 320 | 220 | 0 | 0 | 3 |  | 7326 | 3079 | 10405 | 4207 | 708 | 1845 | 2719 | 401 | 164 | 136 | 108 | 117 | 0 | 105.49
11:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 177 |  | 0 | 300 | 275 | 0 | 0 | 55 | 325 | 0 | 91 | 0 | 24 | 16 | 4 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 22 | 25 | 33 | 25 | 0 | 89 | 75 | 115 | 0 | 2 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 82 | 0 | 19 | 21 | 2 | 0 | 0 | 0 | 290 | 280 | 180 | 36 | 140 | 20 | 56 | 0 | 35 | 0 | 0 | 20 | 19 | 8 | 33 | 16 | 122 | 117 | 8 | 17 | 1 | 30 | 0 | 25 | 0 | 130 | 158 | 0 | 78 | 0 | 221 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 167 | 0 | 0 | 37 | 0 | 149 | 19 | 76 | 186 | 123 | 328 | 38 | 52 | 105 | 5 | 305 | 47 | 98 | 105 | 97 | 90 | 330 | 88 | 43 | 162 | 114 | 0 | 17 | 35 |  | 707 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 43 | 0 | 18 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 0 | 22 | 0 | 201 | 0 | 412 | 75 | 0 | 94 | 0 | 92 | 0 | 7 | 113 | 340 | 220 | 0 | 0 | 4 |  | 7449 | 3231 | 10680 | 4055 | 707 | 1832 | 3128 | 422 | 164 | 136 | 122 | 114 | 0 | 105.49
12:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 113 | 172 |  | 0 | 300 | 285 | 0 | 0 | 55 | 324 | 0 | 92 | 0 | 40 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 22 | 25 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 12 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 82 | 0 | 21 | 21 | 2 | 0 | 0 | 0 | 300 | 290 | 208 | 36 | 142 | 20 | 55 | 0 | 35 | 0 | 0 | 51 | 19 | 8 | 33 | 16 | 120 | 109 | 8 | 19 | 3 | 30 | 0 | 25 | 0 | 130 | 156 | 0 | 77 | 0 | 221 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 263 | 0 | 0 | 37 | 0 | 149 | 19 | 76 | 200 | 123 | 315 | 37 | 52 | 105 | 5 | 305 | 54 | 110 | 114 | 95 | 90 | 320 | 90 | 54 | 160 | 114 | 0 | 17 | 32 |  | 707 | 0 | 330 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 27 | 0 | 0 | 34 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 22 | 0 | 202 | 0 | 413 | 85 | 0 | 94 | 0 | 110 | 0 | 7 | 113 | 370 | 219 | 0 | 0 | 5 |  | 7811 | 3357 | 11168 | 4057 | 707 | 1821 | 3375 | 451 | 166 | 346 | 120 | 125 | 0 | 105.49
13:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 172 |  | 0 | 300 | 290 | 0 | 0 | 55 | 322 | 0 | 37 | 0 | 85 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 24 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 82 | 0 | 44 | 21 | 3 | 0 | 0 | 0 | 320 | 305 | 202 | 36 | 140 | 23 | 54 | 0 | 35 | 0 | 0 | 49 | 19 | 8 | 33 | 21 | 126 | 95 | 8 | 19 | 2 | 30 | 0 | 24 | 0 | 130 | 156 | 0 | 77 | 0 | 222 | 0 | 0 | 0 | 310 | 8 | 11 | 20 | 275 | 0 | 0 | 37 | 50 | 149 | 19 | 76 | 200 | 122 | 315 | 46 | 52 | 105 | 5 | 305 | 54 | 98 | 114 | 96 | 100 | 320 | 92 | 54 | 144 | 114 | 0 | 17 | 32 |  | 707 | 0 | 330 | 0 | 0 | 223 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 43 | 0 | 18 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 0 | 195 | 0 | 406 | 85 | 0 | 94 | 0 | 113 | 0 | 7 | 113 | 380 | 216 | 0 | 0 | 5 |  | 7951 | 3436 | 11387 | 4007 | 707 | 1825 | 3546 | 462 | 167 | 423 | 126 | 124 | 0 | 105.49
14:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 171 |  | 0 | 280 | 270 | 0 | 0 | 55 | 321 | 0 | 37 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 28 | 25 | 33 | 25 | 0 | 94 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 285 | 280 | 204 | 36 | 140 | 23 | 54 | 0 | 35 | 0 | 17 | 51 | 19 | 11 | 25 | 21 | 130 | 99 | 8 | 19 | 2 | 30 | 0 | 25 | 0 | 163 | 156 | 0 | 77 | 0 | 221 | 0 | 0 | 0 | 300 | 8 | 11 | 20 | 275 | 0 | 0 | 37 | 50 | 149 | 19 | 76 | 200 | 128 | 316 | 37 | 52 | 105 | 4 | 304 | 54 | 106 | 114 | 96 | 100 | 320 | 86 | 51 | 155 | 114 | 0 | 17 | 29 |  | 708 | 0 | 325 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 43 | 0 | 19 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 0 | 196 | 0 | 410 | 87 | 0 | 94 | 0 | 113 | 0 | 7 | 113 | 400 | 220 | 0 | 0 | 4 |  | 7937 | 3464 | 11401 | 3944 | 708 | 1838 | 3572 | 482 | 169 | 442 | 130 | 116 | 0 | 105.49
15:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 171 |  | 0 | 280 | 285 | 0 | 0 | 55 | 319 | 0 | 37 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 28 | 25 | 33 | 25 | 0 | 94 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 300 | 300 | 182 | 36 | 140 | 23 | 54 | 0 | 35 | 0 | 49 | 51 | 20 | 11 | 25 | 21 | 136 | 96 | 8 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 155 | 0 | 74 | 0 | 221 | 0 | 0 | 0 | 310 | 8 | 11 | 74 | 275 | 76 | 40 | 37 | 99 | 149 | 7 | 76 | 200 | 128 | 316 | 37 | 52 | 105 | 3 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 87 | 27 | 162 | 114 | 0 | 17 | 20 |  | 707 | 0 | 325 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 84 | 25 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 46 | 0 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 22 | 12 | 190 | 0 | 405 | 102 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 410 | 218 | 0 | 0 | 2 |  | 8187 | 3479 | 11666 | 3939 | 707 | 1839 | 3846 | 490 | 169 | 474 | 136 | 66 | 0 | 105.49
16:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 171 |  | 0 | 280 | 260 | 0 | 0 | 42 | 320 | 0 | 38 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 15 | 25 | 28 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 82 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 174 | 36 | 142 | 23 | 54 | 0 | 35 | 0 | 49 | 51 | 20 | 11 | 25 | 20 | 128 | 99 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 130 | 157 | 0 | 74 | 0 | 221 | 0 | 0 | 0 | 290 | 16 | 11 | 70 | 282 | 76 | 40 | 37 | 99 | 143 | 9 | 76 | 200 | 130 | 316 | 37 | 52 | 105 | 1 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 89 | 13 | 162 | 114 | 0 | 17 | 10 |  | 707 | 0 | 320 | 0 | 0 | 230 | 0 | 0 | 0 | 0 | 0 | 86 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 27 | 0 | 0 | 46 | 0 | 19 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 22 | 20 | 194 | 0 | 406 | 102 | 0 | 94 | 0 | 113 | 0 | 6 | 113 | 400 | 219 | 0 | 0 | 1 |  | 7993 | 3479 | 11472 | 3907 | 707 | 1787 | 3779 | 477 | 167 | 479 | 128 | 41 | 0 | 105.49
17:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 173 |  | 0 | 280 | 235 | 0 | 0 | 47 | 316 | 0 | 35 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 35 | 35 | 17 | 25 | 28 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 17 | 50 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 181 | 36 | 139 | 23 | 54 | 0 | 35 | 0 | 48 | 51 | 20 | 11 | 25 | 20 | 116 | 110 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 159 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 285 | 16 | 11 | 10 | 275 | 0 | 0 | 115 | 0 | 132 | 1 | 100 | 200 | 123 | 316 | 41 | 83 | 105 | 0 | 304 | 54 | 102 | 90 | 88 | 100 | 320 | 89 | 8 | 162 | 114 | 0 | 17 | 3 |  | 707 | 0 | 315 | 0 | 0 | 230 | 0 | 0 | 4 | 0 | 0 | 85 | 22 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 27 | 0 | 0 | 46 | 0 | 19 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 22 | 0 | 201 | 0 | 362 | 70 | 0 | 94 | 0 | 113 | 0 | 2 | 113 | 390 | 182 | 0 | 0 | 1 |  | 7733 | 3343 | 11076 | 3919 | 707 | 1704 | 3474 | 470 | 167 | 504 | 116 | 15 | 0 | 105.49
18:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 171 |  | 0 | 280 | 300 | 0 | 0 | 55 | 280 | 0 | 37 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 25 | 28 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 32 | 0 | 50 | 21 | 3 | 0 | 0 | 0 | 280 | 280 | 204 | 8 | 142 | 23 | 54 | 0 | 35 | 0 | 48 | 52 | 20 | 11 | 25 | 18 | 128 | 130 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 155 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 10 | 275 | 56 | 50 | 191 | 0 | 149 | 0 | 75 | 180 | 120 | 315 | 79 | 90 | 105 | 0 | 267 | 54 | 104 | 52 | 94 | 60 | 320 | 101 | 0 | 162 | 114 | 0 | 17 | 0 |  | 707 | 0 | 320 | 0 | 0 | 226 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 50 | 8 | 30 | 27 | 0 | 8 | 52 | 12 | 21 | 0 | 11 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 22 | 0 | 160 | 0 | 349 | 55 | 0 | 94 | 0 | 84 | 0 | 0 | 113 | 400 | 130 | 0 | 0 | 0 |  | 7961 | 3250 | 11211 | 3863 | 707 | 1630 | 3613 | 482 | 167 | 621 | 128 | 0 | 0 | 105.49
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 115 | 171 |  | 0 | 280 | 315 | 0 | 0 | 55 | 325 | 0 | 61 | 0 | 102 | 150 | 23 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 20 | 25 | 33 | 40 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 82 | 0 | 50 | 21 | 6 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 142 | 23 | 54 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 18 | 128 | 117 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 200 | 277 | 256 | 97 | 191 | 98 | 149 | 0 | 100 | 200 | 125 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 33 | 0 |  | 707 | 0 | 320 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 50 | 18 | 93 | 27 | 34 | 8 | 52 | 26 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 22 | 76 | 204 | 0 | 372 | 100 | 185 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 222 | 0 | 30 | 0 |  | 9008 | 4029 | 13037 | 3991 | 707 | 1779 | 4954 | 575 | 168 | 735 | 128 | 0 | 0 | 105.49
19:30 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 119 | 171 |  | 0 | 280 | 260 | 0 | 0 | 55 | 328 | 0 | 87 | 0 | 102 | 150 | 36 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 42 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 82 | 0 | 50 | 21 | 4 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 138 | 23 | 54 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 140 | 118 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 200 | 284 | 164 | 96 | 191 | 98 | 149 | 0 | 100 | 200 | 124 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 708 | 0 | 320 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 50 | 30 | 93 | 27 | 43 | 8 | 52 | 25 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 22 | 99 | 211 | 0 | 414 | 102 | 185 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 216 | 0 | 45 | 0 |  | 8906 | 4179 | 13085 | 4053 | 708 | 1803 | 4860 | 607 | 168 | 746 | 140 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 119 | 171 |  | 0 | 300 | 315 | 0 | 0 | 55 | 330 | 0 | 87 | 0 | 102 | 150 | 38 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 42 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 82 | 0 | 50 | 21 | 12 | 0 | 0 | 0 | 280 | 280 | 207 | 8 | 141 | 23 | 55 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 138 | 117 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 275 | 24 | 11 | 200 | 283 | 111 | 97 | 192 | 97 | 149 | 0 | 100 | 200 | 125 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 20 | 0 |  | 707 | 0 | 325 | 0 | 0 | 230 | 0 | 0 | 23 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 25 | 93 | 27 | 43 | 24 | 52 | 25 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 22 | 98 | 212 | 0 | 414 | 102 | 120 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 224 | 0 | 35 | 0 |  | 8938 | 4125 | 13063 | 4060 | 707 | 1837 | 4793 | 607 | 168 | 753 | 138 | 0 | 0 | 105.49
21:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 119 | 162 |  | 0 | 300 | 320 | 0 | 0 | 55 | 330 | 0 | 90 | 0 | 102 | 150 | 38 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 32 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 15 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 142 | 23 | 56 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 138 | 116 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 200 | 284 | 110 | 99 | 191 | 99 | 149 | 0 | 100 | 200 | 125 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 35 | 0 |  | 708 | 0 | 315 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 18 | 93 | 27 | 43 | 24 | 52 | 25 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 22 | 99 | 205 | 0 | 415 | 102 | 100 | 94 | 0 | 113 | 0 | 0 | 113 | 550 | 224 | 0 | 17 | 0 |  | 8997 | 4077 | 13074 | 4047 | 708 | 1858 | 4786 | 625 | 168 | 744 | 138 | 0 | 0 | 105.49
22:00 | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 119 | 162 |  | 0 | 300 | 275 | 0 | 0 | 55 | 330 | 0 | 89 | 0 | 102 | 150 | 37 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 33 | 0 | 91 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 25 | 0 | 0 | 0 | 320 | 290 | 213 | 8 | 139 | 23 | 56 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 138 | 118 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 275 | 24 | 11 | 200 | 284 | 54 | 100 | 196 | 98 | 149 | 0 | 100 | 200 | 128 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 35 | 0 |  | 707 | 0 | 315 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 50 | 35 | 93 | 27 | 43 | 24 | 52 | 19 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 22 | 70 | 208 | 0 | 417 | 102 | 43 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 213 | 0 | 17 | 0 |  | 8939 | 3984 | 12923 | 4100 | 707 | 1834 | 4608 | 615 | 166 | 755 | 138 | 0 | 0 | 105.49
23:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 172 |  | 0 | 300 | 305 | 0 | 0 | 55 | 330 | 0 | 90 | 0 | 102 | 150 | 36 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 42 | 0 | 91 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 28 | 0 | 0 | 0 | 320 | 310 | 210 | 8 | 141 | 23 | 55 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 130 | 117 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 150 | 284 | 55 | 100 | 197 | 97 | 149 | 0 | 100 | 200 | 133 | 317 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 320 | 96 | 0 | 162 | 114 | 0 | 35 | 0 |  | 707 | 0 | 310 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 31 | 93 | 27 | 0 | 24 | 52 | 19 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 22 | 20 | 208 | 0 | 417 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 540 | 223 | 0 | 17 | 0 |  | 8767 | 3846 | 12613 | 3904 | 707 | 1881 | 4458 | 616 | 166 | 751 | 130 | 0 | 0 | 105.49
24:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 200 |  | 0 | 300 | 265 | 0 | 0 | 55 | 330 | 0 | 91 | 0 | 102 | 150 | 37 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 29 | 25 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 28 | 0 | 0 | 0 | 300 | 290 | 214 | 8 | 141 | 23 | 55 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 0 | 21 | 114 | 139 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 115 | 284 | 52 | 96 | 162 | 50 | 149 | 0 | 100 | 200 | 127 | 317 | 89 | 52 | 105 | 0 | 304 | 54 | 110 | 114 | 97 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 708 | 0 | 310 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 50 | 32 | 93 | 27 | 0 | 0 | 52 | 23 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 22 | 20 | 210 | 0 | 422 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 223 | 0 | 17 | 0 |  | 8475 | 3823 | 12298 | 3866 | 708 | 1914 | 4192 | 606 | 166 | 732 | 114 | 0 | 0 | 105.49
KWH | 0 | 0 | 0 | 0 | 4653900 | 0 | 0 | 2922480 | 5422000 |  | 0 | 7070000 | 6721687 | 0 | 0 | 1178382 | 7672803 | 0 | 1542000 | 0 | 1512432 | 2360640 | 320711 | 0 | 0 | 0 | 648720 | 968908 | 785046 | 398556 | 600000 | 596880 | 614500 | 743300 | 473280 | 0 | 2106087 | 1812000 | 2700000 | 0 | 345517 | 0 | 0 | 0 | 0 |  | 572400 | 0 | 610513 | 1352760 | 0 | 757440 | 498336 | 327840 | 0 | 0 | 0 | 7159500 | 6964000 | 4980000 | 702545 | 3353800 | 511488 | 1320960 | 0 | 831932 | 0 | 481568 | 858158 | 482112 | 225720 | 685800 | 506050 | 2954880 | 2913040 | 155520 | 413748 | 13100 | 715000 | 0 | 595800 | 0 | 3503945 | 3726000 | 0 | 1955520 | 0 | 5156570 | 0 | 0 | 0 | 7252000 | 383064 | 264000 | 1281216 | 5141125 | 867031 | 669689 | 2356800 | 879169 | 3228624 | 137565 | 2005440 | 4521120 | 3066095 | 7738000 | 1603200 | 1485600 | 2550909 | 33000 | 5630400 | 1103560 | 2611125 | 2269740 | 2294040 | 2156160 | 7734500 | 2319360 | 399800 | 3912480 | 2747454 | 0 | 531720 | 2820396 |  | 17057454 | 0 | 8028288 | 0 | 0 | 4357440 | 0 | 0 | 120960 | 0 | 0 | 2109489 | 639222 | 0 | 0 | 0 | 0 | 614832 | 146989 | 681496 | 398340 | 165604 | 39244 | 1091040 | 156623 | 470400 | 0 | 262464 | 1937018 | 0 | 0 | 0 | 0 | 0 | 0 | 4909273 | 0 | 537999 | 474240 | 5214055 | 0 | 9122218 | 1422720 | 502132 | 2200608 | 0 | 2117126 | 0 | 54126 | 2672448 | 11063000 | 5196327 | 0 | 151200 | 35340 |  | 191450256 | 83949715 | 275399971 | 97378716 | 17057454 | 44948708 | 83078476 | 13000018 | 3918087 | 9570305 | 2954880 | 3493327 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 5165829 | 0 | 0 | 2951704.8 | 5584660 |  | 0 | 7706300 | 7461072.57 | 0 | 0 | 9969111.72 | 7979715.12 | 0 | 2667660 | 0 | 13793379.84 | 23228697.6 | 2956955.42 | 0 | 0 | 0 | 4735656 | 7489658.84 | 7740553.56 | 298917 | 450000 | 0 | 0 | 0 | 4576617.6 | 0 | 568643.49 | 489240 | 4887000 | 0 | 3209852.93 | 0 | 0 | 0 | 0 |  | 0 | 0 | 5921976.1 | 12918858 | 0 | 5998924.8 | 627903.36 | 973684.8 | 0 | 0 | 0 | 5298030 | 6964000 | 4581600 | 906283.05 | 3856870 | 577981.44 | 1849344 | 0 | 1422603.72 | 0 | 4863836.8 | 8195408.9 | 612282.24 | 169290 | 1200150 | 379537.5 | 22161600 | 3087822.4 | 1412121.6 | 525459.96 | 208814 | 1172600 | 0 | 1060524 | 0 | 3994497.3 | 3875040 | 0 | 3735043.2 | 0 | 8920866.1 | 0 | 0 | 0 | 7324520 | 287298 | 200640 | 21793484.16 | 38866905 | 14722186.38 | 11197200.08 | 12255360 | 14699705.68 | 31769660.16 | 1608134.85 | 16344336 | 49054152 | 21615969.75 | 7196340 | 14621184 | 14038920 | 22218417.39 | 0 | 42565824 | 9612007.6 | 22951788.75 | 22652005.2 | 19659922.8 | 14360025.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98250935.04 | 0 | 8429702.4 | 0 | 0 | 60394118.4 | 0 | 0 | 1268870.4 | 0 | 0 | 2383722.57 | 990794.1 | 0 | 0 | 0 | 0 | 6049946.88 | 1493408.24 | 6031239.6 | 3067218 | 2238966.08 | 380274.36 | 10572177.6 | 1519243.1 | 903168 | 0 | 198685.248 | 11680218.54 | 0 | 0 | 0 | 0 | 0 | 0 | 6480240.36 | 0 | 806998.5 | 8066822.4 | 6100444.35 | 0 | 9030995.82 | 14853196.8 | 8541265.32 | 20883769.92 | 0 | 16428897.76 | 0 | 598092.3 | 19749390.72 | 48566570 | 0 | 0 | 0 | 0 |  | 673000166.16 | 375959372.808 | 1048959538.968 | 97527331.848 | 98250935.04 | 46289416.49 | 609858930.93 | 60246788.54 | 1057883.49 | 111151611.48 | 22161600 | 2415041.15 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 113 | 172 |  | 0 | 300 | 285 | 0 | 0 | 55 | 324 | 0 | 92 | 0 | 40 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 35 | 15 | 25 | 22 | 25 | 33 | 25 | 0 | 91 | 75 | 115 | 0 | 12 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 82 | 0 | 21 | 21 | 2 | 0 | 0 | 0 | 300 | 290 | 208 | 36 | 142 | 20 | 55 | 0 | 35 | 0 | 0 | 51 | 19 | 8 | 33 | 16 | 120 | 109 | 8 | 19 | 3 | 30 | 0 | 25 | 0 | 130 | 156 | 0 | 77 | 0 | 221 | 0 | 0 | 0 | 295 | 16 | 11 | 0 | 263 | 0 | 0 | 37 | 0 | 149 | 19 | 76 | 200 | 123 | 315 | 37 | 52 | 105 | 5 | 305 | 54 | 110 | 114 | 95 | 90 | 320 | 90 | 54 | 160 | 114 | 0 | 17 | 32 |  | 707 | 0 | 330 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 41 | 0 | 0 | 27 | 0 | 0 | 34 | 0 | 18 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 22 | 0 | 202 | 0 | 413 | 85 | 0 | 94 | 0 | 110 | 0 | 7 | 113 | 370 | 219 | 0 | 0 | 5 |  | 11168 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 205 | 0 | 0 | 119 | 171 | 0 | 0 | 280 | 260 | 0 | 0 | 55 | 328 | 0 | 87 | 0 | 102 | 150 | 36 | 0 | 0 | 0 | 54 | 55 | 55 | 19 | 25 | 28 | 25 | 33 | 42 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 85 | 82 | 0 | 50 | 21 | 4 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 138 | 23 | 54 | 0 | 35 | 0 | 48 | 52 | 21 | 11 | 25 | 21 | 140 | 118 | 8 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 200 | 284 | 164 | 96 | 191 | 98 | 149 | 0 | 100 | 200 | 124 | 316 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 708 | 0 | 320 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 86 | 32 | 0 | 0 | 0 | 0 | 50 | 30 | 93 | 27 | 43 | 8 | 52 | 25 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 195 | 0 | 22 | 99 | 211 | 0 | 414 | 102 | 185 | 94 | 0 | 113 | 0 | 0 | 113 | 530 | 216 | 0 | 45 | 0 |  | 13085 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 120 | 300 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 335 | 0 | 100 | 0 | 102 | 149 | 13 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 21 | 20 | 0 | 0 | 0 | 320 | 310 | 210 | 8 | 142 | 23 | 55 | 0 | 35 | 0 | 50 | 51 | 22 | 11 | 33 | 21 | 164 | 152 | 8 | 22 | 0 | 30 | 0 | 25 | 0 | 163 | 162 | 0 | 80 | 0 | 225 | 0 | 0 | 0 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 138 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 100 | 100 | 383 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 727 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 27 | 40 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 93 | 27 | 43 | 40 | 52 | 25 | 22 | 0 | 11 | 77 | 0 | 0 | 16 | 10 | 0 | 0 | 206 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 184 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 120 | 300 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 326 | 0 | 100 | 0 | 100 | 149 | 10 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 25 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 0 | 50 | 20 | 15 | 0 | 0 | 0 | 300 | 300 | 210 | 8 | 142 | 23 | 55 | 0 | 35 | 0 | 0 | 50 | 22 | 11 | 33 | 20 | 138 | 152 | 8 | 22 | 1.6 | 30 | 0 | 25 | 0 | 163 | 160 | 0 | 80 | 0 | 225 | 0 | 0 | 0 | 341 | 24 | 11 | 100 | 300 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 138 | 400 | 115 | 90 | 105 | 5 | 300 | 54 | 110 | 114 | 100 | 100 | 383 | 100 | 50 | 162 | 116 | 0 | 17 | 30 |  | 727 | 0 | 355 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 43 | 0 | 52 | 0 | 20 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 116 | 241 | 0 | 0 | 300 | 275 | 0 | 0 | 50 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 0 |  | 8 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 10 | 0 | 1 | 21 | 5 | 0 | 0 | 0 | 295 | 270 | 213 | 8 | 142 | 23 | 56 | 0 | 35 | 0 | 0 | 1 | 19 | 11 | 25 | 19 | 94 | 152 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 78 | 0 | 205 | 0 | 0 | 0 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 35 | 0 | 88 | 7 | 60 | 120 | 138 | 328 | 55 | 17 | 105 | 2 | 87 | 17 | 110 | 52 | 99 | 25 | 320 | 54 | 9 | 162 | 114 | 0 | 17 | 6 | 0 | 715 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 11 | 0 | 194 | 0 | 333 | 17 | 0 | 35 | 0 | 71 | 0 | 2 | 35 | 380 | 180 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9339 | 7:00
| Highest Generation |  | 13085 | 19:30
| Day Peak Generation |  | 11168 | 12:00
| Evening Peak Generation |  | 13085 | 19:30
| HVDC Max Flow |  | 708 | 10:00
| HVDC EvPeak Flow |  | 708 | 19:30
| Load factor L.F |  | 87.7%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-16
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-15 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11168 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9348 | MW
Evening Peak Generation : |  | 13085 | MW Hour : | 19:30 | Available Max Generation : |  | 14619 | MW
E.P. Demand (at gen end) : |  | 13085 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 13500 | MW
Maximum Generation : |  | 13085 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1119 | MW
Total Gen. (MKWH) : |  | 275.4 | System Load Factor : | 87.7% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -78 | MW at | 23:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-16
Actual : | 105.5 | Ft.(MSL) , | Rule curve : | 102.45 | Ft.( MSL )
Gas Consumed : | Total = | 1114.5 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 143816748.338
: |  | Coal : | 60246788.54 | Oil : | 721010542.41 | Total : | 925074079.288
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4756.5558 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1623.3547 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1455.5166 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1315.5529 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1188.6416 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 959.2065 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 528.797 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 246.7702 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 739.8238 |  |  | 0 | 0%
Total | 0 |  | 12814.2192 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
7) Raozan #02
8) Fenchuganj 3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barishal132/33 kV T4 transformer was under shut down from 09:14 to 18:51 for C/M.
b) Faridpur S/S-Faridpur P/S 132 kV Ckt was under shut down from 11:26 to 13:47 for C/M.
c) Ghorasal-Joydebpur 132 kV Ckt-1 was under shut down from 11:50 to 13:47 for relay testing at Ghorasal end.
d) Gopalganj(old)- Gallamari 132 kv Ckt-1,2 were under shut down from 09:53 to 17:25 for D/W.
e) Hasnabad-Aurahati 132 kv Ckt was under shut down since 08:38 for D/W.
f) Hasnabad-Keraniganj 230 kv Ckt-2 was under shut down since 12:25 for D/W.
g) Keraniganj 230/132 kV T02 transformer was under shut down since 11:42 for D/W.
h) Ramganj-Chandpur Desh 132 kV Ckt-1 was under shut down from 08:40 to 10:17 due to red hot maint.
i) Rampura-Bashundhara 132 kV Ckt-1 was under shut down from 12:31 to 13:05 for tree trimming.
j) Saidpur132/33 kV T-3 transformer was shut down from 08:35 to 16:03 for A/M.
k) Chattak-Sunamganj 132 kV Ckt tripped at 10:54 showing dist R-phase Z1 at Chattak end and was |  |  |  |  | About 30 MW power interruption occurred under Sunamganj S/S
switched on at 14:00. |  |  |  |  | area from 10:54 to 14:00.
l) Ghorasal-Joydebpur 132 kV Ckt-2 was under shut down from 14:28 to 15:40 for C/M.
m) Siddhirganj 230/132 kV T02 transformer was under shut down from 14:28 to 17:34 for C/M.
n) Cumilla(N) 230/132 kV T02 transformer was charged from 230 kV side.
o) B.Baria-Norsingdi 132 kV Ckt-1 tripped at 00:53 from B.Baria end showing dist.Y-phase Z2 and was |  |  |  |  | About 55 MW power interruption occurred under Norsingdi S/S
switched on at 01:47(16-09-21). |  |  |  |  | area from 00:53 to 01:20.
p) B.Baria-Norsingdi 132 kV Ckt-2 tripped at 00:53 from B.Baria end showing dist.B-phase Z1 and was
switched on at 01:20(16-09-21).
q) Ghorasal #07 CCPP ST was synchronized at 02:49(16-09-21).
r) Ghorasal-Ashuganj 132 kV Ckt-1 tripped at 03:21 from Ashuganj end and was switched on at 04:18(16-9-21).
s) Shahjibazar-Ashuganj 132 kV Ckt-3 tripped at 03:22 from both end showing dist Z2,45.8 km at Shahjibazar
end &dist Z1,3-phase at Ashuganj end and was switched on at 04:16(16-9-21).
t) Ashuganj-Kishoreganj 132 kV Ckt-2 tripped at 03:21 from Ashuganj end and was switched on at 04:17(16-9-21).
u) Ashuganj 132/33 kV T-4 transformer tripped at 03:21 and was switched on at 04:20.
v) Kishoreganj 132/33 kV T1 & T2 transformer were under shut down from 03:12 to 03:48 due to as fire |  |  |  |  | About 10 MW power interruption occurred under Kishoreganj S/S
originated from 33 kV Karimganj PLBS feeder. |  |  |  |  | area from 03:12 to 03:48.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-15 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 205 | 4653900 | ST under maint
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 119 | 2922480
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 171 | 5422000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 7070000 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 260 | 6721687 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1178382
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 36 | 320711 | Fuel shortage
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 398556
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 87 | 1542000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7672803
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1512432
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 648720
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 2360640
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 968908
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 785046
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1196880 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 614500 | Engine problem
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 743300
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 42 | 473280
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 284 | 5141125
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 164 | 867031 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 96 | 669689
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 879169
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3228624
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1485600 | Fuel shortage
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2319360
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3912480
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 2820396
| Dhaka area Total |  |  |  | 5719 | 3276 | 68529699
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2700000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 345517
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 137565
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 757440
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 168 | 3918087 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2550909
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 610513 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 82 | 1352760
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2005440
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 498336
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 4 | 327840
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 33000
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5630400
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1103560
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2611125
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2156160
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 114 | 2747454
| Chattogram area Total |  |  |  | 2382 | 1437 | 29486106
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4980000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7159500 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 6964000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 511488 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 54 | 1320960
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 702545 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 831932 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 124 | 3066095 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 481568
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3353800 | Engine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4521120
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 482112
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 225720
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 140 | 2954880
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 25 | 685800
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 858158
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 506050
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 200 | 1281216
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2269740
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 2294040 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 531720 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2095 | 45982444
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 118 | 2913040 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 413748
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 8 | 155520 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 13100
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 191 | 2356800
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 1603200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 399800
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 572400
| Mymensingh Area Total |  |  |  | 709 | 473 | 8427608
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 715000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3503945
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3726000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 595800 | Machine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1955520
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5156570
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 383064
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7252000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7738000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7734500 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1625 | 39024399
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 708 | 17057454
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 120960 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 4357440
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 320 | 8028288 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 99 | 474240
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 102 | 1422720
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1486 | 31461102
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 639222
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2109489 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 537999 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 11063000
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 216 | 5196327
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 45 | 151200 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 931 | 19697237
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 614832
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 146989 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 398340 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 165604 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 8 | 39244 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 195 | 4909273 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 211 | 5214055 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 414 | 9122218 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 25 | 156623 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 470400
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 262464
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 1091040
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 93 | 681496 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 185 | 502132
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 94 | 2200608 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2672448
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 35340
| Rajshahi Area Total |  |  |  | 2179 | 1572 | 28683106
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 77 | 1937018
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2117126
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 54126
| Rangpur Area Total |  |  |  | 605 | 190 | 4108270
| Total |  |  |  | 21180 | 13085 | 275399971
| Eastern Grid Total |  |  |  | 14221 | 8906 | 191450256
| Western Grid Total |  |  |  | 6959 | 4179 | 83949715
| National Grid Total |  |  |  | 21180 | 13085 | 275399971
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-15
(a) ENTIRE EASTERN GRID : |  | 8557 | MW | (b) ENTIRE WESTERN GRID : |  | 3852 | MW
i) Dhaka area |  | 4636 | MW | i) Khulna area |  | 1444 | MW
ii) Chittagong area |  | 1327 | MW | ii) Rajshahi area |  | 1330 | MW
iii) Comilla area |  | 1207 | MW | iii) Barisal area |  | 358 | MW
iv) Mymensingh area |  | 962 | MW | iv) Rangpur area |  | 720 | MW
v) Sylhet area |  | 425 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12409 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 132 | 15:00 | Kishoreganj | 156 | 19:30 | Jessore | 108 | 21:00
Munsiganj | 96 | 0:00 | Netrokona | 108 | 22:00 | Benapol | 56 | 19:00
Sonargaon | 84 | 18:30 | Jamalpur | 133 | 23:00 | Jhenida | 112 | 19:00
Shyampur | 206 | 0:00 | Sherpur | 114 | 2:00 | Bottail | 132 | 19:00
Bhulta | 218 | 0:00 | Srimongal | 69 | 18:30 | G.K Project | 56 | 21:00
Madanganj | 46 | 13:00 | Shahjibazar | 115 | 20:00 | Faridpur | 142 | 19:00
Shitalakhya | 110 | 15:00 | Fenchuganj | 51 | 1:00 | Rajbari | 54 | 21:00
Rahim steel | 28 | 9:00 | Kulawara | 52 | 18:30 | Madaripur | 97 | 23:00
Matuail | 66 | 10:00 | Sylhet | 158 | 18:00 | Sariatpur | 66 | 21:00
Ghorasal | 86 | 21:00 | Chatak | 34 | 21:00 | Gopalganj | 88 | 19:00
Narsingdi | 191 | 21:00 | Sunamganj | 59 | 21:00 | Bagerhat | 94 | 19:30
Haripur (SBU) | 123 | 19:00 | Biani Bazar | 76 | 19:30 | Mongla | 36 | 11:00
Sreenagar | 42 | 21:00 | Comilla (S) | 140 | 19:30 | Satkhira | 89 | 19:30
Ullon | 53 | 19:30 | Comilla(N) | 135 | 22:00 | Gallamari | 41 | 13:00
Hasnabad | 85 | 22:00 | Chandpur | 78 | 21:00 | Magura | 52 | 20:00
Magbazar | 122 | 13:00 | Feni | 134 | 19:30 | Norail | 44 | 19:00
Maniknagar | 80 | 14:00 | Chowmuhani | 220 | 23:00 | Chuadanga | 96 | 21:00
Bangabhaban | 13 | 10:00 | Ashuganj | 47 | 1:00 | Borguna | 18 | 19:00
Motijheel | 31 | 12:00 | Daudkandi | 149 | 22:00 | Barisal(N) | 43 | 22:00
Narinda | 76 | 13:00 | B.Baria | 169 | 19:00 | Barisal (S) | 106 | 21:00
Kazla | 85 | 18:00 | Ramganj | 86 | 21:00 | Patuakhali | 112 | 20:00
Dhanmondi | 188 | 13:00 | Chaddagram | 47 | 22:00 | Bhandaria | 51 | 22:00
Lalbag | 92 | 18:30 | PHP | 10 | 15:00 | Borhan Uddin | 48 | 21:00
Madartek | 74 | 23:00 | Kochua | 6 | 0:00 | Ishurdi | 67 | 19:00
Dhaka University | 41 | 12:00 | Madunaghat | 62 | 12:00 | Ruppur Paromanobik | 4 | 13:00
Aftabnagar | 17 | 13:00 | Hathazari | 105 | 18:30 | Natore | 126 | 19:30
Fatullah | 64 | 11:00 | Khulshi | 169 | 15:00 | Bogra | 171 | 20:00
Nawabganj | 52 | 22:00 | Halishahar | 100 | 14:00 | Noagaon | 112 | 21:00
Keraniganj | 68 | 19:30 | Baraulia | 147 | 6:00 | Rajshahi | 148 | 20:00
Mirpur | 127 | 18:30 | Sikalbaha | 42 | 19:00 | Rajshahi New | 19 | 21:00
Kalyanpur | 111 | 18:30 | Dohazari | 104 | 19:30 | C.Nawabganj | 60 | 21:00
Gulshan | 130 | 13:00 | Cox'sbazar | 103 | 18:30 | Amnura | 50 | 21:00
Uttara | 86 | 18:30 | Chandraghona | 26 | 1:00 | Pabna | 108 | 19:30
Uttara New | 23 | 11:00 | Kaptai | 4.8 | 18:30 | Shahjadpur | 96 | 20:00
Kamrangirchar | 103 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 113 | 20:00
Savar | 174 | 19:00 | Bakulia | 115 | 15:00 | Niyamatpur | 70 | 20:00
Bhasantec | 144 | 13:00 | Julda | 24 | 1:00 | Joypurhat | 61 | 21:00
Agargaon | 88 | 13:00 | TK chemical | 30 | 19:00 | Sherpur(Bogura) | 60 | 19:30
Satmosjid | 101 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 68 | 19:30
Tongi | 125 | 18:00 | Shahmirpur | 25 | 18:30 | Bhangura | 32 | 20:00
Kabirpur | 271 | 16:00 | Khagrachhari | 22 | 21:00 | Rangpur | 116 | 1:00
Basundhara | 204 | 15:00 | Matarbari | 41 | 19:30 | Lalmonirhat | 40 | 18:30
Manikganj | 74 | 23:00 | Baroiar Hat | 56 | 18:30 | Saidpur | 96 | 20:00
Joydevpur | 190 | 19:00 | Rangamati | 14 | 18:00 | Purbasadipur | 98 | 15:00
New Tongi | 96 | 18:30 | Abul Khair 230 | 10 | 18:30 | Thakurgaon | 71 | 19:00
Kodda | 277 | 21:00 | BSRM | 147 | 21:00 | Palashbari | 118 | 19:30
Dhamrai | 126 | 15:00 | GPH Ispat | 93 | 14:00 | Barapukuria | 50 | 13:00
Rajendrapur | 112 | 18:30 | Agrabad | 87 | 15:00 | Panchagar | 48 | 1:00
Valuka | 112 | 12:00 | Goalpara | 25 | 19:30 | Joldhaka | 58 | 18:30
Tangail | 206 | 18:00 | Central S/S | 87 | 19:00 | Kurigram | 56 | 1:00
Mymensing | 224 | 18:00 | Noapara | 45 | 20:00 | Mithapukur | 27 | 19:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-15 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 1:00 | 399 | 10:00 | Kaliakoir | 391 | 0.20833 | 380 | 0.5
| Bheramara | 405 | 1:00 | 396 | 19:30 | Bhulta | 386 | 0.041667 | 374 | 0.41667
| Ashuganj(N) | 392 | 1:00 | 381 | 12:00 | Gopalganj | 404 | 0.625 | 394 | 0.91667
| Payra | 409 | 1:00 | 403 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 15:00 | Hathazari | 236 | 24:00 | 230 | 5:00
| Ishurdi | 232 | 3:00 | 225 | 23:00 | Megnaghat | 232 | 7:00 | 227 | 23:00
| Ashuganj | 240 | 1:00 | 235 | 11:00 | Fenchuganj | 242 | 1:00 | 236 | 18:00
| Serajganj | 230 | 17:00 | 225 | 18:30 | Siddhirganj | 231 | 1:00 | 224 | 11:00
| Baghabari | 232 | 18:00 | 225 | 23:00 | Maniknagar | 230 | 1:00 | 222 | 10:00
| Barapukuria | 234 | 18:00 | 223 | 24:00 | Agargaon | 229 | 5:00 | 218 | 12:00
| Bogra | 224 | 17:00 | 212 | 24:00 | Barisal | 239 | 17:00 | 231 | 23:00
| Rajshahi | 227 | 17:00 | 219 | 23:00 | Bhola 225 MW | 244 | 19:00 | 237 | 22:00
| Khulna South | 233 | 6:00 | 227 | 23:00 | AKSML | 236 | 17:00 | 230 | 3:00
| Rampura | 229 | 1:00 | 221 | 10:00 | BSRM | 233 | 9:00 | 230 | 4:00
| Haripur | 229 | 1:00 | 222 | 12:00 | Bibiyana | 241 | 1:00 | 235 | 15:00
| Hasnabad | 227 | 1:00 | 220 | 9:00 | Bhulta | 233 | 22:00 | 223 | 11:00
| Shyampur | 227 | 1:00 | 219 | 12:00 | Ashuganj (S) | 237 | 1:00 | 232 | 11:00
| Aminbazar | 230 | 1:00 | 220 | 2:00 | Kaliakoir | 227 | 1:00 | 216 | 12:00
| Tongi | 226 | 1:00 | 215 | 10:00 | GPH | 236 | 17:00 | 231 | 3:00
| Comilla (N) | 232 | 1:00 | 228 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 128 | 10:00 | Madanhat | 136 | 0.041667 | 135 | 0.083333
| Munsiganj | 136 | 21:00 | 128 | 10:00 | Hathazari | 138 | 0.70833 | 135 | 0.75
| Sonargaon | 133 | 3:00 | 127 | 12:00 | Khulshi | 135 | 0.70833 | 132 | 0.16667
| Shyampur | 137 | 22:00 | 129 | 12:00 | Halishahar | 136 | 0.70833 | 132 | 0.25
| Bhulta | 128 | 4:00 | 121 | 12:00 | Baraulia | 138 | 0.70833 | 133 | 0.5
| Madanganj | 134 | 6:00 | 127 | 12:00 | Sikalbaha | 137 | 0.66667 | 132 | 0.041667
| Shitalakhya | 136 | 19:00 | 128 | 10:00 | Dohazari | 132 | 0.70833 | 127 | 0.20833
| Rahim steal | 133 | 1:00 | 128 | 11:00 | Cox'sbazar | 125 | 0.70833 | 109 | 0.5
| Matuail | 133 | 1:00 | 128 | 10:00 | Chandraghona | 137 | 0.66667 | 135 | 0.125
| Ghorasal | 140 | 1:00 | 135 | 15:00 | Kaptai | 135 | 0.041667 | 135 | 0.041667
| Narsinghdi | 132 | 6:00 | 123 | 20:00 | A. Khaer Stl. | 135 | 0.041667 | 133 | 0.29167
| Haripur (SBU) | 133 | 1:00 | 128 | 12:00 | Bakulia | 136 | 0.58333 | 133 | 0.125
| Sreenagar | 130 | 1:00 | 121 | 12:00 | Julda | 136 | 0.041667 | 134 | 0.125
| Ullon | 134 | 1:00 | 126 | 12:00 | TK Chemical | 137 | 0.041667 | 134 | 0.25
| Hasnabad | 137 | 20:00 | 128 | 10:00 | Modern Steel | 136 | 0.58333 | 132 | 0.25
| Magbazar | 134 | 2:00 | 126 | 12:00 | Shahmirpur | 137 | 0.58333 | 133 | 0.29167
| Maniknagar | 134 | 1:00 | 127 | 13:00 | Khagrachhari | 136 | 0.875 | 133 | 0.29167
| Bangabhaban | 134 | 1:00 | 127 | 13:00 | Matarbari | 125 | 0.58333 | 115 | 0.5
| Motijheel | 134 | 1:00 | 127 | 13:00 | Baroiar Hat | 135 | 0.375 | 133 | 0.125
| Narinda | 134 | 1:00 | 127 | 13:00 | Rangamati | 136 | 17:00 | 134 | 2:00
| Kazla | 134 | 1:00 | 127 | 13:00 | Agrabad | 135 | 17:00 | 132 | 2:00
| Dhanmondi | 134 | 1:00 | 127 | 11:00 | Goalpara S/S | 138 | 3:00 | 135 | 0.54167
| Lalbag | 131 | 1:00 | 120 | 12:00 | Khulna Central S/S | 137 | 1:00 | 135 | 0.33333
| Madartek | 134 | 1:00 | 126 | 11:00 | Noapara | 136 | 18:00 | 132 | 0.5
| Dhaka University | 134 | 1:00 | 126 | 12:00 | Jessore | 132 | 6:00 | 128 | 0.95833
| Aftabnagar | 134 | 1:00 | 126 | 11:00 | Benapol | 132 | 0.25 | 126 | 0.54167
| Fatullah | 137 | 19:00 | 129 | 10:00 | Jhenida | 131 | 17:00 | 124 | 0.79167
| Nawabganj | 130 | 1:00 | 121 | 12:00 | Bottail | 133 | 0.20833 | 128 | 0.79167
| Keraniganj | 130 | 1:00 | 121 | 12:00 | G.K Project | 138 | 0.70833 | 134 | 0.95833
| Mirpur | 129 | 3:00 | 124 | 12:00 | Faridpur | 135 | 0.41667 | 130 | 0.54167
| Kalyanpur | 133 | 1:00 | 125 | 13:00 | Rajbari | 134 | 0.75 | 130 | 0.5
| Gulshan | 133 | 1:00 | 126 | 11:00 | Madaripur | 140 | 0.20833 | 133 | 0.875
| Uttara | 132 | 1:00 | 123 | 16:00 | Shariyatpur S/S | 138 | 5:00 | 133 | 0.95833
| Uttara New | 133 | 1:00 | 124 | 12:00 | Gopalganj | 143 | 0.25 | 136 | 0.58333
| Kamrangirchar | 130 | 1:00 | 121 | 12:00 | Bagerhat | 136 | 2:00 | 131 | 0.54167
| Savar | 134 | 1:00 | 126 | 13:00 | Mongla | 135 | 3:00 | 131 | 0.33333
| Bhasantec | 136 | 3:00 | 127 | 12:00 | Satkhira | 136 | 4:00 | 132 | 19:00
| Agargaon | 137 | 1:00 | 128 | 12:00 | Gallamari | 138 | 0.20833 | 135 | 8:00
| Satmosjid | 136 | 1:00 | 129 | 11:00 | Magura | 130 | 9:00 | 123 | 0.875
| Tongi | 136 | 1:00 | 128 | 12:00 | Narail | 129 | 0.375 | 120 | 0.79167
| Kabirpur | 136 | 1:00 | 129 | 12:00 | Chuadanga | 135 | 17:00 | 126 | 0.875
| Basundhara | 135 | 18:30 | 125 | 15:00 | Borguna | 136 | 7:00 | 128 | 0.91667
| Manikganj | 137 | 3:00 | 132 | 16:00 | Barisal(N) | 139 | 5:00 | 132 | 23:00
| Joydevpur | 138 | 2:00 | 134 | 12:00 | Barisal (S) | 137 | 0.33333 | 130 | 0.91667
| New Tongi | 137 | 1:00 | 126 | 10:00 | Patuakhali(S) | 135 | 0.33333 | 127 | 0.91667
| Kodda | 132 | 2:00 | 120 | 12:00 | Bhandaria | 135 | 0.29167 | 125 | 0.91667
| Dhamrai | 134 | 24:00 | 124 | 10:00 | Ishurdi | 135 | 5:00 | 132 | 21:00
| Rajendrapur | 129 | 1:00 | 117 | 11:00 | Ruppur Paromanobik | 136 | 17:00 | 132 | 10:00
| Valuka | 117 | 18:00 | 106 | 11:00 | Natore | 134 | 4:00 | 130 | 19:00
| Tangail | 130 | 17:00 | 123 | 11:00 | Bogra | 135 | 17:00 | 127 | 18:30
| Mymensing | 120 | 18:00 | 111 | 12:00 | Noagaon | 131 | 17:00 | 120 | 20:00
| Kishorganj | 124 | 18:00 | 118 | 21:00 | Rajshahi | 134 | 17:00 | 130 | 13:00
| Netrokona | 118 | 18:00 | 110 | 2:00 | Rajshahi New | 134 | 17:00 | 130 | 21:00
| Jamalpur | 132 | 19:00 | 113 | 10:00 | C.Nawabganj | 133 | 18:00 | 129 | 13:00
| Sherpur | 131 | 19:00 | 109 | 12:00 | Amnura | 134 | 17:00 | 127 | 6:00
| Srimongal | 136 | 7:00 | 130 | 2:00 | Pabna | 133 | 5:00 | 128 | 20:00
| Shahjibazar | 134 | 7:00 | 128 | 21:00 | Shahjadpur | 136 | 4:00 | 134 | 19:30
| Fenchuganj | 135 | 7:00 | 129 | 18:30 | Serajganj | 132 | 3:00 | 125 | 20:00
| Khulawara | 133 | 7:00 | 129 | 18:30 | Niyamatpur | 131 | 17:00 | 115 | 19:30
| Sylhet | 132 | 6:00 | 127 | 18:00 | Joypurhat | 132 | 17:00 | 119 | 20:00
| Chatak | 132 | 6:00 | 126 | 18:30 | Sherpur(Bogura) | 134 | 17:00 | 125 | 20:00
| Sunamganj | 126 | 7:00 |  | 11:00 | Mohastangor | 134 | 17:00 | 124 | 21:00
| Biani Bazar | 130 | 8:00 | 123 | 19:00 | Bangura | 135 | 6:00 | 130 | 18:30
| Comilla(s) | 128 | 0:00 | 123 | 15:00 | Rangpur | 131 | 17:00 | 118 | 18:30
| Comilla(n) | 137 | 22:00 | 134 | 21:00 | Lalmonirhat | 130 | 17:00 | 119 | 1:00
| Chandpur | 140 | 7:00 | 136 | 21:00 | Saidpur | 130 | 18:00 | 114 | 18:30
| Feni | 138 | 11:00 | 132 | 19:00 | Purbasadipur | 130 | 17:00 | 112 | 18:30
| Chowmuhani | 135 | 10:00 | 130 | 19:30 | Thakurgaon | 132 | 17:00 | 114 | 18:30
| Ashuganj | 137 | 7:00 | 133 | 20:00 | Palashbari | 130 | 18:00 | 120 | 19:00
| Daudkandi | 136 | 19:00 | 128 | 11:00 | Barapukuria | 134 | 18:00 | 126 | 18:30
| B.Baria | 131 | 7:00 | 126 | 19:30 | Panchagar | 134 | 17:00 | 116 | 18:30
| Ramganj | 136 | 11:00 | 131 | 21:00 | Joldhaka | 128 | 0.70833 | 112 | 0.77083
| Chaddagram | 136 | 17:00 | 133 | 6:00 | Kurigram | 133 | 0.70833 | 117 | 0.77083
| PHP | 136 | 17:00 | 132 | 21:00 | Mithapukur | 133 | 0.70833 | 122 | 0.77083
| Kochua | 136 | 21:00 | 135 | 19:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-15
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 68 | 8475 | 3823 | 12298 |  |  |  | QF-LDC-11
0:30 | 73 | 8178 | 3650.5 | 11828.5 | Date: | 2021-09-15
1:00 | 78 | 7881 | 3478 | 11359
1:30 | 74 | 7763.5 | 3402 | 11165.5
2:00 | 70 | 7646 | 3326 | 10972
2:30 | 87 | 7539.5 | 3319.5 | 10859 | [5 empty] | Gen. at Eve. Peak | 13085 | 13085 MW (19:30 )
3:00 | 104 | 7433 | 3313 | 10746 | [6 empty] | 19:30
3:30 | 157 | 7312 | 3295.5 | 10607.5 | [5 empty] | Gen. at Day Peak | 11168 | 11168 MW (12:00 )
4:00 | 210 | 7191 | 3278 | 10469 | [6 empty] | 12:00
4:30 | 210 | 7137.5 | 3239 | 10376.5 | [5 empty] | Highest Generation | 13085
5:00 | 210 | 7084 | 3200 | 10284 | [6 empty] | 19:30
5:30 | 238 | 6857 | 3090 | 9947
6:00 | 266 | 6630 | 2980 | 9610
6:30 | 213 | 6545 | 2929.5 | 9474.5
7:00 | 160 | 6460 | 2879 | 9339
7:30 | 178 | 6522.5 | 2878 | 9400.5
8:00 | 196 | 6585 | 2877 | 9462
8:30 | 244 | 6802.5 | 2907.5 | 9710
9:00 | 292 | 7020 | 2938 | 9958
9:30 | 338 | 7173 | 3008.5 | 10181.5
10:00 | 384 | 7326 | 3079 | 10405
10:30 | 371 | 7387.5 | 3155 | 10542.5
11:00 | 358 | 7449 | 3231 | 10680
11:30 | 337 | 7630 | 3294 | 10924
12:00 | 316 | 7811 | 3357 | 11168
12:30 | 278 | 7881 | 3396.5 | 11277.5
13:00 | 240 | 7951 | 3436 | 11387
13:30 | 277 | 7944 | 3450 | 11394
14:00 | 314 | 7937 | 3464 | 11401
14:30 | 326 | 8062 | 3471.5 | 11533.5
15:00 | 338 | 8187 | 3479 | 11666
15:30 | 387 | 8090 | 3479 | 11569
16:00 | 436 | 7993 | 3479 | 11472
16:30 | 435 | 7863 | 3411 | 11274
17:00 | 434 | 7733 | 3343 | 11076
17:30 | 387 | 7847 | 3296.5 | 11143.5
18:00 | 340 | 7961 | 3250 | 11211
18:30 | 189 | 8484.5 | 3639.5 | 12124
19:00 | 38 | 9008 | 4029 | 13037
19:30 | 90 | 8906 | 4179 | 13085
20:00 | 0 | 8938 | 4125 | 13063 |  |  |  | Executive Engineer
20:30 | 12 | 8967.5 | 4101 | 13068.5 |  |  |  | Network Operation Division
21:00 | 24 | 8997 | 4077 | 13074
21:30 | 37 | 8968 | 4030.5 | 12998.5
22:00 | 50 | 8939 | 3984 | 12923 |  |  |  |  | Page 6 of 7
22:30 | 64 | 8853 | 3915 | 12768
23:00 | 78 | 8767 | 3846 | 12613
23:30 | 73 | 8621 | 3834.5 | 12455.5
24:00 | 68 | 8475 | 3823 | 12298
13085 MW (19:30 )
11168 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-15 |  | Energy | 275399971
[11 empty] | 2021-09-15 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 3866 | 708 | 1914 | 4458 | 606 | 166 | 732 | 0 | 114 | 0
0:30 | 3951.5 | 705.5 | 1897 | 3947.5 | 572 | 162 | 605 | 0 | 121 | 0 | Date: | 2021-09-15
1:00 | 4037 | 703 | 1880 | 3437 | 538 | 158 | 478 | 0 | 128 | 0
1:30 | 4048 | 702.5 | 1913.5 | 3353 | 533.5 | 158 | 331 | 0 | 126 | 0 | [7 empty] | Total Energy | 275.4 | Total Energy Gen 275.400 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 275.400 MKWHr
2:00 | 4059 | 702 | 1947 | 3269 | 529 | 158 | 184 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4062 | 702 | 1948.5 | 3157.5 | 524 | 158 | 184 | 0 | 123 | 0 | [7 empty] | Energy Requirement | 275.4
3:00 | 4065 | 702 | 1950 | 3046 | 519 | 158 | 184 | 0 | 122 | 0
3:30 | 4064.5 | 702.5 | 1957.5 | 2923.5 | 503.5 | 159 | 176 | 0 | 121 | 0 | [6 empty] | Shortage
4:00 | 4064 | 703 | 1965 | 2801 | 488 | 160 | 168 | 0 | 120 | 0
4:30 | 4072 | 703 | 1965.5 | 2721 | 478 | 160 | 160 | 0 | 117 | 0
5:00 | 4080 | 703 | 1966 | 2641 | 468 | 160 | 152 | 0 | 114 | 0
5:30 | 4033.5 | 703 | 1957.5 | 2378.5 | 458.5 | 160 | 144 | 0 | 111 | 1
6:00 | 3987 | 703 | 1949 | 2116 | 449 | 160 | 136 | 0 | 108 | 2
6:30 | 3958.5 | 703 | 1948 | 2008 | 439 | 161 | 136 | 0 | 105 | 16 |  |  |  |  | Coal
7:00 | 3930 | 703 | 1947 | 1900 | 429 | 162 | 136 | 0 | 102 | 30
7:30 | 3967 | 703.5 | 1927.5 | 1949 | 409 | 160.5 | 136 | 0 | 103 | 45 |  |  |  | Oil |  |  |  | ,
8:00 | 4004 | 704 | 1908 | 1998 | 389 | 159 | 136 | 0 | 104 | 60
8:30 | 4081.5 | 704 | 1850.5 | 2216.5 | 387.5 | 158.5 | 136 | 0 | 104 | 71.5
9:00 | 4159 | 704 | 1793 | 2435 | 386 | 158 | 136 | 0 | 104 | 83
9:30 | 4183 | 706 | 1819 | 2577 | 393.5 | 161 | 136 | 0 | 106 | 100
10:00 | 4207 | 708 | 1845 | 2719 | 401 | 164 | 136 | 0 | 108 | 117
10:30 | 4131 | 707.5 | 1838.5 | 2923.5 | 411.5 | 164 | 136 | 0 | 115 | 115.5
11:00 | 4055 | 707 | 1832 | 3128 | 422 | 164 | 136 | 0 | 122 | 114
11:30 | 4056 | 707 | 1826.5 | 3251.5 | 436.5 | 165 | 241 | 0 | 121 | 119.5
12:00 | 4057 | 707 | 1821 | 3375 | 451 | 166 | 346 | 0 | 120 | 125
12:30 | 4032 | 707 | 1823 | 3460.5 | 456.5 | 166.5 | 384.5 | 0 | 123 | 124.5
13:00 | 4007 | 707 | 1825 | 3546 | 462 | 167 | 423 | 0 | 126 | 124
13:30 | 4007 | 707 | 1825 | 3546 | 462 | 167 | 423 | 0 | 126 | 124
14:00 | 4007 | 707 | 1825 | 3546 | 462 | 167 | 423 | 0 | 126 | 124
14:30 | 3973 | 707 | 1832 | 3696 | 476 | 168 | 448.5 | 0 | 131 | 95
15:00 | 3939 | 707 | 1839 | 3846 | 490 | 169 | 474 | 0 | 136 | 66
15:30 | 3923 | 707 | 1813 | 3812.5 | 483.5 | 168 | 476.5 | 0 | 132 | 53.5
16:00 | 3907 | 707 | 1787 | 3779 | 477 | 167 | 479 | 0 | 128 | 41
16:30 | 3913 | 707 | 1745.5 | 3626.5 | 473.5 | 167 | 491.5 | 0 | 122 | 28
17:00 | 3919 | 707 | 1704 | 3474 | 470 | 167 | 504 | 0 | 116 | 15
17:30 | 3891 | 707 | 1667 | 3543.5 | 476 | 167 | 562.5 | 0 | 122 | 7.5
18:00 | 3863 | 707 | 1630 | 3613 | 482 | 167 | 621 | 0 | 128 | 0
18:30 | 3927 | 707 | 1704.5 | 4283.5 | 528.5 | 167.5 | 678 | 0 | 128 | 0
19:00 | 3991 | 707 | 1779 | 4954 | 575 | 168 | 735 | 0 | 128 | 0
19:30 | 4053 | 708 | 1803 | 4860 | 607 | 168 | 746 | 0 | 140 | 0
20:00 | 4060 | 707 | 1837 | 4793 | 607 | 168 | 753 | 0 | 138 | 0
20:30 | 4053.5 | 707.5 | 1847.5 | 4789.5 | 616 | 168 | 748.5 | 0 | 138 | 0
21:00 | 4047 | 708 | 1858 | 4786 | 625 | 168 | 744 | 0 | 138 | 0
21:30 | 4073.5 | 707.5 | 1846 | 4697 | 620 | 167 | 749.5 | 0 | 138 | 0
22:00 | 4100 | 707 | 1834 | 4608 | 615 | 166 | 755 | 0 | 138 | 0
22:30 | 4002 | 707 | 1857.5 | 4533 | 615.5 | 166 | 753 | 0 | 134 | 0
23:00 | 3904 | 707 | 1881 | 4458 | 616 | 166 | 751 | 0 | 130 | 0
23:30 | 3885 | 707.5 | 1897.5 | 4458 | 611 | 166 | 741.5 | 0 | 122 | 0 | Max Temp. in Dhaka |  | 35.3° C
24:00 | 3866 | 708 | 1914 | 4458 | 606 | 166 | 732 | 0 | 114 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 275.400 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 275.400 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-15
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 83 | 83 | 83 | 85 | 85 | 85 | 87 | 84 | 83 | 89 | 89 | 91 | 92 | 94 | 94 | 92 | 92 | 92 |  | 93 | 93 | 93 | 93 | 91 | 91 | 91 | 2106087
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1812000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2700000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [9 empty] | 2 | 12 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 345517
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 10 | 14 | 18 | 19 | 19 | 19 | 19 | 7 | 9 | 1 | [9 empty] | 137565
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | [15 empty] | 17 | 85 |  | 85 | 85 | 85 | 85 | 85 | 85 | 85 | 610513
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2550909
| Daudkandi 200 MW PP (B.Trac) | [12 empty] | 20 | 20 | 74 | 70 | 10 | 10 |  | 200 | 200 | 200 | 200 | 200 | 150 | 115 | 1281216
14 | Titas 50 MW Peaking PP | [13 empty] | 17 | 49 | 49 | 48 | 48 |  | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 481568
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 90 | 92 | 91 | 92 | 37 | 37 | 37 | 38 | 35 | 37 |  | 61 | 87 | 87 | 90 | 89 | 90 | 91 | 1542000
17 | Siddhirganj 335 MW CCPP | 335 | 335 | 335 | 334 | 335 | 280 | 250 | 250 | 334 | 330 | 325 | 324 | 322 | 321 | 319 | 320 | 316 | 280 |  | 325 | 328 | 330 | 330 | 330 | 330 | 330 | 7672803
18 | Kodda 300 MW PP Unit-2 (Summit) | 300 | 300 | 250 | 95 | 30 | 15 | 15 | 15 | 30 | 117 | 167 | 263 | 275 | 275 | 275 | 282 | 275 | 275 |  | 277 | 284 | 283 | 284 | 284 | 284 | 284 | 5141125
19 | Ashuganj 195MW PP (APSCL-United) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 702545
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 | 205 |  | 205 | 205 | 205 | 205 | 205 | 0 | 0 | 4653900
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 511488
33 | Ashuganj 225 MW CCPP | 216 | 213 | 213 | 213 | 213 | 213 | 214 | 212 | 214 | 213 | 180 | 208 | 202 | 204 | 182 | 174 | 181 | 204 |  | 210 | 210 | 207 | 211 | 213 | 210 | 214 | 4980000
34 | Ashuganj 450 MW CCPP(South) | 265 | 265 | 265 | 270 | 265 | 265 | 280 | 280 | 300 | 350 | 280 | 290 | 305 | 280 | 300 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 290 | 310 | 290 | 6964000
| Ashuganj 450 MW CCPP(North) | 265 | 265 | 265 | 270 | 265 | 265 | 280 | 300 | 290 | 320 | 290 | 300 | 320 | 285 | 300 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 320 | 320 | 300 | 7159500
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 56 | 55 | 56 | 55 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 55 | 56 | 56 | 55 | 55 | 1320960
36 | Chandpur 150 MW CCPP | 138 | 141 | 140 | 140 | 140 | 140 | 140 | 141 | 141 | 141 | 140 | 142 | 140 | 140 | 140 | 142 | 139 | 142 |  | 142 | 138 | 141 | 142 | 139 | 141 | 141 | 3353800
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 115 | 113 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 119 | 119 | 119 | 119 | 117 | 116 | 2922480
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 300 | 300 | 300 | 300 | 300 | 7070000
41 | Haripur 360MW CCPP(HPL) | 296 | 316 | 324 | 324 | 330 | 327 | 323 | 298 | 232 | 191 | 177 | 172 | 172 | 171 | 171 | 171 | 173 | 171 |  | 171 | 171 | 171 | 162 | 162 | 172 | 200 | 5422000
42 | RPCL 210MW CCPP | 142 | 142 | 142 | 142 | 150 | 157 | 154 | 145 | 130 | 118 | 117 | 109 | 95 | 99 | 96 | 99 | 110 | 130 |  | 117 | 118 | 117 | 116 | 118 | 117 | 139 | 2913040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 18 | 27 | 43 | 53 | 43 | 54 | 54 | 51 | 27 | 13 | 8 | 0 | [8 empty] | 399800
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 715000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 162 | 162 | 161 | 160 | 160 | 162 | 161 | 160 | 159 | 157 | 158 | 156 | 156 | 156 | 155 | 157 | 159 | 155 |  | 158 | 158 | 158 | 160 | 161 | 160 | 161 | 3726000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 81 | 78 | 78 | 78 | 77 | 77 | 77 | 74 | 74 | 77 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1955520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 180 | 180 | 221 | 220 | 220 | 221 | 221 | 222 | 221 | 221 | 221 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5156570
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 595800
56 | Shahjahanulla 25 MW PP | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 8 | 8 | 8 | 16 | 16 | 24 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 383064
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 290 | 295 | 300 | 300 | 290 | 295 | 310 | 300 | 305 | 300 | 295 | 310 | 300 | 310 | 290 | 285 | 300 |  | 290 | 280 | 275 | 300 | 275 | 300 | 300 | 7252000
| Bibiyana South 400 MW | 330 | 330 | 330 | 330 | 330 | 330 | 330 | 331 | 330 | 330 | 330 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7734500
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 |  |  | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 785046
59 | Tangail Palli Power Gen 22 MW | 23 | 23 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 572400
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 498336
61 | Narshingdi 22 MW PP (Doreen) | 22 | 22 | 22 | 21 | 21 | 21 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 17 |  |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 398556
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 17 | 17 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 413748
63 | Impoprt (Tripura) | 128 | 124 | 122 | 120 | 114 | 108 | 102 | 104 | 104 | 108 | 122 | 120 | 126 | 130 | 136 | 128 | 116 | 128 |  | 128 | 140 | 138 | 138 | 138 | 130 | 114 | 2954880
64 | Malancha, Ctg. EPZ (United) | 31 | 31 | 31 | 32 | 40 | 30 | 30 | 2 | 2 | 2 | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 3 |  | 6 | 4 | 12 | 15 | 25 | 28 | 28 | 327840
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 20 | 20 | 20 | 20 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 482112
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 2 | 5 | 8 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 225720
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 685800
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 17 | 16 | 16 | 16 | 21 | 21 | 21 | 20 | 20 | 18 |  | 18 | 21 | 21 | 21 | 21 | 21 | 21 | 506050
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 29 | 29 | 29 | 22 | 29 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 24 | 28 | 28 | 28 | 28 | 28 |  | 20 | 28 | 28 | 28 | 28 | 29 | 29 | 596880
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 614500
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 16 | 16 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 743300
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 107 | 107 | 108 | 108 | 108 | 52 | 17 | 17 | 51 | 52 | 105 | 114 | 114 | 114 | 114 | 114 | 90 | 52 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2269740
| Chowmuhani 113 MW | 97 | 97 | 98 | 94 | 94 | 98 | 99 | 91 | 91 | 96 | 97 | 95 | 96 | 96 | 94 | 94 | 88 | 94 |  | 94 | 94 | 95 | 94 | 95 | 95 | 97 | 2294040
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 160 | 144 | 155 | 162 | 162 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3912480
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 25 | [7 empty] | 16 | 16 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 40 | 42 | 42 | 32 | 33 | 42 | 25 | 473280
79 | Kodda 150MW PP | 150 | 64 | 64 | 48 | 32 | 16 | 16 | 16 | 16 | 16 | 16 | 150 | 150 | 150 | 150 | 150 | 150 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 2360640
80 | Jamalpur 95 MW PP(Powerpac) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  |  |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 0 | 155520
81 | Jangalia 52 MW PP (Lakdanavi) | 51 | 51 | 25 | [5 empty] | 4 | 8 | 20 | 51 | 49 | 51 | 51 | 51 | 51 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 858158
| Gazipur 100 MW PP | 52 | 35 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 83 | 90 |  | 90 | 90 | 90 | 90 | 90 | 90 | 52 | 1485600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 3 | 4 | 4 | 5 | 5 | 5 | 4 | 3 | 1 | 0 | [9 empty] | 33000
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 17 |  |  | 12 | 24 | 47 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1103560
| Karnaphuli Power Ltd. | 94 | 105 | 105 | 105 | 110 | 110 | 110 | 110 | 110 | 98 | 98 | 110 | 98 | 106 | 110 | 110 | 102 | 104 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2611125
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 13 | [9 empty] | 4 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |  | 23 | 36 | 38 | 38 | 37 | 36 | 37 | 320711
86 | Meghnaghat CCPP ( Summit) | 250 | 280 | 270 | 270 | 270 | 270 | 285 | 285 | 280 | 290 | 275 | 285 | 290 | 270 | 285 | 260 | 235 | 300 |  | 315 | 260 | 315 | 320 | 275 | 305 | 265 | 6721687
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 92 | 89 | 92 | 90 | 89 | 90 | 88 | 90 | 92 | 86 | 87 | 89 | 89 | 101 |  | 104 | 104 | 104 | 104 | 104 | 96 | 104 | 2319360
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | [6 empty] | 10 | 26 | 82 | 82 | 82 | 92 | 92 | 82 | 50 | 32 |  | 82 | 82 | 82 | 100 | 100 | 100 | 100 | 1352760
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 831932
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 40 | [6 empty] | 7 | 16 | 24 | 40 | 85 | 102 | 102 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1512432
95 | Patenga 50MW PP (Baraka) | 50 | 12 | [6 empty] | 7 | 19 | 19 | 21 | 44 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 757440
96 | Chattogram 108 MW PP (ECPV) | [19 empty] | 0 | 0 |  |  |  |  | 0 | 0
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 50 | 55 | 55 | 40 | 15 | 15 | 15 | 25 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 42 | 47 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1178382
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 35 | 17 |  |  | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 35 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 968908
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 163 | 163 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3503945
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 2 | 2 | 1 | 3 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 13100
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 648720
104 | Keranigonj 300 MW PP (APR) | [14 empty] | 76 | 76 |  | 56 |  | 256 | 164 | 111 | 110 | 54 | 55 | 52 | 867031
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 40 | 40 |  | 50 |  | 97 | 96 | 97 | 99 | 100 | 100 | 96 | 669689
106 | Mymensingh 200 MW PP (United) | 115 | 116 | 116 | 115 | 115 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 37 | 115 | 191 |  | 191 | 191 | 192 | 191 | 196 | 197 | 162 | 2356800
112 | Aurahati 100MW PP (Aggreko) | [12 empty] | 50 | 50 | 99 | 99 |  |  |  | 98 | 98 | 97 | 99 | 98 | 97 | 50 | 879169
114 | Kodda 149 MW PP Unit-1 (Summit) | 133 | 129 | 115 | 90 | 86 | 86 | 85 | 98 | 147 | 149 | 149 | 149 | 149 | 149 | 149 | 143 | 132 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3228624
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 90 | 50 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 100 | 75 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2005440
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 170 | 155 | 155 | 155 | 155 | 186 | 200 | 200 | 200 | 200 | 200 | 200 | 180 |  | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 4521120
117 | Ashuganj 150MW PP (Midland) | 142 | 137 | 138 | 132 | 128 | 133 | 130 | 123 | 115 | 115 | 123 | 123 | 122 | 128 | 128 | 130 | 123 | 120 |  | 125 | 124 | 125 | 125 | 128 | 133 | 127 | 3066095
118 | Bibiyana-III 400 MW CCPP | 328 | 328 | 329 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 315 | 315 | 316 | 316 | 316 | 316 | 315 |  | 316 | 316 | 316 | 316 | 316 | 317 | 317 | 7738000
| Jamalpur 115 MW PP (United) | 76 | 77 | 77 | 77 | 77 | 37 | 37 | 37 | 38 | 38 | 38 | 37 | 46 | 37 | 37 | 37 | 41 | 79 |  | 115 | 115 | 115 | 115 | 115 | 115 | 89 | 1603200
| Anwara 300 MW PP (United) | 106 | 106 | 106 | 106 | 106 | 106 | 106 | 157 | 214 | 305 | 305 | 305 | 305 | 304 | 304 | 304 | 304 | 267 |  | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 5630400
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 50 | 20 | 25 | 90 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2156160
| Anlima Energy Ltd. | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2747454
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 33 | 17 | 20 | 35 | 35 | 35 | 17 | 531720
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 5 | 15 | 11 | 32 | 35 | 32 | 32 | 29 | 20 | 10 | 3 | 0 | [8 empty] | 2820396
120 | Eastern Zone Total | 7881 | 7646 | 7433 | 7191 | 7084 | 6630 | 6460 | 6585 | 7020 | 7326 | 7449 | 7811 | 7951 | 7937 | 8187 | 7993 | 7733 | 7961 |  | 9008 | 8906 | 8938 | 8997 | 8939 | 8767 | 8475 | 191450256
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [16 empty] | 4 | 4 |  | 27 | 27 | 23 | 21 | 21 | 21 | 21 | 120960
| Khulna 225 MW CCPP | 175 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 155 | 223 | 225 | 225 | 230 | 230 | 226 |  | 230 | 230 | 230 | 230 | 230 | 230 | 230 | 4357440
129 | Rupsha 105 MW PP (Orion rupsha) | 102 | 102 | 102 | 102 | 102 | 17 |  |  | 11 | 17 | 75 | 85 | 85 | 87 | 102 | 102 | 70 | 55 |  | 100 | 102 | 102 | 102 | 102 | 102 | 102 | 1422720
130
131
132 | United Payra Power Ltd. | [19 empty] | 30 | 45 | 35 | 17 | 17 | 17 | 17 | 151200
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 223 | 223 | 223 | 222 | 222 | 223 | 223 | 221 | 220 | 220 | 219 | 216 | 220 | 218 | 219 | 182 | 130 |  | 222 | 216 | 224 | 224 | 213 | 223 | 223 | 5196327
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 537999
| Bhola 225 MW CCPP | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 84 | 86 | 85 | 87 |  | 87 | 86 | 87 | 87 | 86 | 87 | 86 | 2109489
140 | Bhola 33 MW PP (Venture) | 33 | 30 | 30 | 27 | 27 | 21 | 21 | 20 | 20 | 20 | 21 | 22 | 22 | 24 | 25 | 24 | 22 | 24 |  | 32 | 32 | 34 | 34 | 34 | 34 | 34 | 639222
141 | Noapara 100 MW PP (Bangla Trac) | [14 empty] | 12 | 20 |  |  |  | 76 | 99 | 98 | 99 | 70 | 20 | 20 | 474240
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 703 | 702 | 702 | 703 | 703 | 703 | 703 | 704 | 704 | 708 | 707 | 707 | 707 | 708 | 707 | 707 | 707 | 707 |  | 707 | 708 | 707 | 708 | 707 | 707 | 708 | 17057454
147 | Bheramara 410 MW CCPP | 320 | 335 | 340 | 340 | 350 | 350 | 330 | 350 | 350 | 345 | 340 | 330 | 330 | 325 | 325 | 320 | 315 | 320 |  | 320 | 320 | 325 | 315 | 315 | 310 | 310 | 8028288
148 | Payra 1320 MW | 460 | 450 | 440 | 410 | 390 | 370 | 350 | 310 | 310 | 320 | 340 | 370 | 380 | 400 | 410 | 400 | 390 | 400 |  | 500 | 530 | 530 | 550 | 540 | 540 | 530 | 11063000
149
150 | Barapukuria TPP Unit-1 | 78 | 79 | 79 | 78 | 78 | 79 | 79 | 79 | 76 | 81 | 82 | 81 | 82 | 82 | 80 | 77 | 80 | 82 |  | 75 | 77 | 77 | 75 | 75 | 76 | 76 | 1937018
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [11 empty] | 41 | 50 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 614832
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 2 | 4 | 3 | 4 | 5 | 5 | 4 | 2 | 1 | 1 | 0 | [8 empty] | 35340
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 188 | 194 | 197 | 197 | 197 | 196 | 198 | 206 | 216 | 213 | 210 | 204 | 200 | 197 | 193 | 192 | 192 | 174 |  | 180 | 195 | 194 | 189 | 189 | 184 | 183 | 4909273
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 216 | 216 | 216 | 216 | 216 | 217 | 216 | 212 | 206 | 202 | 201 | 202 | 195 | 196 | 190 | 194 | 201 | 160 |  | 204 | 211 | 212 | 205 | 208 | 208 | 210 | 5214055
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 310 | 350 | 340 | 352 | 340 | 352 | 348 | 348 | 315 | 408 | 412 | 413 | 406 | 410 | 405 | 406 | 362 | 349 |  | 372 | 414 | 414 | 415 | 417 | 417 | 422 | 9122218
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 8 |  | 18 | 30 | 25 | 18 | 35 | 31 | 32 | 146989
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 18 | 18 | 18 | 19 | 19 | 19 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 470400
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 262464
165 | Amnura 50 MW PP(Sinha) | 27 | [9 empty] | 12 | 27 | 27 | 27 | 27 | 27 | 27 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 398340
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 34 | 43 | 43 | 43 | 43 |  | 0 | 165604
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 8 | 8 | 24 | 24 | 24 | 24 | 0 | 39244
168 | Santahar 50 MW Peaking PP | 25 | [16 empty] | 12 |  | 26 | 25 | 25 | 25 | 19 | 19 | 23 | 156623
169 | Natore 52 MW PP (Rajlanka) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 34 | 43 | 43 | 46 | 46 | 46 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 1091040
170 | Chapainawabganj 100 MW Peaking PP | 94 | [16 empty] | 30 |  | 93 | 93 | 93 | 93 | 93 | 93 | 93 | 681496
171 | Baghabari 200 MW PP (Paramount) | [19 empty] | 185 | 185 | 120 | 100 | 43 |  | 0 | 502132
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 49 | 84 | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 94 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 2200608
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 113 | 70 | 80 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2672448
173 | Rangpur 20 MW GTPP | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 |  | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 99 | 44 |  |  |  | 34 | 39 | 92 | 110 | 113 | 113 | 113 | 113 | 113 | 84 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2117126
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 3 | 5 | 5 | 7 | 7 | 7 | 7 | 6 | 6 | 2 | 0 | [8 empty] | 54126
178
178