## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-17 | Friday
|  |  | Date (day): | 2021-09-17 |  | Friday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13954.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14721 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-16 | 2021-09-17 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 310 | 310 | 310 |  | 55
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 116 | 115 | 120 | 120 |  | 292 | GBC problem
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 198 | 222 | 300 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 300 | 300 | 300 | 300 | 150 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 295 | 280 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 50 | 50 |  | 50 | Fuel shortage
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 20 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 62 | 59 | 100 | 100 | 110 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 325 | 328 | 326 | 335
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 58 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 32 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 35 | 17 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 54 | 53 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 25 | 25 |  | 8 | Engine problem
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 25 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 25 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 270 | 295 | 300 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 128 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 50 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 98 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 132 | 140 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 34 | 90 | 90 | 90 |  | 15 | Engine problem
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 89 | 104 | 100 | 104
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 141 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 34 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2670 | 3364 | 3482 | 3781 | 777 | 1125
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 80 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 19 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 164 | 167 | 168 | 168 | 62 |  | Low water level & Unit-3 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 81 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 45 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100 |  | 0
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 15 | 30 | 40
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 140 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 17 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 97 | 114 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1034 | 1465 | 1418 | 1489 | 250 | 670
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 197 | 206 | 210 | 210
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 360 | 270 | 300 | 320 | 40 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 325 | 270 | 300 | 310 | 50 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 56 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 73 | 26 | 26 | 26 | 169 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 123 | 140 | 138 | 140 |  | 10 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 138 | 142 | 142 |  | 21 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 200 | 200 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 22 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 114 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 25 | 52 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 21 | 21 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 150 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 114 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 91 | 94 | 94 | 94
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1995 | 2040 | 2089 | 2247 | 657 | 98
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 131 | 131 | 160 | 160 | 42 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 19 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 105 | 191 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 48 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 17 | 22 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 436 | 478 | 553.6 | 527 | 42 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 30 | 30 | 30 | 30 |  | 40 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 157 | 158 | 161 | 162 | 168 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 25 | 25 | 25 | 25 |  | 26 | Engine problem
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 77 | 78 | 80 | 80
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 225 | 225
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 18 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 16 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 310 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 328 | 328 | 400 | 400
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 383 | 383
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1654 | 1637 | 1843 | 1844 | 262 | 256
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 710 | 709 | 726 | 726
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 27 | 0 | 27 |  | 27 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 145 | 230 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 330 | 330 | 355 | 400 | 10 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 100 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 102 | 102 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1287 | 1498 | 1561 | 1723 | 10 | 96
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 32 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 87 | 87 | 87 | 87 |  | 107 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 13 | 22 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 360 | 580 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 220 | 221 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 701 | 959 | 1244 | 1244 | 73 | 107
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 43 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 31 | 30 | 31 |  | 40 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 | 23 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 43 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 0 | 0 | 40 |  | 10 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 183 | 202 | 206 | 206 | 14 |  | Gas shortage
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 206 | 210 | 200 | 220 | 0 |  | Gas shortage
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 415 | 397 | 400 | 400
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 31 | 0 | 25 |  | 25 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 17 | 21 | 22 | 22 |  | 0 | Engine problem
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 43 | 52 | 52 | 52 |  | 0
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1085 | 1388 | 1563 | 1647 | 417 | 92
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 75 | 78 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 | 274 |  | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 16 |  | 4 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 1 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 189 | 191 | 201 | 219 | 274 | 99
|  | Total |  |  |  |  | 22031 | 21180 | 11051 | 13020 | 13954.6 | 14721 | 2762 | 2630
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10565.5029 | 12448 | 13341.5408 | 14074.271
| A. |  | 2021-09-16 | (Yesterday) |  |  |  |  | Thursday
| 1 | Highest Generation : |  |  | 13020 | MW at | 19:30 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:30 | hrs.
| 2 | Minimum Generation : |  |  | 9348 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13020 | MW
| 3 | Day peak Generation : |  |  | 11051 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12448 | MW
| 4 | Evening peak Generation : |  |  | 13020 | MW at | 19:30 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 273.779 | MKWHr | By Solar | 0.6516 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 144.6915 | MKWHr |  | By Oil: | 90.7822 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.6264 | MKWHr |  | By Hydro: | 4.0169 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2762 | MW | Dhaka | 4565 | 4565 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2630 | MW | Chittagong | 1258 | 1258 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5392 | MW | Khulna | 1534 | 1534 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1127.2 | MMCFD |  |  | Rajshahi | 1296 | 1296 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 146438795.382 | ii) Oil : | Taka | 683078043.46 | Comilla | 1166 | 1166 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 62766210.27 | Total | Taka | 892283049.112 | Mymensingh | 985 | 985 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.549 | MKWHr. | Sylhet | 542 | 542 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -106 | MW (E to W) at | 19:30 | hrs | Barisal | 365 | 365 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -120 | MW at | 18:30 | hrs | Rangpur | 737 | 737 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 33.2° C |  |  | Total | 12448 | 12448 |  | 0
| B. |  | 2021-09-17 | (Today) |  |  |  | Friday |  |  | Probable max. temperature in Dhaka |  |  | 32.4° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 12900 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14721 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 9300 | MW
| 4 | Reserve(Generation end) |  |  |  | 1821 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 271.2557 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 8814 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.1956 | MKWHr. | ii) HVDC Flow at Peak Time |  | 709 | MW at | 19:30 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8147 | MKWHr. | iii) Maximum HVDC Flow : |  | 715 | MW at | 5:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 105.5 |  | (b) Today: | 105.56 |  | (c) Rule Curve: |  | 102.68
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-16
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 30 | 0 | 0 | 116 | 260 |  | 0 | 300 | 260 | 0 | 0 | 55 | 331 | 0 | 90 | 0 | 102 | 150 | 37 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 30 | 25 | 33 | 25 | 0 | 90 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 92 | 0 | 50 | 21 | 28 | 0 | 0 | 0 | 300 | 290 | 213 | 8 | 139 | 23 | 50 | 0 | 35 | 0 | 48 | 52 | 19 | 11 | 25 | 21 | 124 | 157 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 284 | 0 | 0 | 162 | 0 | 149 | 0 | 100 | 200 | 132 | 318 | 89 | 52 | 105 | 0 | 304 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 714 | 0 | 310 | 0 | 0 | 230 | 0 | 0 | 16 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 31 | 92 | 27 | 0 | 0 | 52 | 19 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 22 | 0 | 212 | 0 | 360 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 510 | 223 | 0 | 0 | 0 |  | 8148 | 3697 | 11845 | 3941 | 714 | 1864 | 3738 | 585 | 165 | 714 | 124 | 0 | 0 | 105.5
2:00 | 0 | 0 | 0 | 0 | 55 | 0 | 0 | 117 | 270 |  | 0 | 300 | 270 | 0 | 0 | 55 | 270 | 0 | 90 | 0 | 48 | 64 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 19 | 25 | 30 | 25 | 33 | 25 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 50 | 21 | 28 | 0 | 0 | 0 | 300 | 290 | 214 | 8 | 141 | 23 | 11 | 0 | 35 | 0 | 0 | 52 | 19 | 11 | 25 | 21 | 124 | 154 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 160 | 0 | 78 | 0 | 205 | 0 | 0 | 0 | 270 | 24 | 11 | 0 | 284 | 0 | 0 | 162 | 0 | 149 | 0 | 100 | 200 | 137 | 318 | 89 | 52 | 105 | 0 | 304 | 54 | 110 | 114 | 97 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 714 | 0 | 320 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 213 | 0 | 370 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 500 | 223 | 0 | 0 | 0 |  | 7730 | 3417 | 11147 | 3910 | 714 | 1813 | 3611 | 576 | 165 | 234 | 124 | 0 | 0 | 105.5
3:00 | 0 | 0 | 0 | 0 | 90 | 0 | 0 | 116 | 292 |  | 0 | 300 | 270 | 0 | 0 | 55 | 270 | 0 | 90 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 30 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 0 | 21 | 37 | 0 | 0 | 0 | 300 | 290 | 214 | 8 | 143 | 23 | 51 | 0 | 35 | 0 | 0 | 50 | 19 | 11 | 25 | 21 | 120 | 160 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 78 | 0 | 206 | 0 | 0 | 0 | 300 | 24 | 11 | 0 | 284 | 0 | 0 | 161 | 0 | 114 | 0 | 100 | 200 | 137 | 327 | 89 | 52 | 105 | 0 | 304 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 714 | 0 | 325 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 211 | 0 | 365 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 490 | 223 | 0 | 0 | 0 |  | 7715 | 3355 | 11070 | 3968 | 714 | 1908 | 3506 | 567 | 167 | 120 | 120 | 0 | 0 | 105.5
4:00 | 0 | 0 | 0 | 0 | 110 | 0 | 0 | 116 | 295 |  | 0 | 300 | 265 | 0 | 0 | 45 | 333 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 30 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 300 | 290 | 214 | 8 | 142 | 0 | 17 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 114 | 165 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 5 | 0 | 206 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 245 | 0 | 0 | 100 | 0 | 96 | 0 | 100 | 200 | 137 | 328 | 55 | 52 | 105 | 0 | 304 | 54 | 105 | 114 | 93 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 714 | 0 | 330 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 12 | 0 | 215 | 0 | 320 | 102 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 470 | 223 | 0 | 0 | 0 |  | 7312 | 3298 | 10610 | 4044 | 714 | 1749 | 3157 | 545 | 167 | 120 | 114 | 0 | 0 | 105.5
5:00 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 116 | 298 |  | 0 | 300 | 275 | 0 | 0 | 45 | 333 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 300 | 290 | 180 | 8 | 140 | 23 | 30 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 108 | 163 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 162 | 0 | 69 | 0 | 205 | 0 | 0 | 0 | 295 | 24 | 11 | 0 | 195 | 0 | 0 | 60 | 0 | 85 | 0 | 100 | 200 | 137 | 328 | 55 | 17 | 105 | 0 | 304 | 17 | 105 | 88 | 92 | 100 | 320 | 92 | 0 | 162 | 114 | 0 | 17 | 0 |  | 715 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 12 | 0 | 215 | 0 | 310 | 70 | 0 | 94 | 0 | 113 | 0 | 0 | 113 | 430 | 224 | 0 | 0 | 0 |  | 7207 | 3229 | 10436 | 4091 | 715 | 1825 | 2905 | 505 | 167 | 120 | 108 | 0 | 0 | 105.5
6:00 | 0 | 0 | 0 | 0 | 200 | 0 | 0 | 116 | 286 |  | 0 | 300 | 275 | 0 | 0 | 45 | 335 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 25 | 33 | 8 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 38 | 0 | 0 | 0 | 270 | 280 | 214 | 8 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 102 | 163 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 78 | 0 | 183 | 0 | 0 | 0 | 290 | 24 | 8 | 0 | 45 | 0 | 0 | 35 | 0 | 85 | 1 | 100 | 155 | 138 | 328 | 55 | 17 | 105 | 0 | 124 | 17 | 110 | 52 | 92 | 60 | 321 | 89 | 0 | 162 | 114 | 0 | 17 | 0 |  | 715 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 12 | 0 | 215 | 0 | 320 | 17 | 0 | 35 | 0 | 106 | 0 | 0 | 35 | 400 | 190 | 0 | 0 | 0 |  | 6688 | 2981 | 9669 | 4054 | 715 | 1817 | 2218 | 475 | 167 | 120 | 102 | 1 | 0 | 105.5
7:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 116 | 266 |  | 0 | 300 | 290 | 0 | 0 | 45 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 25 | 33 | 8 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 0 | 0 | 0 | 21 | 35 | 0 | 0 | 0 | 270 | 265 | 214 | 8 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 11 | 25 | 21 | 96 | 161 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 162 | 0 | 78 | 0 | 205 | 0 | 0 | 0 | 295 | 24 | 8 | 0 | 45 | 0 | 0 | 35 | 0 | 85 | 3 | 60 | 120 | 137 | 327 | 55 | 0 | 105 | 1 | 87 | 17 | 110 | 52 | 99 | 20 | 320 | 58 | 4 | 162 | 114 | 0 | 17 | 3 |  | 715 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 11 | 0 | 215 | 0 | 344 | 17 | 0 | 35 | 0 | 70 | 0 | 1 | 35 | 400 | 180 | 0 | 0 | 0 |  | 6513 | 2914 | 9427 | 4075 | 715 | 1808 | 1959 | 475 | 167 | 120 | 96 | 12 | 0 | 105.5
8:00 | 0 | 0 | 0 | 0 | 250 | 0 | 0 | 116 | 241 |  | 0 | 300 | 275 | 0 | 0 | 50 | 300 | 0 | 37 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 0 | 33 | 8 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 1 | 21 | 5 | 0 | 0 | 0 | 295 | 270 | 213 | 8 | 142 | 23 | 56 | 0 | 35 | 0 | 0 | 1 | 19 | 11 | 25 | 19 | 94 | 152 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 130 | 161 | 0 | 78 | 0 | 205 | 0 | 0 | 0 | 280 | 24 | 8 | 0 | 45 | 0 | 0 | 35 | 0 | 88 | 7 | 60 | 120 | 138 | 328 | 55 | 17 | 105 | 2 | 87 | 17 | 110 | 52 | 99 | 25 | 320 | 54 | 9 | 162 | 114 | 0 | 17 | 6 |  | 715 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 22 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 11 | 0 | 194 | 0 | 333 | 17 | 0 | 35 | 0 | 71 | 0 | 2 | 35 | 380 | 180 | 0 | 0 | 0 |  | 6473 | 2875 | 9348 | 4059 | 715 | 1725 | 1986 | 456 | 167 | 120 | 94 | 26 | 0 | 105.51
9:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 116 | 232 |  | 0 | 300 | 270 | 0 | 0 | 55 | 300 | 0 | 36 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 25 | 33 | 25 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 15 | 21 | 2 | 0 | 0 | 0 | 290 | 275 | 178 | 8 | 141 | 20 | 54 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 25 | 15 | 102 | 149 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 110 | 160 | 0 | 75 | 0 | 205 | 0 | 0 | 0 | 295 | 24 | 0 | 0 | 152 | 0 | 0 | 8 | 0 | 109 | 9 | 100 | 120 | 130 | 328 | 51 | 17 | 105 | 4 | 88 | 17 | 110 | 52 | 97 | 100 | 320 | 53 | 13 | 162 | 114 | 0 | 17 | 18 |  | 715 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 22 | 0 | 5 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 172 | 0 | 327 | 17 | 0 | 35 | 0 | 113 | 0 | 4 | 100 | 360 | 180 | 0 | 0 | 1 |  | 6748 | 2935 | 9683 | 4023 | 715 | 1696 | 2376 | 435 | 167 | 120 | 102 | 49 | 0 | 105.51
10:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 117 | 228 |  | 0 | 300 | 280 | 0 | 0 | 55 | 300 | 0 | 91 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 25 | 33 | 25 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 290 | 295 | 182 | 45 | 140 | 20 | 51 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 25 | 15 | 116 | 131 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 159 | 0 | 75 | 0 | 220 | 0 | 0 | 0 | 305 | 24 | 0 | 0 | 195 | 0 | 0 | 12 | 0 | 115 | 19 | 100 | 135 | 127 | 328 | 78 | 17 | 105 | 4 | 122 | 17 | 110 | 52 | 98 | 100 | 320 | 56 | 22 | 162 | 114 | 0 | 17 | 25 |  | 714 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 21 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 11 | 0 | 192 | 0 | 405 | 17 | 0 | 57 | 0 | 113 | 0 | 4 | 113 | 360 | 180 | 0 | 0 | 3 |  | 7114 | 3066 | 10180 | 4128 | 714 | 1866 | 2560 | 433 | 165 | 120 | 116 | 78 | 0 | 105.51
11:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 206 |  | 0 | 300 | 290 | 0 | 0 | 55 | 327 | 0 | 90 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 29 | 25 | 25 | 25 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 350 | 330 | 200 | 45 | 140 | 20 | 49 | 0 | 35 | 0 | 0 | 12 | 22 | 11 | 25 | 15 | 116 | 132 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 157 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 305 | 24 | 8 | 0 | 200 | 0 | 0 | 65 | 0 | 127 | 20 | 90 | 200 | 125 | 328 | 112 | 17 | 105 | 5 | 157 | 17 | 110 | 114 | 96 | 100 | 320 | 88 | 26 | 160 | 97 | 0 | 17 | 34 |  | 710 | 0 | 345 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 18 | 0 | 8 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 11 | 0 | 210 | 0 | 410 | 30 | 0 | 94 | 0 | 113 | 0 | 5 | 113 | 350 | 180 | 0 | 0 | 3 |  | 7544 | 3124 | 10668 | 4283 | 710 | 1848 | 2907 | 425 | 165 | 120 | 116 | 94 | 0 | 105.51
12:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 198 |  | 0 | 300 | 295 | 0 | 0 | 55 | 325 | 0 | 62 | 0 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 29 | 25 | 25 | 25 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 45 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 360 | 325 | 197 | 73 | 141 | 23 | 52 | 0 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 140 | 131 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 157 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 270 | 0 | 0 | 105 | 0 | 132 | 19 | 100 | 200 | 123 | 328 | 115 | 34 | 81 | 5 | 140 | 17 | 110 | 114 | 91 | 100 | 320 | 89 | 48 | 141 | 97 | 0 | 17 | 34 |  | 710 | 0 | 330 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 13 | 0 | 206 | 0 | 415 | 102 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 360 | 220 | 0 | 0 | 3 |  | 7789 | 3262 | 11051 | 4245 | 710 | 1921 | 3148 | 435 | 164 | 177 | 140 | 111 | 0 | 105.51
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 197 |  | 0 | 300 | 275 | 0 | 0 | 55 | 325 | 0 | 62 | 0 | 102 | 115 | 11 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 29 | 25 | 8 | 25 | 0 | 88 | 75 | 115 | 0 | 4 | 0 | 0 | 0 | 0 |  | 18 | 0 | 0 | 92 | 0 | 26 | 21 | 7 | 0 | 0 | 0 | 330 | 290 | 183 | 73 | 140 | 23 | 52 | 0 | 35 | 0 | 0 | 49 | 22 | 11 | 25 | 21 | 142 | 119 | 0 | 19 | 2 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 283 | 0 | 0 | 160 | 0 | 130 | 19 | 100 | 200 | 123 | 328 | 115 | 34 | 84 | 6 | 140 | 17 | 110 | 114 | 92 | 100 | 320 | 91 | 51 | 126 | 97 | 0 | 17 | 17 |  | 710 | 0 | 330 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 22 | 0 | 204 | 0 | 417 | 102 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 370 | 221 | 0 | 0 | 2 |  | 7971 | 3277 | 11248 | 4133 | 710 | 1943 | 3319 | 445 | 163 | 295 | 142 | 98 | 0 | 105.52
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 197 |  | 0 | 300 | 275 | 0 | 0 | 55 | 321 | 0 | 62 | 0 | 102 | 150 | 13 | 0 | 0 | 0 | 17 | 55 | 0 | 21 | 25 | 28 | 25 | 8 | 25 | 0 | 89 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 39 | 21 | 4 | 0 | 0 | 0 | 320 | 300 | 183 | 73 | 141 | 23 | 55 | 0 | 35 | 0 | 29 | 52 | 22 | 11 | 25 | 21 | 132 | 118 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 130 | 158 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 295 | 16 | 8 | 0 | 291 | 0 | 0 | 160 | 0 | 130 | 8 | 90 | 200 | 123 | 328 | 108 | 52 | 105 | 1 | 140 | 11 | 110 | 114 | 95 | 100 | 320 | 89 | 34 | 140 | 96 | 0 | 17 | 18 |  | 710 | 0 | 330 | 0 | 0 | 222 | 0 | 0 | 4 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 22 | 0 | 205 | 0 | 414 | 102 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 380 | 221 | 0 | 0 | 1 |  | 7969 | 3321 | 11290 | 4120 | 710 | 1892 | 3348 | 455 | 164 | 405 | 132 | 64 | 0 | 105.52
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 200 |  | 0 | 300 | 285 | 0 | 0 | 55 | 320 | 0 | 37 | 0 | 102 | 150 | 12 | 0 | 0 | 0 | 17 | 55 | 17 | 0 | 25 | 28 | 33 | 8 | 25 | 0 | 88 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 45 | 21 | 2 | 0 | 0 | 0 | 350 | 325 | 201 | 73 | 141 | 23 | 55 | 0 | 35 | 0 | 48 | 52 | 22 | 8 | 25 | 21 | 136 | 118 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 155 | 0 | 74 | 0 | 220 | 0 | 0 | 0 | 315 | 16 | 8 | 30 | 295 | 0 | 25 | 166 | 30 | 144 | 13 | 90 | 200 | 122 | 328 | 108 | 52 | 105 | 2 | 142 | 17 | 110 | 114 | 93 | 100 | 320 | 91 | 43 | 162 | 96 | 0 | 17 | 23 |  | 710 | 0 | 325 | 0 | 0 | 220 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 22 | 0 | 192 | 0 | 414 | 102 | 0 | 94 | 0 | 113 | 0 | 2 | 113 | 400 | 217 | 0 | 0 | 4 |  | 8260 | 3333 | 11593 | 4144 | 710 | 1936 | 3518 | 476 | 163 | 422 | 136 | 88 | 0 | 105.51
16:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 199 |  | 0 | 300 | 255 | 0 | 0 | 55 | 316 | 0 | 34 | 0 | 102 | 48 | 16 | 0 | 0 | 0 | 17 | 35 | 17 | 0 | 25 | 28 | 33 | 25 | 25 | 0 | 89 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 92 | 0 | 45 | 21 | 2 | 0 | 0 | 0 | 320 | 300 | 180 | 73 | 139 | 23 | 51 | 0 | 35 | 0 | 48 | 52 | 22 | 8 | 25 | 21 | 128 | 121 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 74 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 8 | 30 | 293 | 0 | 25 | 178 | 30 | 140 | 9 | 100 | 200 | 118 | 328 | 108 | 52 | 105 | 2 | 290 | 28 | 110 | 114 | 95 | 100 | 320 | 90 | 11 | 158 | 96 | 0 | 17 | 9 |  | 710 | 0 | 320 | 0 | 0 | 224 | 0 | 0 | 4 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 23 | 0 | 170 | 0 | 386 | 102 | 0 | 113 | 0 | 113 | 0 | 2 | 113 | 400 | 208 | 0 | 0 | 1 |  | 8141 | 3375 | 11516 | 4046 | 710 | 1882 | 3711 | 476 | 164 | 364 | 128 | 35 | 0 | 105.5
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 198 |  | 0 | 300 | 250 | 0 | 0 | 55 | 320 | 0 | 36 | 0 | 48 | 48 | 50 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 28 | 33 | 25 | 25 | 0 | 91 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 20 | 0 | 45 | 21 | 3 | 0 | 0 | 0 | 320 | 300 | 183 | 26 | 137 | 23 | 55 | 0 | 35 | 0 | 48 | 25 | 22 | 8 | 33 | 11 | 114 | 123 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 159 | 0 | 78 | 0 | 195 | 0 | 0 | 0 | 285 | 16 | 8 | 0 | 293 | 0 | 0 | 140 | 0 | 131 | 3 | 90 | 150 | 117 | 328 | 115 | 72 | 105 | 1 | 304 | 33 | 110 | 52 | 94 | 100 | 320 | 70 | 6 | 162 | 109 | 0 | 17 | 4 |  | 710 | 0 | 325 | 0 | 0 | 224 | 0 | 0 | 4 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 23 | 0 | 204 | 0 | 337 | 70 | 0 | 113 | 0 | 34 | 0 | 2 | 113 | 400 | 180 | 0 | 0 | 0 |  | 7721 | 3215 | 10936 | 4058 | 710 | 1749 | 3281 | 475 | 166 | 367 | 114 | 16 | 0 | 105.5
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 197 |  | 0 | 300 | 275 | 0 | 0 | 55 | 252 | 0 | 37 | 0 | 48 | 90 | 50 | 0 | 0 | 0 | 17 | 35 | 35 | 0 | 25 | 28 | 33 | 25 | 32 | 0 | 92 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 76 | 30 | 0 | 46 | 21 | 8 | 0 | 0 | 0 | 310 | 305 | 187 | 26 | 141 | 23 | 55 | 0 | 35 | 0 | 48 | 25 | 22 | 8 | 33 | 19 | 112 | 131 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 110 | 156 | 0 | 78 | 0 | 191 | 0 | 0 | 0 | 300 | 16 | 8 | 0 | 293 | 0 | 0 | 122 | 0 | 149 | 0 | 100 | 154 | 127 | 328 | 101 | 72 | 105 | 0 | 232 | 33 | 110 | 52 | 94 | 100 | 320 | 55 | 0 | 162 | 101 | 0 | 17 | 0 |  | 710 | 0 | 330 | 0 | 0 | 226 | 0 | 0 | 8 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 43 | 5 | 51 | 27 | 0 | 0 | 52 | 18 | 21 | 0 | 11 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 22 | 0 | 140 | 0 | 368 | 70 | 0 | 50 | 0 | 60 | 0 | 0 | 70 | 420 | 150 | 0 | 0 | 0 |  | 7693 | 3211 | 10904 | 3953 | 710 | 1717 | 3186 | 494 | 167 | 565 | 112 | 0 | 0 | 105.5
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 214 |  | 0 | 300 | 300 | 0 | 0 | 55 | 328 | 0 | 59 | 0 | 102 | 125 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 0 | 25 | 28 | 33 | 25 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 72 | 100 | 0 | 50 | 21 | 9 | 0 | 0 | 0 | 270 | 270 | 197 | 26 | 138 | 23 | 55 | 0 | 0 | 0 | 48 | 48 | 22 | 8 | 33 | 21 | 116 | 131 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 200 | 293 | 214 | 50 | 191 | 98 | 140 | 0 | 100 | 192 | 128 | 328 | 115 | 90 | 105 | 0 | 304 | 49 | 110 | 114 | 101 | 100 | 320 | 86 | 0 | 162 | 114 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 43 | 18 | 94 | 27 | 43 | 0 | 52 | 31 | 21 | 0 | 11 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 22 | 77 | 199 | 0 | 398 | 102 | 0 | 110 | 0 | 107 | 0 | 0 | 113 | 550 | 221 | 0 | 17 | 0 |  | 8993 | 3947 | 12940 | 4103 | 709 | 1863 | 4668 | 626 | 167 | 688 | 116 | 0 | 0 | 105.5
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 115 | 222 |  | 0 | 300 | 280 | 0 | 0 | 55 | 328 | 0 | 59 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 20 | 25 | 28 | 33 | 25 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 15 | 0 | 0 | 0 | 270 | 270 | 206 | 26 | 138 | 23 | 56 | 0 | 35 | 0 | 48 | 52 | 22 | 11 | 33 | 21 | 114 | 131 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 150 | 295 | 128 | 50 | 191 | 98 | 140 | 0 | 100 | 200 | 140 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 43 | 31 | 94 | 27 | 43 | 0 | 52 | 31 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 22 | 100 | 210 | 0 | 397 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 221 | 0 | 17 | 0 |  | 8984 | 4036 | 13020 | 4154 | 709 | 1893 | 4586 | 658 | 167 | 739 | 114 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 223 |  | 0 | 300 | 310 | 0 | 0 | 55 | 326 | 0 | 92 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 20 | 25 | 29 | 33 | 25 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 19 | 0 | 0 | 0 | 305 | 300 | 199 | 26 | 141 | 23 | 56 | 0 | 35 | 0 | 48 | 52 | 22 | 11 | 33 | 21 | 114 | 131 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 23 | 11 | 100 | 295 | 47 | 50 | 192 | 70 | 140 | 0 | 100 | 200 | 137 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 99 | 100 | 320 | 104 | 0 | 162 | 101 | 0 | 17 | 0 |  | 709 | 0 | 320 | 0 | 0 | 227 | 0 | 0 | 27 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 33 | 94 | 27 | 43 | 0 | 52 | 31 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 0 | 22 | 100 | 207 | 0 | 414 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 590 | 222 | 0 | 17 | 0 |  | 8963 | 4051 | 13014 | 4233 | 709 | 1918 | 4467 | 668 | 167 | 738 | 114 | 0 | 0 | 105.5
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 220 |  | 0 | 300 | 315 | 0 | 0 | 55 | 328 | 0 | 92 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 26 | 0 | 0 | 0 | 270 | 270 | 201 | 26 | 141 | 23 | 56 | 0 | 35 | 0 | 42 | 52 | 22 | 11 | 33 | 21 | 114 | 129 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 305 | 23 | 11 | 100 | 295 | 44 | 50 | 200 | 70 | 149 | 0 | 100 | 200 | 140 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 100 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 709 | 0 | 325 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 32 | 94 | 27 | 43 | 0 | 52 | 31 | 21 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 22 | 100 | 205 | 0 | 416 | 102 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 590 | 223 | 0 | 17 | 0 |  | 8970 | 4041 | 13011 | 4174 | 709 | 1950 | 4496 | 666 | 167 | 735 | 114 | 0 | 0 | 105.5
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 236 |  | 0 | 300 | 285 | 0 | 0 | 55 | 329 | 0 | 90 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 35 | 0 | 0 | 0 | 265 | 260 | 207 | 26 | 141 | 23 | 56 | 0 | 43 | 0 | 42 | 52 | 22 | 11 | 33 | 21 | 118 | 130 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 23 | 11 | 20 | 295 | 0 | 0 | 200 | 25 | 149 | 0 | 100 | 200 | 140 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 96 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 709 | 0 | 325 | 0 | 0 | 230 | 0 | 0 | 21 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 32 | 94 | 27 | 43 | 0 | 52 | 27 | 21 | 0 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 22 | 20 | 208 | 0 | 418 | 102 | 0 | 113 | 0 | 112 | 0 | 0 | 113 | 590 | 223 | 0 | 17 | 0 |  | 8741 | 3967 | 12708 | 4168 | 709 | 1980 | 4169 | 666 | 167 | 731 | 118 | 0 | 0 | 105.5
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 260 |  | 0 | 300 | 275 | 0 | 0 | 55 | 330 | 0 | 90 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 85 | 92 | 0 | 50 | 21 | 29 | 0 | 0 | 0 | 265 | 265 | 212 | 26 | 140 | 23 | 56 | 0 | 43 | 0 | 42 | 52 | 22 | 11 | 33 | 21 | 118 | 139 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 23 | 11 | 0 | 296 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 142 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 97 | 90 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 710 | 0 | 320 | 0 | 0 | 210 | 0 | 0 | 21 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 43 | 31 | 94 | 27 | 43 | 0 | 52 | 27 | 21 | 0 | 5 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 12 | 0 | 214 | 0 | 399 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 223 | 0 | 17 | 0 |  | 8689 | 3874 | 12563 | 4188 | 710 | 1949 | 4081 | 647 | 167 | 703 | 118 | 0 | 0 | 105.5
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 275 |  | 0 | 300 | 280 | 0 | 0 | 55 | 331 | 0 | 92 | 0 | 102 | 32 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 21 | 25 | 29 | 33 | 33 | 25 | 0 | 90 | 75 | 100 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 81 | 92 | 0 | 50 | 21 | 29 | 0 | 0 | 0 | 270 | 265 | 212 | 26 | 141 | 23 | 56 | 0 | 43 | 0 | 42 | 52 | 22 | 11 | 33 | 21 | 116 | 143 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 300 | 23 | 11 | 0 | 296 | 0 | 0 | 200 | 0 | 149 | 0 | 100 | 200 | 138 | 328 | 115 | 52 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 710 | 0 | 320 | 0 | 0 | 200 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 43 | 31 | 94 | 27 | 43 | 0 | 52 | 27 | 21 | 0 | 5 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 194 | 0 | 12 | 0 | 207 | 0 | 406 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 570 | 223 | 0 | 17 | 0 |  | 8541 | 3842 | 12383 | 4177 | 710 | 1990 | 4026 | 649 | 165 | 550 | 116 | 0 | 0 | 105.5
KWH | 0 | 0 | 0 | 0 | 5933891 | 0 | 0 | 2909630 | 5644000 |  | 0 | 7198000 | 6763840 | 0 | 0 | 1299034 | 7617603 | 0 | 1766000 | 0 | 1438704 | 1637280 | 519419 | 0 | 0 | 0 | 645840 | 905277 | 696359 | 394452 | 600000 | 670860 | 645100 | 680900 | 696000 | 0 | 2200865 | 1816000 | 2800000 | 0 | 245500 | 0 | 0 | 0 | 0 |  | 534480 | 0 | 642685 | 1358520 | 0 | 743040 | 486960 | 438240 | 0 | 0 | 0 | 7490000 | 7137000 | 4868000 | 752727 | 3328290 | 476064 | 1193760 | 0 | 848104 | 0 | 507432 | 802013 | 481644 | 238500 | 644100 | 519090 | 2814720 | 3249360 | 0 | 436176 | 9000 | 717000 | 0 | 593400 | 0 | 3592390 | 3673000 | 0 | 1739520 | 0 | 5133890 | 0 | 0 | 0 | 7270960 | 504888 | 200640 | 586176 | 5911416 | 371225 | 259878 | 3194400 | 424966 | 3070368 | 122715 | 2256960 | 4390080 | 3164786 | 7851000 | 2256000 | 1179600 | 2496545 | 34801 | 5427164 | 833398 | 2712325 | 2303940 | 2309160 | 2218560 | 7773300 | 2116800 | 252060 | 3849120 | 2608200 | 0 | 444240 | 178432 |  | 17195636 | 0 | 8163936 | 0 | 0 | 4335360 | 0 | 0 | 144480 | 0 | 0 | 2118761 | 642241 | 0 | 0 | 0 | 0 | 427088 | 196729 | 711968 | 231990 | 224096 | 0 | 980160 | 208024 | 484080 | 0 | 212346 | 1796509 | 0 | 0 | 0 | 0 | 0 | 0 | 4749618 | 0 | 400635 | 347520 | 5156000 | 0 | 9236000 | 1862400 | 0 | 2167200 | 0 | 2514432 | 0 | 28907 | 2502048 | 11829900 | 5029473 | 0 | 108000 | 25680 |  | 189747762 | 84031217 | 273778979 | 99627999 | 17195636 | 45063530 | 81971179 | 13626409 | 4016865 | 8811046 | 2814720 | 651595 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 6586619.01 | 0 | 0 | 2938726.3 | 5813320 |  | 0 | 7845820 | 7507862.4 | 0 | 0 | 10989827.64 | 7922307.12 | 0 | 3055180 | 0 | 13120980.48 | 16110835.2 | 4789043.18 | 0 | 0 | 0 | 4714632 | 6997791.21 | 6866099.74 | 295839 | 450000 | 0 | 0 | 0 | 6730320 | 0 | 594233.55 | 490320 | 5068000 | 0 | 2280695 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6234044.5 | 12973866 | 0 | 5884876.8 | 613569.6 | 1301572.8 | 0 | 0 | 0 | 5542600 | 7137000 | 4478560 | 971017.83 | 3827533.5 | 537952.32 | 1671264 | 0 | 1450257.84 | 0 | 5125063.2 | 7659224.15 | 611687.88 | 178875 | 1127175 | 389317.5 | 21110400 | 3444321.6 | 0 | 553943.52 | 143460 | 1175880 | 0 | 1056252 | 0 | 4095324.6 | 3819920 | 0 | 3322483.2 | 0 | 8881629.7 | 0 | 0 | 0 | 7343669.6 | 378666 | 152486.4 | 9970853.76 | 44690304.96 | 6303400.5 | 4345160.16 | 16610880 | 7105431.52 | 30212421.12 | 1434538.35 | 18394224 | 47632368 | 22311741.3 | 7301430 | 20574720 | 11147220 | 21744906.95 | 0 | 41029359.84 | 7258896.58 | 23841336.75 | 22993321.2 | 19789501.2 | 14775609.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99046863.36 | 0 | 8572132.8 | 0 | 0 | 60088089.6 | 0 | 0 | 1515595.2 | 0 | 0 | 2394199.93 | 995473.55 | 0 | 0 | 0 | 0 | 4202545.92 | 1998766.64 | 6300916.8 | 1786323 | 3029777.92 | 0 | 9497750.4 | 2017832.8 | 929433.6 | 0 | 160745.922 | 10832949.27 | 0 | 0 | 0 | 0 | 0 | 0 | 6269495.76 | 0 | 600952.5 | 5911315.2 | 6032520 | 0 | 9143640 | 19443456 | 0 | 20566728 | 0 | 19511992.32 | 0 | 319422.35 | 18490134.72 | 51933261 | 0 | 0 | 0 | 0 |  | 643829972.16 | 371592314.562 | 1015422286.722 | 99898313.862 | 99046863.36 | 46540481.52 | 579484353.6 | 62766210.27 | 1084553.55 | 103593689.86 | 21110400 | 1897420.7 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 198 |  | 0 | 300 | 295 | 0 | 0 | 55 | 325 | 0 | 62 | 0 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 29 | 25 | 25 | 25 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 45 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 360 | 325 | 197 | 73 | 141 | 23 | 52 | 0 | 35 | 0 | 0 | 25 | 22 | 11 | 25 | 21 | 140 | 131 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 163 | 157 | 0 | 77 | 0 | 220 | 0 | 0 | 0 | 310 | 16 | 8 | 0 | 270 | 0 | 0 | 105 | 0 | 132 | 19 | 100 | 200 | 123 | 328 | 115 | 34 | 81 | 5 | 140 | 17 | 110 | 114 | 91 | 100 | 320 | 89 | 48 | 141 | 97 | 0 | 17 | 34 |  | 710 | 0 | 330 | 0 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 0 | 17 | 0 | 11 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 13 | 0 | 206 | 0 | 415 | 102 | 0 | 94 | 0 | 113 | 0 | 1 | 113 | 360 | 220 | 0 | 0 | 3 |  | 11051 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 115 | 222 | 0 | 0 | 300 | 280 | 0 | 0 | 55 | 328 | 0 | 59 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 54 | 35 | 55 | 20 | 25 | 28 | 33 | 25 | 51 | 0 | 92 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 85 | 100 | 0 | 50 | 21 | 15 | 0 | 0 | 0 | 270 | 270 | 206 | 26 | 138 | 23 | 56 | 0 | 35 | 0 | 48 | 52 | 22 | 11 | 33 | 21 | 114 | 131 | 0 | 19 | 0 | 30 | 0 | 25 | 0 | 163 | 158 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 150 | 295 | 128 | 50 | 191 | 98 | 140 | 0 | 100 | 200 | 140 | 328 | 115 | 90 | 105 | 0 | 304 | 54 | 110 | 114 | 94 | 100 | 320 | 104 | 0 | 162 | 114 | 0 | 17 | 0 |  | 709 | 0 | 330 | 0 | 0 | 230 | 0 | 0 | 27 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 43 | 31 | 94 | 27 | 43 | 0 | 52 | 31 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 202 | 0 | 22 | 100 | 210 | 0 | 397 | 102 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 580 | 221 | 0 | 17 | 0 |  | 13020 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 120 | 300 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 335 | 0 | 100 | 0 | 102 | 149 | 50 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 25 | 33 | 51 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 0 | 50 | 21 | 40 | 0 | 0 | 0 | 320 | 310 | 210 | 26 | 142 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 160 | 8 | 22 | 0 | 30 | 0 | 25 | 0 | 163 | 162 | 0 | 80 | 0 | 225 | 0 | 0 | 0 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 140 | 400 | 115 | 90 | 105 | 0 | 300 | 54 | 110 | 114 | 94 | 100 | 383 | 104 | 0 | 162 | 116 | 0 | 17 |  |  | 726 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 27 | 40 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 31 | 94 | 27 | 43 | 40 | 52 | 25 | 22 | 0 | 11 | 80 | 0 | 0 | 16 | 10 | 0 | 0 | 206 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 184 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 120 | 300 | 0 | 0 | 300 | 305 | 0 | 0 | 55 | 326 | 0 | 100 | 0 | 100 | 149 | 50 | 0 | 0 | 0 | 54 | 17 | 55 | 22 | 25 | 30 | 25 | 33 | 25 | 0 | 93 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 0 | 50 | 20 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 26 | 142 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 138 | 160 | 8 | 22 | 1.6 | 30 | 0 | 25 | 0 | 163 | 161 | 0 | 80 | 0 | 225 | 0 | 0 | 0 | 341 | 24 | 11 | 150 | 300 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 138 | 400 | 115 | 90 | 105 | 5 | 300 | 54 | 110 | 114 | 94 | 100 | 383 | 100 | 50 | 162 | 116 | 0 | 17 | 30 |  | 726 | 0 | 355 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 43 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 206 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 116 | 292 | 0 | 0 | 300 | 270 | 0 | 0 | 15 | 250 | 0 | 36 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 29 | 33 |  | 0 | 0 | 93 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 0 | 18 | 27 | 0 | 0 | 0 | 270 | 265 | 213 | 26 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 19 | 11 | 33 | 21 | 72 | 159 | 0 | 19 | 1 | 30 | 0 | 25 | 0 | 110 | 161 | 0 | 78 | 0 | 179 | 0 | 0 | 0 | 280 | 23 | 11 | 0 | 15 | 0 | 0 | 35 | 0 | 80 | 8 | 10 | 136 | 122 | 328 | 55 | 0 | 34 | 2 | 0 | 17 | 51 | 17 | 55 | 10 | 320 | 17 | 6 | 90 | 114 | 0 | 17 | 8 | 0 | 714 | 0 | 345 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 12 | 3 | 182 | 0 | 333 | 35 | 0 | 35 | 0 | 89 | 0 | 3 | 35 | 350 | 162 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 9348 | 8:00
| Highest Generation |  | 13020 | 19:30
| Day Peak Generation |  | 11051 | 12:00
| Evening Peak Generation |  | 13020 | 19:30
| HVDC Max Flow |  | 715 | 5:00
| HVDC EvPeak Flow |  | 709 | 19:30
| Load factor L.F |  | 87.61%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-17
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-16 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11051 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 8814 | MW
Evening Peak Generation : |  | 13020 | MW Hour : | 19:30 | Available Max Generation : |  | 14721 | MW
E.P. Demand (at gen end) : |  | 13020 | MW Hour : | 19:30 | Max Demand (Evening) : |  | 12900 | MW
Maximum Generation : |  | 13020 | MW Hour : | 19:30 | Reserve(Generation end) |  | 1821 | MW
Total Gen. (MKWH) : |  | 273.779 | System Load Factor : | 87.61% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -120 | MW at | 18:30 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-17
Actual : | 105.56 | Ft.(MSL) , | Rule curve : | 102.68 | Ft.( MSL )
Gas Consumed : | Total = | 1127.2 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 146438795.382
: |  | Coal : | 62766210.27 | Oil : | 683078043.46 | Total : | 892283049.112
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4583.4293 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1563.2269 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1401.4205 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1266.5931 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1144.4411 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 923.5351 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 510.4665 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 237.6285 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 712.3045 |  |  | 0 | 0%
Total | 0 |  | 12343.0456 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
7) Raozan #02
8) Fenchuganj 3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barishal(N) 132/33 kV T5 transformer was under shut down from 07:43 to 12:05 for D/W.
b) Sylhet S/S-Fenchuganj P/S 132 kV Ckt was under shut down from 08:28 to 12:08 for D/W.
c) Gopalganj(old)- Gallamari 132 kv Ckt-1,2 were under shut down from 08:04 to 17:50 for D/W.
d) Saidpur132/33 kV T-3 transformer was shut down from 08:25 to 11:35 for A/M.
e) Bibiyana 400/230 kV T2 transformer was under shut down from 11:22 to 12:29 for D/W.
f) Rampura-Bhulta 230 kV Ckt-1 was under shut down from 12:03 to 13:02 for tree trimming by Haripur S/S.
g) Rampura-Aftabnagar 132 kV cable Ckt charged at 12:24 from Aftabnagar end.
h) Rampal 230/11 kV transformer charged 11:50 from HT side.
i) Keraniganj 230/132 kV T02 transformer was switched on at 12:48.
j) Hasnabad-Keraniganj 230 kv Ckt-2 was switched on at 13:24.
k) BSRM-Mirorsharai EPZ 230 kV Ckt was charged at 16:00 and later charge 230 kV bus-1,2.
l) Rampura-Aftabnagar-Mothertek 132 kV Ckt-1 tripped at 14:25 showing 87L & 86 distance relay and was |  |  |  |  | About 15 MW power interruption occurred under Mothertek S/S
switched on at 14:51. |  |  |  |  | area from 14:25 to 14:51.
m) Noagaon-Niamotpur 132 kV Ckt tripped at 00:05 from Noagaon end showing dist Z1 and was |  |  |  |  | About 67 MW power interruption occurred under Niamotpur S/S
switched on at 00:20(17-09-21). |  |  |  |  | area from 00:05 to 00:20(17/09/2021).
n) Sikalbaha-Anowara 230 kV Ckt-2 was under shut down since 07:13(17-09-2021) for D/W.
o) Rampura 230/132 kV T02 transformer was under shut down since 06:40(17-9-21) for C/M.
p) Satmosjid 132/33 kV T2 transformer was under shut down since 07:16(17-9-21) for C/M.
q) Bagerhat-Orion Rupsha 132 kV Ckt was under shut down since 05:15(17-09-2021) for D/W.
r) Polashbari-Mohastangor 132 kV Ckt-1 was under shut down since 07:43(17-09-2021) for C/M.
s) Dohazari-Cox's Bazar 132 kV Ckt-1 was under shut down since 06:00(17-09-2021) for D/W.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-16 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 5933891 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 115 | 2909630 | Machine problem
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 222 | 5644000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 300 | 7198000 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 280 | 6763840 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1299034
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 519419 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 20 | 394452
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 59 | 1766000 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 328 | 7617603
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1438704
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 645840
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1637280
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 35 | 905277 | Engine problem
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 696359
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1270860 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 645100
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 25 | 680900
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 696000
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 295 | 5911416
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 128 | 371225 | Low demand
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 50 | 259878 | Low demand
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 98 | 424966
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 140 | 3070368
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 90 | 1179600 | Engine problem
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 104 | 2116800
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3849120
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 178432
| Dhaka area Total |  |  |  | 5719 | 3364 | 66023994
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 245500
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 122715
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 743040
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 167 | 4016865 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2496545
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 642685 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1358520
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2256960
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 486960
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 15 | 438240
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 0 | 0 | Fuel shortage
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 34801
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 5427164
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 833398
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2712325
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2218560
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 114 | 2608200
| Chattogram area Total |  |  |  | 2382 | 1465 | 29442478
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 206 | 4868000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 7490000 | Gas shortage
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 270 | 7137000 | Gas shortage
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 476064 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 56 | 1193760
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 26 | 752727 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 848104 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 140 | 3164786 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 507432
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3328290 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 200 | 4390080
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 481644
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 238500
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 114 | 2814720
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 644100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 52 | 802013
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 21 | 519090
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 150 | 586176
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 2303940
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 2309160 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 444240 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 2040 | 45299826
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 131 | 3249360 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 436176
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9000
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 191 | 3194400
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2256000
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 252060
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 22 | 534480
| Mymensingh Area Total |  |  |  | 709 | 478 | 9931476
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 30 | 717000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Machine problem
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3592390
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 158 | 3673000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 25 | 593400 | Machine problem
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 200640
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1739520 | Engine problem
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5133890
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 504888
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7270960 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 328 | 7851000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7773300 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1637 | 39049988
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 709 | 17195636
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 27 | 144480 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 230 | 4335360
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 330 | 8163936 | Gas shortage
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 100 | 347520
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 102 | 1862400
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1498 | 32049332
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 32 | 642241
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2118761 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 400635 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 580 | 11829900
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 221 | 5029473
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 108000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 959 | 20129010
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 43 | 427088 | Engine problem
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 31 | 196729 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 231990 | Engine problem
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 224096 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 0 | 0 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 202 | 4749618 | Gas shortage
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 210 | 5156000 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 397 | 9236000 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 31 | 208024 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 484080
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 212346
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 980160
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 711968 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2167200
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2502048
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 25680
| Rajshahi Area Total |  |  |  | 2179 | 1388 | 27513027
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 78 | 1796509
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 2514432
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 28907
| Rangpur Area Total |  |  |  | 605 | 191 | 4339848
| Total |  |  |  | 21180 | 13020 | 273778979
| Eastern Grid Total |  |  |  | 14221 | 8984 | 189747762
| Western Grid Total |  |  |  | 6959 | 4036 | 84031217
| National Grid Total |  |  |  | 21180 | 13020 | 273778979
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-16
(a) ENTIRE EASTERN GRID : |  | 8516 | MW | (b) ENTIRE WESTERN GRID : |  | 3932 | MW
i) Dhaka area |  | 4565 | MW | i) Khulna area |  | 1534 | MW
ii) Chittagong area |  | 1258 | MW | ii) Rajshahi area |  | 1296 | MW
iii) Comilla area |  | 1166 | MW | iii) Barisal area |  | 365 | MW
iv) Mymensingh area |  | 985 | MW | iv) Rangpur area |  | 737 | MW
v) Sylhet area |  | 542 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12448 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 128 | 16:00 | Kishoreganj | 142 | 23:00 | Jessore | 111 | 19:00
Munsiganj | 106 | 0:00 | Netrokona | 118 | 21:00 | Benapol | 60 | 21:00
Sonargaon | 90 | 12:00 | Jamalpur | 144 | 3:00 | Jhenida | 111 | 18:30
Shyampur | 194 | 1:00 | Sherpur | 132 | 1:00 | Bottail | 126 | 18:30
Bhulta | 209 | 1:00 | Srimongal | 56 | 18:30 | G.K Project | 58 | 19:00
Madanganj | 39 | 18:30 | Shahjibazar | 118 | 21:00 | Faridpur | 150 | 21:00
Shitalakhya | 113 | 11:00 | Fenchuganj | 46 | 18:30 | Rajbari | 56 | 18:30
Rahim steel | 30 | 10:00 | Kulawara | 52 | 20:00 | Madaripur | 107 | 22:00
Matuail | 60 | 11:00 | Sylhet | 141 | 19:00 | Sariatpur | 70 | 22:00
Ghorasal | 85 | 22:00 | Chatak | 32 | 20:00 | Gopalganj | 94 | 19:00
Narsingdi | 182 | 21:00 | Sunamganj | 55 | 1:00 | Bagerhat | 100 | 18:30
Haripur (SBU) | 124 | 15:00 | Biani Bazar | 71 | 19:00 | Mongla | 36 | 12:00
Sreenagar | 40 | 1:00 | Comilla (S) | 142 | 13:00 | Satkhira | 102 | 21:00
Ullon | 55 | 23:00 | Comilla(N) | 151 | 0:00 | Gallamari | 43 | 13:00
Hasnabad | 81 | 0:00 | Chandpur | 78 | 21:00 | Magura | 56 | 19:00
Magbazar | 118 | 13:00 | Feni | 130 | 20:00 | Norail | 48 | 19:00
Maniknagar | 76 | 13:00 | Chowmuhani | 218 | 22:00 | Chuadanga | 97 | 20:00
Bangabhaban | 12 | 10:00 | Ashuganj | 43 | 0:00 | Borguna | 18 | 20:00
Motijheel | 29 | 11:00 | Daudkandi | 150 | 20:00 | Barisal(N) | 47 | 21:00
Narinda | 74 | 13:00 | B.Baria | 174 | 22:00 | Barisal (S) | 110 | 19:00
Kazla | 83 | 19:00 | Ramganj | 82 | 21:00 | Patuakhali | 114 | 23:00
Dhanmondi | 187 | 13:00 | Chaddagram | 45 | 19:00 | Bhandaria | 54 | 21:00
Lalbag | 92 | 16:00 | PHP | 10 | 7:00 | Borhan Uddin | 46 | 22:00
Madartek | 73 | 23:00 | Kochua | 66 | 22:00 | Ishurdi | 70 | 19:00
Dhaka University | 40 | 13:00 | Madunaghat | 62 | 18:30 | Ruppur Paromanobik | 4 | 10:00
Aftabnagar | 16 | 18:00 | Hathazari | 100 | 20:00 | Natore | 129 | 21:00
Fatullah | 64 | 15:00 | Khulshi | 192 | 16:00 | Bogra | 169 | 20:00
Nawabganj | 49 | 22:00 | Halishahar | 85 | 8:00 | Noagaon | 110 | 21:00
Keraniganj | 80 | 19:30 | Baraulia | 152 | 0:00 | Rajshahi | 142 | 20:00
Mirpur | 122 | 18:30 | Sikalbaha | 36 | 19:00 | Rajshahi New | 18 | 20:00
Kalyanpur | 105 | 18:30 | Dohazari | 106 | 18:30 | C.Nawabganj | 59 | 19:30
Gulshan | 140 | 15:00 | Cox'sbazar | 95 | 22:00 | Amnura | 46 | 21:00
Uttara | 84 | 13:00 | Chandraghona | 26 | 19:30 | Pabna | 103 | 19:30
Uttara New | 24 | 15:00 | Kaptai | 4.5 | 19:00 | Shahjadpur | 99 | 19:30
Kamrangirchar | 103 | 18:30 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 101 | 20:00
Savar | 178 | 18:30 | Bakulia | 117 | 16:00 | Niyamatpur | 70 | 21:00
Bhasantec | 136 | 18:30 | Julda | 22 | 14:00 | Joypurhat | 58 | 20:00
Agargaon | 88 | 13:00 | TK chemical | 31.8 | 20:00 | Sherpur(Bogura) | 58 | 18:30
Satmosjid | 97 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 64 | 20:00
Tongi | 124 | 18:00 | Shahmirpur | 24 | 18:00 | Bhangura | 32 | 20:00
Kabirpur | 231 | 15:00 | Khagrachhari | 24 | 1:00 | Rangpur | 127 | 19:30
Basundhara | 208 | 13:00 | Matarbari | 41 | 18:30 | Lalmonirhat | 42 | 2:00
Manikganj | 76 | 20:00 | Baroiar Hat | 50 | 15:00 | Saidpur | 96 | 21:00
Joydevpur | 174 | 19:00 | Rangamati | 14 | 18:30 | Purbasadipur | 98 | 20:00
New Tongi | 96 | 12:00 | Abul Khair 230 | 18 | 10:00 | Thakurgaon | 81 | 19:30
Kodda | 285 | 12:00 | BSRM | 156 | 4:00 | Palashbari | 115 | 21:00
Dhamrai | 106 | 22:00 | GPH Ispat | 76 | 7:00 | Barapukuria | 53 | 21:00
Rajendrapur | 108 | 19:00 | Agrabad | 88 | 18:00 | Panchagar | 52 | 5:00
Valuka | 108 | 16:00 | Goalpara | 26 | 17:00 | Joldhaka | 60 | 3:00
Tangail | 215 | 22:00 | Central S/S | 93 | 19:00 | Kurigram | 52 | 3:00
Mymensing | 222 | 1:00 | Noapara | 53 | 19:00 | Mithapukur | 30 | 20:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-16 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 5:00 | 400 | 11:00 | Kaliakoir | 396 | 0.375 | 381 | 0.45833
| Bheramara | 402 | 3:00 | 396 | 18:30 | Bhulta | 388 | 0.125 | 375 | 0.41667
| Ashuganj(N) | 393 | 4:00 | 383 | 10:00 | Gopalganj | 408 | 0.625 | 387 | 0.77083
| Payra | 411 | 3:00 | 399 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 232 | 1:00 | 230 | 18:00 | Hathazari | 235 | 15:00 | 226 | 12:00
| Ishurdi | 232 | 6:00 | 225 | 20:00 | Megnaghat | 235 | 6:00 | 228 | 1:00
| Ashuganj | 241 | 5:00 | 236 | 9:00 | Fenchuganj | 242 | 2:00 | 239 | 1:00
| Serajganj | 230 | 16:00 | 225 | 1:00 | Siddhirganj | 233 | 3:00 | 225 | 13:00
| Baghabari | 237 | 9:00 | 225 | 19:30 | Maniknagar | 230 | 3:00 | 223 | 10:00
| Barapukuria | 237 | 9:00 | 226 | 1:00 | Agargaon | 229 | 7:00 | 219 | 11:00
| Bogra | 224 | 9:00 | 213 | 1:00 | Barisal | 241 | 19:00 | 229 | 22:00
| Rajshahi | 230 | 18:00 | 220 | 3:00 | Bhola 225 MW | 243 | 8:00 | 234 | 22:00
| Khulna South | 233 | 6:00 | 224 | 22:00 | AKSML | 238 | 19:00 | 227 | 12:00
| Rampura | 230 | 4:00 | 223 | 9:00 | BSRM | 235 | 19:00 | 226 | 11:00
| Haripur | 229 | 1:00 | 223 | 10:00 | Bibiyana | 243 | 6:00 | 237 | 24:00
| Hasnabad | 228 | 22:00 | 218 | 12:00 | Bhulta | 231 | 1:00 | 224 | 11:00
| Shyampur | 228 | 3:00 | 218 | 12:00 | Ashuganj (S) | 237 | 3:00 | 232 | 10:00
| Aminbazar | 230 | 1:00 | 221 | 2:00 | Kaliakoir | 227 | 7:00 | 221 | 10:00
| Tongi | 227 | 23:00 | 220 | 11:00 | GPH | 237 | 19:30 | 228 | 11:00
| Comilla (N) | 233 | 2:00 | 227 | 12:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 133 | 1:00 | 128 | 10:00 | Madanhat | 139 | 0.77083 | 133 | 0.083333
| Munsiganj | 135 | 1:00 | 128 | 10:00 | Hathazari | 139 | 0.95833 | 134 | 0.625
| Sonargaon | 132 | 1:00 | 126 | 12:00 | Khulshi | 135 | 0.041667 | 129 | 0.5
| Shyampur | 136 | 21:00 | 129 | 11:00 | Halishahar | 137 | 0.79167 | 130 | 0.625
| Bhulta | 127 | 8:00 | 122 | 10:00 | Baraulia | 138 | 0.79167 | 132 | 0.5
| Madanganj | 134 | 19:30 | 127 | 10:00 | Sikalbaha | 137 | 0.041667 | 132 | 0.33333
| Shitalakhya | 135 | 1:00 | 127 | 11:00 | Dohazari | 132 | 0.79167 | 125 | 0.58333
| Rahim steal | 133 | 1:00 | 129 | 10:00 | Cox'sbazar | 124 | 0.375 | 117 | 0.5
| Matuail | 133 | 1:00 | 128 | 10:00 | Chandraghona | 137 | 0.041667 | 133 | 0.375
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 135 | 0.041667 | 135 | 0.041667
| Narsinghdi | 134 | 7:00 | 124 | 21:00 | A. Khaer Stl. | 135 | 0.041667 | 130 | 0.58333
| Haripur (SBU) | 133 | 1:00 | 129 | 10:00 | Bakulia | 136 | 0.79167 | 130 | 0.5
| Sreenagar | 133 | 19:30 | 120 | 11:00 | Julda | 137 | 0.041667 | 132 | 0.70833
| Ullon | 134 | 3:00 | 127 | 10:00 | TK Chemical | 137 | 0 | 131 | 0.54167
| Hasnabad | 137 | 1:00 | 134 | 10:00 | Modern Steel | 136 | 0.79167 | 130 | 0.5
| Magbazar | 134 | 3:00 | 126 | 13:00 | Shahmirpur | 137 | 0.041667 | 131 | 0.625
| Maniknagar | 134 | 3:00 | 128 | 11:00 | Khagrachhari | 136 | 0.041667 | 131 | 0.625
| Bangabhaban | 134 | 3:00 | 128 | 11:00 | Matarbari | 125 | 0.70833 | 119 | 0.625
| Motijheel | 134 | 3:00 | 128 | 11:00 | Baroiar Hat | 136 | 0.66667 | 132 | 0.375
| Narinda | 134 | 3:00 | 128 | 11:00 | Rangamati | 136 | 1:00 | 132 | 12:00
| Kazla | 134 | 3:00 | 128 | 11:00 | Agrabad | 136 | 23:00 | 130 | 12:00
| Dhanmondi | 134 | 3:00 | 127 | 11:00 | Goalpara S/S | 139 | 6:00 | 134 | 0.91667
| Lalbag | 133 | 19:00 | 120 | 11:00 | Khulna Central S/S | 138 | 6:00 | 132 | 0.95833
| Madartek | 134 | 2:00 | 127 | 11:00 | Noapara | 136 | 6:00 | 129 | 0.95833
| Dhaka University | 135 | 5:00 | 127 | 10:00 | Jessore | 133 | 6:00 | 124 | 0.95833
| Aftabnagar | 135 | 4:00 | 127 | 14:00 | Benapol | 133 | 0.20833 | 123 | 0.95833
| Fatullah | 136 | 2:00 | 129 | 10:00 | Jhenida | 132 | 9:00 | 120 | 0.95833
| Nawabganj | 134 | 19:30 | 121 | 11:00 | Bottail | 133 | 0.25 | 126 | 0.95833
| Keraniganj | 134 | 19:00 | 122 | 10:00 | G.K Project | 138 | 0.75 | 133 | 0.91667
| Mirpur | 129 | 2:00 | 125 | 10:00 | Faridpur | 135 | 0.25 | 128 | 0.77083
| Kalyanpur | 133 | 2:00 | 126 | 11:00 | Rajbari | 134 | 0.29167 | 127 | 0.875
| Gulshan | 134 | 3:00 | 127 | 10:00 | Madaripur | 140 | 0.33333 | 130 | 0.8125
| Uttara | 132 | 2:00 | 125 | 13:00 | Shariyatpur S/S | 140 | 8:00 | 131 | 0.83333
| Uttara New | 132 | 1:00 | 124 | 11:00 | Gopalganj | 144 | 0.33333 | 129 | 0.95833
| Kamrangirchar | 133 | 19:00 | 120 | 11:00 | Bagerhat | 136 | 6:00 | 130 | 0.95833
| Savar | 134 | 2:00 | 126 | 10:00 | Mongla | 136 | 6:00 | 128 | 0.95833
| Bhasantec | 136 | 4:00 | 128 | 11:00 | Satkhira | 136 | 5:00 | 129 | 22:00
| Agargaon | 137 | 4:00 | 129 | 12:00 | Gallamari | 138 | 0.20833 | 132 | 23:00
| Satmosjid | 136 | 2:00 | 128 | 11:00 | Magura | 130 | 6:00 | 117 | 0.95833
| Tongi | 136 | 1:00 | 132 | 12:00 | Narail | 130 | 0.25 | 117 | 0.95833
| Kabirpur | 137 | 4.00 | 129 | 12:00 | Chuadanga | 135 | 9:00 | 123 | 0.83333
| Basundhara | 136 | 18:30 | 128 | 10:00 | Borguna | 138 | 7:00 | 127 | 0.875
| Manikganj | 140 | 5.00 | 131 | 12:00 | Barisal(N) | 140 | 7:00 | 130 | 22:00
| Joydevpur | 138 | 7.00 | 134 | 10:00 | Barisal (S) | 138 | 0.375 | 128 | 0.875
| New Tongi | 136 | 3:00 | 126 | 10:00 | Patuakhali(S) | 135 | 0.25 | 124 | 0.91667
| Kodda | 132 | 1:00 | 124 | 9:00 | Bhandaria | 137 | 0.45833 | 120 | 0.91667
| Dhamrai | 136 | 2:00 | 130 | 14:00 | Ishurdi | 135 | 6:00 | 131 | 20:00
| Rajendrapur | 131 | 23:00 | 118 | 10:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 1:00
| Valuka | 129 | 4:00 | 110 | 20:00 | Natore | 135 | 17:00 | 129 | 2:00
| Tangail | 138 | 6:00 | 124 | 18:30 | Bogra | 136 | 10:00 | 126 | 1:00
| Mymensing | 134 | 4:00 | 113 | 20:00 | Noagaon | 131 | 18:00 | 120 | 1:00
| Kishorganj | 134 | 4:00 | 118 | 22:00 | Rajshahi | 133 | 9:00 | 129 | 1:00
| Netrokona | 129 | 6:00 | 109 | 20:00 | Rajshahi New | 136 | 18:00 | 128 | 3:00
| Jamalpur | 135 | 4:00 | 122 | 20:00 | C.Nawabganj | 134 | 18:00 | 126 | 3:00
| Sherpur | 136 | 4:00 | 119 | 1:00 | Amnura | 135 | 18:00 | 124 | 2:00
| Srimongal | 137 | 9:00 | 130 | 22:00 | Pabna | 134 | 6:00 | 128 | 19:00
| Shahjibazar | 136 | 6:00 | 128 | 4:00 | Shahjadpur | 139 | 17:00 | 134 | 20:00
| Fenchuganj | 135 | 6:00 | 131 | 20:00 | Serajganj | 133 | 7:00 | 126 | 19:30
| Khulawara | 135 | 5:00 | 130 | 20:00 | Niyamatpur | 131 | 9:00 | 117 | 1:00
| Sylhet | 133 | 2:00 | 129 | 18:30 | Joypurhat | 132 | 9:00 | 120 | 1:00
| Chatak | 133 | 5:00 | 127 | 19:00 | Sherpur(Bogura) | 135 | 9:00 | 126 | 1:00
| Sunamganj | 131 | 7:00 | 123 | 1:00 | Mohastangor | 135 | 9:00 | 124 | 1:00
| Biani Bazar | 132 | 7:00 | 124 | 1:00 | Bangura | 136 | 16:00 | 130 | 19:30
| Comilla(s) | 129 | 6:00 | 123 | 12:00 | Rangpur | 133 | 9:00 | 115 | 1:00
| Comilla(n) | 137 | 6:00 | 134 | 18:00 | Lalmonirhat | 132 | 9:00 | 116 | 2:00
| Chandpur | 141 | 11:00 | 137 | 23:00 | Saidpur | 132 | 9:00 | 118 | 1:00
| Feni | 136 | 8:00 | 132 | 11:00 | Purbasadipur | 130 | 9:00 | 111 | 1:00
| Chowmuhani | 134 | 8:00 | 130 | 3:00 | Thakurgaon | 130 | 6:00 | 111 | 1:00
| Ashuganj | 140 | 17:00 | 134 | 22:00 | Palashbari | 132 | 9:00 | 117 | 1:00
| Daudkandi | 136 | 18:30 | 128 | 10:00 | Barapukuria | 137 | 9:00 | 126 | 1:00
| B.Baria | 136 | 7:00 | 126 | 22:00 | Panchagar | 134 | 9:00 | 110 | 1:00
| Ramganj | 136 | 9:00 | 131 | 0:00 | Joldhaka | 129 | 0.375 | 111 | 0.083333
| Chaddagram | 136 | 7:00 | 133 | 18:30 | Kurigram | 134 | 0.375 | 115 | 0.041667
| PHP | 136 | 16:00 | 132 | 15:00 | Mithapukur | 135 | 0.375 | 120 | 0.041667
| Kochua | 136 | 5:00 | 134 | 9:00
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-16
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 12 | 8541 | 3842 | 12383 |  |  |  | QF-LDC-11
0:30 | 54 | 8344.5 | 3769.5 | 12114 | Date: | 2021-09-16
1:00 | 96 | 8148 | 3697 | 11845
1:30 | 105 | 7939 | 3557 | 11496
2:00 | 114 | 7730 | 3417 | 11147
2:30 | 104 | 7722.5 | 3386 | 11108.5 | [5 empty] | Gen. at Eve. Peak | 13020 | 13020 MW (19:30 )
3:00 | 94 | 7715 | 3355 | 11070 | [6 empty] | 19:30
3:30 | 105 | 7513.5 | 3326.5 | 10840 | [5 empty] | Gen. at Day Peak | 11051 | 11051 MW (12:00 )
4:00 | 116 | 7312 | 3298 | 10610 | [6 empty] | 12:00
4:30 | 105 | 7259.5 | 3263.5 | 10523 | [5 empty] | Highest Generation | 13020
5:00 | 94 | 7207 | 3229 | 10436 | [6 empty] | 19:30
5:30 | 62 | 6947.5 | 3105 | 10052.5
6:00 | 30 | 6688 | 2981 | 9669
6:30 | 63 | 6600.5 | 2947.5 | 9548
7:00 | 96 | 6513 | 2914 | 9427
7:30 | 118 | 6493 | 2894.5 | 9387.5
8:00 | 140 | 6473 | 2875 | 9348
8:30 | 240 | 6610.5 | 2905 | 9515.5
9:00 | 340 | 6748 | 2935 | 9683
9:30 | 403 | 6931 | 3000.5 | 9931.5
10:00 | 466 | 7114 | 3066 | 10180
10:30 | 431 | 7329 | 3095 | 10424
11:00 | 396 | 7544 | 3124 | 10668
11:30 | 342 | 7666.5 | 3193 | 10859.5
12:00 | 288 | 7789 | 3262 | 11051
12:30 | 237 | 7880 | 3269.5 | 11149.5
13:00 | 186 | 7971 | 3277 | 11248
13:30 | 191 | 7970 | 3299 | 11269
14:00 | 196 | 7969 | 3321 | 11290
14:30 | 174 | 8114.5 | 3327 | 11441.5
15:00 | 152 | 8260 | 3333 | 11593
15:30 | 216 | 8200.5 | 3354 | 11554.5
16:00 | 280 | 8141 | 3375 | 11516
16:30 | 333 | 7931 | 3295 | 11226
17:00 | 386 | 7721 | 3215 | 10936
17:30 | 371 | 7707 | 3213 | 10920
18:00 | 356 | 7693 | 3211 | 10904
18:30 | 233 | 8343 | 3579 | 11922
19:00 | 110 | 8993 | 3947 | 12940
19:30 | 106 | 8984 | 4036 | 13020
20:00 | 120 | 8963 | 4051 | 13014 |  |  |  | Executive Engineer
20:30 | 115 | 8966.5 | 4046 | 13012.5 |  |  |  | Network Operation Division
21:00 | 110 | 8970 | 4041 | 13011
21:30 | 108 | 8855.5 | 4004 | 12859.5
22:00 | 106 | 8741 | 3967 | 12708 |  |  |  |  | Page 6 of 7
22:30 | 113 | 8715 | 3920.5 | 12635.5
23:00 | 120 | 8689 | 3874 | 12563
23:30 | 66 | 8615 | 3858 | 12473
24:00 | 12 | 8541 | 3842 | 12383
13020 MW (19:30 )
11051 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-16 |  | Energy | 273778979
[11 empty] | 2021-09-16 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4177 | 710 | 1990 | 4081 | 649 | 165 | 550 | 0 | 116 | 0
0:30 | 4059 | 712 | 1927 | 3909.5 | 617 | 165 | 632 | 0 | 120 | 0 | Date: | 2021-09-16
1:00 | 3941 | 714 | 1864 | 3738 | 585 | 165 | 714 | 0 | 124 | 0
1:30 | 3925.5 | 714 | 1838.5 | 3674.5 | 580.5 | 165 | 474 | 0 | 124 | 0 | [7 empty] | Total Energy | 273.779 | Total Energy Gen 273.779 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 273.779 MKWHr
2:00 | 3910 | 714 | 1813 | 3611 | 576 | 165 | 234 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 3939 | 714 | 1860.5 | 3558.5 | 571.5 | 166 | 177 | 0 | 122 | 0 | [7 empty] | Energy Requirement | 273.779
3:00 | 3968 | 714 | 1908 | 3506 | 567 | 167 | 120 | 0 | 120 | 0
3:30 | 4006 | 714 | 1828.5 | 3331.5 | 556 | 167 | 120 | 0 | 117 | 0 | [6 empty] | Shortage
4:00 | 4044 | 714 | 1749 | 3157 | 545 | 167 | 120 | 0 | 114 | 0
4:30 | 4067.5 | 714.5 | 1787 | 3031 | 525 | 167 | 120 | 0 | 111 | 0
5:00 | 4091 | 715 | 1825 | 2905 | 505 | 167 | 120 | 0 | 108 | 0
5:30 | 4072.5 | 715 | 1821 | 2561.5 | 490 | 167 | 120 | 0 | 105 | 0.5
6:00 | 4054 | 715 | 1817 | 2218 | 475 | 167 | 120 | 0 | 102 | 1
6:30 | 4064.5 | 715 | 1812.5 | 2088.5 | 475 | 167 | 120 | 0 | 99 | 6.5 |  |  |  |  | Coal
7:00 | 4075 | 715 | 1808 | 1959 | 475 | 167 | 120 | 0 | 96 | 12
7:30 | 4067 | 715 | 1766.5 | 1972.5 | 465.5 | 167 | 120 | 0 | 95 | 19 |  |  |  | Oil |  |  |  | ,
8:00 | 4059 | 715 | 1725 | 1986 | 456 | 167 | 120 | 0 | 94 | 26
8:30 | 4041 | 715 | 1710.5 | 2181 | 445.5 | 167 | 120 | 0 | 98 | 37.5
9:00 | 4023 | 715 | 1696 | 2376 | 435 | 167 | 120 | 0 | 102 | 49
9:30 | 4075.5 | 714.5 | 1781 | 2468 | 434 | 166 | 120 | 0 | 109 | 63.5
10:00 | 4128 | 714 | 1866 | 2560 | 433 | 165 | 120 | 0 | 116 | 78
10:30 | 4205.5 | 712 | 1857 | 2733.5 | 429 | 165 | 120 | 0 | 116 | 86
11:00 | 4283 | 710 | 1848 | 2907 | 425 | 165 | 120 | 0 | 116 | 94
11:30 | 4264 | 710 | 1884.5 | 3027.5 | 430 | 164.5 | 148.5 | 0 | 128 | 102.5
12:00 | 4245 | 710 | 1921 | 3148 | 435 | 164 | 177 | 0 | 140 | 111
12:30 | 4189 | 710 | 1932 | 3233.5 | 440 | 163.5 | 236 | 0 | 141 | 104.5
13:00 | 4133 | 710 | 1943 | 3319 | 445 | 163 | 295 | 0 | 142 | 98
13:30 | 4133 | 710 | 1943 | 3319 | 445 | 163 | 295 | 0 | 142 | 98
14:00 | 4133 | 710 | 1943 | 3319 | 445 | 163 | 295 | 0 | 142 | 98
14:30 | 4138.5 | 710 | 1939.5 | 3418.5 | 460.5 | 163 | 358.5 | 0 | 139 | 93
15:00 | 4144 | 710 | 1936 | 3518 | 476 | 163 | 422 | 0 | 136 | 88
15:30 | 4095 | 710 | 1909 | 3614.5 | 476 | 163.5 | 393 | 0 | 132 | 61.5
16:00 | 4046 | 710 | 1882 | 3711 | 476 | 164 | 364 | 0 | 128 | 35
16:30 | 4052 | 710 | 1815.5 | 3496 | 475.5 | 165 | 365.5 | 0 | 121 | 25.5
17:00 | 4058 | 710 | 1749 | 3281 | 475 | 166 | 367 | 0 | 114 | 16
17:30 | 4005.5 | 710 | 1733 | 3233.5 | 484.5 | 166.5 | 466 | 0 | 113 | 8
18:00 | 3953 | 710 | 1717 | 3186 | 494 | 167 | 565 | 0 | 112 | 0
18:30 | 4028 | 709.5 | 1790 | 3927 | 560 | 167 | 626.5 | 0 | 114 | 0
19:00 | 4103 | 709 | 1863 | 4668 | 626 | 167 | 688 | 0 | 116 | 0
19:30 | 4154 | 709 | 1893 | 4586 | 658 | 167 | 739 | 0 | 114 | 0
20:00 | 4233 | 709 | 1918 | 4467 | 668 | 167 | 738 | 0 | 114 | 0
20:30 | 4203.5 | 709 | 1934 | 4481.5 | 667 | 167 | 736.5 | 0 | 114 | 0
21:00 | 4174 | 709 | 1950 | 4496 | 666 | 167 | 735 | 0 | 114 | 0
21:30 | 4171 | 709 | 1965 | 4332.5 | 666 | 167 | 733 | 0 | 116 | 0
22:00 | 4168 | 709 | 1980 | 4169 | 666 | 167 | 731 | 0 | 118 | 0
22:30 | 4178 | 709.5 | 1964.5 | 4125 | 656.5 | 167 | 717 | 0 | 118 | 0
23:00 | 4188 | 710 | 1949 | 4081 | 647 | 167 | 703 | 0 | 118 | 0
23:30 | 4182.5 | 710 | 1969.5 | 4081 | 648 | 166 | 626.5 | 0 | 117 | 0 | Max Temp. in Dhaka |  | 33.2° C
24:00 | 4177 | 710 | 1990 | 4081 | 649 | 165 | 550 | 0 | 116 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 273.779 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 273.779 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-16
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 90 | 90 | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 90 | 89 | 88 | 89 | 88 | 89 | 91 | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 90 | 2200865
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1816000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 100 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | 0 | [10 empty] | 4 | 8 | 8 | 8 | 8 | 8 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 245500
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 3 | 7 | 9 | 19 | 20 | 19 | 19 | 8 | 13 | 9 | 3 | [9 empty] | 122715
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 85 | 0 | [15 empty] | 76 |  | 72 | 85 | 85 | 85 | 85 | 85 | 81 | 642685
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 81 | 84 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2496545
| Daudkandi 200 MW PP (B.Trac) | [14 empty] | 30 | 30 |  |  |  | 200 | 150 | 100 | 100 | 20 |  |  | 586176
14 | Titas 50 MW Peaking PP | 48 | 0 | [11 empty] | 29 | 48 | 48 | 48 | 48 |  | 48 | 48 | 48 | 42 | 42 | 42 | 42 | 507432
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP | 90 | 90 | 90 | 90 | 91 | 37 | 37 | 37 | 36 | 91 | 90 | 62 | 62 | 62 | 37 | 34 | 36 | 37 |  | 59 | 59 | 92 | 92 | 90 | 90 | 92 | 1766000
17 | Siddhirganj 335 MW CCPP | 331 | 270 | 270 | 333 | 333 | 335 | 300 | 300 | 300 | 300 | 327 | 325 | 325 | 321 | 320 | 316 | 320 | 252 |  | 328 | 328 | 326 | 328 | 329 | 330 | 331 | 7617603
18 | Kodda 300 MW PP Unit-2 (Summit) | 284 | 284 | 284 | 245 | 195 | 45 | 45 | 45 | 152 | 195 | 200 | 270 | 283 | 291 | 295 | 293 | 293 | 293 |  | 293 | 295 | 295 | 295 | 295 | 296 | 296 | 5911416
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 45 | 45 | 73 | 73 | 73 | 73 | 73 | 26 | 26 |  | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 752727
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 30 | 55 | 90 | 110 | 160 | 200 | 250 | 250 | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 5933891
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 0 | 23 | 23 | 23 | 23 | 20 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 476064
33 | Ashuganj 225 MW CCPP | 213 | 214 | 214 | 214 | 180 | 214 | 214 | 213 | 178 | 182 | 200 | 197 | 183 | 183 | 201 | 180 | 183 | 187 |  | 197 | 206 | 199 | 201 | 207 | 212 | 212 | 4868000
34 | Ashuganj 450 MW CCPP(South) | 290 | 290 | 290 | 290 | 290 | 280 | 265 | 270 | 275 | 295 | 330 | 325 | 290 | 300 | 325 | 300 | 300 | 305 |  | 270 | 270 | 300 | 270 | 260 | 265 | 265 | 7137000
| Ashuganj 450 MW CCPP(North) | 300 | 300 | 300 | 300 | 300 | 270 | 270 | 295 | 290 | 290 | 350 | 360 | 330 | 320 | 350 | 320 | 320 | 310 |  | 270 | 270 | 305 | 270 | 265 | 265 | 270 | 7490000
35 | Ashuganj 55 MW PP (Precision) | 50 | 11 | 51 | 17 | 30 | 56 | 56 | 56 | 54 | 51 | 49 | 52 | 52 | 55 | 55 | 51 | 55 | 55 |  | 55 | 56 | 56 | 56 | 56 | 56 | 56 | 1193760
36 | Chandpur 150 MW CCPP | 139 | 141 | 143 | 142 | 140 | 141 | 140 | 142 | 141 | 140 | 140 | 141 | 140 | 141 | 141 | 139 | 137 | 141 |  | 138 | 138 | 141 | 141 | 141 | 140 | 141 | 3328290
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 116 | 117 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 117 | 116 | 116 | 116 | 116 | 116 | 116 | 116 | 116 |  | 116 | 115 | 116 | 116 | 116 | 116 | 116 | 2909630
40 | Meghnaghat 450 MW CCPP(MPL) | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 |  | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 7198000
41 | Haripur 360MW CCPP(HPL) | 260 | 270 | 292 | 295 | 298 | 286 | 266 | 241 | 232 | 228 | 206 | 198 | 197 | 197 | 200 | 199 | 198 | 197 |  | 214 | 222 | 223 | 220 | 236 | 260 | 275 | 5644000
42 | RPCL 210MW CCPP | 157 | 154 | 160 | 165 | 163 | 163 | 161 | 152 | 149 | 131 | 132 | 131 | 119 | 118 | 118 | 121 | 123 | 131 |  | 131 | 131 | 131 | 129 | 130 | 139 | 143 | 3249360
43 | Sutiakhali 50 MW Solar PP | [6 empty] | 4 | 9 | 13 | 22 | 26 | 48 | 51 | 34 | 43 | 11 | 6 | 0 | [8 empty] | 252060
44 | Fenchugonj CCPP Phase-1 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |  | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 717000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 160 | 160 | 161 | 161 | 162 | 161 | 162 | 161 | 160 | 159 | 157 | 157 | 158 | 158 | 155 | 158 | 159 | 156 |  | 158 | 158 | 158 | 160 | 161 | 161 | 161 | 3673000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 5 | 69 | 78 | 78 | 78 | 75 | 75 | 78 | 77 | 77 | 77 | 74 | 74 | 78 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1739520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 205 | 206 | 206 | 205 | 183 | 205 | 205 | 205 | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 195 | 191 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5133890
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 |  |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 200640
55 | Fenchugonj 51 MW PP (Barakatullah) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 593400
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 16 | 16 | 16 | 16 | 16 |  | 16 | 24 | 23 | 23 | 23 | 23 | 23 | 504888
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 270 | 300 | 290 | 295 | 290 | 295 | 280 | 295 | 305 | 305 | 310 | 310 | 295 | 315 | 300 | 285 | 300 |  | 300 | 280 | 280 | 305 | 300 | 280 | 300 | 7270960
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7773300
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 17 | 17 | 35 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 696359
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 17 | 18 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 534480
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 486960
61 | Narshingdi 22 MW PP (Doreen) | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | [6 empty] | 20 | 20 | 21 | 21 | 21 | 21 | 394452
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 436176
63 | Impoprt (Tripura) | 124 | 124 | 120 | 114 | 108 | 102 | 96 | 94 | 102 | 116 | 116 | 140 | 142 | 132 | 136 | 128 | 114 | 112 |  | 116 | 114 | 114 | 114 | 118 | 118 | 116 | 2814720
64 | Malancha, Ctg. EPZ (United) | 28 | 28 | 37 | 38 | 38 | 38 | 35 | 5 | 2 | 2 | 2 | 2 | 7 | 4 | 2 | 2 | 3 | 8 |  | 9 | 15 | 19 | 26 | 35 | 29 | 29 | 438240
65 | Feni 22MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 481644
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 238500
67 | Jangalia 33MW PP (Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 644100
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 15 | 15 | 15 | 21 | 21 | 21 | 21 | 21 | 11 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 519090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 29 | 29 | 29 | 28 | 28 | 28 | 28 | 28 |  | 28 | 28 | 29 | 29 | 29 | 29 | 29 | 670860
71 | Maona 33 MW PP(Summit) | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 25 | 25 | 25 | 25 | 25 | 25 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 645100
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 8 | 8 | 8 | 25 | 25 | 25 |  | 25 | 25 | 25 | 33 | 33 | 33 | 33 | 680900
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 114 | 114 | 88 | 52 | 52 | 52 | 52 | 52 | 114 | 114 | 114 | 114 | 114 | 114 | 52 | 52 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 2303940
| Chowmuhani 113 MW | 96 | 97 | 96 | 93 | 92 | 92 | 99 | 99 | 97 | 98 | 96 | 91 | 92 | 95 | 93 | 95 | 94 | 94 |  | 101 | 94 | 99 | 100 | 96 | 97 | 95 | 2309160
| Manikgonj 162MW PP(MPGL) | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 160 | 141 | 126 | 140 | 162 | 158 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3849120
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 25 | 25 | 25 | 25 | 25 | 8 | 8 | 8 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 32 |  | 51 | 51 | 51 | 51 | 51 | 51 | 25 | 696000
79 | Kodda 150MW PP | 150 | 64 | 0 | [8 empty] | 32 | 115 | 150 | 150 | 48 | 48 | 90 |  | 125 | 150 | 150 | 150 | 150 | 150 | 32 | 1637280
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | 52 | 52 | 50 | 0 |  |  |  | 1 | 8 | 8 | 12 | 25 | 49 | 52 | 52 | 52 | 25 | 25 |  | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 802013
| Gazipur 100 MW PP | 52 | 52 | 52 | 52 | 17 | 17 |  | 17 | 17 | 17 | 17 | 34 | 34 | 52 | 52 | 52 | 72 | 72 |  | 90 | 90 | 90 | 90 | 90 | 90 | 52 | 1179600
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 5 | 6 | 1 | 2 | 2 | 1 | [9 empty] | 34801
| Jodiac Power | 54 | 54 | 54 | 54 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 28 | 33 | 33 |  | 49 | 54 | 54 | 54 | 54 | 54 | 54 | 833398
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 105 | 105 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2712325
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 37 | 0 | [10 empty] | 11 | 13 | 12 | 16 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 519419
86 | Meghnaghat CCPP ( Summit) | 260 | 270 | 270 | 265 | 275 | 275 | 290 | 275 | 270 | 280 | 290 | 295 | 275 | 275 | 285 | 255 | 250 | 275 |  | 300 | 280 | 310 | 315 | 285 | 275 | 280 | 6763840
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 104 | 104 | 104 | 104 | 92 | 89 | 58 | 54 | 53 | 56 | 88 | 89 | 91 | 89 | 91 | 90 | 70 | 55 |  | 86 | 104 | 104 | 104 | 104 | 104 | 104 | 2116800
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 92 | 92 | 92 | 0 |  |  |  | 10 | 10 | 10 | 10 | 45 | 92 | 92 | 92 | 92 | 20 | 30 |  | 100 | 100 | 100 | 100 | 100 | 92 | 92 | 1358520
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  |  | 35 | 35 | 35 | 43 | 43 | 43 | 848104
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 48 | 32 | 0 |  |  |  |  | 10 | 16 | 16 | 58 | 102 | 102 | 102 | 102 | 48 | 48 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1438704
95 | Patenga 50MW PP (Baraka) | 50 | 50 | 0 |  |  |  |  | 1 | 15 | 18 | 18 | 18 | 26 | 39 | 45 | 45 | 45 | 46 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 743040
96 | Chattogram 108 MW PP (ECPV) | [26 empty] | 0
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 45 | 45 | 45 | 45 | 50 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1299034
100 | Manikganj 55 MW PP (Northern) | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 55 | 55 | 55 | 35 | 35 | 35 |  | 35 | 35 | 55 | 55 | 55 | 55 | 55 | 905277
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 163 | 163 | 163 | 163 | 130 | 163 | 163 | 163 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3592390
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 0 | 0 | 1 | 1 | 1 | 2 | 1 | 1 | 1 | 0 | [9 empty] | 9000
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 645840
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 214 | 128 | 47 | 44 |  |  |  | 371225
105 | Bramhangoan 100 MW PP (Aggreko) | [14 empty] | 25 | 25 |  |  |  | 50 | 50 | 50 | 50 |  |  |  | 259878
106 | Mymensingh 200 MW PP (United) | 162 | 162 | 161 | 100 | 60 | 35 | 35 | 35 | 8 | 12 | 65 | 105 | 160 | 160 | 166 | 178 | 140 | 122 |  | 191 | 191 | 192 | 200 | 200 | 200 | 200 | 3194400
112 | Aurahati 100MW PP (Aggreko) | [14 empty] | 30 | 30 |  |  |  | 98 | 98 | 70 | 70 | 25 |  |  | 424966
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 149 | 114 | 96 | 85 | 85 | 85 | 88 | 109 | 115 | 127 | 132 | 130 | 130 | 144 | 140 | 131 | 149 |  | 140 | 140 | 140 | 149 | 149 | 149 | 149 | 3070368
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 | 100 | 90 | 100 | 100 | 90 | 90 | 100 | 90 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2256960
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 155 | 120 | 120 | 120 | 135 | 200 | 200 | 200 | 200 | 200 | 200 | 150 | 154 |  | 192 | 200 | 200 | 200 | 200 | 200 | 200 | 4390080
117 | Ashuganj 150MW PP (Midland) | 132 | 137 | 137 | 137 | 137 | 138 | 137 | 138 | 130 | 127 | 125 | 123 | 123 | 123 | 122 | 118 | 117 | 127 |  | 128 | 140 | 137 | 140 | 140 | 142 | 138 | 3164786
118 | Bibiyana-III 400 MW CCPP | 318 | 318 | 327 | 328 | 328 | 328 | 327 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 328 |  | 328 | 328 | 328 | 328 | 328 | 328 | 328 | 7851000
| Jamalpur 115 MW PP (United) | 89 | 89 | 89 | 55 | 55 | 55 | 55 | 55 | 51 | 78 | 112 | 115 | 115 | 108 | 108 | 108 | 115 | 101 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2256000
| Anwara 300 MW PP (United) | 304 | 304 | 304 | 304 | 304 | 124 | 87 | 87 | 88 | 122 | 157 | 140 | 140 | 140 | 142 | 290 | 304 | 232 |  | 304 | 304 | 304 | 304 | 304 | 304 | 304 | 5427164
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 60 | 20 | 25 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 90 | 100 | 2218560
| Anlima Energy Ltd. | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 97 | 97 | 97 | 96 | 96 | 96 | 109 | 101 |  | 114 | 114 | 101 | 114 | 114 | 114 | 114 | 2608200
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 444240
| Spectra Solar Plant Ltd. | [6 empty] | 3 | 6 | 18 | 25 | 34 | 34 | 17 | 18 | 23 | 9 | 4 | [9 empty] | 178432
120 | Eastern Zone Total | 8148 | 7730 | 7715 | 7312 | 7207 | 6688 | 6513 | 6473 | 6748 | 7114 | 7544 | 7789 | 7971 | 7969 | 8260 | 8141 | 7721 | 7693 |  | 8993 | 8984 | 8963 | 8970 | 8741 | 8689 | 8541 | 189747762
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 16 | 0 | [11 empty] | 4 | 4 | 4 | 4 | 8 |  | 27 | 27 | 27 | 21 | 21 | 21 |  | 144480
| Khulna 225 MW CCPP | 230 | 170 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 | 180 | 222 | 220 | 224 | 224 | 226 |  | 230 | 230 | 227 | 230 | 230 | 210 | 200 | 4335360
129 | Rupsha 105 MW PP (Orion rupsha) | 102 | 102 | 102 | 102 | 70 | 17 | 17 | 17 | 17 | 17 | 30 | 102 | 102 | 102 | 102 | 102 | 70 | 70 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1862400
130
131
132 | United Payra Power Ltd. | [19 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 108000
133 | Bhola Nutan Biddut BD LTD (GAS) | 223 | 223 | 223 | 223 | 224 | 190 | 180 | 180 | 180 | 180 | 180 | 220 | 221 | 221 | 217 | 208 | 180 | 150 |  | 221 | 221 | 222 | 223 | 223 | 223 | 223 | 5029473
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 22 | 12 | 12 | 12 | 12 | 12 | 11 | 11 | 11 | 11 | 11 | 13 | 22 | 22 | 22 | 23 | 23 | 22 |  | 22 | 22 | 22 | 22 | 22 | 12 | 12 | 400635
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2118761
140 | Bhola 33 MW PP (Venture) | 34 | 32 | 31 | 29 | 29 | 27 | 23 | 21 | 20 | 20 | 21 | 21 | 23 | 23 | 24 | 23 | 20 | 22 |  | 31 | 32 | 34 | 34 | 34 | 34 | 33 | 642241
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 77 | 100 | 100 | 100 | 20 |  |  | 347520
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 714 | 714 | 714 | 714 | 715 | 715 | 715 | 715 | 715 | 714 | 710 | 710 | 710 | 710 | 710 | 710 | 710 | 710 |  | 709 | 709 | 709 | 709 | 709 | 710 | 710 | 17195636
147 | Bheramara 410 MW CCPP | 310 | 320 | 325 | 330 | 340 | 345 | 350 | 355 | 350 | 350 | 345 | 330 | 330 | 330 | 325 | 320 | 325 | 330 |  | 330 | 330 | 320 | 325 | 325 | 320 | 320 | 8163936
148 | Payra 1320 MW | 510 | 500 | 490 | 470 | 430 | 400 | 400 | 380 | 360 | 360 | 350 | 360 | 370 | 380 | 400 | 400 | 400 | 420 |  | 550 | 580 | 590 | 590 | 590 | 570 | 570 | 11829900
149
150 | Barapukuria TPP Unit-1 | 75 | 76 | 77 | 75 | 75 | 75 | 75 | 76 | 75 | 73 | 75 | 75 | 75 | 75 | 76 | 76 | 75 | 74 |  | 76 | 78 | 78 | 76 | 76 | 77 | 79 | 1796509
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | 0 | [13 empty] | 40 | 43 | 43 |  | 43 | 43 | 43 | 50 | 50 | 43 | 43 | 427088
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 0 | 1 | 3 | 3 | 3 | 2 | 1 | 4 | 1 | 0 | [9 empty] | 25680
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 186 | 194 | 194 | 196 | 197 | 197 | 198 | 206 | 178 | 175 | 178 | 183 | 181 | 172 | 186 | 177 | 167 | 176 |  | 201 | 202 | 201 | 197 | 196 | 196 | 194 | 4749618
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 212 | 213 | 211 | 215 | 215 | 215 | 215 | 194 | 172 | 192 | 210 | 206 | 204 | 205 | 192 | 170 | 204 | 140 |  | 199 | 210 | 207 | 205 | 208 | 214 | 207 | 5156000
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 360 | 370 | 365 | 320 | 310 | 320 | 344 | 333 | 327 | 405 | 410 | 415 | 417 | 414 | 414 | 386 | 337 | 368 |  | 398 | 397 | 414 | 416 | 418 | 399 | 406 | 9236000
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 31 | 0 | [15 empty] | 5 |  | 18 | 31 | 33 | 32 | 32 | 31 | 31 | 196729
162 | Bogra 22 MW PP (GBB) | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 18 | 17 | 21 | 21 | 17 | 20 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 484080
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 5 | 5 | 8 | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 5 | 5 | 5 | 5 | 212346
165 | Amnura 50 MW PP(Sinha) | 27 | 0 | [15 empty] | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 | 27 | 231990
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 224096
167 | Katakhali 50 MW Peaking PP
168 | Santahar 50 MW Peaking PP | 19 | 0 | [15 empty] | 18 |  | 31 | 31 | 31 | 31 | 27 | 27 | 27 | 208024
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 52 | 8 | 10 | 43 | 43 | 43 | 43 | 0 | 0 | 0 | 52 | 52 | 52 |  | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 980160
170 | Chapainawabganj 100 MW Peaking PP | 92 | 0 | [15 empty] | 51 |  | 94 | 94 | 94 | 94 | 94 | 94 | 94 | 711968
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 35 | 35 | 35 | 35 | 57 | 94 | 94 | 94 | 94 | 94 | 113 | 113 | 50 |  | 110 | 113 | 113 | 113 | 113 | 113 | 113 | 2167200
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 100 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 70 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2502048
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [11 empty] | 0 |  | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 113 | 113 | 106 | 70 | 71 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 34 | 60 |  | 107 | 113 | 113 | 106 | 112 | 113 | 113 | 2514432
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 4 | 5 | 1 | 1 | 1 | 2 | 2 | 2 | [9 empty] | 28907
178
178