## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-22 | Wednesday
|  |  | Date (day): | 2021-09-22 |  | Wednesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13994.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14842 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-21 | 2021-09-22 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 215 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 399 | 395 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 153 | 141 | 250 | 300 | 60 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 260 | 300 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 43 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 0 | 50 | 60 | 60 |  | 40 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 326 | 325 | 330 | 5 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 102 | 100 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 35 | 35 | 35 |  | 19 | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 0 | 100 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 35 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 55 | 55 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 51 | 42 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 25 | 51 | 25 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 281 | 280 | 280 |  | 20 | Engine problem
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 17 | 105 | 52 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 90 | 86 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 144 | 144 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 14 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2623 | 3174 | 3576 | 3927 | 902 | 849
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 120 | 120 | 120 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 20 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 18 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 0 | 44 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 169 | 166 | 168 | 168 | 62 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 85 | 0 | 85 |  | 17 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 7 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 76 | 90 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 20 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 3 | 5 | 13 | 20
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 85 | 80 | 88 | 88 |  | 20 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 286 | 304 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 0 | 43 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 96 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 96 | 104 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1175 | 1497 | 1494 | 1562 | 122 | 690
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 210 | 211 | 210 | 210 | 11 |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 320 | 330 | 30 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 280 | 280 | 310 | 320 | 40 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 20 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 55 | 55 | 55
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 8 | 8 | 36 | 36 | 159 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 118 | 127 | 135 | 145 |  | 5 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 0 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 141 | 137 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 178 | 170 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 116 | 144 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 0 | 45 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 17 | 20 | 21 | 21
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 98 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 94 | 94 | 95 | 96 |  | 17 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1705 | 1831 | 2125 | 2282 | 638 | 112
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 102 | 122 | 120 | 140 | 62 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 17 | 19 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 1 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 108 | 165 | 175 | 200
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 25 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 22 | 21 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 390 | 442 | 513.6 | 507 | 62 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 130 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 161 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 44 | 50 | 51 | 51
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 0 | 0 | 0 | 0 | 66 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 78 | 81 | 78 | 78
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 220 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 0 | 18 |  | Gas shortage
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 280 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1626 | 1661 | 1727 | 1727 | 411 | 217
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 716 | 715 | 729 | 729
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 26 | 0 | 27 |  | 27 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 180 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 300 | 400 | 400 | 400 | 10 |  | Gas shortage
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 40 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 85 | 90 | 105 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1221 | 1451 | 1609 | 1726 | 10 | 96
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 17 | 29 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 15 | 87 | 87 | 87 |  | 107 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 63 | 22 | 22 | 22 | 73 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 330 | 470 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 224 | 218 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 17 | 150 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 649 | 843 | 1244 | 1244 | 73 | 107
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 30 | 30 | 30 |  | 41 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 0 | 27 | 27 | 23 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 16 | 0 | 30 |  | 20 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 185 | 198 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 186 | 183 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 320 | 387 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 34 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 21 | 22 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 52 | 34 | 43 | 43 |  | 9 | Engine problem
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 113 | 96 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113 |  | 0 | Engine problem
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 3 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1001 | 1311 | 1505 | 1649 | 403 | 104
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 80 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 34 | 113 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 121 | 193 | 201 | 218 | 0 | 374
|  | Total |  |  |  |  | 22031 | 21180 | 10511 | 12403 | 13994.6 | 14842 | 2621 | 2636
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 9986.4152 | 11783.989 | 13296.1551 | 14101.263
| A. |  | 2021-09-21 | (Yesterday) |  |  |  |  | Tuesday
| 1 | Highest Generation : |  |  | 12523 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9046 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12403 | MW
| 3 | Day peak Generation : |  |  | 10511 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 11898 | MW
| 4 | Evening peak Generation : |  |  | 12523 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 260.3906 | MKWHr | By Solar | 0.60371 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 147.4129 | MKWHr |  | By Oil: | 75.8607 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 12.3765 | MKWHr |  | By Hydro: | 3.9294 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2621 | MW | Dhaka | 4452 | 4452 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2636 | MW | Chittagong | 1202 | 1202 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5257 | MW | Khulna | 1373 | 1373 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1118.01 | MMCFD |  |  | Rajshahi | 1200 | 1200 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 148407847.968 | ii) Oil : | Taka | 543817626.67 | Comilla | 1116 | 1116 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 57493006.46 | Total | Taka | 749718481.098 | Mymensingh | 979 | 979 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 0.7645 | MKWHr. | Sylhet | 516 | 516 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 28 | MW (E to W) at | 19:00 | hrs | Barisal | 325 | 325 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -230 | MW at | 5:00 | hrs | Rangpur | 735 | 735 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 32.7° C |  |  | Total | 11898 | 11898 |  | 0
| B. |  | 2021-09-22 | (Today) |  |  |  | Wednesday |  |  | Probable max. temperature in Dhaka |  |  | 33.5° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14842 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1642 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 274.4674 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9183 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.312 | MKWHr. | ii) HVDC Flow at Peak Time |  | 715 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 2.8954 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 20:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.59 |  | (b) Today: | 106.68 |  | (c) Rule Curve: |  | 103.84
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-21
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 263 |  | 0 | 280 | 272 | 0 | 0 | 45 | 334 | 0 | 0 | 0 | 24 | 84 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 0 | 25 | 30 | 33 | 33 | 0 | 0 | 92 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 34 | 0 | 86 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 280 | 202 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 126 | 132 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 163 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 260 | 0 | 0 | 188 | 0 | 134 | 0 | 90 | 200 | 133 | 315 | 115 | 52 | 100 | 0 | 305 | 0 | 95 | 114 | 90 | 100 | 321 | 94 | 0 | 144 | 114 | 0 | 17 | 0 |  | 716 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 22 | 0 | 185 | 0 | 392 | 35 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 470 | 210 | 0 | 0 | 0 |  | 8055 | 3295 | 11350 | 4372 | 716 | 1910 | 3272 | 549 | 167 | 238 | 126 | 0 | 0 | 106.56
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 272 |  | 0 | 280 | 254 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 7 | 48 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 91 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 34 | 0 | 80 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 280 | 201 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 124 | 134 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 0 | 230 | 0 | 0 | 188 | 0 | 134 | 0 | 90 | 200 | 120 | 316 | 115 | 52 | 97 | 0 | 205 | 0 | 107 | 66 | 95 | 100 | 320 | 60 | 0 | 126 | 114 | 0 | 17 | 0 |  | 715 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 22 | 0 | 185 | 0 | 405 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 460 | 214 | 0 | 0 | 0 |  | 7741 | 3272 | 11013 | 4400 | 715 | 1925 | 2942 | 539 | 166 | 202 | 124 | 0 | 0 | 106.57
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 291 |  | 0 | 280 | 263 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 34 | 0 | 82 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 280 | 201 | 8 | 142 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 135 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 161 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 275 | 24 | 11 | 0 | 230 | 0 | 0 | 187 | 0 | 134 | 0 | 90 | 187 | 127 | 316 | 115 | 52 | 91 | 0 | 167 | 0 | 110 | 4 | 95 | 80 | 321 | 0 | 0 | 90 | 114 | 0 | 17 | 0 |  | 715 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 22 | 0 | 185 | 0 | 395 | 0 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 430 | 211 | 0 | 0 | 0 |  | 7498 | 3229 | 10727 | 4405 | 715 | 1925 | 2720 | 509 | 163 | 170 | 120 | 0 | 0 | 106.57
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 396 | 307 |  | 0 | 280 | 263 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 30 | 33 | 33 | 0 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 19 | 0 | 86 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 280 | 201 | 8 | 140 | 23 | 57 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 120 | 147 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 160 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 230 | 0 | 0 | 187 | 0 | 124 | 0 | 90 | 155 | 127 | 315 | 115 | 52 | 101 | 0 | 106 | 0 | 105 | 0 | 95 | 50 | 320 | 0 | 0 | 90 | 114 | 0 | 17 | 0 |  | 716 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 22 | 0 | 185 | 0 | 364 | 0 | 0 | 35 | 0 | 74 | 0 | 0 | 113 | 400 | 215 | 0 | 0 | 0 |  | 7394 | 3059 | 10453 | 4416 | 716 | 1929 | 2475 | 479 | 163 | 155 | 120 | 0 | 0 | 106.58
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 397 | 317 |  | 0 | 280 | 275 | 0 | 0 | 55 | 336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 86 | 0 | 21 | 39 | 0 | 0 | 0 | 280 | 280 | 201 | 8 | 138 | 23 | 57 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 114 | 147 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 148 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 195 | 0 | 0 | 188 | 0 | 122 | 0 | 90 | 155 | 128 | 315 | 115 | 52 | 96 | 0 | 105 | 0 | 110 | 0 | 96 | 50 | 320 | 0 | 0 | 90 | 114 | 0 | 17 | 0 |  | 715 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 22 | 0 | 182 | 0 | 325 | 0 | 0 | 0 | 0 | 70 | 0 | 0 | 35 | 390 | 224 | 0 | 0 | 0 |  | 7310 | 2891 | 10201 | 4392 | 715 | 1910 | 2318 | 469 | 163 | 120 | 114 | 0 | 0 | 106.58
6:00 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 366 | 317 |  | 0 | 280 | 257 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 22 | 25 | 27 | 33 | 33 | 0 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 0 | 86 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 280 | 203 | 8 | 138 | 23 | 57 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 110 | 147 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 130 | 155 | 0 | 81 | 0 | 192 | 0 | 0 | 0 | 270 | 24 | 11 | 0 | 195 | 0 | 0 | 100 | 0 | 115 | 1 | 60 | 136 | 50 | 315 | 115 | 17 | 93 | 0 | 105 | 0 | 110 | 0 | 89 | 50 | 320 | 0 | 0 | 54 | 114 | 0 | 17 | 0 |  | 716 | 0 | 385 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 22 | 0 | 177 | 0 | 325 | 0 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 370 | 203 | 0 | 0 | 0 |  | 6860 | 2719 | 9579 | 4265 | 716 | 1866 | 1888 | 449 | 164 | 120 | 110 | 1 | 0 | 106.59
7:00 | 0 | 0 | 0 | 0 | 210 | 0 | 0 | 352 | 251 |  | 0 | 280 | 294 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 27 | 33 | 33 | 0 | 0 | 90 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 86 | 0 | 21 | 37 | 0 | 0 | 0 | 280 | 280 | 205 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 21 | 96 | 136 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 110 | 156 | 0 | 20 | 0 | 165 | 0 | 0 | 0 | 275 | 24 | 11 | 0 | 195 | 0 | 0 | 40 | 0 | 100 | 5 | 60 | 100 | 50 | 315 | 115 | 0 | 105 | 1 | 69 | 0 | 110 | 0 | 96 | 20 | 320 | 0 | 8 | 35 | 114 | 0 | 17 | 3 |  | 715 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 160 | 0 | 22 | 0 | 180 | 0 | 353 | 0 | 0 | 0 | 0 | 35 | 0 | 1 | 0 | 350 | 202 | 0 | 0 | 0 |  | 6408 | 2638 | 9046 | 4036 | 715 | 1746 | 1721 | 429 | 165 | 120 | 96 | 18 | 0 | 106.59
8:00 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 364 | 191 |  | 0 | 280 | 270 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 25 | 27 | 33 | 33 | 5 | 0 | 91 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 86 | 0 | 21 | 8 | 0 | 0 | 0 | 280 | 280 | 199 | 8 | 140 | 23 | 57 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 18 | 96 | 117 | 0 | 19 | 1 | 43 | 0 | 44 | 0 | 130 | 154 | 0 | 20 | 0 | 205 | 0 | 0 | 0 | 300 | 24 | 11 | 0 | 200 | 0 | 0 | 65 | 0 | 114 | 7 | 76 | 100 | 68 | 316 | 115 | 4 | 93 | 2 | 70 | 0 | 105 | 0 | 95 | 20 | 320 | 2 | 15 | 60 | 114 | 0 | 17 | 12 |  | 716 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 60 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 22 | 0 | 179 | 0 | 373 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 35 | 330 | 201 | 0 | 0 | 1 |  | 6379 | 2703 | 9082 | 4013 | 716 | 1716 | 1806 | 409 | 166 | 120 | 96 | 40 | 0 | 106.6
9:00 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 397 | 167 |  | 0 | 280 | 240 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 21 | 25 | 27 | 33 | 33 | 25 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 86 | 0 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 196 | 8 | 140 | 20 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 102 | 105 | 0 | 19 | 1 | 43 | 0 | 44 | 0 | 163 | 155 | 0 | 20 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 260 | 0 | 0 | 100 | 0 | 141 | 12 | 76 | 100 | 112 | 316 | 115 | 17 | 94 | 3 | 140 | 0 | 94 | 0 | 96 | 90 | 321 | 17 | 27 | 90 | 114 | 0 | 17 | 21 |  | 716 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 28 | 0 | 191 | 0 | 374 | 0 | 0 | 6 | 0 | 34 | 0 | 4 | 100 | 330 | 193 | 0 | 0 | 1 |  | 6803 | 2822 | 9625 | 4047 | 716 | 1707 | 2288 | 408 | 168 | 120 | 102 | 69 | 0 | 106.6
10:00 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 397 | 164 |  | 0 | 280 | 260 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 17 | 21 | 25 | 27 | 33 | 33 | 25 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 17 | 0 | 0 | 0 | 86 | 0 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 205 | 8 | 140 | 23 | 56 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 17 | 106 | 105 | 0 | 19 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 0 | 20 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 273 | 0 | 0 | 100 | 0 | 142 | 19 | 76 | 108 | 120 | 316 | 115 | 17 | 96 | 4 | 196 | 0 | 95 | 17 | 96 | 90 | 320 | 28 | 29 | 120 | 114 | 0 | 17 | 7 |  | 716 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 75 | 0 | 195 | 0 | 322 | 10 | 0 | 50 | 0 | 34 | 0 | 4 | 100 | 320 | 223 | 0 | 0 | 1 |  | 7082 | 2853 | 9935 | 4024 | 716 | 1696 | 2642 | 399 | 168 | 120 | 106 | 64 | 0 | 106.61
11:00 | 0 | 0 | 0 | 0 | 160 | 0 | 0 | 398 | 159 |  | 0 | 280 | 265 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 30 | 21 | 25 | 22 | 33 | 33 | 25 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 13 | 0 | 0 | 0 | 86 | 0 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 140 | 20 | 55 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 110 | 104 | 0 | 0 | 1 | 43 | 0 | 44 | 0 | 130 | 161 | 0 | 20 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 275 | 0 | 0 | 100 | 0 | 149 | 20 | 76 | 155 | 118 | 316 | 115 | 17 | 93 | 4 | 266 | 0 | 94 | 80 | 88 | 90 | 320 | 88 | 48 | 135 | 97 | 0 | 17 | 17 |  | 716 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 81 | 0 | 198 | 0 | 331 | 53 | 0 | 113 | 0 | 34 | 0 | 6 | 113 | 330 | 223 | 0 | 0 | 2 |  | 7288 | 2999 | 10287 | 3976 | 716 | 1697 | 2993 | 409 | 168 | 120 | 110 | 98 | 0 | 106.61
12:00 | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 399 | 153 |  | 0 | 280 | 260 | 0 | 0 | 43 | 250 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 21 | 25 | 26 | 33 | 33 | 25 | 0 | 94 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 7 | 85 | 0 | 21 | 3 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 141 | 20 | 52 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 116 | 102 | 0 | 17 | 1 | 43 | 0 | 44 | 0 | 130 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 0 | 275 | 0 | 0 | 108 | 0 | 149 | 18 | 76 | 178 | 118 | 316 | 115 | 17 | 105 | 3 | 286 | 0 | 96 | 98 | 94 | 90 | 320 | 90 | 25 | 144 | 96 | 0 | 17 | 14 |  | 716 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 63 | 0 | 186 | 0 | 320 | 85 | 0 | 113 | 0 | 34 | 0 | 7 | 113 | 330 | 224 | 0 | 0 | 3 |  | 7519 | 2992 | 10511 | 4039 | 716 | 1708 | 3162 | 410 | 169 | 120 | 116 | 71 | 0 | 106.62
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 400 | 152 |  | 0 | 280 | 240 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 85 | 0 | 5 | 0 | 0 | 0 | 17 | 35 | 55 | 0 | 25 | 26 | 33 | 33 | 23 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 80 | 18 | 21 | 6 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 139 | 23 | 51 | 0 | 43 | 0 | 0 | 4 | 22 | 8 | 33 | 21 | 118 | 100 | 0 | 19 | 2 | 43 | 0 | 47 | 0 | 130 | 161 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 278 | 56 | 0 | 148 | 0 | 149 | 19 | 76 | 200 | 118 | 315 | 115 | 29 | 98 | 3 | 275 | 8 | 96 | 98 | 87 | 100 | 320 | 90 | 27 | 144 | 96 | 0 | 17 | 20 |  | 715 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 22 | 0 | 189 | 0 | 295 | 90 | 0 | 113 | 0 | 113 | 0 | 7 | 113 | 330 | 201 | 0 | 0 | 5 |  | 7818 | 3063 | 10881 | 4212 | 715 | 1647 | 3408 | 410 | 168 | 120 | 118 | 83 | 0 | 106.62
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 331 | 152 |  | 0 | 280 | 265 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 94 | 0 | 37 | 0 | 0 | 0 | 17 | 35 | 55 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 10 | 80 | 41 | 21 | 5 | 0 | 0 | 0 | 280 | 280 | 183 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 126 | 99 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 110 | 161 | 0 | 81 | 0 | 166 | 0 | 0 | 0 | 270 | 24 | 11 | 0 | 278 | 165 | 0 | 80 | 100 | 149 | 18 | 76 | 155 | 122 | 316 | 115 | 52 | 105 | 3 | 125 | 17 | 96 | 17 | 94 | 60 | 320 | 92 | 41 | 144 | 96 | 0 | 17 | 19 |  | 715 | 0 | 250 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 82 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 0 | 22 | 0 | 156 | 0 | 337 | 17 | 0 | 35 | 0 | 34 | 0 | 7 | 113 | 290 | 182 | 0 | 0 | 0 |  | 7640 | 2712 | 10352 | 3988 | 715 | 1630 | 3150 | 370 | 164 | 120 | 126 | 89 | 0 | 106.63
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 152 |  | 0 | 280 | 240 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 102 | 0 | 40 | 0 | 0 | 0 | 17 | 35 | 55 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 20 | 0 | 0 | 10 | 80 | 50 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 179 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 21 | 126 | 103 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 163 | 161 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 273 | 0 | 0 | 80 | 0 | 149 | 12 | 76 | 155 | 122 | 316 | 115 | 52 | 105 | 1 | 178 | 17 | 94 | 17 | 92 | 100 | 320 | 94 | 21 | 144 | 96 | 0 | 17 | 13 |  | 715 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 81 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 20 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 22 | 0 | 177 | 0 | 296 | 17 | 0 | 35 | 0 | 34 | 0 | 6 | 113 | 330 | 211 | 0 | 0 | 0 |  | 7642 | 2926 | 10568 | 4319 | 715 | 1695 | 2964 | 411 | 164 | 120 | 126 | 54 | 0 | 106.63
16:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 153 |  | 0 | 280 | 275 | 0 | 0 | 55 | 336 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 10 | 84 | 19 | 21 | 3 | 0 | 0 | 0 | 330 | 280 | 179 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 122 | 103 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 163 | 158 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 273 | 0 | 0 | 40 | 0 | 149 | 9 | 76 | 52 | 117 | 316 | 115 | 52 | 105 | 0 | 178 | 17 | 94 | 17 | 90 | 100 | 320 | 36 | 8 | 144 | 96 | 0 | 17 | 3 |  | 715 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 22 | 0 | 189 | 0 | 307 | 17 | 0 | 35 | 0 | 34 | 0 | 3 | 50 | 350 | 221 | 0 | 0 | 0 |  | 7428 | 2918 | 10346 | 4429 | 715 | 1710 | 2628 | 431 | 164 | 124 | 122 | 23 | 0 | 106.64
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 148 |  | 0 | 280 | 250 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 102 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 55 | 21 | 25 | 28 | 33 | 33 | 25 | 0 | 89 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 5 | 0 | 0 | 10 | 84 | 19 | 21 | 7 | 0 | 0 | 0 | 280 | 280 | 179 | 8 | 139 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 8 | 33 | 20 | 114 | 103 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 0 | 275 | 0 | 0 | 40 | 0 | 149 | 2 | 30 | 52 | 123 | 316 | 115 | 52 | 105 | 0 | 106 | 17 | 94 | 17 | 95 | 50 | 320 | 36 | 4 | 144 | 106 | 0 | 17 | 1 |  | 715 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 24 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 0 | 21 | 0 | 192 | 0 | 365 | 17 | 0 | 35 | 0 | 34 | 0 | 0 | 50 | 350 | 182 | 0 | 0 | 0 |  | 7202 | 2915 | 10117 | 4387 | 715 | 1741 | 2430 | 430 | 164 | 129 | 114 | 7 | 0 | 106.64
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 362 | 143 |  | 0 | 280 | 300 | 0 | 0 | 55 | 260 | 0 | 0 | 0 | 102 | 35 | 13 | 0 | 0 | 0 | 35 | 35 | 55 | 21 | 25 | 17 | 33 | 33 | 32 | 0 | 89 | 75 | 120 | 0 | 4 | 0 | 0 | 0 | 0 |  | 6 | 0 | 82 | 20 | 77 | 19 | 21 | 2 | 0 | 0 | 0 | 280 | 280 | 208 | 8 | 141 | 23 | 55 | 0 | 43 | 0 | 36 | 8 | 22 | 5 | 33 | 20 | 132 | 113 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 159 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 300 | 16 | 11 | 0 | 281 | 0 | 50 | 74 | 0 | 149 | 0 | 76 | 57 | 120 | 316 | 115 | 60 | 105 | 0 | 178 | 17 | 94 | 22 | 94 | 60 | 321 | 38 | 0 | 144 | 95 | 0 | 17 | 0 |  | 716 | 0 | 380 | 0 | 0 | 120 | 0 | 0 | 11 | 0 | 0 | 87 | 28 | 0 | 0 | 0 | 0 | 14 | 5 | 29 | 0 | 0 | 8 | 24 | 15 | 22 | 0 | 11 | 79 | 0 | 0 | 16 | 0 | 0 | 0 | 187 | 0 | 22 | 0 | 190 | 0 | 356 | 17 | 0 | 36 | 0 | 75 | 0 | 0 | 90 | 350 | 183 | 0 | 0 | 0 |  | 7613 | 3071 | 10684 | 4287 | 716 | 1736 | 2849 | 429 | 164 | 371 | 132 | 0 | 0 | 106.65
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 141 |  | 0 | 280 | 300 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 102 | 100 | 50 | 0 | 0 | 0 | 35 | 55 | 55 | 21 | 25 | 17 | 33 | 33 | 51 | 0 | 91 | 75 | 120 |  | 20 | 0 | 0 | 0 | 0 |  | 21 | 0 | 85 | 100 | 80 | 44 | 21 | 5 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 137 | 23 | 55 | 0 | 43 | 0 | 0 | 45 | 22 | 8 | 33 | 20 | 144 | 122 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 161 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 281 | 0 | 0 | 165 | 25 | 149 | 0 | 90 | 170 | 127 | 316 | 115 | 105 | 105 | 0 | 304 | 43 | 110 | 114 | 94 | 100 | 320 | 86 | 0 | 144 | 104 | 0 | 17 | 0 |  | 715 | 0 | 400 | 0 | 0 | 180 | 0 | 0 | 26 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 0 | 43 | 16 | 34 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 22 | 40 | 183 | 0 | 387 | 90 | 0 | 96 | 0 | 113 | 0 | 0 | 113 | 470 | 218 | 0 | 17 | 0 |  | 8725 | 3798 | 12523 | 4542 | 715 | 1784 | 4007 | 550 | 166 | 615 | 144 | 0 | 0 | 106.66
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 143 |  | 0 | 280 | 310 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 74 | 150 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 21 | 25 | 20 | 33 | 33 | 51 | 0 | 91 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 77 | 19 | 21 | 9 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 146 | 123 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 159 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 310 | 16 | 11 | 0 | 281 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 200 | 128 | 316 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 114 | 95 | 100 | 321 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 719 | 0 | 395 | 0 | 0 | 180 | 0 | 0 | 25 | 0 | 0 | 88 | 29 | 0 | 0 | 0 | 0 | 25 | 0 | 47 | 0 | 43 | 0 | 52 | 33 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 22 | 0 | 185 | 0 | 416 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 224 | 0 | 17 | 0 |  | 8536 | 3737 | 12273 | 4426 | 719 | 1855 | 3871 | 579 | 166 | 511 | 146 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 142 |  | 0 | 280 | 300 | 0 | 0 | 55 | 331 | 0 | 0 | 0 | 74 | 150 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 21 | 25 | 20 | 33 | 33 | 51 | 0 | 91 | 75 | 120 | 0 | 8 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 77 | 19 | 21 | 20 | 0 | 0 | 0 | 280 | 280 | 209 | 8 | 139 | 23 | 55 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 146 | 136 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 16 | 11 | 0 | 281 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 200 | 128 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 94 | 100 | 320 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 720 | 0 | 390 | 0 | 0 | 180 | 0 | 0 | 25 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 25 | 0 | 47 | 0 | 43 | 0 | 52 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 22 | 0 | 189 | 0 | 419 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 500 | 224 | 0 | 0 | 0 |  | 8533 | 3723 | 12256 | 4441 | 720 | 1848 | 3844 | 580 | 166 | 511 | 146 | 0 | 0 | 106.66
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 141 |  | 0 | 280 | 290 | 0 | 0 | 55 | 335 | 0 | 0 | 0 | 74 | 150 | 10 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 51 | 0 | 92 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 50 | 86 | 0 | 21 | 16 | 0 | 0 | 0 | 280 | 310 | 212 | 8 | 137 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 22 | 8 | 33 | 20 | 142 | 136 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 162 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 290 | 24 | 11 | 0 | 281 | 0 | 0 | 171 | 0 | 149 | 0 | 90 | 200 | 128 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 719 | 0 | 390 | 0 | 0 | 180 | 0 | 0 | 25 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 43 | 0 | 52 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 22 | 0 | 186 | 0 | 399 | 90 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 223 | 0 | 0 | 0 |  | 8550 | 3692 | 12242 | 4489 | 719 | 1823 | 3817 | 600 | 167 | 485 | 142 | 0 | 0 | 106.66
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 142 |  | 0 | 280 | 290 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 16 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 86 | 0 | 21 | 37 | 0 | 0 | 0 | 280 | 320 | 205 | 8 | 139 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 142 | 135 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 161 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 285 | 24 | 11 | 0 | 281 | 0 | 0 | 181 | 0 | 149 | 0 | 90 | 200 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 720 | 0 | 380 | 0 | 0 | 180 | 0 | 0 | 9 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 15 | 0 | 184 | 0 | 405 | 89 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 540 | 223 | 0 | 0 | 0 |  | 8344 | 3604 | 11948 | 4480 | 720 | 1839 | 3644 | 620 | 168 | 335 | 142 | 0 | 0 | 106.67
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 161 |  | 0 | 280 | 285 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 24 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 29 | 33 | 33 | 16 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 86 | 0 | 21 | 37 | 0 | 0 | 0 | 280 | 320 | 197 | 8 | 142 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 138 | 133 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 155 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 300 | 24 | 11 | 0 | 281 | 0 | 0 | 180 | 0 | 149 | 0 | 87 | 200 | 132 | 316 | 115 | 105 | 105 | 0 | 305 | 17 | 110 | 114 | 91 | 100 | 320 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 720 | 0 | 375 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 87 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 15 | 0 | 193 | 0 | 420 | 89 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 510 | 220 | 0 | 0 | 0 |  | 8301 | 3490 | 11791 | 4468 | 720 | 1886 | 3541 | 591 | 168 | 279 | 138 | 0 | 0 | 106.67
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 187 |  | 0 | 280 | 250 | 0 | 0 | 55 | 334 | 0 | 0 | 0 | 32 | 48 | 0 | 0 | 0 | 0 | 17 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 16 | 0 | 93 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 51 | 10 | 86 | 0 | 21 | 38 | 0 | 0 | 0 | 280 | 320 | 190 | 8 | 138 | 23 | 56 | 0 | 43 | 0 | 0 | 25 | 22 | 11 | 33 | 20 | 122 | 131 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 156 | 0 | 80 | 0 | 220 | 0 | 0 | 0 | 285 | 24 | 11 | 0 | 281 | 0 | 0 | 189 | 0 | 149 | 0 | 87 | 200 | 133 | 316 | 115 | 105 | 105 | 0 | 305 | 17 | 110 | 114 | 58 | 100 | 320 | 94 | 0 | 144 | 108 | 0 | 17 | 0 |  | 720 | 0 | 375 | 0 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 87 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 12 | 0 | 190 | 0 | 400 | 89 | 0 | 113 | 0 | 70 | 0 | 0 | 113 | 480 | 220 | 0 | 0 | 0 |  | 8236 | 3425 | 11661 | 4446 | 720 | 1874 | 3491 | 561 | 168 | 279 | 122 | 0 | 0 | 106.68
KWH | 0 | 0 | 0 | 0 | 6559545 | 0 | 0 | 9385980 | 4690000 |  | 0 | 6716000 | 6548393 | 0 | 0 | 1303120 | 7363558 | 0 | 0 | 0 | 1127808 | 743040 | 186184 | 0 | 0 | 0 | 514440 | 637501 | 783500 | 397152 | 600000 | 647460 | 820200 | 830400 | 498720 | 0 | 2105400 | 1824000 | 2900000 | 0 | 46141 | 0 | 0 | 0 | 0 |  | 381120 | 0 | 506435 | 331680 | 2006400 | 264960 | 490512 | 454080 | 0 | 0 | 0 | 7068400 | 7011000 | 4888000 | 217454 | 3342420 | 494136 | 1321920 | 0 | 999756 | 0 | 49240 | 255274 | 462312 | 238140 | 797200 | 506750 | 2895360 | 2835440 | 0 | 410976 | 9450 | 1025000 | 0 | 1147200 | 0 | 3487009 | 3679000 | 0 | 1654080 | 0 | 5157670 | 0 | 0 | 0 | 7120500 | 524784 | 264000 | 21504 | 6225052 | 245730 | 27063 | 3223200 | 141474 | 3387888 | 138240 | 1836480 | 3758880 | 2838618 | 7582000 | 2772000 | 1357200 | 2442181 | 22469 | 4885200 | 392401 | 2495698 | 1271100 | 2228520 | 1882560 | 7668600 | 1385280 | 240270 | 2999520 | 2573073 | 0 | 443520 | 132693 |  | 17312000 | 0 | 8877024 | 0 | 0 | 2378880 | 0 | 0 | 97920 | 0 | 0 | 1527046 | 546159 | 0 | 0 | 0 | 0 | 86624 | 30018 | 242000 | 0 | 104198 | 11894 | 1104480 | 109611 | 495120 | 0 | 247104 | 1926982 | 0 | 0 | 0 | 0 | 0 | 0 | 4572064 | 0 | 688963 | 78720 | 4724564 | 0 | 8842036 | 980640 | 0 | 1763136 | 0 | 1698364 | 0 | 43543 | 2116512 | 10449500 | 5134227 | 0 | 39600 | 17040 |  | 184144614 | 76245969 | 260390583 | 103898437 | 17312000 | 43514504 | 71605033 | 12376482 | 3929400 | 4255662 | 2895360 | 603705 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 7281094.95 | 0 | 0 | 9479839.8 | 4830700 |  | 0 | 7320440 | 7268716.23 | 0 | 0 | 11024395.2 | 7658100.32 | 0 | 0 | 0 | 10285608.96 | 7311513.6 | 1716616.48 | 0 | 0 | 0 | 3755412 | 4927882.73 | 7725310 | 297864 | 450000 | 0 | 0 | 0 | 4822622.4 | 0 | 568458 | 492480 | 5249000 | 0 | 428649.89 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4912419.5 | 3167544 | 17455680 | 2098483.2 | 618045.12 | 1348617.6 | 0 | 0 | 0 | 5230616 | 7011000 | 4496960 | 280515.66 | 3843783 | 558373.68 | 1850688 | 0 | 1709582.76 | 0 | 497324 | 2437866.7 | 587136.24 | 178605 | 1395100 | 380062.5 | 21715200 | 3005566.4 | 0 | 521939.52 | 150633 | 1681000 | 0 | 2042016 | 0 | 3975190.26 | 3826160 | 0 | 3159292.8 | 0 | 8922769.1 | 0 | 0 | 0 | 7191705 | 393588 | 200640 | 365783.04 | 47061393.12 | 4172495.4 | 452493.36 | 16760640 | 2365445.28 | 33336817.92 | 1616025.6 | 14967312 | 40783848 | 20012256.9 | 7051260 | 25280640 | 12825540 | 21271396.51 | 0 | 36932112 | 3417812.71 | 21937185.42 | 12685578 | 19098416.4 | 12537849.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99717120 | 0 | 9320875.2 | 0 | 0 | 32971276.8 | 0 | 0 | 1027180.8 | 0 | 0 | 1725561.98 | 846546.45 | 0 | 0 | 0 | 0 | 852380.16 | 304982.88 | 2141700 | 0 | 1408756.96 | 115252.86 | 10702411.2 | 1063226.7 | 950630.4 | 0 | 187057.728 | 11619701.46 | 0 | 0 | 0 | 0 | 0 | 0 | 6035124.48 | 0 | 1033444.5 | 1339027.2 | 5527739.88 | 0 | 8753615.64 | 10237881.6 | 0 | 16732160.64 | 0 | 13179304.64 | 0 | 481150.15 | 15641023.68 | 45873305 | 0 | 0 | 0 | 0 |  | 574671108.86 | 299788438.988 | 874459547.848 | 103114862.898 | 99717120 | 45292985.07 | 492620369.37 | 57493006.46 | 1060938 | 51197257.3 | 21715200 | 2247808.75 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 215 | 0 | 0 | 399 | 153 |  | 0 | 280 | 260 | 0 | 0 | 43 | 250 | 0 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 55 | 21 | 25 | 26 | 33 | 33 | 25 | 0 | 94 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 22 | 0 | 0 | 7 | 85 | 0 | 21 | 3 | 0 | 0 | 0 | 280 | 280 | 210 | 8 | 141 | 20 | 52 | 0 | 35 | 0 | 0 | 0 | 0 | 8 | 33 | 17 | 116 | 102 | 0 | 17 | 1 | 43 | 0 | 44 | 0 | 130 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 280 | 24 | 11 | 0 | 275 | 0 | 0 | 108 | 0 | 149 | 18 | 76 | 178 | 118 | 316 | 115 | 17 | 105 | 3 | 286 | 0 | 96 | 98 | 94 | 90 | 320 | 90 | 25 | 144 | 96 | 0 | 17 | 14 |  | 716 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 15 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 0 | 63 | 0 | 186 | 0 | 320 | 85 | 0 | 113 | 0 | 34 | 0 | 7 | 113 | 330 | 224 | 0 | 0 | 3 |  | 10511 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 395 | 141 | 0 | 0 | 280 | 300 | 0 | 0 | 55 | 326 | 0 | 0 | 0 | 102 | 100 | 50 | 0 | 0 | 0 | 35 | 55 | 55 | 21 | 25 | 17 | 33 | 33 | 51 | 0 | 91 | 75 | 120 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 85 | 100 | 80 | 44 | 21 | 5 | 0 | 0 | 0 | 280 | 280 | 211 | 8 | 137 | 23 | 55 | 0 | 43 | 0 | 0 | 45 | 22 | 8 | 33 | 20 | 144 | 122 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 163 | 161 | 0 | 81 | 0 | 220 | 0 | 0 | 0 | 280 | 16 | 11 | 0 | 281 | 0 | 0 | 165 | 25 | 149 | 0 | 90 | 170 | 127 | 316 | 115 | 105 | 105 | 0 | 304 | 43 | 110 | 114 | 94 | 100 | 320 | 86 | 0 | 144 | 104 | 0 | 17 | 0 |  | 715 | 0 | 400 | 0 | 0 | 180 | 0 | 0 | 26 | 0 | 0 | 87 | 29 | 0 | 0 | 0 | 0 | 50 | 30 | 94 | 0 | 43 | 16 | 34 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 0 | 22 | 40 | 183 | 0 | 387 | 90 | 0 | 96 | 0 | 113 | 0 | 0 | 113 | 470 | 218 | 0 | 17 | 0 |  | 12523 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 300 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 330 | 0 | 0 | 0 | 102 | 149 | 60 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 93 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 85 | 100 | 88 | 50 | 21 | 20 | 0 | 0 | 0 | 330 | 320 | 210 | 36 | 140 | 23 | 55 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 21 | 164 | 140 | 8 | 22 | 0 | 43 | 0 | 51 | 0 | 163 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 341 | 24 | 11 | 200 | 280 | 300 | 100 | 200 | 100 | 149 | 0 | 100 | 200 | 145 | 316 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 729 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 27 | 40 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 94 | 27 | 43 | 30 | 43 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 15 | 10 | 0 | 0 | 220 | 0 | 22 | 100 | 220 | 0 | 400 | 105 | 184 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 250 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 325 | 0 | 0 | 0 | 100 | 149 | 60 | 0 | 0 | 0 | 35 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 93 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 88 | 50 | 20 | 13 | 0 | 0 | 0 | 320 | 310 | 210 | 36 | 140 | 23 | 55 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 21 | 138 | 120 | 8 | 22 | 1.6 | 43 | 0 | 51 | 0 | 163 | 160 | 0 | 78 | 0 | 220 | 0 | 0 | 0 | 341 | 24 | 11 | 150 | 280 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 52 | 105 | 5 | 300 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 729 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 30 | 90 | 27 | 0 | 0 | 43 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 22 | 50 | 200 | 0 | 400 | 105 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 150 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 252 | 0 | 0 | 280 | 275 | 0 | 0 | 46 | 280 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 17 | 35 | 0 | 22 | 25 | 30 | 33 |  | 6 | 0 | 88 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86 | 0 | 21 | 13 | 0 | 0 | 0 | 280 | 320 | 180 | 8 | 141 | 20 | 53 | 0 | 43 | 0 | 0 | 0 | 22 | 11 | 33 | 20 | 98 | 119 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 130 | 156 | 0 | 81 | 0 | 179 | 0 | 0 | 0 | 290 | 16 | 2 | 0 | 218 | 0 | 0 | 72 | 0 | 115 | 8 | 30 | 16 | 132 | 316 | 115 | 0 | 68 | 1 | 16 | 2 | 68 | 17 | 57 | 10 | 321 | 17 | 19 | 90 | 108 | 0 | 17 | 12 | 0 | 713 | 0 | 270 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 0 | 12 | 0 | 203 | 0 | 315 | 15 | 0 | 15 | 0 | 0 | 0 | 4 | 35 | 340 | 191 | 0 | 0 | 1 | 0
199
| Minimum Generation |  | 9046 | 7:00
| Highest Generation |  | 12523 | 19:00
| Day Peak Generation |  | 10511 | 12:00
| Evening Peak Generation |  | 12523 | 19:00
| HVDC Max Flow |  | 720 | 20:00
| HVDC EvPeak Flow |  | 715 | 19:00
| Load factor L.F |  | 86.64%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-22
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-21 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10511 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 9183 | MW
Evening Peak Generation : |  | 12523 | MW Hour : | 19:00 | Available Max Generation : |  | 14842 | MW
E.P. Demand (at gen end) : |  | 12403 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 12523 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1642 | MW
Total Gen. (MKWH) : |  | 260.3906 | System Load Factor : | 86.64% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -230 | MW at | 5:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-22
Actual : | 106.68 | Ft.(MSL) , | Rule curve : | 103.84 | Ft.( MSL )
Gas Consumed : | Total = | 1118.01 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 148407847.968
: |  | Coal : | 57493006.46 | Oil : | 543817626.67 | Total : | 749718481.098
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4660.3754 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1589.9507 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1425.4635 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1288.3533 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1164.086 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 939.3893 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 518.6135 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 241.6916 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 724.5354 |  |  | 0 | 0%
Total | 0 |  | 12552.4588 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
7) Raozan #02
8) Fenchuganj 3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Gallamari-Gopalganj 132 kV Ckt-1 & 2 were under shut down from 08:11 to 17:30 for D/W.
b) Kochua 132/33 kV T-1 transformer was under shut down from 11:40 to 12:10 for red hot maintenance.
c) Kallyanpur 132/33 kV T-3 transformer & main bus was under shut down from 08:31 to 15:31 for C/M.
d) Kishoreganj 132 kV bus-A was under shut down from 09:20 to 16:35 for C/M.
e) Mymensingh-Kishoreganj 132 kV Ckt-1 is under shut down from 07:44 to 17:56 for CT
replacement of Kishoreganj end.
f) Netrokona 132/33 kV T1 transformer was under shut down from 10:50 to 13:07 for D/W.
g) Rangamati-Chandraghona 132 kV Ckt-1 was under shut down from 08:53 to 13:46 for D/W.
h) Saidpur 132/33 kV T5 transformer was under shut down from 08:26 to 15:50 for A/M.
i) Siddhirganj S/S-Siddhirganj Peaking 132 kV Ckt was under shut down since10:36 for Energy meter work.
j) Sikalbaha 132/33 kV T4 transformer was under shut down from 08:50 to 12:13 for A/M.
k) Tangail 132/33 kV T-1 transformer was under shut down from 09:30 to 10:15 for C/M.
l) Modunaghat-Chandrogona 132 kV Ckt-1 & 2 were under shut down from 11:40 to 13:28 for project work.
m) Gallamari S/S 132 kV bay E01 & E02 were under shut down since 13:13 for project work.
n) Meghnaghat 230 kV bus-1tripped at 12:55 showing TCS & lockout relay at the same time
Meghnaghat-Shympur 230 kV Ckt-1 & Meghnaghat-Aminbazar 230 kV Ckt-1 got trip showing dist Z3
and was switched on at 14:02.
o) Cumilla(N)-Meghnaghat 230 kV Ckt-1 was under shut down from 06:48 to for C/M.
p) Jamalpur 132/33 kV T3 transformer was under shut down from 07:47 to 08:30(22-09-21) for C/M.
q) Kishoreganj 132 kV bus-A was under shut down since 07:56(22-09-21) for C/M.
r) Mymensingh-Kishoreganj 132 kV Ckt-2 was under shut down since 07:00(22-09-21) for C/M.
s) Mymensingh-Kishoreganj 132 kV Ckt-1 tripped at 07:00 showing O/C relay and was switched on at
07:50(22-09-21).
t) Chowmuhoni 132/33 kV T3 transformer tripped at 06:29(22-9-21) showing O/C relay and was switched |  |  |  |  | About 40 MW power interruption occurred under Chowmuhoni S/S area
on at 06:58. |  |  |  |  | from 06:29 to 06:58.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-21 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 6559545 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 395 | 9385980 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 141 | 4690000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6716000 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 300 | 6548393 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1303120
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 50 | 186184 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 397152
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 326 | 7363558
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1127808
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 35 | 514440 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 100 | 743040 | High Voltage.
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 637501
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 55 | 783500
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 42 | 1247460 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 820200
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 830400
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 498720
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 6225052 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 245730 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 27063 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 141474 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3387888
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1357200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 86 | 1385280 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 144 | 2999520 | Engine problem
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 132693
| Dhaka area Total |  |  |  | 5719 | 3174 | 66254901
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2900000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 20 | 46141
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 138240
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 44 | 264960 | Engine problem
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 166 | 3929400 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2442181
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 85 | 506435 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 331680
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 90 | 1836480 | Engine problem
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 490512
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 5 | 454080
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 80 | 2006400 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 22469
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 304 | 4885200
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 43 | 392401
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2495698
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 1882560
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 104 | 2573073
| Chattogram area Total |  |  |  | 2382 | 1497 | 27597910
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 211 | 4888000 | Gas shortage
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 280 | 7068400 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 280 | 7011000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 494136 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 55 | 1321920
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 8 | 217454 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 999756 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 127 | 2838618 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 0 | 49240
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 137 | 3342420 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 170 | 3758880
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 462312
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 238140
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 144 | 2895360
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 797200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 45 | 255274
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 506750
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 21504 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1271100
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 94 | 2228520 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 443520 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1831 | 41109504
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 122 | 2835440 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 19 | 410976
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 9450
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 165 | 3223200 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2772000
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 240270
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 21 | 381120
| Mymensingh Area Total |  |  |  | 709 | 442 | 9872456
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1025000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3487009
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 161 | 3679000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1147200
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 264000
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 0 | 0 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 81 | 1654080
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 5157670
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Gas shortage
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 524784
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7120500 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7582000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7668600 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1661 | 39309843
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 715 | 17312000
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 26 | 97920 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 180 | 2378880
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 8877024
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 40 | 78720 | Low demand
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 90 | 980640
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1451 | 29725184
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 29 | 546159 | Engine problem
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 1527046 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 22 | 688963 | Gas shortage
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 470 | 10449500 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 218 | 5134227
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 17 | 39600 | Low demand
| Barisal Area Total |  |  |  | 2046 | 843 | 18385495
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 86624
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 30 | 30018 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 0 | 0 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 104198
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 16 | 11894 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 198 | 4572064 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 183 | 4724564 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 387 | 8842036 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 34 | 109611 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 22 | 495120
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 247104
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 34 | 1104480 | Engine problem
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 242000
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 96 | 1763136 | Engine problem
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2116512
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 17040
| Rajshahi Area Total |  |  |  | 2179 | 1311 | 24466401
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 80 | 1926982
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 113 | 1698364
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 43543
| Rangpur Area Total |  |  |  | 605 | 193 | 3668889
| Total |  |  |  | 21180 | 12403 | 260390583
| Eastern Grid Total |  |  |  | 14221 | 8605 | 184144614
| Western Grid Total |  |  |  | 6959 | 3798 | 76245969
| National Grid Total |  |  |  | 21180 | 12403 | 260390583
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-21
(a) ENTIRE EASTERN GRID : |  | 8265 | MW | (b) ENTIRE WESTERN GRID : |  | 3633 | MW
i) Dhaka area |  | 4452 | MW | i) Khulna area |  | 1373 | MW
ii) Chittagong area |  | 1202 | MW | ii) Rajshahi area |  | 1200 | MW
iii) Comilla area |  | 1116 | MW | iii) Barisal area |  | 325 | MW
iv) Mymensingh area |  | 979 | MW | iv) Rangpur area |  | 735 | MW
v) Sylhet area |  | 516 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 11898 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 126 | 18:30 | Kishoreganj | 138 | 19:00 | Jessore | 101 | 18:30
Munsiganj | 97 | 0:00 | Netrokona | 111 | 22:00 | Benapol | 54 | 18:30
Sonargaon | 84 | 0:00 | Jamalpur | 139 | 1:00 | Jhenida(Old) | 106 | 18:30
Shyampur | 194 | 10:00 | Sherpur | 120 | 1:00 | Bottail | 118 | 19:00
Bhulta | 209 | 17:00 | Srimongal | 53 | 18:30 | G.K Project | 53 | 19:00
Madanganj | 46 | 16:00 | Shahjibazar | 117 | 21:00 | Faridpur | 134 | 19:00
Shitalakhya | 113 | 12:00 | Fenchuganj | 44 | 18:30 | Rajbari | 48 | 19:00
Rahim steel | 28 | 19:00 | Kulawara | 46 | 19:00 | Madaripur | 94 | 22:00
Matuail | 62 | 15:00 | Sylhet | 134 | 20:00 | Sariatpur | 62 | 21:00
Ghorasal | 81 | 0:00 | Chatak | 30 | 22:00 | Gopalganj | 83 | 19:00
Narsingdi | 177 | 23:00 | Sunamganj | 51 | 1:00 | Bagerhat | 86 | 19:30
Haripur (SBU) | 119 | 22:00 | Biani Bazar | 64 | 20:00 | Mongla | 38 | 11:00
Sreenagar | 38 | 19:30 | Comilla (S) | 146 | 19:30 | Satkhira | 87 | 18:30
Ullon | 51 | 20:00 | Comilla(N) | 125 | 21:00 | Gallamari | 32 | 13:00
Hasnabad | 87 | 21:00 | Chandpur | 73 | 22:00 | Magura | 48 | 19:00
Magbazar | 117 | 15:00 | Feni | 104 | 19:30 | Norail | 47 | 18:30
Maniknagar | 74 | 13:00 | Chowmuhani | 177 | 20:00 | Chuadanga | 92 | 18:30
Bangabhaban | 12 | 10:00 | Ashuganj | 45 | 23:00 | Barisal(N) | 38 | 18:30
Motijheel | 28 | 13:00 | Daudkandi | 146 | 21:00 | Barisal (S) | 98 | 19:00
Narinda | 68 | 13:00 | B.Baria | 161 | 21:00 | Patuakhali | 107 | 18:30
Kazla | 78 | 14:00 | Ramganj | 76 | 22:00 | Bhandaria | 50 | 21:00
Dhanmondi | 158 | 13:00 | Chaddagram | 43 | 18:30 | Borguna | 16 | 21:00
Lalbag | 90 | 13:00 | PHP | 10 | 20:00 | Borhan Uddin | 42 | 22:00
Madartek | 69 | 21:00 | Kochua | 60 | 21:00 | Ishurdi | 61 | 18:30
Dhaka University | 37 | 12:00 | Madunaghat | 56 | 18:30 | Ruppur Paromanobik | 4 | 9:00
Aftabnagar | 15 | 13:00 | Hathazari | 90 | 19:30 | Natore | 120 | 19:00
Fatullah | 68 | 11:00 | Khulshi | 174 | 10:00 | Bogra | 153 | 20:00
Nawabganj | 49 | 21:00 | Halishahar | 84 | 10:00 | Noagaon | 105 | 19:30
Keraniganj | 68 | 19:00 | Baraulia | 147 | 0:00 | Rajshahi | 135 | 20:00
Mirpur | 117 | 18:30 | Sikalbaha | 42 | 18:00 | Rajshahi New | 17 | 1:00
Kalyanpur | 102 | 18:30 | Dohazari | 100 | 18:30 | C.Nawabganj | 55 | 19:00
Gulshan | 124 | 13:00 | Cox'sbazar | 93 | 18:30 | Amnura | 43 | 19:30
Uttara | 81 | 13:00 | Chandraghona | 26 | 18:30 | Pabna | 96 | 19:00
Uttara New | 28 | 12:00 | Kaptai | 4 | 18:00 | Shahjadpur | 97 | 20:00
Kamrangirchar | 97 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 96 | 19:30
Savar | 176 | 10:00 | Bakulia | 107 | 19:00 | Niyamatpur | 69 | 1:00
Bhasantec | 133 | 13:00 | Julda | 20 | 16:00 | Joypurhat | 50 | 1:00
Agargaon | 83 | 13:00 | TK chemical | 29.8 | 20:00 | Sherpur(Bogura) | 48 | 20:00
Satmosjid | 87 | 13:00 | Modern Steel | 0 | 1:00 | Mohastangor | 60 | 1:00
Tongi | 129 | 18:00 | Shahmirpur | 27 | 16:00 | Bhangura | 30 | 19:00
Kabirpur | 229 | 20:00 | Khagrachhari | 28 | 6:00 | Rangpur | 120 | 1:00
Basundhara | 178 | 15:00 | Matarbari | 40 | 18:30 | Lalmonirhat | 39 | 1:00
Manikganj | 74 | 21:00 | Baroiar Hat | 56 | 18:30 | Saidpur | 94 | 18:30
Joydevpur | 179 | 18:30 | Rangamati | 14 | 18:30 | Purbasadipur | 102 | 18:30
New Tongi | 92 | 12:00 | Abul Khair 230 | 159 | 4:00 | Thakurgaon | 77 | 21:00
Kodda | 293 | 18:00 | BSRM | 122 | 0:00 | Palashbari | 106 | 3:00
Dhamrai | 134 | 14:00 | GPH Ispat | 31 | 1:00 | Barapukuria | 51 | 18:30
Rajendrapur | 104 | 19:00 | Agrabad | 81 | 18:00 | Panchagar | 47 | 19:30
Valuka | 110 | 18:30 | Goalpara | 26 | 13:00 | Joldhaka | 53 | 19:00
Tangail | 194 | 20:00 | Central S/S | 87 | 19:00 | Kurigram | 54 | 2:00
Mymensing | 208 | 19:00 | Noapara | 42 | 18:30 | Mithapukur | 28 | 2:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-21 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 407 | 6:00 | 399 | 9:00 | Kaliakoir | 392 | 0.375 | 382 | 0.8125
| Bheramara | 402 | 6:00 | 397 | 18:30 | Bhulta | 386 | 0.125 | 376 | 0.625
| Ashuganj(N) | 391 | 6:00 | 384 | 12:00 | Gopalganj | 409 | 0.625 | 390 | 0.8125
| Payra | 412 | 5:00 | 401 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 236 | 7:00 | 227 | 17:00
| Ishurdi | 235 | 9:00 | 227 | 1:00 | Megnaghat | 232 | 8:00 | 230 | 1:00
| Ashuganj | 240 | 4:00 | 236 | 15:00 | Fenchuganj | 243 | 4:00 | 239 | 2:00
| Serajganj | 230 | 10:00 | 225 | 1:00 | Siddhirganj | 231 | 5:00 | 225 | 12:00
| Baghabari | 231 | 9:00 | 225 | 1:00 | Maniknagar | 229 | 5:00 | 224 | 12:00
| Barapukuria | 236 | 15:00 | 225 | 1:00 | Agargaon | 227 | 9:00 | 219 | 16:00
| Bogra | 225 | 16:00 | 213 | 1:00 | Barisal | 241 | 13:00 | 232 | 20:00
| Rajshahi | 230 | 8:00 | 219 | 1:00 | Bhola 225 MW | 244 | 8:00 | 237 | 21:00
| Khulna South | 234 | 11:00 | 224 | 2:00 | AKSML | 236 | 13:00 | 228 | 16:00
| Rampura | 229 | 4:00 | 223 | 12:00 | BSRM | 234 | 1:00 | 228 | 17:00
| Haripur | 229 | 4:00 | 224 | 11:00 | Bibiyana | 242 | 9:00 | 234 | 18:00
| Hasnabad | 228 | 14:00 | 223 | 1:00 | Bhulta | 230 | 1:00 | 225 | 16:00
| Shyampur | 227 | 5:00 | 220 | 13:00 | Ashuganj (S) | 237 | 14:00 | 233 | 16:00
| Aminbazar | 229 | 1:00 | 220 | 2:00 | Kaliakoir | 228 | 13:00 | 222 | 11:00
| Tongi | 226 | 13:00 | 220 | 11:00 | GPH | 236 | 13:00 | 223 | 22:00
| Comilla (N) | 231 | 4:00 | 226 | 16:00 | Jhenaidah
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 132 | 5:00 | 129 | 12:00 | Madanhat | 138 | 0.041667 | 133 | 0.25
| Munsiganj | 133 | 4:00 | 129 | 12:00 | Hathazari | 138 | 0.041667 | 134 | 0.66667
| Sonargaon | 131 | 13:00 | 128 | 8:00 | Khulshi | 135 | 0.041667 | 131 | 0.66667
| Shyampur | 135 | 5:00 | 131 | 11:00 | Halishahar | 137 | 0.77083 | 132 | 0.66667
| Bhulta | 127 | 4:00 | 122 | 11:00 | Baraulia | 137 | 0.041667 | 132 | 0.66667
| Madanganj | 134 | 18:00 | 129 | 9:00 | Sikalbaha | 139 | 0.75 | 131 | 0.5
| Shitalakhya | 133 | 4:00 | 130 | 9:00 | Dohazari | 132 | 0.125 | 127 | 0.70833
| Rahim steal | 133 | 13:00 | 129 | 11:00 | Cox'sbazar | 120 | 0.20833 | 109 | 0.95833
| Matuail | 132 | 5:00 | 129 | 12:00 | Chandraghona | 138 | 0.54167 | 133 | 0.66667
| Ghorasal | 138 | 1:00 | 138 | 1:00 | Kaptai | 136 | 0.58333 | 135 | 0.041667
| Narsinghdi | 132 | 7:00 | 123 | 1:00 | A. Khaer Stl. | 136 | 0.041667 | 132 | 0.29167
| Haripur (SBU) | 133 | 18:30 | 130 | 10:00 | Bakulia | 137 | 0.79167 | 130 | 0.66667
| Sreenagar | 133 | 14:00 | 127 | 16:00 | Julda | 139 | 0.79167 | 133 | 0.66667
| Ullon | 134 | 6:00 | 128 | 12:00 | TK Chemical | 137 | 0.041667 | 133 | 0.70833
| Hasnabad | 136 | 1:00 | 132 | 16:00 | Modern Steel | 137 | 0.041667 | 130 | 0.66667
| Magbazar | 135 | 4:00 | 127 | 15:00 | Shahmirpur | 138 | 0.79167 | 132 | 0.70833
| Maniknagar | 134 | 3:00 | 130 | 10:00 | Khagrachhari | 136 | 0.25 | 132 | 0.70833
| Bangabhaban | 134 | 3:00 | 130 | 10:00 | Matarbari | 130 | 0.29167 | 124 | 0.70833
| Motijheel | 134 | 3:00 | 130 | 10:00 | Baroiar Hat | 137 | 0.54167 | 132 | 0.16667
| Narinda | 134 | 3:00 | 130 | 10:00 | Rangamati | 136 | 1:00 | 133 | 16:00
| Kazla | 134 | 3:00 | 130 | 10:00 | Agrabad | 136 | 19:00 | 131 | 14:00
| Dhanmondi | 133 | 1:00 | 128 | 12:00 | Goalpara S/S | 138 | 11:00 | 134 | 0.125
| Lalbag | 133 | 4:00 | 127 | 16:00 | Khulna Central S/S | 137 | 6:00 | 133 | 0.041667
| Madartek | 134 | 3:00 | 128 | 11:00 | Noapara | 135 | 8:00 | 130 | 0.8125
| Dhaka University | 134 | 3:00 | 128 | 11:00 | Jessore | 132 | 9:00 | 124 | 0.8125
| Aftabnagar | 134 | 2:00 | 128 | 15:00 | Benapol | 132 | 0.33333 | 124 | 0.8125
| Fatullah | 134 | 6:00 | 131 | 10:00 | Jhenida(Old) | 132 | 9:00 | 121 | 0.8125
| Nawabganj | 133 | 14:00 | 127 | 16:00 | Bottail | 134 | 0.375 | 126 | 0.041667
| Keraniganj | 134 | 5:00 | 128 | 13:00 | G.K Project | 140 | 0.375 | 133 | 0.041667
| Mirpur | 129 | 3:00 | 125 | 14:00 | Faridpur | 135 | 0.20833 | 129 | 0.91667
| Kalyanpur | 132 | 14:00 | 126 | 16:00 | Rajbari | 135 | 0.58333 | 127 | 0.91667
| Gulshan | 134 | 5:00 | 127 | 15:00 | Madaripur | 141 | 0.375 | 132 | 0.83333
| Uttara | 130 | 5:00 | 123 | 15:00 | Shariyatpur S/S | 139 | 8:00 | 131 | 0.8125
| Uttara New | 130 | 1:00 | 125 | 13:00 | Gopalganj | 144 | 0.29167 | 134 | 0.8125
| Kamrangirchar | 133 | 5:00 | 127 | 13:00 | Bagerhat | 137 | 13:00 | 130 | 0.083333
| Savar | 131 | 1:00 | 125 | 15:00 | Mongla | 136 | 13:0 | 128 | 0.041667
| Bhasantec | 135 | 5:00 | 129 | 13:00 | Satkhira | 136 | 6:00 | 129 | 20:00
| Agargaon | 136 | 4:00 | 130 | 13:00 | Gallamari | 138 | 0.375 | 133 | 2:00
| Satmosjid | 135 | 3:00 | 130 | 13:00 | Magura | 130 | 8:00 | 120 | 0.041667
| Tongi | 136 | 13:00 | 131 | 16:00 | Narail | 130 | 0.375 | 119 | 0.041667
| Kabirpur | 136 | 6:00 | 131 | 21:00 | Chuadanga | 136 | 10:00 | 126 | 0.875
| Basundhara | 134 | 18:30 | 129 | 12:00 | Barisal(N) | 140 | 9:00 | 132 | 0.83333
| Manikganj | 141 | 5:00 | 134 | 20:00 | Barisal (S) | 138 | 8:00 | 130 | 20:00
| Joydevpur | 138 | 5:00 | 134 | 10:00 | Patuakhali(S) | 136 | 0.29167 | 127 | 0.83333
| New Tongi | 135 | 4:00 | 130 | 12:00 | Bhandaria | 136 | 0.25 | 125 | 0.83333
| Kodda | 130 | 21:00 | 122 | 15:00 | Borguna | 138 | 0.375 | 128 | 0.875
| Dhamrai | 135 | 3:00 | 130 | 19:00 | Jhenaidah(New) | 130 | 10:00 | 121 | 20:00
| Rajendrapur | 129 | 14:00 | 120 | 13:00 | Ishurdi | 136 | 9:00 | 132 | 2:00
| Valuka | 125 | 10:00 | 110 | 1:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 1:00
| Tangail | 136 | 14:00 | 122 | 20:00 | Natore | 135 | 9:00 | 129 | 1:00
| Mymensing | 131 | 13:00 | 115 | 1:00 | Bogra | 135 | 10:00 | 127 | 2:00
| Kishorganj | 132 | 13:00 | 118 | 19:00 | Noagaon | 131 | 18:00 | 121 | 1:00
| Netrokona | 127 | 10:00 | 110 | 1:00 | Rajshahi | 134 | 9:00 | 129 | 2:00
| Jamalpur | 138 | 13:00 | 122 | 1:00 | Rajshahi New | 135 | 8:00 | 128 | 2:00
| Sherpur | 136 | 13:00 | 122 | 1:00 | C.Nawabganj | 133 | 9:0 | 125 | 1:00
| Srimongal | 135 | 11:00 | 130 | 1:00 | Amnura | 134 | 18:30 | 123 | 2:00
| Shahjibazar | 135 | 6:00 | 129 | 1:00 | Pabna | 134 | 10:00 | 130 | 19:30
| Fenchuganj | 136 | 7:00 | 132 | 1:00 | Shahjadpur | 138 | 8:00 | 135 | 3:00
| Khulawara | 134 | 5:00 | 131 | 19:30 | Serajganj | 132 | 13:00 | 123 | 4:00
| Sylhet | 133 | 5:00 | 129 | 23:00 | Niyamatpur | 130 | 16:00 | 118 | 2:00
| Chatak | 133 | 7:00 | 128 | 22:00 | Joypurhat | 132 | 9:00 | 120 | 1:00
| Sunamganj | 133 | 7:00 | 123 | 24:00 | Sherpur(Bogura) | 135 | 18:00 | 127 | 1:00
| Biani Bazar | 132 | 6:00 | 126 | 19:30 | Mohastangor | 134 | 18:00 | 125 | 1:00
| Comilla(s) | 129 | 7:00 | 123 | 18:30 | Bangura | 136 | 17:00 | 131 | 1:00
| Comilla(n) | 138 | 24:00 | 134 | 16:00 | Rangpur | 132 | 16:00 | 116 | 1:00
| Chandpur | 142 | 11:00 | 134 | 15:00 | Lalmonirhat | 133 | 16:00 | 118 | 1:00
| Feni | 138 | 13:00 | 130 | 16:00 | Saidpur | 132 | 15:00 | 117 | 1:00
| Chowmuhani | 134 | 4:00 | 130 | 16:00 | Purbasadipur | 130 | 17:00 | 113 | 1:00
| Ashuganj | 140 | 13:00 | 133 | 22:00 | Thakurgaon | 132 | 16:00 | 113 | 1:00
| Daudkandi | 134 | 18:30 | 128 | 16:00 | Palashbari | 131 | 15:00 | 117 | 1:00
| B.Baria | 133 | 17:00 | 126 | 22:00 | Barapukuria | 136 | 15:00 | 125 | 1:00
| Ramganj | 139 | 13:00 | 133 | 23:00 | Panchagar | 136 | 0.66667 | 114 | 0.041667
| Chaddagram | 137 | 13:00 | 131 | 3:00 | Joldhaka | 131 | 0.66667 | 113 | 0.041667
| PHP | 137 | 13:00 | 130 | 16:00 | Kurigram | 133 | 0.625 | 117 | 0.041667
| Kochua | 137 | 10:00 | 133 | 14:00 | Mithapukur | 135 | 0.70833 | 121 | 0.041667
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-21
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 26 | 8236 | 3425 | 11661 |  |  |  | QF-LDC-11
0:30 | 123 | 8145.5 | 3360 | 11505.5 | Date: | 2021-09-21
1:00 | 220 | 8055 | 3295 | 11350
1:30 | 199 | 7898 | 3283.5 | 11181.5
2:00 | 178 | 7741 | 3272 | 11013
2:30 | 171 | 7619.5 | 3250.5 | 10870 | [5 empty] | Gen. at Eve. Peak | 12523 | 12523 MW (19:00 )
3:00 | 164 | 7498 | 3229 | 10727 | [6 empty] | 19:00
3:30 | 169 | 7446 | 3144 | 10590 | [5 empty] | Gen. at Day Peak | 10511 | 10511 MW (12:00 )
4:00 | 174 | 7394 | 3059 | 10453 | [6 empty] | 12:00
4:30 | 202 | 7352 | 2975 | 10327 | [5 empty] | Highest Generation | 12523
5:00 | 230 | 7310 | 2891 | 10201 | [6 empty] | 19:00
5:30 | 171 | 7085 | 2805 | 9890
6:00 | 112 | 6860 | 2719 | 9579
6:30 | 86 | 6634 | 2678.5 | 9312.5
7:00 | 60 | 6408 | 2638 | 9046
7:30 | 31 | 6393.5 | 2670.5 | 9064
8:00 | 2 | 6379 | 2703 | 9082
8:30 | 108 | 6591 | 2762.5 | 9353.5
9:00 | 214 | 6803 | 2822 | 9625
9:30 | 232.5 | 6942.5 | 2837.5 | 9780
10:00 | 251 | 7082 | 2853 | 9935
10:30 | 238.5 | 7185 | 2926 | 10111
11:00 | 226 | 7288 | 2999 | 10287
11:30 | 160 | 7403.5 | 2995.5 | 10399
12:00 | 94 | 7519 | 2992 | 10511
12:30 | 112 | 7668.5 | 3027.5 | 10696
13:00 | 130 | 7818 | 3063 | 10881
13:30 | 85 | 7729 | 2887.5 | 10616.5
14:00 | 40 | 7640 | 2712 | 10352
14:30 | 130 | 7641 | 2819 | 10460
15:00 | 220 | 7642 | 2926 | 10568
15:30 | 295 | 7535 | 2922 | 10457
16:00 | 370 | 7428 | 2918 | 10346
16:30 | 390 | 7315 | 2916.5 | 10231.5
17:00 | 410 | 7202 | 2915 | 10117
17:30 | 342 | 7407.5 | 2993 | 10400.5
18:00 | 274 | 7613 | 3071 | 10684
18:30 | 151 | 8169 | 3434.5 | 11603.5
19:00 | 28 | 8725 | 3798 | 12523
19:30 | 28 | 8536 | 3737 | 12273
20:00 | 84 | 8533 | 3723 | 12256 |  |  |  | Executive Engineer
20:30 | 117 | 8541.5 | 3707.5 | 12249 |  |  |  | Network Operation Division
21:00 | 150 | 8550 | 3692 | 12242
21:30 | 83 | 8447 | 3648 | 12095
22:00 | 16 | 8344 | 3604 | 11948 |  |  |  |  | Page 6 of 7
22:30 | 22 | 8322.5 | 3547 | 11869.5
23:00 | 28 | 8301 | 3490 | 11791
23:30 | 27 | 8268.5 | 3457.5 | 11726
24:00 | 26 | 8236 | 3425 | 11661
12523 MW (19:00 )
10511 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-21 |  | Energy | 260390583
[11 empty] | 2021-09-21 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4446 | 720 | 1874 | 3541 | 561 | 168 | 279 | 0 | 122 | 0
0:30 | 4409 | 718 | 1892 | 3406.5 | 555 | 167.5 | 258.5 | 0 | 124 | 0 | Date: | 2021-09-21
1:00 | 4372 | 716 | 1910 | 3272 | 549 | 167 | 238 | 0 | 126 | 0
1:30 | 4386 | 715.5 | 1917.5 | 3107 | 544 | 166.5 | 220 | 0 | 125 | 0 | [7 empty] | Total Energy | 260.3906 | Total Energy Gen 260.391 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.391 MKWHr
2:00 | 4400 | 715 | 1925 | 2942 | 539 | 166 | 202 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4402.5 | 715 | 1925 | 2831 | 524 | 164.5 | 186 | 0 | 122 | 0 | [7 empty] | Energy Requirement | 260.3906
3:00 | 4405 | 715 | 1925 | 2720 | 509 | 163 | 170 | 0 | 120 | 0
3:30 | 4410.5 | 715.5 | 1927 | 2597.5 | 494 | 163 | 162.5 | 0 | 120 | 0 | [6 empty] | Shortage
4:00 | 4416 | 716 | 1929 | 2475 | 479 | 163 | 155 | 0 | 120 | 0
4:30 | 4404 | 715.5 | 1919.5 | 2396.5 | 474 | 163 | 137.5 | 0 | 117 | 0
5:00 | 4392 | 715 | 1910 | 2318 | 469 | 163 | 120 | 0 | 114 | 0
5:30 | 4328.5 | 715.5 | 1888 | 2103 | 459 | 163.5 | 120 | 0 | 112 | 0.5
6:00 | 4265 | 716 | 1866 | 1888 | 449 | 164 | 120 | 0 | 110 | 1
6:30 | 4150.5 | 715.5 | 1806 | 1804.5 | 439 | 164.5 | 120 | 0 | 103 | 9.5 |  |  |  |  | Coal
7:00 | 4036 | 715 | 1746 | 1721 | 429 | 165 | 120 | 0 | 96 | 18
7:30 | 4024.5 | 715.5 | 1731 | 1763.5 | 419 | 165.5 | 120 | 0 | 96 | 29 |  |  |  | Oil |  |  |  | ,
8:00 | 4013 | 716 | 1716 | 1806 | 409 | 166 | 120 | 0 | 96 | 40
8:30 | 4030 | 716 | 1711.5 | 2047 | 408.5 | 167 | 120 | 0 | 99 | 54.5
9:00 | 4047 | 716 | 1707 | 2288 | 408 | 168 | 120 | 0 | 102 | 69
9:30 | 4035.5 | 716 | 1701.5 | 2465 | 403.5 | 168 | 120 | 0 | 104 | 66.5
10:00 | 4024 | 716 | 1696 | 2642 | 399 | 168 | 120 | 0 | 106 | 64
10:30 | 4000 | 716 | 1696.5 | 2817.5 | 404 | 168 | 120 | 0 | 108 | 81
11:00 | 3976 | 716 | 1697 | 2993 | 409 | 168 | 120 | 0 | 110 | 98
11:30 | 4007.5 | 716 | 1702.5 | 3077.5 | 409.5 | 168.5 | 120 | 0 | 113 | 84.5
12:00 | 4039 | 716 | 1708 | 3162 | 410 | 169 | 120 | 0 | 116 | 71
12:30 | 4125.5 | 715.5 | 1677.5 | 3285 | 410 | 168.5 | 120 | 0 | 117 | 77
13:00 | 4212 | 715 | 1647 | 3408 | 410 | 168 | 120 | 0 | 118 | 83
13:30 | 4212 | 715 | 1647 | 3408 | 410 | 168 | 120 | 0 | 118 | 83
14:00 | 4212 | 715 | 1647 | 3408 | 410 | 168 | 120 | 0 | 118 | 83
14:30 | 4265.5 | 715 | 1671 | 3186 | 410.5 | 166 | 120 | 0 | 122 | 68.5
15:00 | 4319 | 715 | 1695 | 2964 | 411 | 164 | 120 | 0 | 126 | 54
15:30 | 4374 | 715 | 1702.5 | 2796 | 421 | 164 | 122 | 0 | 124 | 38.5
16:00 | 4429 | 715 | 1710 | 2628 | 431 | 164 | 124 | 0 | 122 | 23
16:30 | 4408 | 715 | 1725.5 | 2529 | 430.5 | 164 | 126.5 | 0 | 118 | 15
17:00 | 4387 | 715 | 1741 | 2430 | 430 | 164 | 129 | 0 | 114 | 7
17:30 | 4337 | 715.5 | 1738.5 | 2639.5 | 429.5 | 164 | 250 | 0 | 123 | 3.5
18:00 | 4287 | 716 | 1736 | 2849 | 429 | 164 | 371 | 0 | 132 | 0
18:30 | 4414.5 | 715.5 | 1760 | 3428 | 489.5 | 165 | 493 | 0 | 138 | 0
19:00 | 4542 | 715 | 1784 | 4007 | 550 | 166 | 615 | 0 | 144 | 0
19:30 | 4426 | 719 | 1855 | 3871 | 579 | 166 | 511 | 0 | 146 | 0
20:00 | 4441 | 720 | 1848 | 3844 | 580 | 166 | 511 | 0 | 146 | 0
20:30 | 4465 | 719.5 | 1835.5 | 3830.5 | 590 | 166.5 | 498 | 0 | 144 | 0
21:00 | 4489 | 719 | 1823 | 3817 | 600 | 167 | 485 | 0 | 142 | 0
21:30 | 4484.5 | 719.5 | 1831 | 3730.5 | 610 | 167.5 | 410 | 0 | 142 | 0
22:00 | 4480 | 720 | 1839 | 3644 | 620 | 168 | 335 | 0 | 142 | 0
22:30 | 4474 | 720 | 1862.5 | 3592.5 | 605.5 | 168 | 307 | 0 | 140 | 0
23:00 | 4468 | 720 | 1886 | 3541 | 591 | 168 | 279 | 0 | 138 | 0
23:30 | 4457 | 720 | 1880 | 3541 | 576 | 168 | 279 | 0 | 130 | 0 | Max Temp. in Dhaka |  | 32.7° C
24:00 | 4446 | 720 | 1874 | 3541 | 561 | 168 | 279 | 0 | 122 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 260.391 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 260.391 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-21
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 92 | 91 | 88 | 88 | 88 | 89 | 90 | 91 | 93 | 93 | 93 | 94 | 93 | 89 | 89 | 89 | 89 | 89 |  | 91 | 91 | 91 | 92 | 93 | 93 | 93 | 2105400
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1824000
3 | Chattogram TPP-1 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 2900000
4 | Chattogram TPP-2 | [19 empty] | 120
5 | Raozan 25 MW PP | [17 empty] | 4 |  | 20 | 8 | 8 |  |  |  | 0 | 46141
| Teknaf 20MW PP (Solartech) | [5 empty] | 1 | 5 | 7 | 12 | 19 | 20 | 18 | 19 | 18 | 12 | 9 | 2 | [9 empty] | 138240
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 34 | 34 | 19 | 0 | [12 empty] | 82 |  | 85 | 51 | 51 | 51 | 51 | 51 | 51 | 506435
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 100 | 97 | 91 | 101 | 96 | 93 | 105 | 93 | 94 | 96 | 93 | 105 | 98 | 105 | 105 | 105 | 105 | 105 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2442181
| Daudkandi 200 MW PP (B.Trac) | [26 empty] | 21504
14 | Titas 50 MW Peaking PP | [17 empty] | 36 | [7 empty] | 0 | 49240
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 334 | 335 | 334 | 334 | 336 | 300 | 300 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 331 | 336 | 331 | 260 |  | 326 | 330 | 331 | 335 | 334 | 334 | 334 | 7363558
18 | Kodda 300 MW PP Unit-2 (Summit) | 260 | 230 | 230 | 230 | 195 | 195 | 195 | 200 | 260 | 273 | 275 | 275 | 278 | 278 | 273 | 273 | 275 | 281 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 6225052
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 217454
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 290 | 210 | 160 | 160 | 160 | 160 | 215 | 310 | 310 | 310 | 310 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 6559545
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 23 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 494136
33 | Ashuganj 225 MW CCPP | 202 | 201 | 201 | 201 | 201 | 203 | 205 | 199 | 196 | 205 | 209 | 210 | 209 | 183 | 179 | 179 | 179 | 208 |  | 211 | 209 | 209 | 212 | 205 | 197 | 190 | 4888000
34 | Ashuganj 450 MW CCPP(South) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 310 | 320 | 320 | 320 | 7011000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 330 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 7068400
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 56 | 57 | 57 | 57 | 56 | 57 | 56 | 56 | 55 | 52 | 51 | 52 | 52 | 52 | 52 | 55 |  | 55 | 55 | 55 | 56 | 56 | 56 | 56 | 1321920
36 | Chandpur 150 MW CCPP | 140 | 140 | 142 | 140 | 138 | 138 | 140 | 140 | 140 | 140 | 140 | 141 | 139 | 140 | 140 | 140 | 139 | 141 |  | 137 | 140 | 139 | 137 | 139 | 142 | 138 | 3342420
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 396 | 396 | 396 | 396 | 397 | 366 | 352 | 364 | 397 | 397 | 398 | 399 | 400 | 331 | 347 | 395 | 394 | 362 |  | 395 | 395 | 399 | 395 | 398 | 398 | 398 | 9385980
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6716000
41 | Haripur 360MW CCPP(HPL) | 263 | 272 | 291 | 307 | 317 | 317 | 251 | 191 | 167 | 164 | 159 | 153 | 152 | 152 | 152 | 153 | 148 | 143 |  | 141 | 143 | 142 | 141 | 142 | 161 | 187 | 4690000
42 | RPCL 210MW CCPP | 132 | 134 | 135 | 147 | 147 | 147 | 136 | 117 | 105 | 105 | 104 | 102 | 100 | 99 | 103 | 103 | 103 | 113 |  | 122 | 123 | 136 | 136 | 135 | 133 | 131 | 2835440
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 8 | 15 | 27 | 29 | 48 | 25 | 27 | 41 | 21 | 8 | 4 | 0 | [8 empty] | 240270
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1025000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 163 | 160 | 161 | 160 | 148 | 155 | 156 | 154 | 155 | 160 | 161 | 160 | 161 | 161 | 161 | 158 | 160 | 159 |  | 161 | 159 | 160 | 162 | 161 | 155 | 156 | 3679000
47 | Shahjibazar GTPP Unit- 8 & 9
48 | Shahjibazar 86MW PP (Shahjibazar) | 81 | 81 | 81 | 81 | 81 | 81 | 20 | 20 | 20 | 20 | 20 | 78 | 81 | 81 | 80 | 80 | 80 | 81 |  | 81 | 81 | 81 | 81 | 80 | 80 | 80 | 1654080
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 192 | 165 | 205 | 220 | 220 | 220 | 220 | 220 | 166 | 220 | 220 | 220 | 220 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 5157670
51 | Sylhet 20 MW GTPP
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [25 empty] | 0 | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 264000
55 | Fenchugonj 51 MW PP (Barakatullah) | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 47 | 47 | 47 | 47 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1147200
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16 | 16 | 24 | 16 |  | 16 | 16 | 16 | 24 | 24 | 24 | 24 | 524784
57 | Bibiana-II 341 MW CCPP (Summit) | 290 | 280 | 275 | 290 | 290 | 270 | 275 | 300 | 290 | 290 | 290 | 280 | 290 | 270 | 300 | 290 | 300 | 300 |  | 280 | 310 | 290 | 290 | 285 | 300 | 285 | 7120500
| Bibiyana South 400 MW | 321 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 321 |  | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 7668600
58 | Nababganj 55 MW PP (Southern power ) | [9 empty] | 17 | 30 | 55 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 783500
59 | Tangail Palli Power Gen 22 MW | 22 | 22 | 22 | 22 | 5 | 5 |  |  |  | 17 | 13 | 22 | 22 | 22 | 20 | 5 | 5 | 6 |  | 21 | 22 | 22 | 22 | 22 | 22 | 22 | 381120
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 490512
61 | Narshingdi 22 MW PP (Doreen) | 0 | 22 | 22 | 22 | 22 | 22 |  |  | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 22 | 22 | 22 | 22 | 397152
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 |  | 17 | 19 | 19 | 19 | 19 | 19 | 19 |  | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 410976
63 | Impoprt (Tripura) | 126 | 124 | 120 | 120 | 114 | 110 | 96 | 96 | 102 | 106 | 110 | 116 | 118 | 126 | 126 | 122 | 114 | 132 |  | 144 | 146 | 146 | 142 | 142 | 138 | 122 | 2895360
64 | Malancha, Ctg. EPZ (United) | 38 | 38 | 38 | 38 | 39 | 38 | 37 | 8 | 2 | 2 | 2 | 3 | 6 | 5 | 2 | 3 | 7 | 2 |  | 5 | 9 | 20 | 16 | 37 | 37 | 38 | 454080
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 |  |  | 22 | 22 | 22 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 462312
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 5 |  | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 238140
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 797200
68 | Cumilla 25 MW PP (Summit) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 18 | 17 | 17 | 17 | 17 | 21 | 21 | 21 | 20 | 20 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 506750
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 27 | 27 | 27 | 27 | 27 | 27 | 22 | 26 | 26 | 28 | 28 | 28 | 28 | 17 |  | 17 | 20 | 20 | 29 | 29 | 29 | 30 | 647460
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 820200
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 830400
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 66 | 4 | 0 | [5 empty] | 17 | 80 | 98 | 98 | 17 | 17 | 17 | 17 | 22 |  | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 1271100
| Chowmuhani 113 MW | 90 | 95 | 95 | 95 | 96 | 89 | 96 | 95 | 96 | 96 | 88 | 94 | 87 | 94 | 92 | 90 | 95 | 94 |  | 94 | 95 | 94 | 95 | 96 | 91 | 58 | 2228520
| Manikgonj 162MW PP(MPGL) | 144 | 126 | 90 | 90 | 90 | 54 | 35 | 60 | 90 | 120 | 135 | 144 | 144 | 144 | 144 | 144 | 144 | 144 |  | 144 | 144 | 144 | 144 | 144 | 144 | 144 | 2999520
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | [7 empty] | 5 | 25 | 25 | 25 | 25 | 23 | 25 | 25 | 25 | 25 | 32 |  | 51 | 51 | 51 | 51 | 16 | 16 | 16 | 498720
79 | Kodda 150MW PP | 84 | 48 | 16 | 16 | 0 | [12 empty] | 35 |  | 100 | 150 | 150 | 150 | 48 | 48 | 48 | 743040
80 | Jamalpur 95 MW PP(Powerpac)
81 | Jangalia 52 MW PP (Lakdanavi) | [12 empty] | 4 | 8 | 8 | 8 | 8 | 8 |  | 45 | 25 | 25 | 25 | 25 | 25 | 25 | 255274
| Gazipur 100 MW PP | 52 | 52 | 52 | 52 | 52 | 17 |  | 4 | 17 | 17 | 17 | 17 | 29 | 52 | 52 | 52 | 52 | 60 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1357200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 4 | 3 | 3 | 3 | 1 | 0 | 0 | [9 empty] | 22469
| Jodiac Power | [12 empty] | 8 | 17 | 17 | 17 | 17 | 17 |  | 43 | 54 | 54 | 54 | 54 | 17 | 17 | 392401
| Karnaphuli Power Ltd. | 95 | 107 | 110 | 105 | 110 | 110 | 110 | 105 | 94 | 95 | 94 | 96 | 96 | 96 | 94 | 94 | 94 | 94 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2495698
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [12 empty] | 5 | 37 | 40 |  |  | 13 |  | 50 | 10 | 10 | 10 |  |  | 0 | 186184
86 | Meghnaghat CCPP ( Summit) | 272 | 254 | 263 | 263 | 275 | 257 | 294 | 270 | 240 | 260 | 265 | 260 | 240 | 265 | 240 | 275 | 250 | 300 |  | 300 | 310 | 300 | 290 | 290 | 285 | 250 | 6548393
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 94 | 60 | 0 |  |  |  |  | 2 | 17 | 28 | 88 | 90 | 90 | 92 | 94 | 36 | 36 | 38 |  | 86 | 94 | 94 | 94 | 94 | 94 | 94 | 1385280
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | [11 empty] | 7 | 10 | 10 | 10 | 10 | 10 | 20 |  | 100 | 50 | 50 | 50 | 10 | 10 | 10 | 331680
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 999756
94 | Gagnagar 102 MW PP (Digital Power) | 24 | 7 | 0 | [6 empty] | 64 | 64 | 64 | 85 | 94 | 102 | 102 | 102 | 102 |  | 102 | 74 | 74 | 74 | 24 | 24 | 32 | 1127808
95 | Patenga 50MW PP (Baraka) | [12 empty] | 18 | 41 | 50 | 19 | 19 | 19 |  | 44 | 19 | 19 |  |  |  | 0 | 264960
96 | Chattogram 108 MW PP (ECPV) | 86 | 80 | 82 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 86 | 85 | 80 | 80 | 80 | 84 | 84 | 77 |  | 80 | 77 | 77 | 86 | 86 | 86 | 86 | 2006400
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 43 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1303120
100 | Manikganj 55 MW PP (Northern) | 35 | 0 | [7 empty] | 35 | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 35 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 637501
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 130 | 163 | 130 | 130 | 130 | 130 | 110 | 163 | 163 | 163 | 163 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3487009
102 | Sarishabari 3 MW Solar Plant | [5 empty] | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 2 | 1 | 1 | 0 | 0 | [9 empty] | 9450
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 514440
104 | Keranigonj 300 MW PP (APR) | [12 empty] | 56 | 165 | [11 empty] | 0 | 245730
105 | Bramhangoan 100 MW PP (Aggreko) | [17 empty] | 50 | [7 empty] | 0 | 27063
106 | Mymensingh 200 MW PP (United) | 188 | 188 | 187 | 187 | 188 | 100 | 40 | 65 | 100 | 100 | 100 | 108 | 148 | 80 | 80 | 40 | 40 | 74 |  | 165 | 171 | 171 | 171 | 181 | 180 | 189 | 3223200
112 | Aurahati 100MW PP (Aggreko) | [13 empty] | 100 | [5 empty] | 25 | [5 empty] | 0 | 141474
114 | Kodda 149 MW PP Unit-1 (Summit) | 134 | 134 | 134 | 124 | 122 | 115 | 100 | 114 | 141 | 142 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3387888
115 | Juldah 100 MW PP Unit-3 (Acorn) | 90 | 90 | 90 | 90 | 90 | 60 | 60 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 30 | 76 |  | 90 | 90 | 90 | 90 | 90 | 87 | 87 | 1836480
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 187 | 155 | 155 | 136 | 100 | 100 | 100 | 108 | 155 | 178 | 200 | 155 | 155 | 52 | 52 | 57 |  | 170 | 200 | 200 | 200 | 200 | 200 | 200 | 3758880
117 | Ashuganj 150MW PP (Midland) | 133 | 120 | 127 | 127 | 128 | 50 | 50 | 68 | 112 | 120 | 118 | 118 | 118 | 122 | 122 | 117 | 123 | 120 |  | 127 | 128 | 128 | 128 | 123 | 132 | 133 | 2838618
118 | Bibiyana-III 400 MW CCPP | 315 | 316 | 316 | 315 | 315 | 315 | 315 | 316 | 316 | 316 | 316 | 316 | 315 | 316 | 316 | 316 | 316 | 316 |  | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 7582000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2772000
| Anwara 300 MW PP (United) | 305 | 205 | 167 | 106 | 105 | 105 | 69 | 70 | 140 | 196 | 266 | 286 | 275 | 125 | 178 | 178 | 106 | 178 |  | 304 | 304 | 305 | 305 | 305 | 305 | 305 | 4885200
| Juldah unit-2 (Acorn) | 100 | 100 | 80 | 50 | 50 | 50 | 20 | 20 | 90 | 90 | 90 | 90 | 100 | 60 | 100 | 100 | 50 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 1882560
| Anlima Energy Ltd. | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 114 | 97 | 96 | 96 | 96 | 96 | 96 | 106 | 95 |  | 104 | 108 | 108 | 108 | 108 | 108 | 108 | 2573073
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 443520
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 12 | 21 | 7 | 17 | 14 | 20 | 19 | 13 | 3 | 1 | [9 empty] | 132693
120 | Eastern Zone Total | 8055 | 7741 | 7498 | 7394 | 7310 | 6860 | 6408 | 6379 | 6803 | 7082 | 7288 | 7519 | 7818 | 7640 | 7642 | 7428 | 7202 | 7613 |  | 8725 | 8536 | 8533 | 8550 | 8344 | 8301 | 8236 | 184144614
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [15 empty] | 4 | 4 | 11 |  | 26 | 25 | 25 | 25 | 9 |  |  | 97920
| Khulna 225 MW CCPP | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 |  | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 2378880
129 | Rupsha 105 MW PP (Orion rupsha) | 35 | 0 | [7 empty] | 10 | 53 | 85 | 90 | 17 | 17 | 17 | 17 | 17 |  | 90 | 90 | 90 | 90 | 89 | 89 | 89 | 980640
130
131
132 | United Payra Power Ltd. | [19 empty] | 17 | 17 |  |  |  |  | 0 | 39600
133 | Bhola Nutan Biddut BD LTD (GAS) | 210 | 214 | 211 | 215 | 224 | 203 | 202 | 201 | 193 | 223 | 223 | 224 | 201 | 182 | 211 | 221 | 182 | 183 |  | 218 | 224 | 224 | 223 | 223 | 220 | 220 | 5134227
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 28 | 75 | 81 | 63 | 22 | 22 | 22 | 22 | 21 | 22 |  | 22 | 22 | 22 | 22 | 15 | 15 | 12 | 688963
| Bhola 225 MW CCPP | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 15 | 15 | 15 | 15 | 82 | 82 | 81 | 87 | 87 | 87 |  | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 1527046
140 | Bhola 33 MW PP (Venture) | 28 | 27 | 26 | 25 | 25 | 23 | 20 | 17 | 17 | 17 | 17 | 17 | 19 | 19 | 19 | 19 | 20 | 28 |  | 29 | 29 | 29 | 29 | 30 | 31 | 30 | 546159
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 40 | [5 empty] | 0 | 78720
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 716 | 715 | 715 | 716 | 715 | 716 | 715 | 716 | 716 | 716 | 716 | 716 | 715 | 715 | 715 | 715 | 715 | 716 |  | 715 | 719 | 720 | 719 | 720 | 720 | 720 | 17312000
147 | Bheramara 410 MW CCPP | 380 | 385 | 385 | 390 | 390 | 385 | 300 | 340 | 340 | 300 | 300 | 300 | 300 | 250 | 400 | 400 | 400 | 380 |  | 400 | 395 | 390 | 390 | 380 | 375 | 375 | 8877024
148 | Payra 1320 MW | 470 | 460 | 430 | 400 | 390 | 370 | 350 | 330 | 330 | 320 | 330 | 330 | 330 | 290 | 330 | 350 | 350 | 350 |  | 470 | 500 | 500 | 520 | 540 | 510 | 480 | 10449500
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 79 | 78 | 79 | 79 | 80 | 80 | 80 | 81 | 81 | 80 | 79 |  | 80 | 79 | 80 | 80 | 80 | 81 | 81 | 1926982
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [17 empty] | 14 |  | 50 | 25 | 25 |  |  |  |  | 86624
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 0 | 1 | 1 | 1 | 2 | 3 | 5 | 0 | 0 | 0 | 0 | [9 empty] | 17040
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 174 | 176 | 177 | 176 | 169 | 158 | 160 | 175 | 190 | 187 | 186 | 185 | 187 | 171 | 186 | 179 | 181 | 187 |  | 198 | 196 | 196 | 196 | 191 | 188 | 180 | 4572064
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 185 | 185 | 185 | 185 | 182 | 177 | 180 | 179 | 191 | 195 | 198 | 186 | 189 | 156 | 177 | 189 | 192 | 190 |  | 183 | 185 | 189 | 186 | 184 | 193 | 190 | 4724564
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 392 | 405 | 395 | 364 | 325 | 325 | 353 | 373 | 374 | 322 | 331 | 320 | 295 | 337 | 296 | 307 | 365 | 356 |  | 387 | 416 | 419 | 399 | 405 | 420 | 400 | 8842036
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [16 empty] | 5 | 5 |  | 30 | [6 empty] | 30018
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 22 | 22 | 20 | 22 | 22 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 495120
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 11 | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 247104
165 | Amnura 50 MW PP(Sinha) | [26 empty] | 0
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 43 | 43 | 43 | 43 |  |  | 0 | 104198
167 | Katakhali 50 MW Peaking PP | [17 empty] | 8 |  | 16 | [6 empty] | 11894
168 | Santahar 50 MW Peaking PP | [17 empty] | 15 |  | 34 | 33 | 33 | 32 |  |  |  | 109611
169 | Natore 52 MW PP (Rajlanka) | 52 | 52 | 52 | 52 | 52 | 8 | 8 | 20 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 24 | 24 |  | 34 | 52 | 52 | 52 | 52 | 52 | 52 | 1104480
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 29 |  | 94 | 47 | 47 | 47 | 47 |  | 0 | 242000
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 35 | 0 |  |  |  | 6 | 50 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 36 |  | 96 | 113 | 113 | 113 | 113 | 113 | 113 | 1763136
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 113 | 35 | 0 |  | 35 | 100 | 100 | 113 | 113 | 113 | 113 | 113 | 50 | 50 | 90 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2116512
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 16 |  | 0 | 0 | 0 |  | 0 |  | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 113 | 113 | 113 | 74 | 70 | 40 | 35 |  | 34 | 34 | 34 | 34 | 113 | 34 | 34 | 34 | 34 | 75 |  | 113 | 113 | 113 | 113 | 113 | 70 | 70 | 1698364
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 4 | 6 | 7 | 7 | 7 | 6 | 3 | [10 empty] | 43543
178
178