## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-26 | Sunday
|  |  | Date (day): | 2021-09-26 |  | Sunday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13987.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14930 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-25 | 2021-09-26 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 285 | 310 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 350 | 353 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 312 | 326 | 325 | 325 | 35 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 275 | 317 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 55 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 12 | 61 | 63 | 63 |  | 37 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 21 | 19 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 290 | 280 | 280 | 290 | 45 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 64 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 35 | 54 | 54 | 54
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 16 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 55 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 49 | 53 | 53 | 53 |  | 27 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 33 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 275 | 298 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 25 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 114 | 130 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 89 | 94 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 26 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 2886 | 3381 | 3672 | 3952 | 917 | 809
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 120 | 115 | 120 | 60 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 0 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 0 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 18 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 169 | 115 | 115 | 165 | 65 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 80 | 105 | 90 | 90 |  | 15 | Engine problem
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 68 | 0 | 68 |  | 34 | Engine problem
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 40 | 100 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 100 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 7 | 10 | 30
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 0 | 87 | 85 | 86 |  | 22 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 5 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 305 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 65 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 100 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1182 | 1475 | 1416 | 1535 | 125 | 724
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 180 | 210 | 210 | 210
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 295 | 270 | 300 | 300 | 60 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 300 | 275 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 51 | 51 | 51 | 51
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 63 | 63 | 63 | 132 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 43 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 133 | 133 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 50 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 142 | 140 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 155 | 193 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 19 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 130 | 134 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 8 | 52 | 52
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 30 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 52 | 114 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 49 | 96 | 90 | 94 |  | 19 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1678 | 1936 | 2112 | 2242 | 650 | 124
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 151 | 167 | 160 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 100 | 182 | 175 | 180 |  | 20 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 54 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 0 | 0 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 443 | 485 | 553.6 | 517 | 32 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 43 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 163 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 160 | 160 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 47 | 47 | 47 | 47
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 11 | 11 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 30 | 25 | 30 | 30 | 36 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 76 | 78 | 78 | 78 |  | 8 | Engine problem
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 152 | 220 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 22 | 24 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 300 | 290 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 315 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 0 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1658 | 1714 | 1771 | 1771 | 363 | 225
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 712 | 719 | 728 | 728
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 25 | 0 | 32 |  | 22 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 225 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 355 | 400 | 400 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 80 | 88 | 88 | 88 |  | 17 | Engine problem
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1267 | 1507 | 1591 | 1723 | 0 | 108
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 16 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 22 | 35 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 88 | 87 | 87 | 87 |  | 107 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 86 | 91 | 81 | 81 | 14 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 370 | 530 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 89 | 106 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 72 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 655 | 937 | 1153 | 1303 | 14 | 107
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 36 | 34 | 36 |  | 35 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 0 | 27 | 27 | 27 | 23 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 43 | 0 | 43 |  | 7 | Engine problem
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 40 | 0 | 35 |  | 15 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 191 | 188 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 192 | 189 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 396 | 420 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 33 | 0 | 33 |  | 17 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 18 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 2 | 52 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 92 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 95 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 1001 | 1428 | 1518 | 1669 | 403 | 84
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 79 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 104 | 110 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 191 | 189 | 201 | 218 | 0 | 374
|  | Total |  |  |  |  | 22031 | 21180 | 10961 | 13052 | 13987.6 | 14930 | 2504 | 2642
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10504.1517 | 12508 | 13404.6047 | 14307.726
| A. |  | 2021-09-25 | (Yesterday) |  |  |  |  | Saturday
| 1 | Highest Generation : |  |  | 13052 | MW at | 20:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 20:00 | hrs.
| 2 | Minimum Generation : |  |  | 9880 | MW at | 7:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 13052 | MW
| 3 | Day peak Generation : |  |  | 10961 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12508 | MW
| 4 | Evening peak Generation : |  |  | 13052 | MW at | 20:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 275.5205 | MKWHr | By Solar | 0.63075 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 151.7341 | MKWHr |  | By Oil: | 86.3336 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.1595 | MKWHr |  | By Hydro: | 3.3275 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2504 | MW | Dhaka | 4387 | 4387 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2642 | MW | Chittagong | 1290 | 1290 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5146 | MW | Khulna | 1566 | 1566 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1160.69 | MMCFD |  |  | Rajshahi | 1307 | 1307 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 157306279.354 | ii) Oil : | Taka | 626794153.49 | Comilla | 1223 | 1223 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 60831533.89 | Total | Taka | 844931966.734 | Mymensingh | 1018 | 1018 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 2.9265 | MKWHr. | Sylhet | 580 | 580 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | -174 | MW (E to W) at | 20:00 | hrs | Barisal | 384 | 384 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -316 | MW at | 1:00 | hrs | Rangpur | 753 | 753 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35° C |  |  | Total | 12508 | 12508 |  | 0
| B. |  | 2021-09-26 | (Today) |  |  |  | Sunday |  |  | Probable max. temperature in Dhaka |  |  | 34.8° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13300 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14930 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 11000 | MW
| 4 | Reserve(Generation end) |  |  |  | 1630 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 280.7556 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 10085 | MW at | 7:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2727 | MKWHr. | ii) HVDC Flow at Peak Time |  | 719 | MW at | 20:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0624 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 23:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.56 |  | (b) Today: | 106.45 |  | (c) Rule Curve: |  | 104.8
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-25
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 384 | 325 |  | 0 | 280 | 270 | 0 | 0 | 45 | 250 | 0 | 0 | 0 | 102 | 150 | 63 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 0 | 16 | 0 | 91 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 22 | 0 | 34 | 88 | 86 | 50 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 207 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 138 | 207 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 0 | 78 | 0 | 227 | 18 | 0 | 0 | 285 | 24 | 11 | 0 | 275 | 0 | 0 | 181 | 0 | 132 | 0 | 100 | 200 | 137 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 57 | 100 | 320 | 90 | 0 | 126 | 108 | 0 | 35 | 0 |  | 714 | 0 | 355 | 0 | 0 | 200 | 0 | 0 | 7 | 0 | 0 | 86 | 34 | 0 | 0 | 0 | 0 | 43 | 21 | 91 | 27 | 0 | 16 | 52 | 32 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 0 | 80 | 0 | 175 | 0 | 325 | 88 | 0 | 94 | 0 | 104 | 0 | 0 | 95 | 490 | 115 | 0 | 116 | 0 |  | 8665 | 3636 | 12301 | 4401 | 714 | 1869 | 3851 | 568 | 166 | 594 | 138 | 0 | 0 | 106.57
2:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 360 | 324 |  | 0 | 280 | 295 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 82 | 40 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 91 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 88 | 0 | 32 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 208 | 8 | 140 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 134 | 204 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 130 | 162 | 0 | 78 | 0 | 200 | 18 | 0 | 0 | 295 | 24 | 11 | 0 | 282 | 0 | 0 | 182 | 0 | 131 | 0 | 100 | 200 | 135 | 316 | 115 | 17 | 105 | 0 | 305 | 54 | 110 | 114 | 57 | 100 | 320 | 93 | 0 | 126 | 108 | 0 | 35 | 0 |  | 714 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 0 | 0 | 0 | 0 | 32 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 82 | 0 | 171 | 0 | 379 | 88 | 0 | 94 | 0 | 104 | 0 | 0 | 95 | 500 | 107 | 0 | 100 | 0 |  | 8331 | 3440 | 11771 | 4421 | 714 | 1925 | 3521 | 579 | 166 | 311 | 134 | 0 | 0 | 106.57
3:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 365 | 323 |  | 0 | 280 | 305 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 17 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 13 | 10 | 0 | 32 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 206 | 8 | 139 | 23 | 51 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 21 | 134 | 206 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 20 | 78 | 0 | 200 | 18 | 0 | 0 | 310 | 24 | 11 | 0 | 290 | 0 | 0 | 182 | 0 | 128 | 0 | 100 | 200 | 118 | 316 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 59 | 57 | 100 | 320 | 94 | 0 | 126 | 108 | 0 | 6 | 0 |  | 713 | 0 | 390 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 83 | 0 | 183 | 0 | 418 | 78 | 0 | 94 | 0 | 104 | 0 | 0 | 95 | 500 | 107 | 0 | 35 | 0 |  | 8105 | 3330 | 11435 | 4448 | 713 | 1978 | 3226 | 579 | 160 | 197 | 134 | 0 | 0 | 106.57
4:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 394 | 322 |  | 0 | 280 | 290 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 48 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 208 | 8 | 140 | 23 | 51 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 21 | 130 | 206 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 30 | 78 | 0 | 200 | 18 | 0 | 0 | 305 | 24 | 11 | 0 | 290 | 0 | 0 | 182 | 0 | 114 | 0 | 100 | 200 | 137 | 316 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 6 | 57 | 100 | 321 | 93 | 0 | 90 | 108 | 0 | 17 | 0 |  | 713 | 0 | 365 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 82 | 0 | 182 | 0 | 416 | 17 | 0 | 94 | 0 | 104 | 0 | 0 | 95 | 500 | 107 | 0 | 17 | 0 |  | 7998 | 3199 | 11197 | 4510 | 713 | 1946 | 2974 | 580 | 160 | 184 | 130 | 0 | 0 | 106.56
5:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 395 | 332 |  | 0 | 280 | 275 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 32 | 64 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 209 | 8 | 141 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 21 | 124 | 207 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 161 | 61 | 75 | 0 | 200 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 290 | 0 | 0 | 182 | 0 | 100 | 0 | 100 | 200 | 138 | 316 | 115 | 0 | 105 | 0 | 305 | 54 | 110 | 0 | 57 | 100 | 320 | 93 | 0 | 90 | 108 | 0 | 17 | 0 |  | 712 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 169 | 0 | 81 | 0 | 173 | 0 | 409 | 0 | 0 | 94 | 0 | 104 | 0 | 0 | 95 | 500 | 108 | 0 | 0 | 0 |  | 7958 | 3143 | 11101 | 4518 | 712 | 1945 | 2878 | 580 | 160 | 184 | 124 | 0 | 0 | 106.56
6:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 377 | 323 |  | 0 | 280 | 270 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 85 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 0 | 0 | 0 | 280 | 350 | 211 | 8 | 141 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 21 | 110 | 207 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 30 | 75 | 0 | 193 | 18 | 0 | 0 | 285 | 24 | 11 | 0 | 195 | 0 | 0 | 183 | 0 | 100 | 0 | 100 | 100 | 137 | 316 | 115 | 0 | 51 | 0 | 244 | 54 | 51 | 0 | 57 | 100 | 320 | 93 | 1 | 90 | 100 | 0 | 17 | 0 |  | 713 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 82 | 0 | 168 | 0 | 310 | 0 | 0 | 50 | 0 | 56 | 0 | 0 | 50 | 380 | 107 | 0 | 0 | 0 |  | 7430 | 2776 | 10206 | 4452 | 713 | 1831 | 2359 | 460 | 160 | 120 | 110 | 1 | 0 | 106.56
7:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 371 | 325 |  | 0 | 280 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 0 | 0 | 89 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 29 | 0 | 0 | 0 | 280 | 300 | 180 | 8 | 138 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 21 | 108 | 207 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 110 | 159 | 30 | 75 | 0 | 140 | 18 | 0 | 0 | 295 | 24 | 11 | 0 | 195 | 0 | 0 | 183 | 0 | 100 | 1 | 50 | 100 | 135 | 316 | 115 | 7 | 51 | 1 | 217 | 54 | 51 | 0 | 57 | 60 | 320 | 55 | 6 | 90 | 53 | 0 | 17 | 4 |  | 713 | 0 | 375 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 82 | 0 | 172 | 0 | 346 | 0 | 0 | 50 | 0 | 56 | 0 | 2 | 50 | 340 | 108 | 0 | 0 | 0 |  | 7078 | 2802 | 9880 | 4307 | 713 | 1842 | 2192 | 420 | 164 | 120 | 108 | 14 | 0 | 106.55
8:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 372 | 325 |  | 0 | 280 | 305 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 28 | 33 | 33 | 19 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 8 | 0 | 0 | 0 | 280 | 300 | 181 | 8 | 140 | 20 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 11 | 33 | 21 | 120 | 204 | 0 | 21 | 1 | 43 | 0 | 47 | 0 | 110 | 161 | 30 | 75 | 0 | 140 | 18 | 0 | 0 | 300 | 24 | 11 | 0 | 195 | 0 | 0 | 140 | 0 | 0 | 0 | 50 | 100 | 123 | 316 | 115 | 90 | 51 | 2 | 215 | 54 | 51 | 0 | 58 | 60 | 320 | 55 | 28 | 90 | 53 | 0 | 17 | 10 |  | 712 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 81 | 0 | 186 | 0 | 354 | 0 | 0 | 50 | 0 | 100 | 0 | 4 | 50 | 280 | 108 | 0 | 0 | 2 |  | 7052 | 2831 | 9883 | 4344 | 712 | 1829 | 2187 | 359 | 165 | 120 | 120 | 47 | 0 | 106.55
9:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 371 | 321 |  | 0 | 280 | 270 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 24 | 33 | 33 | 37 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 0 | 0 | 275 | 320 | 178 | 8 | 137 | 20 | 52 | 0 | 43 | 0 | 0 | 8 | 19 | 0 | 33 | 20 | 114 | 204 | 0 | 21 | 2 | 43 | 0 | 47 | 0 | 130 | 163 | 30 | 78 | 0 | 140 | 18 | 0 | 0 | 300 | 24 | 11 | 0 | 218 | 0 | 0 | 140 | 0 | 0 | 0 | 88 | 100 | 133 | 316 | 115 | 105 | 51 | 3 | 215 | 54 | 51 | 0 | 57 | 100 | 320 | 55 | 41 | 90 | 53 | 0 | 17 | 16 |  | 713 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 0 | 80 | 0 | 200 | 0 | 363 | 0 | 0 | 50 | 0 | 104 | 0 | 5 | 50 | 280 | 108 | 0 | 0 | 4 |  | 7232 | 2826 | 10058 | 4366 | 713 | 1849 | 2299 | 361 | 165 | 120 | 114 | 71 | 0 | 106.55
10:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 371 | 320 |  | 0 | 280 | 290 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 21 | 25 | 24 | 25 | 33 | 33 | 0 | 90 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 2 | 0 | 0 | 0 | 305 | 315 | 184 | 8 | 140 | 23 | 52 | 0 | 35 | 0 | 0 | 8 | 19 | 0 | 33 | 12 | 114 | 181 | 0 | 21 | 2 | 43 | 0 | 47 | 0 | 130 | 161 | 30 | 77 | 0 | 140 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 273 | 0 | 0 | 100 | 0 | 10 | 0 | 88 | 100 | 133 | 316 | 115 | 105 | 51 | 4 | 215 | 54 | 51 | 0 | 57 | 100 | 320 | 55 | 51 | 90 | 53 | 0 | 17 | 23 |  | 713 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 82 | 0 | 194 | 0 | 409 | 0 | 0 | 50 | 0 | 104 | 0 | 5 | 50 | 300 | 89 | 0 | 0 | 4 |  | 7285 | 2892 | 10177 | 4380 | 713 | 1860 | 2358 | 378 | 165 | 120 | 114 | 89 | 0 | 106.54
11:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 361 | 320 |  | 0 | 280 | 282 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 40 | 0 | 0 | 0 | 0 | 0 | 35 | 17 | 17 | 21 | 25 | 24 | 25 | 33 | 33 | 0 | 92 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 1 | 21 | 5 | 0 | 0 | 0 | 300 | 310 | 184 | 36 | 140 | 23 | 51 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 33 | 12 | 130 | 166 | 0 | 21 | 1 | 43 | 0 | 47 | 0 | 163 | 161 | 30 | 77 | 0 | 140 | 18 | 0 | 0 | 300 | 22 | 11 | 0 | 273 | 0 | 0 | 100 | 0 | 107 | 0 | 88 | 112 | 135 | 316 | 115 | 105 | 53 | 2 | 302 | 54 | 51 | 17 | 54 | 100 | 321 | 56 | 57 | 90 | 66 | 0 | 17 | 33 |  | 713 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 0 | 82 | 0 | 191 | 0 | 409 | 0 | 0 | 65 | 0 | 104 | 0 | 7 | 90 | 340 | 89 | 0 | 0 | 4 |  | 7593 | 2984 | 10577 | 4336 | 713 | 1934 | 2652 | 421 | 167 | 120 | 130 | 104 | 0 | 106.54
12:00 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 350 | 312 |  | 0 | 280 | 275 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 64 | 16 | 12 | 0 | 0 | 0 | 35 | 17 | 17 | 21 | 25 | 24 | 25 | 33 | 33 | 0 | 94 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 40 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 295 | 300 | 180 | 36 | 142 | 23 | 51 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 12 | 130 | 151 | 0 | 21 | 2 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 76 | 0 | 152 | 18 | 0 | 0 | 300 | 22 | 11 | 0 | 275 | 0 | 0 | 100 | 0 | 114 | 0 | 100 | 155 | 133 | 316 | 115 | 105 | 80 | 5 | 305 | 54 | 65 | 52 | 49 | 100 | 320 | 89 | 54 | 108 | 108 | 0 | 17 | 26 |  | 712 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 18 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 86 | 0 | 192 | 0 | 396 | 80 | 0 | 94 | 0 | 104 | 0 | 7 | 95 | 370 | 89 | 0 | 0 | 5 |  | 7847 | 3114 | 10961 | 4279 | 712 | 1913 | 3073 | 450 | 169 | 136 | 130 | 99 | 0 | 106.54
13:00 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 348 | 312 |  | 0 | 280 | 240 | 0 | 0 | 44 | 290 | 0 | 0 | 0 | 102 | 32 | 20 | 0 | 0 | 0 | 35 | 17 | 17 | 19 | 25 | 24 | 25 | 33 | 0 | 0 | 42 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 60 | 0 | 48 | 21 | 4 | 0 | 0 | 0 | 295 | 300 | 180 | 63 | 138 | 23 | 50 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 18 | 128 | 142 | 0 | 21 | 1 | 43 | 0 | 44 | 0 | 163 | 160 | 30 | 76 | 0 | 213 | 18 | 0 | 0 | 280 | 16 | 11 | 0 | 283 | 0 | 0 | 140 | 0 | 128 | 0 | 90 | 195 | 130 | 316 | 115 | 105 | 105 | 1 | 305 | 44 | 110 | 52 | 49 | 100 | 321 | 94 | 56 | 126 | 108 | 0 | 17 | 31 |  | 713 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 86 | 0 | 192 | 0 | 362 | 84 | 0 | 94 | 0 | 110 | 0 | 7 | 95 | 370 | 89 | 0 | 0 | 5 |  | 8050 | 3090 | 11140 | 4316 | 713 | 1885 | 3278 | 450 | 117 | 152 | 128 | 101 | 0 | 106.53
14:00 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 352 | 290 |  | 0 | 280 | 265 | 0 | 0 | 44 | 290 | 0 | 0 | 0 | 64 | 16 | 10 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 25 | 25 | 33 | 16 | 0 | 42 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 50 | 21 | 3 | 0 | 0 | 0 | 265 | 265 | 179 | 63 | 139 | 23 | 49 | 0 | 35 | 0 | 0 | 8 | 19 | 0 | 33 | 18 | 132 | 144 | 0 | 0 | 1 | 43 | 0 | 44 | 0 | 110 | 160 | 30 | 76 | 0 | 214 | 17 | 0 | 0 | 260 | 16 | 11 | 0 | 293 | 0 | 0 | 100 | 0 | 131 | 0 | 100 | 100 | 128 | 316 | 115 | 52 | 105 | 4 | 305 | 43 | 110 | 17 | 49 | 100 | 320 | 94 | 48 | 144 | 108 | 0 | 17 | 4 |  | 713 | 0 | 300 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 0 | 86 | 0 | 179 | 0 | 307 | 53 | 0 | 94 | 0 | 110 | 0 | 7 | 95 | 350 | 103 | 0 | 0 | 1 |  | 7582 | 2889 | 10471 | 4102 | 713 | 1749 | 3027 | 430 | 117 | 136 | 132 | 65 | 0 | 106.52
15:00 | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 321 | 317 |  | 0 | 280 | 280 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 64 | 16 | 10 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 41 | 75 | 115 | 0 | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 265 | 265 | 181 | 63 | 139 | 23 | 51 | 0 | 35 | 0 | 0 | 25 | 19 | 0 | 33 | 18 | 136 | 143 | 0 | 0 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 30 | 77 | 0 | 221 | 17 | 0 | 0 | 290 | 16 | 8 | 0 | 293 | 0 | 0 | 70 | 0 | 88 | 0 | 100 | 100 | 130 | 315 | 85 | 52 | 105 | 3 | 305 | 54 | 110 | 17 | 47 | 100 | 321 | 94 | 12 | 144 | 108 | 0 | 11 | 0 |  | 713 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 11 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 85 | 0 | 175 | 0 | 346 | 53 | 0 | 94 | 0 | 108 | 0 | 6 | 95 | 370 | 107 | 0 | 0 | 0 |  | 7485 | 3021 | 10506 | 4111 | 713 | 1871 | 2951 | 451 | 116 | 136 | 136 | 21 | 0 | 106.52
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 314 | 320 |  | 0 | 280 | 275 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 64 | 16 | 12 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 28 | 25 | 33 | 16 | 0 | 40 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 0 | 50 | 21 | 2 | 0 | 0 | 0 | 265 | 265 | 212 | 63 | 139 | 23 | 45 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 130 | 155 | 0 | 21 | 0 | 43 | 0 | 44 | 0 | 130 | 160 | 25 | 78 | 0 | 221 | 17 | 0 | 0 | 310 | 20 | 0 | 0 | 300 | 0 | 0 | 70 | 0 | 81 | 0 | 100 | 100 | 132 | 315 | 85 | 52 | 68 | 0 | 305 | 54 | 68 | 34 | 52 | 100 | 320 | 94 | 10 | 146 | 108 | 0 | 17 | 0 |  | 713 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 0 | 17 | 0 | 5 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 88 | 0 | 184 | 0 | 400 | 35 | 0 | 70 | 0 | 102 | 0 | 4 | 70 | 410 | 105 | 0 | 0 | 0 |  | 7524 | 3099 | 10623 | 4241 | 713 | 1941 | 2838 | 491 | 115 | 140 | 130 | 14 | 0 | 106.51
17:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 314 | 320 |  | 0 | 280 | 252 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 64 | 16 | 20 | 0 | 0 | 0 | 35 | 17 | 17 | 0 | 25 | 20 | 25 | 33 | 16 | 0 | 39 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 30 | 17 | 50 | 21 | 4 | 0 | 0 | 0 | 265 | 265 | 212 | 63 | 132 | 23 | 46 | 0 | 35 | 0 | 0 | 8 | 19 | 11 | 33 | 18 | 134 | 164 | 0 | 18 | 0 | 43 | 0 | 44 | 0 | 130 | 161 | 30 | 40 | 0 | 220 | 17 | 0 | 0 | 280 | 20 | 0 | 0 | 300 | 0 | 0 | 70 | 0 | 98 | 1 | 60 | 100 | 140 | 316 | 85 | 52 | 68 | 0 | 305 | 54 | 68 | 34 | 60 | 60 | 320 | 93 | 4 | 162 | 108 | 0 | 17 | 1 |  | 713 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 12 | 8 | 0 | 16 | 0 | 14 | 0 | 5 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 0 | 86 | 0 | 174 | 0 | 355 | 35 | 0 | 70 | 0 | 74 | 0 | 2 | 70 | 430 | 100 | 0 | 17 | 0 |  | 7435 | 3061 | 10496 | 4228 | 713 | 1820 | 2825 | 510 | 114 | 144 | 134 | 8 | 0 | 106.51
18:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 314 | 320 |  | 0 | 280 | 305 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 85 | 82 | 35 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 20 | 25 | 33 | 25 | 0 | 39 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 50 | 37 | 50 | 21 | 2 | 0 | 0 | 0 | 300 | 305 | 210 | 63 | 138 | 23 | 47 | 0 | 41 | 0 | 50 | 8 | 22 | 11 | 33 | 18 | 136 | 164 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 130 | 161 | 30 | 50 | 0 | 221 | 17 | 0 | 0 | 290 | 16 | 0 | 0 | 285 | 0 | 0 | 81 | 0 | 104 | 0 | 90 | 105 | 130 | 313 | 88 | 52 | 74 | 0 | 305 | 54 | 75 | 70 | 86 | 60 | 321 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 350 | 0 | 0 | 145 | 0 | 0 | 11 | 0 | 0 | 87 | 33 | 4 | 0 | 0 | 0 | 40 | 5 | 92 | 27 | 43 | 23 | 16 | 19 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 175 | 0 | 76 | 0 | 181 | 0 | 388 | 35 | 0 | 75 | 0 | 100 | 0 | 0 | 95 | 420 | 106 | 0 | 35 | 0 |  | 7986 | 3409 | 11395 | 4284 | 719 | 1894 | 3216 | 497 | 114 | 535 | 136 | 0 | 0 | 106.5
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 347 | 326 |  | 0 | 280 | 300 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 35 | 35 | 0 | 25 | 26 | 33 | 33 | 51 | 0 | 39 | 75 | 115 | 0 | 19 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 100 | 86 | 50 | 21 | 4 | 0 | 0 | 0 | 265 | 265 | 211 | 63 | 139 | 23 | 50 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 134 | 165 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 300 | 24 | 8 | 30 | 291 | 35 | 0 | 182 | 50 | 122 | 0 | 100 | 179 | 132 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 100 | 92 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 405 | 0 | 0 | 224 | 0 | 0 | 27 | 0 | 0 | 87 | 33 | 16 | 0 | 0 | 0 | 50 | 26 | 92 | 27 | 43 | 38 | 42 | 35 | 21 | 0 | 11 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 91 | 43 | 191 | 0 | 398 | 84 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 520 | 106 | 0 | 72 | 0 |  | 8916 | 4003 | 12919 | 4384 | 719 | 2003 | 4208 | 597 | 114 | 760 | 134 | 0 | 0 | 106.49
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 353 | 326 |  | 0 | 280 | 310 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 35 | 35 | 16 | 25 | 26 | 33 | 33 | 51 | 0 | 39 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 100 | 87 | 50 | 21 | 6 | 0 | 0 | 0 | 265 | 270 | 211 | 63 | 140 | 23 | 52 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 136 | 165 | 0 | 19 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 300 | 24 | 11 | 30 | 298 | 31 | 0 | 182 | 25 | 130 | 0 | 100 | 200 | 133 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 27 | 0 | 0 | 87 | 34 | 16 | 0 | 0 | 0 | 50 | 36 | 92 | 27 | 43 | 38 | 52 | 33 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 91 | 50 | 188 | 0 | 414 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 106 | 0 | 72 | 0 |  | 8996 | 4053 | 13049 | 4406 | 719 | 2024 | 4272 | 609 | 114 | 769 | 136 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 353 | 326 |  | 0 | 280 | 317 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 100 | 87 | 50 | 21 | 7 | 0 | 0 | 0 | 270 | 275 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 134 | 167 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 11 | 30 | 298 | 0 | 0 | 182 | 25 | 130 | 0 | 100 | 193 | 133 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 25 | 0 | 0 | 87 | 35 | 16 | 0 | 0 | 0 | 50 | 36 | 92 | 27 | 43 | 40 | 52 | 33 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 91 | 50 | 189 | 0 | 420 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 106 | 0 | 72 | 0 |  | 8991 | 4061 | 13052 | 4425 | 719 | 2021 | 4260 | 609 | 115 | 769 | 134 | 0 | 0 | 106.49
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 353 | 326 |  | 0 | 280 | 310 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 41 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 100 | 87 | 50 | 21 | 7 | 0 | 0 | 0 | 265 | 265 | 211 | 63 | 139 | 23 | 52 | 0 | 43 | 0 | 43 | 8 | 22 | 11 | 33 | 20 | 136 | 170 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 161 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 298 | 0 | 0 | 182 | 0 | 135 | 0 | 100 | 200 | 133 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 95 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 405 | 0 | 0 | 226 | 0 | 0 | 24 | 0 | 0 | 87 | 35 | 16 | 0 | 0 | 0 | 50 | 36 | 92 | 27 | 43 | 38 | 52 | 32 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 92 | 50 | 190 | 0 | 403 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 107 | 0 | 72 | 0 |  | 8926 | 4050 | 12976 | 4421 | 719 | 2007 | 4209 | 609 | 116 | 759 | 136 | 0 | 0 | 106.49
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 340 | 328 |  | 0 | 280 | 315 | 0 | 0 | 55 | 270 | 0 | 0 | 0 | 102 | 150 | 62 | 0 | 0 | 0 | 54 | 55 | 17 | 20 | 25 | 28 | 33 | 33 | 51 | 0 | 41 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 68 | 100 | 87 | 50 | 21 | 27 | 0 | 0 | 0 | 265 | 265 | 213 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 134 | 170 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 161 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 280 | 24 | 11 | 0 | 298 | 0 | 0 | 182 | 0 | 147 | 0 | 100 | 200 | 127 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 97 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 400 | 0 | 0 | 227 | 0 | 0 | 24 | 0 | 0 | 87 | 34 | 16 | 0 | 0 | 0 | 50 | 36 | 92 | 27 | 43 | 38 | 52 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 91 | 50 | 187 | 0 | 400 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 107 | 0 | 72 | 0 |  | 8918 | 4038 | 12956 | 4391 | 719 | 2014 | 4204 | 610 | 116 | 768 | 134 | 0 | 0 | 106.48
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 328 |  | 0 | 280 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 17 | 17 | 20 | 25 | 28 | 33 | 33 | 51 | 0 | 42 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 70 | 87 | 50 | 21 | 30 | 0 | 0 | 0 | 265 | 290 | 211 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 130 | 171 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 162 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 11 | 0 | 296 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 200 | 127 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 100 | 100 | 320 | 95 | 0 | 162 | 108 | 0 | 17 | 0 |  | 720 | 0 | 405 | 0 | 0 | 226 | 0 | 0 | 24 | 0 | 0 | 87 | 34 | 16 | 0 | 0 | 0 | 43 | 20 | 92 | 27 | 8 | 38 | 52 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 83 | 50 | 190 | 0 | 412 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 106 | 0 | 72 | 0 |  | 8772 | 3995 | 12767 | 4392 | 720 | 2030 | 4091 | 610 | 117 | 677 | 130 | 0 | 0 | 106.48
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 327 |  | 0 | 280 | 275 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 17 | 17 | 0 | 25 | 29 | 33 | 33 | 51 | 0 | 42 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 51 | 70 | 87 | 50 | 21 | 32 | 0 | 0 | 0 | 265 | 300 | 212 | 63 | 138 | 23 | 52 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 126 | 181 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 295 | 24 | 11 | 0 | 298 | 0 | 0 | 183 | 0 | 149 | 0 | 100 | 200 | 118 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 63 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 405 | 0 | 0 | 228 | 0 | 0 | 24 | 0 | 0 | 87 | 34 | 16 | 0 | 0 | 0 | 43 | 0 | 92 | 0 | 0 | 16 | 52 | 32 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 193 | 0 | 82 | 50 | 193 | 0 | 402 | 88 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 530 | 107 | 0 | 72 | 0 |  | 8703 | 3915 | 12618 | 4396 | 719 | 2027 | 3987 | 610 | 117 | 636 | 126 | 0 | 0 | 106.47
KWH | 0 | 0 | 0 | 0 | 7218364 | 0 | 0 | 8579216 | 7692000 |  | 0 | 6720250 | 6856844 | 0 | 0 | 1296515 | 6590339 | 0 | 0 | 0 | 1773792 | 1527840 | 627122 | 0 | 0 | 0 | 820080 | 539466 | 480634 | 349236 | 600000 | 609660 | 713500 | 741000 | 599520 | 0 | 1511504 | 1816000 | 2800000 | 0 | 213514 | 0 | 0 | 0 | 0 |  | 39840 | 0 | 504184 | 1031160 | 692160 | 768480 | 496128 | 410460 | 0 | 0 | 0 | 6992500 | 7443000 | 4838000 | 903272 | 3334900 | 505008 | 1216320 | 0 | 976746 | 0 | 282124 | 231130 | 478440 | 209700 | 803200 | 459370 | 3062400 | 4205040 | 0 | 403164 | 11050 | 1029000 | 0 | 1138800 | 0 | 3398563 | 3671000 | 650688 | 1781760 | 0 | 4617090 | 382000 | 0 | 0 | 7229000 | 517320 | 210960 | 57600 | 6656616 | 89755 | 0 | 3542400 | 93061 | 2530080 | 1755 | 2127360 | 3774240 | 3166472 | 7575000 | 2689200 | 1792800 | 2182909 | 28680 | 6902509 | 1265889 | 2284935 | 1298460 | 1576680 | 2254080 | 7648300 | 2064960 | 364110 | 3134880 | 2349764 | 0 | 457920 | 150931 |  | 17272727 | 0 | 9174816 | 0 | 0 | 3714240 | 0 | 0 | 171460 | 0 | 0 | 2118998 | 623750 | 95424 | 0 | 0 | 0 | 350032 | 184661 | 772624 | 221040 | 203760 | 206588 | 457440 | 262620 | 459360 | 0 | 236592 | 1866763 | 0 | 0 | 0 | 0 | 0 | 0 | 4485100 | 0 | 1989208 | 314880 | 4684927 | 0 | 9246800 | 1207680 | 0 | 2159232 | 0 | 2429020 | 0 | 47288 | 2159904 | 11292700 | 2576209 | 0 | 846000 | 26940 |  | 193661699 | 81858783 | 275520482 | 105371556 | 17272727 | 46362498 | 78357207 | 13159463 | 3327504 | 7976373 | 3062400 | 630754 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8012384.04 | 0 | 0 | 8665008.16 | 7922760 |  | 0 | 7325072.5 | 7611096.84 | 0 | 0 | 10968516.9 | 6853952.56 | 0 | 0 | 0 | 16176983.04 | 15033945.6 | 5782064.84 | 0 | 0 | 0 | 5986584 | 4170072.18 | 4739051.24 | 261927 | 450000 | 0 | 0 | 0 | 5797358.4 | 0 | 408106.08 | 490320 | 5068000 | 0 | 1983545.06 | 0 | 0 | 0 | 0 |  | 0 | 0 | 4890584.8 | 9847578 | 6021792 | 6086361.6 | 625121.28 | 1219066.2 | 0 | 0 | 0 | 5174450 | 7443000 | 4450960 | 1165220.88 | 3835135 | 570659.04 | 1702848 | 0 | 1670235.66 | 0 | 2849452.4 | 2207291.5 | 607618.8 | 157275 | 1405600 | 344527.5 | 22968000 | 4457342.4 | 0 | 512018.28 | 176137 | 1687560 | 0 | 2027064 | 0 | 3874361.82 | 3817840 | 1281855.36 | 3403161.6 | 0 | 7987565.7 | 836580 | 0 | 0 | 7301290 | 387990 | 160329.6 | 979776 | 50324016.96 | 1524039.9 | 0 | 18420480 | 1555979.92 | 24895987.2 | 20515.95 | 17337984 | 40950504 | 22323627.6 | 7044750 | 24525504 | 16941960 | 19013137.39 | 0 | 52182968.04 | 11025893.19 | 20084578.65 | 12958630.8 | 13512147.6 | 15012172.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99490907.52 | 0 | 9633556.8 | 0 | 0 | 51479366.4 | 0 | 0 | 1798615.4 | 0 | 0 | 2394467.74 | 966812.5 | 931338.24 | 0 | 0 | 0 | 3444314.88 | 1876155.76 | 6837722.4 | 1702008 | 2754835.2 | 2001837.72 | 4432593.6 | 2547414 | 881971.2 | 0 | 179100.144 | 11256580.89 | 0 | 0 | 0 | 0 | 0 | 0 | 5920332 | 0 | 2983812 | 5356108.8 | 5481364.59 | 0 | 9154332 | 12608179.2 | 0 | 20491111.68 | 0 | 18849195.2 | 0 | 522532.4 | 15961690.56 | 49574953 | 0 | 0 | 0 | 0 |  | 617495275.86 | 351513209.824 | 969008485.684 | 105708270.994 | 99490907.52 | 51598008.36 | 534034744.13 | 60831533.89 | 898426.08 | 92759409.36 | 22968000 | 719185.35 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 285 | 0 | 0 | 350 | 312 |  | 0 | 280 | 275 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 64 | 16 | 12 | 0 | 0 | 0 | 35 | 17 | 17 | 21 | 25 | 24 | 25 | 33 | 33 | 0 | 94 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 40 | 0 | 18 | 21 | 2 | 0 | 0 | 0 | 295 | 300 | 180 | 36 | 142 | 23 | 51 | 0 | 35 | 0 | 0 | 8 | 19 | 8 | 33 | 12 | 130 | 151 | 0 | 21 | 2 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 76 | 0 | 152 | 18 | 0 | 0 | 300 | 22 | 11 | 0 | 275 | 0 | 0 | 100 | 0 | 114 | 0 | 100 | 155 | 133 | 316 | 115 | 105 | 80 | 5 | 305 | 54 | 65 | 52 | 49 | 100 | 320 | 89 | 54 | 108 | 108 | 0 | 17 | 26 |  | 712 | 0 | 355 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 88 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 18 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 191 | 0 | 86 | 0 | 192 | 0 | 396 | 80 | 0 | 94 | 0 | 104 | 0 | 7 | 95 | 370 | 89 | 0 | 0 | 5 |  | 10961 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 353 | 326 | 0 | 0 | 280 | 317 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 150 | 61 | 0 | 0 | 0 | 54 | 55 | 35 | 19 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 100 | 87 | 50 | 21 | 7 | 0 | 0 | 0 | 270 | 275 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 134 | 167 | 0 | 21 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 11 | 30 | 298 | 0 | 0 | 182 | 25 | 130 | 0 | 100 | 193 | 133 | 315 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 114 | 96 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 719 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 25 | 0 | 0 | 87 | 35 | 16 | 0 | 0 | 0 | 50 | 36 | 92 | 27 | 43 | 40 | 52 | 33 | 21 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 188 | 0 | 91 | 50 | 189 | 0 | 420 | 88 | 0 | 113 | 0 | 110 | 0 | 0 | 113 | 530 | 106 | 0 | 72 | 0 |  | 13052 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 325 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 102 | 149 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 90 | 75 | 120 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 68 | 100 | 86 | 50 | 21 | 30 | 0 | 0 | 0 | 300 | 300 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 50 | 52 | 22 | 11 | 33 | 20 | 164 | 170 | 8 | 22 | 0 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 180 | 100 | 149 | 0 | 100 | 200 | 135 | 316 | 115 | 100 | 90 | 0 | 300 | 54 | 110 | 114 | 94 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 728 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 32 | 40 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 43 | 35 | 52 | 33 | 22 | 0 | 11 | 80 | 0 | 0 | 15 | 10 | 0 | 0 | 220 | 0 | 81 | 100 | 220 | 0 | 400 | 88 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 325 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 149 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 85 | 50 | 21 | 10 | 0 | 0 | 0 | 300 | 300 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 0 | 52 | 22 | 11 | 33 | 20 | 138 | 160 | 8 | 22 | 1.6 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 175 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 90 | 5 | 300 | 54 | 110 | 114 | 90 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 728 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 0 | 0 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 81 | 50 | 200 | 0 | 400 | 88 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 323 | 327 | 0 | 0 | 280 | 270 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 18 | 25 | 29 | 33 |  | 0 | 0 | 40 | 75 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 21 | 2 | 0 | 0 | 0 | 340 | 310 | 213 | 63 | 140 | 23 | 52 | 0 | 35 | 0 | 0 | 8 | 19 | 0 | 33 | 20 | 102 | 189 | 0 | 19 | 1 | 43 | 0 | 47 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 300 | 24 | 0 | 0 | 195 | 0 | 0 | 60 | 0 | 114 | 12 | 100 | 70 | 140 | 316 | 115 | 0 | 72 | 2 | 304 | 54 | 18 | 0 | 48 | 100 | 320 | 19 | 28 | 90 | 108 | 0 | 17 | 14 | 0 | 506 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 80 | 0 | 193 | 0 | 398 | 17 | 0 | 36 | 0 | 90 | 0 | 3 | 40 | 420 | 108 | 0 | 0 | 2 | 0
199
| Minimum Generation |  | 9880 | 7:00
| Highest Generation |  | 13052 | 20:00
| Day Peak Generation |  | 10961 | 12:00
| Evening Peak Generation |  | 13052 | 20:00
| HVDC Max Flow |  | 720 | 23:00
| HVDC EvPeak Flow |  | 719 | 20:00
| Load factor L.F |  | 87.96%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-26
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-25 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 10961 | MW Hour : | 12:00 | Min. Gen. at | 7:00 | 10085 | MW
Evening Peak Generation : |  | 13052 | MW Hour : | 20:00 | Available Max Generation : |  | 14930 | MW
E.P. Demand (at gen end) : |  | 13052 | MW Hour : | 20:00 | Max Demand (Evening) : |  | 13300 | MW
Maximum Generation : |  | 13052 | MW Hour : | 20:00 | Reserve(Generation end) |  | 1630 | MW
Total Gen. (MKWH) : |  | 275.5205 | System Load Factor : | 87.96% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -316 | MW at | 1:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-26
Actual : | 106.45 | Ft.(MSL) , | Rule curve : | 104.8 | Ft.( MSL )
Gas Consumed : | Total = | 1160.69 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 157306279.354
: |  | Coal : | 60831533.89 | Oil : | 626794153.49 | Total : | 844931966.734
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4734.735 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1615.7762 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1448.6984 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1309.3821 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1183.0706 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 954.7105 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 526.4866 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 245.618 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 736.3553 |  |  | 0 | 0%
Total | 0 |  | 12754.8328 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
7) Raozan #02
8) Fenchuganj 3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Maniknagar-Bangabhaban 132 kV Ckt-1 was under shut down from 09:34 to 15:46 for DPDC work.
b) Barishal 132/33 kV T-2 transformer was under shut down from 11:50 to 13:20 due to R/H maintenance. |  |  |  |  | About 20 MW power interruption occurred under Barishal S/S area
from 11:50 to 13:20.
c) Ghorashal-Ashuganj 132 kV Ckt-2 tripped at 10:01 from both ends showing Dist. C-phase
and was switched on at 10:21.
d) Madunaghat-Chandraghona 132 kV both Ckts were under shut down from 10:56 to 12:03 to pass
Transformer(750 MVA) of Dhaka-Chattogram main power strengthening project.
e) Polashbari-Mahasthangar 132 kV Ckt-1 was under shut down from 08:26 to 13:00 for D/W.
f) Bogura-Natore 132 kV Ckt-1 tripped at 10:11 from both ends showing Dist. Z1, R-phase at Bogura
end & Dist. 3-phase at Natore end and was switched on at 12:21.
g) Hathazari-Raozan 230 kV Ckt-2 tripped at 12:17 from both ends showing Dist. Z1, B-phase at Hathazari
end & Dist. protection at Raozan end and was switched on at 13:46.
h) Barishal 132/33 kV T-1 transformer tripped at 13:16 due to O/C and was switched on at 13:19. |  |  |  |  | About 80 MW power interruption occurred under Barishal S/S area
from 13:16 to 13:19.
i) Polashbari-Mahasthangar 132 kV Ckt-2 was under shut down from 13:20 to 14:54 for D/W.
j) Aminbazar-Kallyanpur 132 kV both Ckts tripped at 14:17 (Ckt-1 from both ends & Ckt-2 from Kallyanpur end)
showing Dist. RST, General trip at Aminbazar end & General trip at Kallyanpur end and were switched
on at 15:06(Ckt-2) & 15:24(Ckt-1).
k) Barishal-Madaripur 132 kV Ckt-1 was under shut down from 15:31 to 16:28 for D/W.
l) Barishal-Madaripur 132 kV Ckt-2 was under shut down from 16:38 to 17:00 for D/W.
m) Rampur-Agrabad 132 Ckt-2 tripped at 20:48 showing Diff. R-phase. |  |  |  |  | About 80 MW power interruption occurred under Agrabad S/S area
from 20:48 to 23:00.
n) Naogaon 132/33 kV T-3 transformer along with 33 kV Bus was under shut down from 23:25 to 00:25(26/09/2021) |  |  |  |  | About 40 MW power interruption occurred under Naogaon S/S area
due to R/H maintenance at 33 kV Santahar feeder. |  |  |  |  | from 23:25 to 00:25(26/09/2021).
o) HVDC Pole-1 tripped at 05:53(26/09/2021) by external protection.

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-25 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 310 | 7218364 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 353 | 8579216 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 326 | 7692000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6720250 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 317 | 6856844 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1296515
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 61 | 627122 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 19 | 349236
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 280 | 6590339 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1773792
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 54 | 820080
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1527840
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 539466
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 480634 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 53 | 1209660 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 713500
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 741000
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 599520
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 298 | 6656616
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 89755 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 0 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 25 | 93061 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 130 | 2530080 | Engine problem
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1792800
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 2064960 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3134880
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 150931
| Dhaka area Total |  |  |  | 5719 | 3381 | 70848461
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 120 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 213514
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 1755
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 768480
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 115 | 3327504 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2182909
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 68 | 504184 | Engine problem
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 100 | 1031160
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2127360
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 496128
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 7 | 410460
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 87 | 692160 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 28680
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 6902509
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1265889
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 2284935
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2254080
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2349764
| Chattogram area Total |  |  |  | 2382 | 1475 | 29641471
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 210 | 4838000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 270 | 6992500 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 275 | 7443000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 505008 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 51 | 1216320
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 63 | 903272 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 43 | 976746 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 133 | 3166472 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 50 | 282124
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 140 | 3334900 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 193 | 3774240
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 478440
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 11 | 209700
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 134 | 3062400
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 803200
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 8 | 231130 | Engine problem
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 459370
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 30 | 57600 | Low demand
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 114 | 1298460
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 96 | 1576680 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 457920 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1936 | 42067482
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 167 | 4205040 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 403164
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 11050
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 182 | 3542400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2689200
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 364110
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 0 | 39840 | Engine problem
| Mymensingh Area Total |  |  |  | 709 | 485 | 11254804
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 43 | 1029000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3398563
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3671000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 47 | 1138800
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 11 | 210960
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 650688 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1781760
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 220 | 4617090
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 382000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 24 | 517320
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 290 | 7229000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 315 | 7575000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 0 | 0 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7648300 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1714 | 39849481
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 719 | 17272727
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 25 | 171460 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 225 | 3714240
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 400 | 9174816 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 314880
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 88 | 1207680 | Engine problem
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1507 | 31855803
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 16 | 95424 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 35 | 623750
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 87 | 2118998 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 91 | 1989208
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 530 | 11292700 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 106 | 2576209 | Engine problem
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 72 | 846000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 937 | 19542289
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 350032
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 36 | 184661 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 221040 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 43 | 203760 | Engine problem
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 40 | 206588 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 188 | 4485100 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 189 | 4684927 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 420 | 9246800 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 33 | 262620 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 459360
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 236592
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 52 | 457440
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 92 | 772624 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2159232
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2159904
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 26940
| Rajshahi Area Total |  |  |  | 2179 | 1428 | 26117620
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 79 | 1866763 | Machine problem
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 110 | 2429020
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 47288
| Rangpur Area Total |  |  |  | 605 | 189 | 4343071
| Total |  |  |  | 21180 | 13052 | 275520482
| Eastern Grid Total |  |  |  | 14221 | 8991 | 193661699
| Western Grid Total |  |  |  | 6959 | 4061 | 81858783
| National Grid Total |  |  |  | 21180 | 13052 | 275520482
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-25
(a) ENTIRE EASTERN GRID : |  | 8498 | MW | (b) ENTIRE WESTERN GRID : |  | 4010 | MW
i) Dhaka area |  | 4387 | MW | i) Khulna area |  | 1566 | MW
ii) Chittagong area |  | 1290 | MW | ii) Rajshahi area |  | 1307 | MW
iii) Comilla area |  | 1223 | MW | iii) Barisal area |  | 384 | MW
iv) Mymensingh area |  | 1018 | MW | iv) Rangpur area |  | 753 | MW
v) Sylhet area |  | 580 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12508 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 134 | 12:00 | Kishoreganj | 148 | 20:00 | Jessore | 106 | 19:00
Munsiganj | 96 | 1:00 | Netrokona | 118 | 23:00 | Benapol | 60 | 1:00
Sonargaon | 68 | 4:00 | Jamalpur | 150 | 2:00 | Jhenida(Old) | 118 | 19:00
Shyampur | 202 | 0:00 | Sherpur | 132 | 22:00 | Bottail | 134 | 19:00
Bhulta | 189 | 21:00 | Srimongal | 63 | 18:30 | G.K Project | 59 | 20:00
Madanganj | 45 | 11:00 | Shahjibazar | 116 | 22:00 | Faridpur | 146 | 21:00
Shitalakhya | 114 | 16:00 | Fenchuganj | 45 | 1:00 | Rajbari | 56 | 19:30
Rahim steel | 22 | 18:30 | Kulawara | 52 | 18:30 | Madaripur | 104 | 22:00
Matuail | 63 | 9:00 | Sylhet | 151 | 21:00 | Sariatpur | 70 | 20:00
Ghorasal | 80 | 22:00 | Chatak | 34 | 20:00 | Gopalganj | 94 | 19:00
Narsingdi | 176 | 22:00 | Sunamganj | 58 | 23:00 | Bagerhat | 101 | 19:30
Haripur (SBU) | 119 | 12:00 | Biani Bazar | 77 | 20:00 | Mongla | 28 | 23:00
Sreenagar | 42 | 22:00 | Comilla (S) | 140 | 18:30 | Satkhira | 101 | 21:00
Ullon | 77 | 12:00 | Comilla(N) | 147 | 19:30 | Gallamari | 49 | 13:00
Hasnabad | 79 | 19:30 | Chandpur | 81 | 21:00 | Magura | 56 | 18:30
Magbazar | 92 | 13:00 | Feni | 127 | 20:00 | Norail | 51 | 18:30
Maniknagar | 70 | 13:00 | Chowmuhani | 225 | 22:00 | Chuadanga | 103 | 20:00
Bangabhaban | 4 | 18:30 | Ashuganj | 43 | 23:00 | Barisal(N) | 46 | 21:00
Motijheel | 30 | 12:00 | Daudkandi | 152 | 21:00 | Barisal (S) | 114 | 19:30
Narinda | 68 | 12:00 | B.Baria | 148 | 21:00 | Patuakhali | 123 | 21:00
Kazla | 74 | 15:00 | Ramganj | 90 | 22:00 | Bhandaria | 58 | 19:00
Dhanmondi | 187 | 13:00 | Chaddagram | 45 | 20:00 | Borguna | 18 | 1:00
Lalbag | 77 | 13:00 | PHP | 10 | 11:00 | Borhan Uddin | 48 | 1:00
Madartek | 75 | 1:00 | Kochua | 66 | 20:00 | Ishurdi | 69 | 19:00
Dhaka University | 33 | 11:00 | Madunaghat | 62 | 18:30 | Ruppur Paromanobik | 3 | 1:00
Aftabnagar | 16 | 13:00 | Hathazari | 96 | 21:00 | Natore | 128 | 21:00
Fatullah | 63 | 12:00 | Khulshi | 194 | 0:00 | Bogra | 161 | 19:30
Nawabganj | 51 | 21:00 | Halishahar | 112 | 23:00 | Noagaon | 118 | 20:00
Keraniganj | 68 | 18:30 | Baraulia | 127 | 8:00 | Rajshahi | 159 | 21:00
Mirpur | 124 | 18:30 | Sikalbaha | 32 | 0:00 | Rajshahi New | 20 | 19:30
Kalyanpur | 105 | 1:00 | Dohazari | 92 | 1:00 | C.Nawabganj | 65 | 19:30
Gulshan | 122 | 12:00 | Cox'sbazar | 103 | 20:00 | Amnura | 51 | 20:00
Uttara | 85 | 12:00 | Chandraghona | 28 | 18:00 | Pabna | 121 | 19:30
Uttara New | 127 | 23:00 | Kaptai | 4.5 | 19:00 | Shahjadpur | 80 | 22:00
Kamrangirchar | 101 | 13:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 98 | 19:30
Savar | 149 | 21:00 | Bakulia | 121 | 18:30 | Niyamatpur | 76 | 21:00
Bhasantec | 141 | 12:00 | Julda | 21 | 10:00 | Joypurhat | 47 | 1:00
Agargaon | 87 | 17:00 | TK chemical | 30.6 | 21:00 | Sherpur(Bogura) | 55 | 18:30
Satmosjid | 107 | 18:30 | Modern Steel | 0 | 1:00 | Mohastangor | 70 | 20:00
Tongi | 124 | 19:00 | Shahmirpur | 31.5 | 18:00 | Bhangura | 32 | 19:00
Kabirpur | 233 | 12:00 | Khagrachhari | 30 | 1:00 | Rangpur | 154 | 19:00
Basundhara | 192 | 13:00 | Matarbari | 40 | 18:00 | Lalmonirhat | 45 | 22:00
Manikganj | 72 | 21:00 | Baroiar Hat | 64 | 18:00 | Saidpur | 97 | 21:00
Joydevpur | 168 | 12:00 | Rangamati | 14 | 18:30 | Purbasadipur | 97 | 14:00
New Tongi | 98 | 11:00 | Abul Khair 230 | 133 | 7:00 | Thakurgaon | 78 | 1:00
Kodda | 291 | 12:00 | BSRM | 154 | 0:00 | Palashbari | 117 | 1:00
Dhamrai | 118 | 12:00 | GPH Ispat | 15 | 11:00 | Barapukuria | 51 | 22:00
Rajendrapur | 106 | 11:00 | Agrabad | 86 | 18:00 | Panchagar | 51 | 23:00
Valuka | 116 | 12:00 | Goalpara | 28 | 13:00 | Joldhaka | 52 | 2:00
Tangail | 195 | 1:00 | Central S/S | 102 | 19:00 | Kurigram | 56 | 2:00
Mymensing | 229 | 19:00 | Noapara | 53 | 19:00 | Mithapukur | 29 | 1:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-25 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 405 | 6:00 | 400 | 17:00 | Kaliakoir | 399 | 0.375 | 385 | 0.375
| Bheramara | 402 | 6:00 | 396 | 18:30 | Bhulta | 387 | 0.25 | 379 | 0.45833
| Ashuganj(N) | 394 | 14:00 | 386 | 11:00 | Gopalganj | 409 | 0.625 | 391 | 0.77083
| Payra | 413 | 6:00 | 402 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 235 | 12:00 | 230 | 8:00
| Ishurdi | 233 | 9:00 | 224 | 21:00 | Megnaghat | 234 | 17:00 | 230 | 1:00
| Ashuganj | 241 | 14:00 | 237 | 1:00 | Fenchuganj | 243 | 3:00 | 240 | 1:00
| Serajganj | 230 | 9:00 | 225 | 1:00 | Siddhirganj | 233 | 5:00 | 227 | 11:00
| Baghabari | 231 | 7:00 | 203 | 11:00 | Maniknagar | 231 | 5:00 | 225 | 11:00
| Barapukuria | 235 | 9:00 | 223 | 20:00 | Agargaon | 229 | 9:00 | 221 | 11:00
| Bogra | 223 | 18:00 | 211 | 20:00 | Barisal | 256 | 12:00 | 235 | 1:00
| Rajshahi | 230 | 18:00 | 219 | 3:00 | Bhola 225 MW | 247 | 8:00 | 238 | 1:00
| Khulna South | 231 | 11:00 | 221 | 4:00 | AKSML | 236 | 12:00 | 227 | 10:00
| Rampura | 230 | 3:00 | 225 | 12:00 | BSRM | 234 | 12:00 | 227 | 10:00
| Haripur | 229 | 1:00 | 224 | 10:00 | Bibiyana | 241 | 6:00 | 239 | 1:00
| Hasnabad | 227 | 4:00 | 221 | 11:00 | Bhulta | 233 | 5:00 | 227 | 11:00
| Shyampur | 229 | 6:00 | 221 | 11:00 | Ashuganj (S) | 238 | 6:00 | 235 | 9:00
| Aminbazar | 230 | 1:00 | 29 | 2:00 | Kaliakoir | 230 | 14:00 | 223 | 11:00
| Tongi | 231 | 13:00 | 221 | 8:00 | GPH | 234 | 1:00 | 223 | 21:00
| Comilla (N) | 231 | 4:00 | 228 | 11:00 | Jhenaidah | 230 | 10:00 | 220 | 20:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 133 | 8:00 | Madanhat | 138 | 0.75 | 132 | 0.29167
| Munsiganj | 135 | 1:00 | 129 | 11:00 | Hathazari | 138 | 0.8125 | 135 | 0.29167
| Sonargaon | 135 | 6:00 | 130 | 10:00 | Khulshi | 135 | 0.8125 | 130 | 0.29167
| Shyampur | 136 | 2:00 | 131 | 11:00 | Halishahar | 137 | 0.041667 | 130 | 0.33333
| Bhulta | 128 | 3:00 | 123 | 11:00 | Baraulia | 135 | 0.041667 | 132 | 0.29167
| Madanganj | 135 | 1:00 | 130 | 7:00 | Sikalbaha | 137 | 0.8125 | 132 | 0.33333
| Shitalakhya | 135 | 1:00 | 130 | 11:00 | Dohazari | 131 | 0.375 | 127 | 0.20833
| Rahim steal | 134 | 1:00 | 130 | 10:00 | Cox'sbazar | 124 | 0.625 | 116 | 0.95833
| Matuail | 134 | 1:00 | 133 | 8:00 | Chandraghona | 137 | 0.041667 | 133 | 0.41667
| Ghorasal | 139 | 13:00 | 136 | 12:00 | Kaptai | 137 | 0.875 | 134 | 0.29167
| Narsinghdi | 136 | 14:00 | 125 | 22:00 | A. Khaer Stl. | 136 | 0.8125 | 133 | 0.41667
| Haripur (SBU) | 134 | 2:00 | 130 | 12:00 | Bakulia | 136 | 0.8125 | 131 | 0.29167
| Sreenagar | 134 | 1:00 | 129 | 11:00 | Julda | 136 | 0.041667 | 133 | 0.25
| Ullon | 134 | 3:00 | 128 | 11:00 | TK Chemical | 137 | 0.875 | 134 | 0.041667
| Hasnabad | 136 | 1:00 | 131 | 11:00 | Modern Steel | 136 | 0.041667 | 132 | 0.29167
| Magbazar | 135 | 4:00 | 127 | 12:00 | Shahmirpur | 137 | 0.79167 | 131 | 0.33333
| Maniknagar | 135 | 4:00 | 130 | 11:00 | Khagrachhari | 136 | 0.041667 | 133 | 0.20833
| Bangabhaban | 135 | 4:00 | 130 | 11:00 | Matarbari | 128 | 0.375 | 120 | 0.041667
| Motijheel | 135 | 4:00 | 130 | 11:00 | Baroiar Hat | 135 | 0.33333 | 131 | 0.625
| Narinda | 135 | 4:00 | 130 | 11:00 | Rangamati | 136 | 1:00 | 133 | 10:00
| Kazla | 135 | 4:00 | 130 | 11:00 | Agrabad | 135 | 1:00 | 131 | 8:00
| Dhanmondi | 134 | 3:00 | 129 | 11:00 | Goalpara S/S | 138 | 9:00 | 132 | 0.875
| Lalbag | 135 | 6:00 | 129 | 11:00 | Khulna Central S/S | 138 | 9:00 | 131 | 0.125
| Madartek | 135 | 6:00 | 128 | 11:00 | Noapara | 136 | 9:00 | 128 | 0.125
| Dhaka University | 134 | 4:00 | 127 | 11:00 | Jessore | 134 | 9:00 | 122 | 0.875
| Aftabnagar | 135 | 5:00 | 127 | 12:00 | Benapol | 134 | 0.41667 | 122 | 0.83333
| Fatullah | 136 | 5:00 | 131 | 11:00 | Jhenida(Old) | 132 | 9:00 | 117 | 0.875
| Nawabganj | 135 | 6:00 | 129 | 11:00 | Bottail | 134 | 0.375 | 124 | 0.875
| Keraniganj | 135 | 5:00 | 129 | 11:00 | G.K Project | 138 | 0.29167 | 133 | 0.083333
| Mirpur | 131 | 2:00 | 125 | 11:00 | Faridpur | 135 | 0.29167 | 128 | 0.041667
| Kalyanpur | 131 | 13:00 | 0 | 15:00 | Rajbari | 135 | 0.375 | 128 | 0.20833
| Gulshan | 134 | 5:00 | 127 | 11:00 | Madaripur | 141 | 0.29167 | 133 | 0.875
| Uttara | 130 | 2:00 | 123 | 12:00 | Shariyatpur S/S | 140 | 8:00 | 131 | 0.875
| Uttara New | 131 | 1:00 | 124 | 11:00 | Gopalganj | 145 | 0.33333 | 134 | 0.875
| Kamrangirchar | 134 | 1:00 | 129 | 11:00 | Bagerhat | 138 | 10:00 | 128 | 0.83333
| Savar | 133 | 15:00 | 125 | 11:00 | Mongla | 136 | 6:00 | 128 | 0.041667
| Bhasantec | 135 | 3:00 | 129 | 11:00 | Satkhira | 137 | 9:00 | 127 | 20:00
| Agargaon | 137 | 6:00 | 130 | 11:00 | Gallamari | 138 | 0.375 | 131 | 2:00
| Satmosjid | 137 | 6:00 | 130 | 11:00 | Magura | 132 | 9:00 | 116 | 0.83333
| Tongi | 140 | 13:00 | 132 | 8:00 | Narail | 131 | 0.375 | 113 | 0.83333
| Kabirpur | 139 | 14:00 | 129 | 18:30 | Chuadanga | 135 | 9:00 | 121 | 0.875
| Basundhara | 138 | 18:30 | 130 | 12:00 | Barisal(N) | 143 | 7:00 | 134 | 0.041667
| Manikganj | 142 | 6:00 | 134 | 20:00 | Barisal (S) | 141 | 7:00 | 133 | 15:00
| Joydevpur | 137 | 1:00 | 133 | 12:00 | Patuakhali(S) | 141 | 0.33333 | 130 | 0.625
| New Tongi | 140 | 0:00 | 131 | 12:00 | Bhandaria | 145 | 0.33333 | 126 | 0.041667
| Kodda | 139 | 13:00 | 125 | 8:00 | Borguna | 140 | 0.33333 | 131 | 0.625
| Dhamrai | 137 | 6:00 | 130 | 11:00 | Jhenaidah(New) | 138 | 17:00 | 122 | 1:00
| Rajendrapur | 136 | 1:00 | 124 | 16:00 | Ishurdi | 135 | 8:00 | 130 | 2:00
| Valuka | 132 | 14:00 | 110 | 1:00 | Ruppur Paromanobik | 136 | 18:00 | 131 | 1:00
| Tangail | 138 | 14:00 | 122 | 19:30 | Natore | 135 | 18:00 | 128 | 2:00
| Mymensing | 133 | 14:00 | 114 | 1:00 | Bogra | 133 | 11:00 | 125 | 21:00
| Kishorganj | 134 | 16:00 | 118 | 1:00 | Noagaon | 131 | 18:00 | 120 | 20:00
| Netrokona | 130 | 14:00 | 108 | 1:00 | Rajshahi | 133 | 8:00 | 127 | 1:00
| Jamalpur | 138 | 7:00 | 121 | 22:00 | Rajshahi New | 136 | 18:00 | 128 | 3:00
| Sherpur | 136 | 14:00 | 118 | 22:00 | C.Nawabganj | 135 | 18:00 | 126 | 5:00
| Srimongal | 138 | 9:00 | 130 | 22:00 | Amnura | 132 | 18:00 | 122 | 3:00
| Shahjibazar | 139 | 15:00 | 130 | 1:00 | Pabna | 133 | 18:00 | 128 | 2:00
| Fenchuganj | 136 | 7:00 | 132 | 19:30 | Shahjadpur | 135 | 5:00 | 132 | 1:00
| Khulawara | 136 | 9:00 | 131 | 1:00 | Serajganj | 130 | 7:00 | 126 | 19:30
| Sylhet | 131 | 1:00 | 129 | 18:00 | Niyamatpur | 128 | 17:00 | 117 | 21:00
| Chatak | 132 | 7:00 | 128 | 1:00 | Joypurhat | 131 | 18:00 | 120 | 20:00
| Sunamganj | 130 | 8:00 | 121 | 23:00 | Sherpur(Bogura) | 134 | 17:00 | 126 | 20:00
| Biani Bazar | 132 | 7:00 | 124 | 20:00 | Mohastangor | 132 | 17:00 | 123 | 20:00
| Comilla(s) | 129 | 6:00 | 124 | 18:30 | Bangura | 135 | 18:00 | 132 | 1:00
| Comilla(n) | 138 | 9:00 | 136 | 1:00 | Rangpur | 131 | 9:00 | 115 | 21:00
| Chandpur | 140 | 9:00 | 135 | 15:00 | Lalmonirhat | 132 | 10:00 | 115 | 21:00
| Feni | 136 | 12:00 | 130 | 15:00 | Saidpur | 132 | 10:00 | 115 | 1:00
| Chowmuhani | 135 | 8:00 | 129 | 23:00 | Purbasadipur | 130 | 11:00 | 111 | 20:00
| Ashuganj | 141 | 14:00 | 134 | 19:30 | Thakurgaon | 132 | 9:00 | 112 | 21:00
| Daudkandi | 134 | 20:00 | 129 | 23:00 | Palashbari | 129 | 18:00 | 118 | 21:00
| B.Baria | 137 | 15:00 | 127 | 22:00 | Barapukuria | 135 | 9:00 | 123 | 20:00
| Ramganj | 136 | 9:00 | 131 | 15:00 | Panchagar | 134 | 0.375 | 113 | 0.83333
| Chaddagram | 136 | 13:00 | 132 | 2:00 | Joldhaka | 128 | 0.375 | 109 | 0.83333
| PHP | 134 | 9:00 | 131 | 4:00 | Kurigram | 133 | 0.41667 | 114 | 0.83333
| Kochua | 137 | 7:00 | 134 | 18:00 | Mithapukur | 135 | 0.41667 | 120 | 0.83333
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-25
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 98 | 8703 | 3915 | 12618 |  |  |  | QF-LDC-11
0:30 | 207 | 8684 | 3775.5 | 12459.5 | Date: | 2021-09-25
1:00 | 316 | 8665 | 3636 | 12301
1:30 | 310 | 8498 | 3538 | 12036
2:00 | 304 | 8331 | 3440 | 11771
2:30 | 302 | 8218 | 3385 | 11603 | [5 empty] | Gen. at Eve. Peak | 13052 | 13052 MW (20:00 )
3:00 | 300 | 8105 | 3330 | 11435 | [6 empty] | 20:00
3:30 | 291 | 8051.5 | 3264.5 | 11316 | [5 empty] | Gen. at Day Peak | 10961 | 10961 MW (12:00 )
4:00 | 282 | 7998 | 3199 | 11197 | [6 empty] | 12:00
4:30 | 269 | 7978 | 3171 | 11149 | [5 empty] | Highest Generation | 13052
5:00 | 256 | 7958 | 3143 | 11101 | [6 empty] | 20:00
5:30 | 250 | 7694 | 2959.5 | 10653.5
6:00 | 244 | 7430 | 2776 | 10206
6:30 | 173 | 7254 | 2789 | 10043
7:00 | 102 | 7078 | 2802 | 9880
7:30 | 102 | 7065 | 2816.5 | 9881.5
8:00 | 102 | 7052 | 2831 | 9883
8:30 | 136 | 7142 | 2828.5 | 9970.5
9:00 | 170 | 7232 | 2826 | 10058
9:30 | 229 | 7258.5 | 2859 | 10117.5
10:00 | 288 | 7285 | 2892 | 10177
10:30 | 280 | 7439 | 2938 | 10377
11:00 | 272 | 7593 | 2984 | 10577
11:30 | 199 | 7720 | 3049 | 10769
12:00 | 126 | 7847 | 3114 | 10961
12:30 | 106 | 7948.5 | 3102 | 11050.5
13:00 | 86 | 8050 | 3090 | 11140
13:30 | 166 | 7816 | 2989.5 | 10805.5
14:00 | 246 | 7582 | 2889 | 10471
14:30 | 219 | 7533.5 | 2955 | 10488.5
15:00 | 192 | 7485 | 3021 | 10506
15:30 | 104 | 7504.5 | 3060 | 10564.5
16:00 | 16 | 7524 | 3099 | 10623
16:30 | 89 | 7479.5 | 3080 | 10559.5
17:00 | 162 | 7435 | 3061 | 10496
17:30 | 148 | 7710.5 | 3235 | 10945.5
18:00 | 134 | 7986 | 3409 | 11395
18:30 | 137 | 8451 | 3706 | 12157
19:00 | 140 | 8916 | 4003 | 12919
19:30 | 122 | 8996 | 4053 | 13049
20:00 | 174 | 8991 | 4061 | 13052 |  |  |  | Executive Engineer
20:30 | 178 | 8958.5 | 4055.5 | 13014 |  |  |  | Network Operation Division
21:00 | 182 | 8926 | 4050 | 12976
21:30 | 159 | 8922 | 4044 | 12966
22:00 | 136 | 8918 | 4038 | 12956 |  |  |  |  | Page 6 of 7
22:30 | 130 | 8845 | 4016.5 | 12861.5
23:00 | 124 | 8772 | 3995 | 12767
23:30 | 111 | 8737.5 | 3955 | 12692.5
24:00 | 98 | 8703 | 3915 | 12618
13052 MW (20:00 )
10961 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-25 |  | Energy | 275520482
[11 empty] | 2021-09-25 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4396 | 719 | 2027 | 4091 | 610 | 117 | 636 | 0 | 126 | 0
0:30 | 4398.5 | 716.5 | 1948 | 3971 | 589 | 141.5 | 615 | 0 | 132 | 0 | Date: | 2021-09-25
1:00 | 4401 | 714 | 1869 | 3851 | 568 | 166 | 594 | 0 | 138 | 0
1:30 | 4411 | 714 | 1897 | 3686 | 573.5 | 166 | 452.5 | 0 | 136 | 0 | [7 empty] | Total Energy | 275.5205 | Total Energy Gen 275.520 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 275.520 MKWHr
2:00 | 4421 | 714 | 1925 | 3521 | 579 | 166 | 311 | 0 | 134 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4434.5 | 713.5 | 1951.5 | 3373.5 | 579 | 163 | 254 | 0 | 134 | 0 | [7 empty] | Energy Requirement | 275.5205
3:00 | 4448 | 713 | 1978 | 3226 | 579 | 160 | 197 | 0 | 134 | 0
3:30 | 4479 | 713 | 1962 | 3100 | 579.5 | 160 | 190.5 | 0 | 132 | 0 | [6 empty] | Shortage
4:00 | 4510 | 713 | 1946 | 2974 | 580 | 160 | 184 | 0 | 130 | 0
4:30 | 4514 | 712.5 | 1945.5 | 2926 | 580 | 160 | 184 | 0 | 127 | 0
5:00 | 4518 | 712 | 1945 | 2878 | 580 | 160 | 184 | 0 | 124 | 0
5:30 | 4485 | 712.5 | 1888 | 2618.5 | 520 | 160 | 152 | 0 | 117 | 0.5
6:00 | 4452 | 713 | 1831 | 2359 | 460 | 160 | 120 | 0 | 110 | 1
6:30 | 4379.5 | 713 | 1836.5 | 2275.5 | 440 | 162 | 120 | 0 | 109 | 7.5 |  |  |  |  | Coal
7:00 | 4307 | 713 | 1842 | 2192 | 420 | 164 | 120 | 0 | 108 | 14
7:30 | 4325.5 | 712.5 | 1835.5 | 2189.5 | 389.5 | 164.5 | 120 | 0 | 114 | 30.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4344 | 712 | 1829 | 2187 | 359 | 165 | 120 | 0 | 120 | 47
8:30 | 4355 | 712.5 | 1839 | 2243 | 360 | 165 | 120 | 0 | 117 | 59
9:00 | 4366 | 713 | 1849 | 2299 | 361 | 165 | 120 | 0 | 114 | 71
9:30 | 4373 | 713 | 1854.5 | 2328.5 | 369.5 | 165 | 120 | 0 | 114 | 80
10:00 | 4380 | 713 | 1860 | 2358 | 378 | 165 | 120 | 0 | 114 | 89
10:30 | 4358 | 713 | 1897 | 2505 | 399.5 | 166 | 120 | 0 | 122 | 96.5
11:00 | 4336 | 713 | 1934 | 2652 | 421 | 167 | 120 | 0 | 130 | 104
11:30 | 4307.5 | 712.5 | 1923.5 | 2862.5 | 435.5 | 168 | 128 | 0 | 130 | 101.5
12:00 | 4279 | 712 | 1913 | 3073 | 450 | 169 | 136 | 0 | 130 | 99
12:30 | 4297.5 | 712.5 | 1899 | 3175.5 | 450 | 143 | 144 | 0 | 129 | 100
13:00 | 4316 | 713 | 1885 | 3278 | 450 | 117 | 152 | 0 | 128 | 101
13:30 | 4316 | 713 | 1885 | 3278 | 450 | 117 | 152 | 0 | 128 | 101
14:00 | 4316 | 713 | 1885 | 3278 | 450 | 117 | 152 | 0 | 128 | 101
14:30 | 4213.5 | 713 | 1878 | 3114.5 | 450.5 | 116.5 | 144 | 0 | 132 | 61
15:00 | 4111 | 713 | 1871 | 2951 | 451 | 116 | 136 | 0 | 136 | 21
15:30 | 4176 | 713 | 1906 | 2894.5 | 471 | 115.5 | 138 | 0 | 133 | 17.5
16:00 | 4241 | 713 | 1941 | 2838 | 491 | 115 | 140 | 0 | 130 | 14
16:30 | 4234.5 | 713 | 1880.5 | 2831.5 | 500.5 | 114.5 | 142 | 0 | 132 | 11
17:00 | 4228 | 713 | 1820 | 2825 | 510 | 114 | 144 | 0 | 134 | 8
17:30 | 4256 | 716 | 1857 | 3020.5 | 503.5 | 114 | 339.5 | 0 | 135 | 4
18:00 | 4284 | 719 | 1894 | 3216 | 497 | 114 | 535 | 0 | 136 | 0
18:30 | 4334 | 719 | 1948.5 | 3712 | 547 | 114 | 647.5 | 0 | 135 | 0
19:00 | 4384 | 719 | 2003 | 4208 | 597 | 114 | 760 | 0 | 134 | 0
19:30 | 4406 | 719 | 2024 | 4272 | 609 | 114 | 769 | 0 | 136 | 0
20:00 | 4425 | 719 | 2021 | 4260 | 609 | 115 | 769 | 0 | 134 | 0
20:30 | 4423 | 719 | 2014 | 4234.5 | 609 | 115.5 | 764 | 0 | 135 | 0
21:00 | 4421 | 719 | 2007 | 4209 | 609 | 116 | 759 | 0 | 136 | 0
21:30 | 4406 | 719 | 2010.5 | 4206.5 | 609.5 | 116 | 763.5 | 0 | 135 | 0
22:00 | 4391 | 719 | 2014 | 4204 | 610 | 116 | 768 | 0 | 134 | 0
22:30 | 4391.5 | 719.5 | 2022 | 4147.5 | 610 | 116.5 | 722.5 | 0 | 132 | 0
23:00 | 4392 | 720 | 2030 | 4091 | 610 | 117 | 677 | 0 | 130 | 0
23:30 | 4394 | 719.5 | 2028.5 | 4091 | 610 | 117 | 656.5 | 0 | 128 | 0 | Max Temp. in Dhaka |  | 35° C
24:00 | 4396 | 719 | 2027 | 4091 | 610 | 117 | 636 | 0 | 126 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 275.520 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 275.520 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-25
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 91 | 91 | 85 | 85 | 85 | 85 | 89 | 90 | 90 | 90 | 92 | 94 | 42 | 42 | 41 | 40 | 39 | 39 |  | 39 | 39 | 40 | 41 | 41 | 42 | 42 | 1511504
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1816000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 120 | 120 | 120 | 120 | 120 | 120 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | 25 | [13 empty] | 1 | 8 | 8 | 8 |  | 19 | 25 | 25 | 25 | 25 | 25 | 25 | 213514
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 1 | [9 empty] | 1 | [9 empty] | 1755
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 17 | 13 | [14 empty] | 68 |  | 68 | 68 | 68 | 68 | 68 | 51 | 51 | 504184
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 105 | 105 | 51 | 51 | 51 | 51 | 51 | 53 | 80 | 105 | 105 | 105 | 68 | 68 | 74 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2182909
| Daudkandi 200 MW PP (B.Trac) | [19 empty] | 30 | 30 | 30 |  |  |  |  | 57600
14 | Titas 50 MW Peaking PP | [17 empty] | 50 |  | 50 | 50 | 50 | 43 | 50 |  |  | 282124
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 250 | 250 | 250 | 280 | 280 | 280 | 250 | 250 | 300 | 300 | 290 | 290 | 290 | 290 | 250 | 250 | 250 | 250 |  | 280 | 280 | 280 | 280 | 270 | 250 | 250 | 6590339
18 | Kodda 300 MW PP Unit-2 (Summit) | 275 | 282 | 290 | 290 | 290 | 195 | 195 | 195 | 218 | 273 | 273 | 275 | 283 | 293 | 293 | 300 | 300 | 285 |  | 291 | 298 | 298 | 298 | 298 | 296 | 298 | 6656616
19 | Ashuganj 195MW PP (APSCL-United) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 36 | 36 | 63 | 63 | 63 | 63 | 63 | 63 |  | 63 | 63 | 63 | 63 | 63 | 63 | 63 | 903272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 285 | 285 | 285 | 285 | 300 | 310 | 310 |  | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 7218364
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 20 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 505008
33 | Ashuganj 225 MW CCPP | 207 | 208 | 206 | 208 | 209 | 211 | 180 | 181 | 178 | 184 | 184 | 180 | 180 | 179 | 181 | 212 | 212 | 210 |  | 211 | 211 | 210 | 211 | 213 | 211 | 212 | 4838000
34 | Ashuganj 450 MW CCPP(South) | 350 | 350 | 350 | 350 | 350 | 350 | 300 | 300 | 320 | 315 | 310 | 300 | 300 | 265 | 265 | 265 | 265 | 305 |  | 265 | 270 | 275 | 265 | 265 | 290 | 300 | 7443000
| Ashuganj 450 MW CCPP(North) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 275 | 305 | 300 | 295 | 295 | 265 | 265 | 265 | 265 | 300 |  | 265 | 265 | 270 | 265 | 265 | 265 | 265 | 6992500
35 | Ashuganj 55 MW PP (Precision) | 52 | 52 | 51 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 51 | 51 | 50 | 49 | 51 | 45 | 46 | 47 |  | 50 | 52 | 51 | 52 | 51 | 51 | 52 | 1216320
36 | Chandpur 150 MW CCPP | 140 | 140 | 139 | 140 | 141 | 141 | 138 | 140 | 137 | 140 | 140 | 142 | 138 | 139 | 139 | 139 | 132 | 138 |  | 139 | 140 | 140 | 139 | 140 | 140 | 138 | 3334900
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 384 | 360 | 365 | 394 | 395 | 377 | 371 | 372 | 371 | 371 | 361 | 350 | 348 | 352 | 321 | 314 | 314 | 314 |  | 347 | 353 | 353 | 353 | 340 | 323 | 323 | 8579216
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 6720250
41 | Haripur 360MW CCPP(HPL) | 325 | 324 | 323 | 322 | 332 | 323 | 325 | 325 | 321 | 320 | 320 | 312 | 312 | 290 | 317 | 320 | 320 | 320 |  | 326 | 326 | 326 | 326 | 328 | 328 | 327 | 7692000
42 | RPCL 210MW CCPP | 207 | 204 | 206 | 206 | 207 | 207 | 207 | 204 | 204 | 181 | 166 | 151 | 142 | 144 | 143 | 155 | 164 | 164 |  | 165 | 165 | 167 | 170 | 170 | 171 | 181 | 4205040
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 1 | 6 | 28 | 41 | 51 | 57 | 54 | 56 | 48 | 12 | 10 | 4 | [9 empty] | 364110
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 1029000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 161 | 162 | 160 | 160 | 161 | 160 | 159 | 161 | 163 | 161 | 161 | 160 | 160 | 160 | 160 | 160 | 161 | 161 |  | 160 | 160 | 160 | 161 | 161 | 162 | 160 | 3671000
47 | Shahjibazar GTPP Unit- 8 & 9 |  |  | 20 | 30 | 61 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 25 | 30 | 30 |  | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 650688
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 75 | 78 | 77 | 77 | 76 | 76 | 76 | 77 | 78 | 40 | 50 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1781760
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 227 | 200 | 200 | 200 | 200 | 193 | 140 | 140 | 140 | 140 | 140 | 152 | 213 | 214 | 221 | 221 | 220 | 221 |  | 220 | 220 | 220 | 220 | 220 | 220 | 220 | 4617090
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 17 | 17 | 17 | 17 | 17 |  | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 382000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [26 empty] | 0
54 | Hobiganj 11MW PP Cofidence-E | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 |  |  |  |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 210960
55 | Fenchugonj 51 MW PP (Barakatullah) | 50 | 50 | 50 | 50 | 50 | 50 | 47 | 47 | 47 | 47 | 47 | 47 | 44 | 44 | 44 | 44 | 44 | 47 |  | 47 | 47 | 47 | 47 | 47 | 47 | 47 | 1138800
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 22 | 22 | 16 | 16 | 16 | 20 | 20 | 16 |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 517320
57 | Bibiana-II 341 MW CCPP (Summit) | 285 | 295 | 310 | 305 | 290 | 285 | 295 | 300 | 300 | 290 | 300 | 300 | 280 | 260 | 290 | 310 | 280 | 290 |  | 300 | 300 | 290 | 290 | 280 | 290 | 295 | 7229000
| Bibiyana South 400 MW | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 321 | 320 | 321 | 320 | 320 | 321 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7648300
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 35 | 35 | 17 | 17 | 17 | 480634
59 | Tangail Palli Power Gen 22 MW | 22 | [25 empty] | 39840
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 496128
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | [7 empty] | 16 | 19 | 19 | 20 | 20 |  | 349236
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  |  | 21 | 18 | 21 |  | 19 | 19 | 21 | 21 | 21 | 21 | 21 | 403164
63 | Impoprt (Tripura) | 138 | 134 | 134 | 130 | 124 | 110 | 108 | 120 | 114 | 114 | 130 | 130 | 128 | 132 | 136 | 130 | 134 | 136 |  | 134 | 136 | 134 | 136 | 134 | 130 | 126 | 3062400
64 | Malancha, Ctg. EPZ (United) | 42 | 42 | 42 | 42 | 42 | 42 | 29 | 8 | 2 | 2 | 5 | 2 | 4 | 3 | 2 | 2 | 4 | 2 |  | 4 | 6 | 7 | 7 | 27 | 30 | 32 | 410460
65 | Feni 22MW PP (Doreen) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 22 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 478440
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 |  |  | 11 | 8 | 8 |  |  | 11 | 11 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 209700
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 803200
68 | Cumilla 25 MW PP (Summit) | 20 | 20 | 21 | 21 | 21 | 21 | 21 | 21 | 20 | 12 | 12 | 12 | 18 | 18 | 18 | 18 | 18 | 18 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 459370
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 25 | 28 | 28 | 20 | 20 |  | 26 | 26 | 28 | 28 | 28 | 28 | 29 | 609660
71 | Maona 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 713500
72 | Rupganj 33 MW PP(Summit) | 0 | 33 | 17 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 741000
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 114 | 114 | 59 | 6 | [6 empty] | 17 | 52 | 52 | 17 | 17 | 34 | 34 | 70 |  | 100 | 114 | 114 | 114 | 114 | 114 | 114 | 1298460
| Chowmuhani 113 MW | 57 | 57 | 57 | 57 | 57 | 57 | 57 | 58 | 57 | 57 | 54 | 49 | 49 | 49 | 47 | 52 | 60 | 86 |  | 92 | 96 | 96 | 95 | 97 | 100 | 63 | 1576680
| Manikgonj 162MW PP(MPGL) | 126 | 126 | 126 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 108 | 126 | 144 | 144 | 146 | 162 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3134880
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 16 | [6 empty] | 19 | 37 | 33 | 33 | 33 |  | 16 | 16 | 16 | 16 | 25 |  | 51 | 51 | 51 | 51 | 51 | 51 | 51 | 599520
79 | Kodda 150MW PP | 150 | 82 | 64 | 64 | 64 | [6 empty] | 16 | 32 | 16 | 16 | 16 | 16 | 82 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1527840
80 | Jamalpur 95 MW PP(Powerpac) | [26 empty] | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 25 | 8 | 8 | 8 |  | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 231130
| Gazipur 100 MW PP | 105 | 17 |  |  |  |  | 7 | 90 | 105 | 105 | 105 | 105 | 105 | 52 | 52 | 52 | 52 | 52 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 1792800
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 3 | 4 | 2 | 5 | 1 | 4 | 3 | 0 | 0 | [9 empty] | 28680
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 44 | 43 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1265889
| Karnaphuli Power Ltd. | 110 | 110 | 110 | 110 | 110 | 51 | 51 | 51 | 51 | 51 | 51 | 65 | 110 | 110 | 110 | 68 | 68 | 75 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 2284935
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | 63 | 40 | [9 empty] | 12 | 20 | 10 | 10 | 12 | 20 | 35 |  | 62 | 62 | 61 | 62 | 62 | 61 | 61 | 627122
86 | Meghnaghat CCPP ( Summit) | 270 | 295 | 305 | 290 | 275 | 270 | 300 | 305 | 270 | 290 | 282 | 275 | 240 | 265 | 280 | 275 | 252 | 305 |  | 300 | 310 | 317 | 310 | 315 | 300 | 275 | 6856844
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 90 | 93 | 94 | 93 | 93 | 93 | 55 | 55 | 55 | 55 | 56 | 89 | 94 | 94 | 94 | 94 | 93 | 94 |  | 94 | 94 | 94 | 93 | 93 | 95 | 94 | 2064960
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 88 | 88 | 10 | [7 empty] | 10 | 40 | 60 | 30 | 10 | 30 | 30 | 50 |  | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 1031160
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 41 |  | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 976746
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 102 | 102 | 48 | 32 | 32 | 32 | 32 | 32 | 32 | 40 | 64 | 102 | 64 | 64 | 64 | 64 | 85 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1773792
95 | Patenga 50MW PP (Baraka) | 50 | 32 | 32 | 12 | [6 empty] | 1 | 18 | 48 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 768480
96 | Chattogram 108 MW PP (ECPV) | 86 | [15 empty] | 17 | 37 |  | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 692160
97 | katpotti 52 MW | [26 empty] | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 45 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 44 | 44 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1296515
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 35 | 35 | 55 | 55 | 55 | 17 | 17 | 539466
101 | Kushiara 163 MW CCPP (KP) | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 130 | 130 | 163 | 163 | 163 | 110 | 130 | 130 | 130 | 130 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3398563
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 2 | 2 | 1 | 2 | 1 | 1 | 0 | 0 | 0 | [9 empty] | 11050
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 820080
104 | Keranigonj 300 MW PP (APR) | [19 empty] | 35 | 31 | [5 empty] | 89755
105 | Bramhangoan 100 MW PP (Aggreko)
106 | Mymensingh 200 MW PP (United) | 181 | 182 | 182 | 182 | 182 | 183 | 183 | 140 | 140 | 100 | 100 | 100 | 140 | 100 | 70 | 70 | 70 | 81 |  | 182 | 182 | 182 | 182 | 182 | 183 | 183 | 3542400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 50 | 25 | 25 |  |  |  |  | 93061
114 | Kodda 149 MW PP Unit-1 (Summit) | 132 | 131 | 128 | 114 | 100 | 100 | 100 |  |  | 10 | 107 | 114 | 128 | 131 | 88 | 81 | 98 | 104 |  | 122 | 130 | 130 | 135 | 147 | 149 | 149 | 2530080
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 88 | 88 | 88 | 100 | 90 | 100 | 100 | 100 | 60 | 90 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2127360
116 | Chandpur 200MW (Desh energy) | 200 | 200 | 200 | 200 | 200 | 100 | 100 | 100 | 100 | 100 | 112 | 155 | 195 | 100 | 100 | 100 | 100 | 105 |  | 179 | 200 | 193 | 200 | 200 | 200 | 200 | 3774240
117 | Ashuganj 150MW PP (Midland) | 137 | 135 | 118 | 137 | 138 | 137 | 135 | 123 | 133 | 133 | 135 | 133 | 130 | 128 | 130 | 132 | 140 | 130 |  | 132 | 133 | 133 | 133 | 127 | 127 | 118 | 3166472
118 | Bibiyana-III 400 MW CCPP | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 315 | 315 | 316 | 313 |  | 315 | 315 | 315 | 315 | 315 | 316 | 316 | 7575000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 85 | 85 | 85 | 88 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2689200
| Anwara 300 MW PP (United) | 305 | 305 | 305 | 305 | 305 | 244 | 217 | 215 | 215 | 215 | 302 | 305 | 305 | 305 | 305 | 305 | 305 | 305 |  | 305 | 305 | 305 | 305 | 305 | 305 | 305 | 6902509
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 60 | 60 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2254080
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 100 | 53 | 53 | 53 | 53 | 66 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2349764
| Bhairob 54.5 MW | 35 | 35 | 6 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 11 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 457920
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 4 | 10 | 16 | 23 | 33 | 26 | 31 | 4 | 0 | 0 | 1 | [9 empty] | 150931
120 | Eastern Zone Total | 8665 | 8331 | 8105 | 7998 | 7958 | 7430 | 7078 | 7052 | 7232 | 7285 | 7593 | 7847 | 8050 | 7582 | 7485 | 7524 | 7435 | 7986 | 0 | 8916 | 8996 | 8991 | 8926 | 8918 | 8772 | 8703 | 193661699
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | 7 | [14 empty] | 4 | 4 | 11 |  | 27 | 27 | 25 | 24 | 24 | 24 | 24 | 171460
| Khulna 225 MW CCPP | 200 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 145 |  | 224 | 225 | 225 | 226 | 227 | 226 | 228 | 3714240
129 | Rupsha 105 MW PP (Orion rupsha) | 88 | 88 | 78 | 17 | [7 empty] | 80 | 84 | 53 | 53 | 35 | 35 | 35 |  | 84 | 88 | 88 | 88 | 88 | 88 | 88 | 1207680
130
131
132 | United Payra Power Ltd. | 116 | 100 | 35 | 17 | [12 empty] | 17 | 35 |  | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 846000
133 | Bhola Nutan Biddut BD LTD (GAS) | 115 | 107 | 107 | 107 | 108 | 107 | 108 | 108 | 108 | 89 | 89 | 89 | 89 | 103 | 107 | 105 | 100 | 106 |  | 106 | 106 | 106 | 107 | 107 | 106 | 107 | 2576209
Bhola Nutan Biddut BD LTD (OIL)
| Barisal 110 MW PP (Summit ) | [17 empty] | 4 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 95424
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 80 | 82 | 83 | 82 | 81 | 82 | 82 | 81 | 80 | 82 | 82 | 86 | 86 | 86 | 85 | 88 | 86 | 76 |  | 91 | 91 | 91 | 92 | 91 | 83 | 82 | 1989208
| Bhola 225 MW CCPP | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 88 | 87 | 87 | 87 | 87 | 87 | 87 |  | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 2118998
140 | Bhola 33 MW PP (Venture) | 34 | 33 | 33 | 10 | 23 | 22 | 20 | 16 | 16 | 18 | 20 | 22 | 23 | 25 | 27 | 24 | 23 | 33 |  | 33 | 34 | 35 | 35 | 34 | 34 | 34 | 623750
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 43 | 50 | 50 | 50 | 50 | 50 | 50 | 314880
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 714 | 714 | 713 | 713 | 712 | 713 | 713 | 712 | 713 | 713 | 713 | 712 | 713 | 713 | 713 | 713 | 713 | 719 |  | 719 | 719 | 719 | 719 | 719 | 720 | 719 | 17272727
147 | Bheramara 410 MW CCPP | 355 | 395 | 390 | 365 | 355 | 355 | 375 | 395 | 355 | 370 | 355 | 355 | 355 | 300 | 350 | 395 | 395 | 350 |  | 405 | 400 | 400 | 405 | 400 | 405 | 405 | 9174816
148 | Payra 1320 MW | 490 | 500 | 500 | 500 | 500 | 380 | 340 | 280 | 280 | 300 | 340 | 370 | 370 | 350 | 370 | 410 | 430 | 420 |  | 520 | 530 | 530 | 530 | 530 | 530 | 530 | 11292700
149
150 | Barapukuria TPP Unit-1 | 78 | 79 | 79 | 80 | 80 | 80 | 80 | 79 | 81 | 78 | 81 | 80 | 80 | 80 | 81 | 81 | 80 | 77 |  | 77 | 79 | 79 | 79 | 80 | 80 | 80 | 1866763
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | 43 | [16 empty] | 40 |  | 50 | 50 | 50 | 50 | 50 | 43 | 43 | 350032
| Sirajgonj 6.55 MW Solar | [6 empty] | 0 | 2 | 4 | 4 | 4 | 5 | 5 | 1 | 0 | 0 | 0 | [9 empty] | 26940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 165 | 167 | 178 | 177 | 169 | 163 | 168 | 174 | 178 | 187 | 196 | 191 | 184 | 145 | 168 | 177 | 167 | 175 |  | 189 | 188 | 188 | 189 | 186 | 190 | 193 | 4485100
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 175 | 171 | 183 | 182 | 173 | 168 | 172 | 186 | 200 | 194 | 191 | 192 | 192 | 179 | 175 | 184 | 174 | 181 |  | 191 | 188 | 189 | 190 | 187 | 190 | 193 | 4684927
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 325 | 379 | 418 | 416 | 409 | 310 | 346 | 354 | 363 | 409 | 409 | 396 | 362 | 307 | 346 | 400 | 355 | 388 |  | 398 | 414 | 420 | 403 | 400 | 412 | 402 | 9246800
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | 21 | [15 empty] | 4 | 5 |  | 26 | 36 | 36 | 36 | 36 | 20 |  | 184661
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 21 | 20 | 18 | 18 | 18 | 17 | 17 | 14 | 21 |  | 21 | 21 | 21 | 21 | 22 | 22 | 22 | 459360
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 11 | 5 | 5 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 236592
165 | Amnura 50 MW PP(Sinha) | 27 | [15 empty] | 12 | 27 |  | 27 | 27 | 27 | 27 | 27 | 27 |  | 221040
166 | Katakhali 50 MW PP (Northern) | [16 empty] | 8 | 43 |  | 43 | 43 | 43 | 43 | 43 | 8 |  | 203760
167 | Katakhali 50 MW Peaking PP | 16 | [16 empty] | 23 |  | 38 | 38 | 40 | 38 | 38 | 38 | 16 | 206588
168 | Santahar 50 MW Peaking PP | 32 | 32 | [15 empty] | 19 |  | 35 | 33 | 33 | 32 | 33 | 33 | 32 | 262620
169 | Natore 52 MW PP (Rajlanka) | 52 | [10 empty] | 2 | 8 | 8 | 8 | 8 | 16 | 16 |  | 42 | 52 | 52 | 52 | 52 | 52 | 52 | 457440
170 | Chapainawabganj 100 MW Peaking PP | 91 | 60 | [15 empty] | 92 |  | 92 | 92 | 92 | 92 | 92 | 92 | 92 | 772624
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 94 | 94 | 94 | 94 | 94 | 50 | 50 | 50 | 50 | 50 | 65 | 94 | 94 | 94 | 94 | 70 | 70 | 75 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2159232
172 | Confidence Power Bogura Unit-1 113 MW | 95 | 95 | 95 | 95 | 95 | 50 | 50 | 50 | 50 | 50 | 90 | 95 | 95 | 95 | 95 | 70 | 70 | 95 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2159904
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 |  | 0 |  | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 104 | 104 | 104 | 104 | 104 | 56 | 56 | 100 | 104 | 104 | 104 | 104 | 110 | 110 | 108 | 102 | 74 | 100 |  | 110 | 110 | 110 | 110 | 110 | 110 | 111 | 2429020
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 2 | 4 | 5 | 5 | 7 | 7 | 7 | 7 | 6 | 4 | 2 | 0 | [8 empty] | 47288
178
178