## QF-MIS-03
Page: 1/1 | [7 empty] | QF-MIS-03
POWER GRID COMPANY OF BANGLADESH LTD.
SYSTEM OPERATION DATA
Month:August 2021
Sl. | Items | Current Month |  | Current Month |  | This Month Last Year |  | Max. Till-to-date
|  | 2021-08-01 |  | 2021-07-01 |  | 2020-08-01
No |  | Value | Date & | Value | Date & | Value | Date & | Value | Date &
|  |  | Time |  | Time |  | Time |  | Time
1 | Maximum Generation (MW) | 13271 | 2021-08-22 | 13525 | 2021-07-15 | 12577 | 31/08/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 19:30 |  | 20:00
2 | Minimum Generation (MW) | 8249 | 2021-08-01 | 6682 | 2021-07-29 | 6840.9 | 01/08/20 | - | -
|  |  | 22:00 |  | 1:00 |  | 9:00 |  | -
3 | Maximum Evening Peak Generation (MW) | 13271 | 2021-08-22 | 13525 | 2021-07-15 | 12577 | 31/08/20 | 13792 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 19:30 |  | 20:00
4 | Maximum Day Peak Generation (MW) | 11410 | 2021-08-31 | 11549 | 2021-07-15 | 10843.5 | 31/08/20 | 11773 | 2021-04-27
|  |  | 12:00 |  | 12:00 |  | 12:00 |  | 12:00
5 | Maximum Evening Peak Demand (MW) Estimated | 13271 | 2021-08-22 | 13525 | 2021-07-15 | 12577 | 31/08/20 | 14097 | 2021-04-27
|  |  | 21:00 |  | 21:00 |  | 19:30 |  | 19:00
6 | Average Generation (MW) at Evening Peak | 12483.5806 |  | 11656.2903 |  | 11541.5161 |  | 12676.7 | 2021-04-27
7 | Average Generation (MW) at Day Peak | 10126.9918 |  | 9260.4516 |  | 9323.5619 |  | 10379.6667 | 2021-04-27
8 | Maximum Power Import from India, BIPTC (MW) | 907 | 2021-07-01 | 907 | 2021-07-01 | 945 | 04/08/2020 | 956 | 27/3/2019
|  |  | 0:30 |  | 0:30 |  | 17:00 |  | 19:00
9 | Maximum Power Import from Tripura, India (MW) | 172 | 2021-07-10 | 172 | 2021-07-10 | 178 | 13/08/2020 | 194 | 12/06/19
|  |  | 23:00 |  | 23:00 |  | 22:00 |  | 19:00
10 | Maximum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | - | 1459 | 04/05/2010
|  |  | - |  | - |  |  |  | 20:00
11 | Generation During Max. Load Shed (MW) at Evening Peak | - | - | - | - | - | - | 13792 | 2021-04-27
|  | - | - | - | - | - | - |  | 20:00
12 | Minimum Load Shed (MW) at Evening Peak | 0 | - | 0 | - | - | -
13 | Generation During Min. Load Shed (MW) at Evening Peak | - | - | - | - | - | -
14 | Maximum Load Shed (MW) at Day Peak | - | - | - | - | - | -
15 | Generation During Max. Load Shed (MW) at Day Peak | - | - | - | - | - | -
16 | Minimum Load Shed (MW) at Day Peak | - | - | - | - | - | -
17 | Generation During Min. Load Shed (MW) at Day Peak | - | - | - | - | - | -
18 | Nos. of Days Load Shed at Evening Peak | 0 |  | 0 |  | -
19 | Nos. of Days Load Shed at Day Peak | - |  | - |  | -
20 | Gross Generation of BPDB (MKWH) | 1762.3785 |  | 1852.5058 |  | 3338.6684 |  | 3805.72 | 2019-09-19
21 | Station Use of BPDB (MKWH) | 118.3845 |  | 113.9022 |  | 112.5022
22 | Net Generation of BPDB (MKWH) | 1643.994 |  | 1738.6035 |  | 3226.1662
23 | Net Generation of IPP (MKWH) | 5157.2882 |  | 4403.448 |  | 2591.1866
24 | Net Generation of REB (MKWH) | 144.3267 |  | 129.0256 |  | 150.3385
24 | Net Generation of Rental Power Plant (MKWH) | 511.1298 |  | 427.9978 |  | 569.7029
25 | Total Net Generation (MKHWh) (BPDB, IPP, RPP & REB) | 7456.7388 |  | 6699.0748 |  | 6537.3941 |  | 7072.7704 | April'21
26 | Energy Generation by Gas (MKWH) | 4736.6321 |  | 4815.0058 |  | 4031.1453 |  | 4756.96 | Sep-19
27 | Energy Generation by Diesel (MKWH) | 442.1105 |  | 290.9346 |  | 434.2084 |  | 771.52 | July-18
28 | Energy Generation by Furnace Oil (MKWH) | 1803.3426 |  | 1187.2509 |  | 1616.2719 |  | 1679.4648 | Sep-20
29 | Energy Generation by Hydro (MKWH) | 86.881 |  | 61.0975 |  | 89.1242 |  | 151.4 | August-19
30 | Energy Generation by Solar (MKWH) | 30.5606 |  | 16.6657 |  | 4.5842 |  | 22.56 | 2019-09-16
31 | Energy Generation by Coal (MKWH) | 475.5964 |  | 442.0225 |  | 474.5624 |  | 627.4399 | April'21
32 | Enegry Import from India (BIPTC & AC) (MKWH) | 593.113 |  | 659.2349 |  | 775.9511 |  | 775.9511 | August-20
33 | Monthly Load Factor (%) | 82.7278 |  | 74.2573 |  | 79.359 |  | 85.18 | Aug-17

## QF-LDC-22
Page: 1/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
Month:August 2021
Sl.No | Description of Item |  |  | Annexed form Nos.
1 | Outage of Sub-Station equipment due to tripping/emergency maintenance |  |  | QF-LDC-23
2 | Outage of Transmission lines due to tripping/emergency maintenance |  |  | QF-LDC-24
3 | Outage of Sub-Station equipment due to schedule maintenance/project work |  |  | QF-LDC-25
4 | Outage of Transmission lines due to schedule maintenance/project work |  |  | QF-LDC-26
5 | Summary of tripping and outage (Emergency / scheduled ) |  |  | QF-LDC-27
6 | Summary of unserved Energy |  |  | QF-LDC-28
7 | Consolidated Statement of Sub-Station performance |  |  | QF-LDC-29
8 | Consolidated Statement of Transmission line's performance |  |  | QF-LDC-30
9 | Power Interruption due to trouble in Transmission/Generation System |  |  | QF-LDC-31
10 | Over all Power interruption report of the system |  |  | QF-LDC-32
11 | Maximum Load recorded at different Sub-Station |  |  | QF-LDC-33
12 | Area & Zone wise maximum load served during peak hour |  |  | QF-LDC-34
13 | Maximum & Minimum Voltages of Grid Sub-Stations |  |  | QF-LDC-35
14 | Maximum load of 230/132KV Auto transformer |  |  | QF-LDC-36
15 | Report on load shedding |  |  | QF-LDC-37
| Description of Item | Unit | Quantity | Date | Time
16 | Area wise supply (At S/S end) during Maximum Peak Generation Period |  | 13271 | 2021-08-22 | 21:00
Generation Period
| Dhaka | MW | 4534
| Chattogram | MW | 1320
| Cumilla | MW | 1210
| Mymensingh | MW | 901
| Sylhet | MW | 496
a) | Total supply in East zone | MW | 8461
| Khulna | MW | 1651
| Barisal | MW | 376
| Rajshahi | MW | 1357
| Rangpur | MW | 820
b) | Total supply in West zone | MW | 4204
c) | Total supply in both zone ( a+b) | MW | 12665
Ref: | 27.21.0000.603.16.087.20.441 | Date: 19/09/2021
Copy to:
(1) Managing Director, PGCB, Dhaka
(2) Executive Director, O&M/ P&D, PGCB, Dhaka
(3) Chief Engineer, System Operation/Transmission (1&2)/P&D, PGCB, Dhaka
(4) Superintendent Engineer, LDC/SPM/Planning/Grid Circle, Dhaka (South/North)/CTG/Comilla/Khulna/Bogra, PGCB
(5) Director, System Planning, BPDB Dhaka.
(6) Executive Engineer, MIS/System Planning/EMD/NOD, PGCB Dhaka
(7) Office Copy
Page: 2/2 |  |  |  |  | QF-LDC-22
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Transmission System
(230KV East-West I/C)
Month:August 2021
SL. No | Description of Item | Unit | Quantity | Date | Time
17 | Daily Maximum power Export through EWI/ NO-1
| a) Ghorashal end | AMPS | 750 | 2021-08-05 | 20:00
| b) Ishurdi end | MW | 208 | 2021-08-27 | 11:00
18 | Daily Maximum power Import through EWI/ NO-1
| a) Ghorashal end | AMPS | 410 | 2021-08-21 | 18:30
| b) Ishurdi end | MW | 310 | 2021-08-06 | 19:00
19 | Daily Maximum Energy Export through EWI/NO-1
| a) Ghorashal end | MKWH | 4.65 | 2021-08-07
| b) Ishurdi end | MKWH | - | -
20 | Daily Maximum Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | - | -
| b) Ishurdi end | MKWH | 4.01 | 2021-08-10
21 | Total Energy Export through EWI/ NO-1
| a) Ghorashal end | MKWH | 73.65
| b) Ishurdi end | MKWH | 9.934
22 | Total Energy Import through EWI/ NO-1
| a) Ghorashal end | MKWH | 9.64
| b) Ishurdi end | MKWH | 71.51
23 | Transmission loss of EWI/ NO-1 | % | 3
24 | Daily Maximum power Export through EWI/ NO-2
| a) Ashuganj end | MW | 450 | 2021-08-05 | 20:00
| b)Serajganj end | MW | 240 | 2021-08-27 | 11:00
25 | Daily Maximum power Import through EWI/ NO-2
| a) Ashuganj end | MW | 220 | 2021-08-27 | 11:00
| b)Sirajganj end | MW | 410 | 2021-08-05 | 20:00
26 | Daily Maximum Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 5.8 | 2021-08-29 |  |  | 186.52
| b)Sirajganj end | MKWH | - | - |  |  | 17.59
27 | Daily Maximum Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | - | -
| b)Sirajganj end | MKWH | 5.78 | 2021-08-18
28 | Total Energy Export through EWI/ NO-2
| a) Ashuganj end | MKWH | 112.87
| b)Sirajganj end | MKWH | 7.66
29 | Total Energy Import through EWI/ NO-2
| a) Ashuganj end | MKWH | 7.54
| b)Sirajganj end | MKWH | 113.06
30 | Transmission loss of EWI /NO-2 | % | 0.056
* Total energy export from Ghorasal end and import from Ishurdi end and the transmission loss of EWI/NO-1 is taken
from the calculation of GMD, PGCB, Ishwardi.
* *Total energy export from Ashuganj end and import from Sirajganj end and the transmission loss of EWI/NO-2 is taken
from the calculation of Sirajganj switching sub station.
* **The energy meter of Ghorasal end is out of order.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.
Ist East-West Interconnector Loss:
| Ghorasal End (KWH): | 109882206.4 | 1000000 | 109.8822 | 836363.65 | 0.83636
| Ishurdi End (KWH): | 106928443.1 | 1000000 | 106.9284 | 811272.74 | 0.81127
| Difference (-) : | 2953763.3 |  |  | 25090.91
| Loss : | 2.688% |  |  | 3%
| 2nd East-West Interconnector Loss: |  |  |  |  | 99387644.47
| Ashuganj End (KWH) | 245578000 | 1000000 | 245.578 |  | 96795991.85
| Sirajganj End (KWH) | 242062000 | 1000000 | 242.062 |  | 2308363.67
| Difference (-) : | 3516000 |  |  |  | 2239112.76
| Loss : | 1.432%

## QF-LDC-23
QF-LDC-23
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division
Outage of Sub-Station Equipment due to Tripping/Emergency Maintenance
Month:August 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensing | 132/33 kV Transformers-T1 & T2 | 2021-08-01 12:26 | 2021-08-01 12:52 | 0:26 | T | Due to 33 kV Aqua feeder cable,CT & PT burst | 0 | 0 | No interruption
Keraniganj | 132/33 kV Transformers-T2 | 2021-08-01 12:39 | 2021-08-01 17:01 | 4:22 | T | Tripped showing buchholz relay | 0 | 0 | No interruption
Kodda | 132/33 kV Transformers-T3 | 2021-08-05 11:55 | 2021-08-05 11:55 | 0:00 | E/O | Due to high temperature | 0 | 0 | No interruption
Fatulla | 132/33 kV Transformers-T1 & T2 | 2021-08-05 17:14 | 2021-08-05 18:14 | 1:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Tangail | 132/33 kV Transformers-T1 and 33 kV Bus | 2021-08-11 07:03 | 2021-08-11 08:10 | 1:07 | E/O | Due to red-hot maint | 50 | 55.8333 | Power interruption
Mymensingh | 132/33 kV Transformers-T3 | 2021-08-12 07:35 | 2021-08-12 16:31 | 8:56 | T | Tripped showing E/F, O/C relay | 35 | 312.6667 | Power interruption
Mirpur | 132/33 kV Transformers-T1 with 33 kV Bus | 2021-08-14 08:20 | 2021-08-14 09:08 | 0:48 | E/O | Due to red-hot maint | 24 | 19.2 | Power interruption
Tangail | 132/33 kV Transformers-T1 & T2 | 2021-08-16 11:20 | 2021-08-16 11:40 | 0:20 | T | Tripped showing E/F relay | 100 | 33.3333 | Power interruption
Mymensing | 132/33 kV Transformers- T2 & 33 kV Bus section | 2021-08-20 07:21 | 2021-08-20 10:52 | 3:31 | E/O | Due to high temperature feeder DS | 30 | 105.5 | Power interruption
Mymensing | 132/33 kV Transformers-T1 & T2 | 2021-08-22 17:54 | 2021-08-22 18:05 | 0:11 | T | Tripped showing 33 kV Shamburg feeder fault | 120 | 22 | Power interruption
Kishoreganj | 132/33 kV Transformers-T1 & T2 | 2021-08-23 12:40 | 2021-08-23 14:05 | 1:25 | T | Tripped showing O/C relay | 90 | 127.5 | Power interruption
Kishoreganj | 132/33 kV Transformers-T3A & T3B | 2021-08-23 12:40 | 2021-08-23 14:05 | 1:25 | T | Tripped due to 33 kV breakers & CT got damage | 0 | 0 | No interruption
Bhulta | 132/33 kV Transformers-T2 | 2021-08-24 07:03 | 2021-08-24 07:03 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Nawabganj | 132/33 kV Transformers-T2 | 2021-08-25 09:51 | 2021-08-25 11:04 | 1:13 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Nawabganj | 132/33 kv transformers T1 with 33 kV bus | 2021-08-09 09:16 | 2021-08-09 11:19 | 2:03 | E/O | Due to red-hot maint | 20 | 41 | Power interruption
Tangail | 132/33 kV transformer T2 with 33 kV Bus section | 2021-08-27 18:08 | 2021-08-27 19:55 | 1:47 | T | Due to 33 kV incoming isolation work | 35 | 62.4167 | Power interruption
Tangail | 132/33 kV Transformers-T1 & T2 | 2021-08-27 18:18 | 2021-08-27 19:05 | 0:47 | T | Due to 33 kV Bus isolator heavy flashing | 68 | 53.2667 | Power interruption
Keraniganj GIS | 230/132 kV Transformer T01 | 2021-08-30 00:34 | 2021-08-30 00:34 | 0:00 | T | Tripped showing PRD | 0 | 0 | No interruption
|  |  | Total : | 29:21 |  | Unserved Energy: |  | 832.7167
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kV Transformers- T1 & T5 | 2021-08-04 06:50 | 2021-08-04 07:17 | 0:27 | T | Tripped due to 33 kV feeder fault | 48 | 21.6 | Power interruption
Haripur | 132 kV Bus-1&2 | 2021-08-04 19:36 | 2021-08-04 20:25 | 0:49 | T | Tripped due to Insulator of R-phase got burst | 370 | 302.1667 | Power interruption
Haripur | 230/132 kV Transformers- T1 & T2 | 2021-08-04 19:36 | 2021-08-04 20:25 | 0:49 | T | Tripped showing O/C relay | 0 | 0 | No interruption
|  |  | Total : | 2:05 |  | Unserved Energy: |  | 323.7667
Chattogram Grid Circle :
Chowmuhoni | 132/33 kv transformers T2 | 2021-08-03 06:42 | 2021-08-03 07:51 | 1:09 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sikalbaha(old) | 132/33 kv transformers T3 | 2021-08-03 18:25 | 2021-08-03 18:25 | 0:00 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T2 | 2021-08-04 14:46 | 2021-08-04 16:42 | 1:56 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-1 & T-3 | 2021-08-04 18:10 | 2021-08-04 18:20 | 0:10 | T | Tripped showing O/C relay | 45 | 7.5 | Power interruption
Juldah | 132/33 kv transformers T2 | 2021-08-05 11:22 | 2021-08-05 13:16 | 1:54 | T | Due to Oil temperature high | 0 | 0 | No interruption
Chowmuhoni | 132/33 kv transformers T-1 & T-2 | 2021-08-05 11:05 | 2021-08-05 11:18 | 0:13 | T | Tripped showing Directional E/F relay | 100 | 21.6667 | Power interruption
Chowmuhoni | 132/33 kv transformers T3 | 2021-08-11 16:15 | 2021-08-11 16:32 | 0:17 | T | Due to Datterhat feeder fault | 58 | 16.4333 | Power interruption
Bakulia | 132/33 kv transformers T4 | 2021-08-12 09:36 | 2021-08-12 10:08 | 0:32 | T | Tripped showing E/F relay | 30 | 16 | Power interruption
Sikalbaha | 132/33 kv transformers T3 | 2021-08-15 05:25 | 2021-08-15 05:35 | 0:10 | T | Tripped showing E/F relay | 28 | 4.6667 | Power interruption
Sikalbaha | 132/33 kv transformers T3 | 2021-08-15 14:45 | 2021-08-15 15:25 | 0:40 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Halishahar | 33 kV upper bus | 2021-08-17 08:15 | 2021-08-17 09:34 | 1:19 | E/O | Due to red-hot maint | 34 | 44.7667 | Power interruption
Sikalbaha | 132/33 kv transformers T3 | 2021-08-17 15:35 | 2021-08-17 15:35 | 0:00 | T | Tripped showing differential relay | 0 | 0 | No interruption
Baroiarhat | 132/33 kv transformers T1 | 2021-08-18 19:06 | 2021-08-18 19:06 | 0:00 | T | Tripped showing PRD | 0 | 0 | No interruption
Halishahar | 132/33 kv transformers T-1 , T2 & T-3 | 2021-08-21 17:40 | 2021-08-21 17:56 | 0:16 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Chowmuhuni | 132/33 kv transformers T1 | 2021-08-27 07:13 | 2021-08-27 09:35 | 2:22 | E/O | Due to red-hot maint | 40 | 94.6667 | Power interruption
Khagrachori | 132/33 kv transformers T1 | 2021-08-30 12:00 | 2021-08-30 12:47 | 0:47 | E/O | Due to red-hot maint | 0 | 0 | No interruption
|  |  | Total : | 11:45 |  | Unserved Energy: |  | 205.7
Cumilla Grid Circle :
Sylhet | 132/33 kv transformers T1 | 2021-08-01 05:37 | 2021-08-01 05:37 | 0:00 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Cumilla(N) | 132/33 kv transformers T3 | 2021-08-01 15:25 | 2021-08-01 15:50 | 0:25 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Daudkandi | 132/33 kv transformers T2 | 2021-08-01 14:39 | 2021-08-01 18:09 | 3:30 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
Cumilla(N) | 132/33 kv transformers T3 & T-4 | 2021-08-02 17:54 | 2021-08-02 18:10 | 0:16 | T | Tripped showing O/C, E/F relay | 72 | 19.2 | Power interruption
Biyanibazar | 132/33 kv transformers T1 | 2021-08-09 14:15 | 2021-08-09 14:40 | 0:25 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Biyanibazar | 132/33 kv transformers T2 | 2021-08-09 14:15 | 2021-08-09 14:52 | 0:37 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Ashuganj | 230/132 kV Transformer OAT-12 | 2021-08-10 00:33 | 2021-08-10 01:39 | 1:06 | T | Tripped showing O/C, E/F relay | 30 | 33 | Power interruption
Biyanibazar | 132/33 kv transformers T2 with 33 kV Bus-2 | 2021-08-17 07:35 | 2021-08-17 08:41 | 1:06 | E/O | Due to red-hot maint | 30 | 33 | Power interruption
Cumilla(S) | 132/33 kv transformers T1 | 2021-08-17 03:25 | 2021-08-17 04:15 | 0:50 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Cumilla(S) | 132/33 kv transformers T2 | 2021-08-17 03:25 | 2021-08-17 04:33 | 1:08 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformers T3 | 2021-08-21 08:35 | 2021-08-21 09:26 | 0:51 | E/O | Due to red-hot maint | 30 | 25.5 | Power interruption
Sreemangal | 132/33 kv transformers T2 and T3 | 2021-08-21 11:02 | 2021-08-21 11:20 | 0:18 | T | Tripped due to 33 kV feeder fault | 17 | 5.1 | Power interruption
Shahjibazar | 132/33 kv transformers T2 and T6 | 2021-08-23 20:58 | 2021-08-23 21:08 | 0:10 | T | Tripped due to 33 kV feeder fault | 0 | 0 | No interruption
Cumilla(S) | 132/33 kv transformers T2 | 2021-08-24 12:43 | 2021-08-24 13:18 | 0:35 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Comilla(N) | 132/33 kv transformers T3 and T4 | 2021-08-27 10:13 | 2021-08-27 10:34 | 0:21 | T | Tripped showing O/C relay | 73 | 25.55 | Power interruption
Biyanibazar | 132/33 kv transformers T2 | 2021-08-29 15:02 | 2021-08-29 16:24 | 1:22 | E/O | Due to red-hot maint | 15 | 20.5 | Power interruption
Comilla(N) | 132/33 kv transformers T3 | 2021-08-29 15:09 | 2021-08-29 15:38 | 0:29 | T | Tripped showing O/C, E/F relay | 0 | 0 | No interruption
Comilla(N) | 132/33 kv transformers T4 | 2021-08-29 15:09 | 2021-08-29 15:37 | 0:28 | T | Tripped showing O/C, E/F relay | 95 | 44.3333 | Power interruption
|  |  | Total : | 13:57 |  |  |  | 206.1833
Khulna Grid Circle :
Jhenaidah | 132/33 kv transformers T1 and T2 | 2021-08-01 10:09 | 2021-08-01 10:17 | 0:08 | T | Tripped showing E/F relay | 71 | 9.4667 | Power interruption
Gollamari | 132/33 kv transformers T-1 | 2021-08-02 16:06 | 2021-08-02 16:56 | 0:50 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Gollamari | 132/33 kv transformers T1 | 2021-08-05 16:57 | 2021-08-05 17:24 | 0:27 | T | Tripped showing O/C relay | 24 | 10.8 | Power interruption
Gollamari | 132/33 kv transformers T2 | 2021-08-05 16:57 | 2021-08-05 17:30 | 0:33 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Gopalganj Old | 132/33 kv transformers T1 and T2 | 2021-08-06 02:50 | 2021-08-06 03:32 | 0:42 | T | Tripped showing E/F relay | 75 | 52.5 | Power interruption
Gallamari | 132/33 kv transformers T2 | 2021-08-06 11:56 | 2021-08-06 12:56 | 1:00 | E/O | Due to red-hot maint | 10 | 10 | Power interruption
Madaripur | 132/33 kv transformers T1, T3 & its 33 kV Bus | 2021-08-07 16:52 | 2021-08-07 18:12 | 1:20 | E/O | Due to red-hot maint | 30 | 40 | Power interruption
Faridpur | 132/33 kv transformers T1 | 2021-08-10 10:17 | 2021-08-10 10:55 | 0:38 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Patuakhali | 132/33 kv transformers T1 and T2 | 2021-08-10 21:05 | 2021-08-10 21:18 | 0:13 | E/O | Due to severe flashing at 33 kV feeder | 80 | 17.3333 | Power interruption
Goalpara | 132/33 kV Transformer-T5 | 2021-08-14 10:34 | 2021-08-14 12:20 | 1:46 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Gollamari | 132/33 kv transformers T1 and T2 | 2021-08-15 15:18 | 2021-08-15 15:40 | 0:22 | T | Tripped showing O/C relay due to fire at WZPDCL | 36 | 13.2 | Power interruption
Gopalganj(Old) | 33 kV Bus-1 | 2021-08-25 11:09 | 2021-08-25 13:55 | 2:46 | E/O | Due to 33 kV Fokirhat PBS feeder fault | 20 | 55.3333 | Power interruption
Rajbari | 33 kV Bus-1 | 2021-08-25 10:45 | 2021-08-25 12:10 | 1:25 | E/O | Due to 33 kV PBS feeder fault | 0 | 0 | No interruption
Faridpur | 132/33 kv transformers T1 and T2 | 2021-08-30 11:22 | 2021-08-30 11:42 | 0:20 | T | Due to 33 kV PBS feeder fault | 90 | 30 | Power interruption
|  |  | Total : | 12:30 |  | Unserved Energy: |  | 238.6333
HVDC Grid Circle : Nil
Nil
|  |  | Total : | 0:00 |  |  |  | 0
Bogura Grid Circle:
Rangpur | 132/33 kV Transformer-T4 | 2021-08-01 23:35 | 2021-08-02 01:02 | 1:27 | E/O | Due to red-hot maint | 42 | 60.9 | Power interruption
Ishwardi | 230/132 kV Transformer-T3 | 2021-08-02 18:20 | 2021-08-02 21:00 | 2:40 | T | Tripped showing showing over all lockout | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 and T2 | 2021-08-02 17:42 | 2021-08-02 17:52 | 0:10 | T | Due to 33 kV Kathalbaria feeder fault | 70 | 11.6667 | Power interruption
Purbasadipur | 132 kV Bus | 2021-08-03 07:55 | 2021-08-03 10:01 | 2:06 | E/O | Due to red-hot maint | 200 | 420 | Power interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2021-08-07 18:55 | 2021-08-07 20:13 | 1:18 | T | Tripped showing Lockout | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2021-08-10 09:30 | 2021-08-10 11:40 | 2:10 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Purbasadipur | 132/33 kV Transformer-T3 | 2021-08-10 16:58 | 2021-08-10 18:22 | 1:24 | T | Tripped showing Lockout | 0 | 0 | No interruption
Rajshahi | 132/33 kV Transformer-T2 | 2021-08-12 16:19 | 2021-08-12 18:18 | 1:59 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T4 | 2021-08-15 13:05 | 2021-08-15 14:06 | 1:01 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 with 33 kV Bus-2 & 3 | 2021-08-17 06:45 | 2021-08-17 09:23 | 2:38 | E/O | Due to red-hot maint | 70 | 184.3333 | Power interruption
Bogura | 132/33 kV Transformer-T4 | 2021-08-17 11:10 | 2021-08-17 12:11 | 1:01 | E/O | Due to red-hot maint | 20 | 20.3333 | Power interruption
Ishwardi | 132/33 kV Transformer-T2 | 2021-08-21 12:11 | 2021-08-21 14:28 | 2:17 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer-T01 | 2021-08-22 06:25 | 2021-08-22 08:10 | 1:45 | E/O | Due to high temperature | 0 | 0 | No interruption
Mohasthangarh | 132/33 kv transformers T1 | 2021-08-24 06:58 | 2021-08-24 06:58 | 0:00 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Ishwardi | 132/33 kv transformers T1 | 2021-08-25 22:25 | 2021-08-25 22:45 | 0:20 | T | Tripped showing 33 kV Mulatuli feeder fault | 14 | 4.6667 | Power interruption
Sherpur(Bogura) | 132/33 kv transformers T-1 | 2021-08-29 11:07 | 2021-08-29 16:25 | 5:18 | T | Due to 33 kV Mohipur feeder CB CT burnout | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kv transformers T-2 | 2021-08-29 11:07 | 2021-08-29 11:45 | 0:38 | T | Due to 33 kV Mohipur feeder CB CT burnout | 35 | 22.1667 | Power interruption
Bogura(O) | 132/33 kv transformers T-2 & 33 kV Bus | 2021-08-29 10:46 | 2021-08-29 12:47 | 2:01 | E/O | Due to red-hot maint | 24 | 48.4 | Power interruption
Panchaghar | 132/33 kv transformers T-3 | 2021-08-29 11:44 | 2021-08-29 13:05 | 1:21 | T | Tripped showing PRD | 0 | 0 | No interruption
Panchaghar | 132/33 kv transformers T-4 | 2021-08-29 16:45 | 2021-08-29 21:21 | 4:36 | T | Tripped showing winding temperature high | 0 | 0 | No interruption
|  |  | Total : | 36:10 |  |  |  | 772.4667
Others :Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 105:48 | Hours
T = Tripping
E/O = Emergency Outage | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-24
Page: 1/2 | [8 empty] | OF-LDC-24
Power Grid Company of Bangladesh Ltd
Information Management Division
Outage of Transmission lines due to Tripping/Emergency Maintenance
Month:August 2021
Name of the | Equipment Name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date & Time | Date & Time |  | Outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Fatulla | Fatulla-Shyampur 132 kV Ckt-1 | 2021-08-04 18:26 | 2021-08-04 18:33 | 0:07 | T | Tripped showing Dist. Z1, O/C relay. | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-08-05 16:18 | 2021-08-05 17:04 | 0:46 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-1 | 2021-08-06 15:46 | 2021-08-06 21:06 | 5:20 | T | Tripped showing Diff, Dist relay and LA burst | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2021-08-09 08:22 | 2021-08-09 08:47 | 0:25 | T | Tripped showing dist T-phase relay | 275 | 114.5833 | Power interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2021-08-09 08:22 | 2021-08-09 11:44 | 3:22 | T | Tripped showing dist T-phase relay | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-1 | 2021-08-09 08:47 | 2021-08-09 11:54 | 3:07 | T | Tripped showing SPTF relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ishurdi 230 kV Ckt-2 | 2021-08-09 12:26 | 2021-08-09 14:04 | 1:38 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorasal GIS | Ghorasal GIS-Ishurdi 230 kV Ckt-2 | 2021-08-09 15:49 | 2021-08-09 21:17 | 5:28 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Kabirpur | Kabirpur-Tangi 132 kV Ckt-1 | 2021-08-09 14:19 | 2021-08-09 14:57 | 0:38 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Ghorashal | Ghorashal-Ashuganj(S) 230 kV Ckt-2 | 2021-08-10 12:44 | 2021-08-10 17:44 | 5:00 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Tongi S/S | Tongi S/S-Tongi 80 MW PP 132 kV Ckt | 2021-08-11 06:25 | 2021-08-11 06:25 | 0:00 | T | Tripped showing protection relay | 0 | 0 | No interruption
Mymensingh RPCL P.P | Mymensingh RPCL P.P.-Mymensingh S/S 132 kV Ckt-1 | 2021-08-11 09:56 | 2021-08-11 13:53 | 3:57 | E/O | Due to red hot maint | 0 | 0 | No interruption
Tangail | Tangail-RPCL 132 kV Ckt-1 | 2021-08-13 21:19 | 2021-08-13 21:39 | 0:20 | T | Tripped showing showing backup relay | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj(S) 230 kV Ckt-2 | 2021-08-14 14:39 | 2021-08-14 21:12 | 6:33 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Manikganj P.P | Manikganj P.P.-Aminbazar S/S 132 kV Ckt-1 | 2021-08-15 20:23 | 2021-08-16 04:22 | 7:59 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shympur 230 kV Ckt-1 | 2021-08-16 10:12 | 2021-08-16 10:28 | 0:16 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Meghnaghat | Meghnaghat-Shympur 230 kV Ckt-1 | 2021-08-17 10:15 | 2021-08-17 10:44 | 0:29 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Rampura | Rampura-Gulshan 132 kV Ckt-1 | 2021-08-20 03:13 | 2021-08-20 03:13 | 0:00 | T | Tripped showing differential relay. | 0 | 0 | No interruption
Rampura | Rampura-Bashundhara 132 kV Ckt-1 | 2021-08-22 15:24 | 2021-08-22 16:16 | 0:52 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
Kaliakoir | Kaliakoir-Summit 300 MW P.P. 230 kV Ckt | 2021-08-26 10:33 | 2021-08-26 11:28 | 0:55 | T | Tripped showing Dist. E/F relay. | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL P.P. 132 kV Ckt | 2021-08-26 13:08 | 2021-08-26 13:29 | 0:21 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Tangail | Tangail-Mymensingh RPCL P.P. 132 kV Ckt | 2021-08-26 17:59 | 2021-08-26 18:16 | 0:17 | T | Tripped showing E/F relay | 0 | 0 | No interruption
Shyampur old | Shyampur old-Shyampur new 132 kV both Ckts | 2021-08-27 08:15 | 2021-08-27 08:38 | 0:23 | T | Tripped showing Dist. E/F relay. | 156 | 59.8 | Power interruption
Mymensing RPCL | Mymensing RPCL-Mymensing S/S 132 kV Ckt-2 | 2021-08-29 10:24 | 2021-08-29 12:52 | 2:28 | E/O | Due to red hot maint | 100 | 246.6667 | Power interruption
Mymensing RPCL | Mymensing RPCL-Mymensing S/S 132 kV Ckt-3 | 2021-08-29 15:13 | 2021-08-29 15:52 | 0:39 | T | Tripped showing Dist. Z1 relay. | 0 | 0 | No interruption
|  |  | Total : | 30:29 |  | Unserved Energy: |  | 421.05
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Matuail 132 kV Ckt | 2021-08-03 12:18 | 2021-08-03 12:30 | 0:12 | T | Tripped showing O/C relay. | 40 | 8 | Power interruption
Siddhirganj | Siddhirganj-Siddhirganj GT-1 132 kV | 2021-08-03 12:18 | 2021-08-03 13:13 | 0:55 | T | Tripped showing master trip relay. | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Siddhirganj GT-2 132 kV | 2021-08-03 12:18 | 2021-08-03 13:38 | 1:20 | T | Tripped showing master trip relay. | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Ullon 132 kV Ckt | 2021-08-04 19:36 | 2021-08-04 20:25 | 0:49 | T | Tripped due to Insulator of R-phase got burst | 0 | 0 | No interruption
Sonargaon | Sonargaon-Megnaghat IEL P/S 132 kV Ckt | 2021-08-18 10:31 | 2021-08-18 11:44 | 1:13 | T | Tripped showing dist.Z1 relay | 0 | 0 | No interruption
Sonargaon | Sonargaon-Megnaghat IEL P/S 132 kV Ckt | 2021-08-18 17:10 | 2021-08-18 18:25 | 1:15 | T | Tripped showing dist.Z1 relay | 0 | 0 | No interruption
Haripur | Haripur-Bhulta 132 kV Ckt | 2021-08-24 04:05 | 2021-08-24 04:24 | 0:19 | T | Tripped due to 33 kV feeder fault | 0 | 0 | No interruption
Haripur | Haripur-Norsingdi 132 kV Ckt | 2021-08-13 08:18 | 2021-08-13 08:52 | 0:34 | T | Tripped showing Dist.Z1 relay | 50 | 28.3333 | Power interruption
|  |  | Total : | 6:37 |  | Unserved Energy: |  | 36.3333
Chattogram Grid Circle :
Hathazari | Hathazari-Baroirhat 132 kV Ckt-1 | 2021-08-06 10:37 | 2021-08-06 10:50 | 0:13 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Hathazari | Hathazari-Madunaghat 132 kV Ckt-1 | 2021-08-07 03:23 | 2021-08-07 04:01 | 0:38 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-1 | 2021-08-07 03:09 | 2021-08-07 04:12 | 1:03 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Khulshi | Khulshi-Halishahar 132 kV Ckt-2 | 2021-08-07 03:28 | 2021-08-07 04:21 | 0:53 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Bakulia | Bakulia-Kulshi 132 kV Ckt-2 | 2021-08-12 08:47 | 2021-08-12 16:49 | 8:02 | T | Tripped showing Dist.Z1 , SOTF relay | 0 | 0 | No interruption
Halishahar | Halishahar-Rampur-Kulshi 132 kV Ckt-1 | 2021-08-13 06:08 | 2021-08-13 07:54 | 1:46 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Baraulia | Baraulia-Hathazari 132 kV Ckt | 2021-08-18 20:34 | 2021-08-18 21:05 | 0:31 | E/O | Due to red-hot maint | 0 | 0 | No interruption
Raozan | Raozan-Hathazari 230 kV Ckt | 2021-08-20 13:46 | 2021-08-20 15:44 | 1:58 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulsi 132 kV Ckt-1 | 2021-08-21 17:13 | 2021-08-21 17:31 | 0:18 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulsi 132 kV Ckt-2 | 2021-08-21 17:40 | 2021-08-21 17:56 | 0:16 | T | Tripped showing Dist.Z1 relay | 74 | 19.7333 | Power interruption
Cox'sbazar | Cox'sbazar-Dohazari 132 kV Ckt-2 | 2021-08-22 14:33 | 2021-08-22 14:42 | 0:09 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-08-23 18:40 | 2021-08-23 18:46 | 0:06 | T | Tripped showing O/C,U/V relay | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt | 2021-08-24 11:24 | 2021-08-24 11:31 | 0:07 | T | Tripped showing Dist.Z1 relay | 94 | 10.9667 | Power interruption
Halishahar | Halishahar-Kulshi 132 kV Ckt-3 | 2021-08-25 04:05 | 2021-08-25 07:44 | 3:39 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Chandraghona | Chandraghona-Madunaghat 132 kV Ckt-2 | 2021-08-28 17:38 | 2021-08-28 17:38 | 0:00 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-3 | 2021-08-31 11:43 | 2021-08-31 12:45 | 1:02 | T | Tripped showing Dist.Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 20:41 |  | Unserved Energy: |  | 30.7
Cumilla Grid Circle :
Comilla(N) | Comilla(N)-Shahjibazar 230 kV Ckt-2 | 2021-08-04 06:09 | 2021-08-04 06:23 | 0:14 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Feni | Feni-Chowmuhoni 132 kV Ckt-2 | 2021-08-05 17:28 | 2021-08-05 17:39 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-08-04 12:43 | 2021-08-04 13:38 | 0:55 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorashal 230 kV Ckt-1 | 2021-08-05 09:46 | 2021-08-05 11:19 | 1:33 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
B. Baria | B. Baria-Shahjibazar 132 kV Ckt-2 | 2021-08-07 23:51 | 2021-08-07 23:51 | 0:00 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-1 | 2021-08-14 11:58 | 2021-08-14 12:09 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Fenchuganj | Fenchuganj-Sylhet 132 kV Ckt | 2021-08-18 10:55 | 2021-08-18 12:09 | 1:14 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Sylhet S/S | Sylhet S/S-Sylhet-50 P/S 132 kV Ckt | 2021-08-18 10:55 | 2021-08-18 12:09 | 1:14 | T | Tripped due to R-phase LA burst at P/S | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-08-18 22:07 | 2021-08-18 22:51 | 0:44 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Shahjibazar 230 kV Ckt-2 | 2021-08-23 21:31 | 2021-08-23 21:58 | 0:27 | T | Tripped showing Dist. E/F 3-phase relay | 0 | 0 | No interruption
Cumilla(N) | Comilla(N)-BSRM 230 kV Ckt-2 | 2021-08-27 11:54 | 2021-08-27 14:04 | 2:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 8:53 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna© | Khulna©-Goalpara 132 kV Ckt-1 | 2021-08-01 07:55 | 2021-08-01 09:08 | 1:13 | T | Tripped showing A/R block at Khulna© | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Magura 132 kV Ckt-2 | 2021-08-03 22:17 | 2021-08-03 22:28 | 0:11 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Bheramara | Bheramara-Ishwardi 132 kV Ckt-1 | 2021-08-04 17:44 | 2021-08-04 18:27 | 0:43 | T | Tripped showing no relay | 0 | 0 | No interruption
Jashore | Jashore-Noapara 132 kV Ckt-2 | 2021-08-06 04:55 | 2021-08-06 05:21 | 0:26 | T | Tripped showing no relay | 0 | 0 | No interruption
Jashore | Jashore-Noapara 132 kV Ckt-1 | 2021-08-06 04:55 | 2021-08-06 05:25 | 0:30 | T | Tripped showing Dist. Z1 and E/F relays | 391 | 195.5 | Power interruption
Bheramara | Bheramara-Bottail 132 kV Ckt-2 | 2021-08-06 04:56 | 2021-08-06 05:26 | 0:30 | T | Tripped showing no relay | 0 | 0 | No interruption
Bheramara | Bheramara-Bottail 132 kV Ckt-1 | 2021-08-06 04:57 | 2021-08-06 05:27 | 0:30 | T | Tripped showing Inst. E/F relays | 0 | 0 | No interruption
Bheramara | Bheramara-Bahrampur 400 kV Ckt-2 | 2021-08-07 09:55 | 2021-08-07 10:17 | 0:22 | T | Tripped showing direct receive channel-2 | 0 | 0 | No interruption
Kustia | Kustia-Bheramara 132 kV Ckt-1 & 2 | 2021-08-13 21:38 | 2021-08-13 21:52 | 0:14 | T | Tripped showing Dist. Z1 and O/C relays | 452 | 105.4667 | Power interruption
Jashore | Jashore-Noapara 132 kV Ckt-1 & 2 | 2021-08-13 21:38 | 2021-08-13 21:56 | 0:18 | T | Tripped showing Dist. Z1 and O/C relays | 0 | 0 | No interruption
Rajbari | Rajbari-Bheramara 132 kV Ckt-2 | 2021-08-25 20:25 | 2021-08-25 21:21 | 0:56 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 5:53 |  | Unserved Energy: |  | 300.9667
HVDC Grid Circle :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle:
Sirajganj | Sirajganj-Sherpur(Bogura) 132 kV Ckt-2 | 2021-08-01 14:50 | 2021-08-01 15:49 | 0:59 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-1 | 2021-08-02 06:11 | 2021-08-02 06:36 | 0:25 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-2 | 2021-08-02 06:11 | 2021-08-02 07:30 | 1:19 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-1 | 2021-08-02 06:42 | 2021-08-02 07:22 | 0:40 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Ishwardi | Ishwardi-Ghorashal 230 kV Ckt-2 | 2021-08-05 11:26 | 2021-08-05 13:50 | 2:24 | T | Tripped showing PT, Dist. Primary, Backup relay | 0 | 0 | No interruption
Ishwardi | Ishwardi-Bheramara 132 kV Ckt-1&2 | 2021-08-06 04:57 | 2021-08-06 06:05 | 1:08 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohosthnghar 132 kV Ckt-1 | 2021-08-07 05:35 | 2021-08-07 05:35 | 0:00 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Palashbari | Palashbari-Mohosthnghar 132 kV Ckt-2 | 2021-08-07 05:35 | 2021-08-07 05:35 | 0:00 | T | Tripped showing Dist. Z1 and E/F relay | 0 | 0 | No interruption
Rangpur Confi. | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-08-08 17:02 | 2021-08-08 17:02 | 0:00 | E/O | Due to SF6 gas leakage | 0 | 0 | No interruption
Palashbari | Palashbari-Mithapukur 132 kV Ckt-1 | 2021-08-09 23:58 | 2021-08-10 00:28 | 0:30 | T | Tripped showing dist main-2 | 80 | 40 | Power interruption
Palashbari | Palashbari-Mithapukur 132 kV Ckt-2 | 2021-08-09 23:58 | 2021-08-10 00:28 | 0:30 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Mohasthangarh | Mohasthangarh-Polashbari 132 kV Ckt-2 | 2021-08-11 00:05 | 2021-08-11 00:15 | 0:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Mohasthangarh | Mohasthangarh-Polashbari 132 kV Ckt-1 | 2021-08-11 00:05 | 2021-08-11 00:15 | 0:10 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Rangpur Confi | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-08-17 09:24 | 2021-08-17 10:35 | 1:11 | E/O | Due to SF6 gas leakage | 0 | 0 | No interruption
Thakurgaon | Thakurgaon-Panchagar 132 kV Ckt | 2021-08-21 16:35 | 2021-08-21 16:45 | 0:10 | T | Tripped showing Dist. Z1 relay | 37 | 6.1667 | Power interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-1 | 2021-08-23 15:37 | 2021-08-23 15:53 | 0:16 | T | Tripped showing Dist. Z1, O/C relay | 0 | 0 | No interruption
Rangpur confi | Rangpur confidence P/S-Mithapukur 132 kV Ckt-2 | 2021-08-25 07:43 | 2021-08-25 09:09 | 1:26 | T | Due to gas leakage at P/S | 0 | 0 | No interruption
Ishwardi | Ishwardi-Bheramara 132 kV Ckt-1&2 | 2021-08-25 22:25 | 2021-08-25 22:34 | 0:09 | T | Tripped showing O/C relay | 0 | 0 | No interruption
Rangpur confi | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-08-30 14:21 | 2021-08-30 14:26 | 0:05 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
Rangpur confi | Rangpur Confidence-Mithapukur 132 kV Ckt-1 | 2021-08-30 14:21 | 2021-08-30 14:40 | 0:19 | T | Tripped showing Dist. Z1 relay | 0 | 0 | No interruption
|  |  | Total : | 11:51 |  | Unserved Energy: |  | 46.1667
Others :Nil
Nil
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-station Equipment : |  |  |  | 84:24 | Hours
T = Tripping | [7 empty] | Executive Engineer
E/O = Emergency Outage | [7 empty] | Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-25
Page: 1/4 | [8 empty] | QF-LDC-25
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Sub-Station Equipment due to Schedule Maintenance/Project Work
Month:August 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Tangail | 132/33 kV transformer T3 | 2021-08-02 11:10 | 2021-08-02 13:07 | 1:57 | S/O | Due to C/M work | 24 | 46.8 | Power interruption
Tongi | 132/33 kV transformer T3 | 2021-08-06 09:42 | 2021-08-06 09:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T2 | 2021-08-08 06:20 | 2021-08-08 09:54 | 3:34 | S/O | Due to Maintenance work | 0 | 0 | No interruption
Jamalpur | 132/33 kV transformer T4 | 2021-08-08 10:35 | 2021-08-08 12:16 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 transformer T01 | 2021-08-08 10:35 | 2021-08-08 12:16 | 1:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T2 | 2021-08-09 07:12 | 2021-08-09 08:42 | 1:30 | S/O | Due to D/W work | 10 | 15 | Power interruption
Aminbazar | 132 kV main bus | 2021-08-09 10:46 | 2021-08-09 15:27 | 4:41 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 132 kV auxiliary bus | 2021-08-09 16:18 | 2021-08-09 16:48 | 0:30 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 230/132 T03 transformer | 2021-08-09 10:20 | 2021-08-09 16:06 | 5:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T1 | 2021-08-09 12:35 | 2021-08-09 13:07 | 0:32 | S/O | Due to OLTC work. | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T2 | 2021-08-09 13:09 | 2021-08-09 13:36 | 0:27 | S/O | Due to OLTC work. | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T3 | 2021-08-10 08:30 | 2021-08-10 09:35 | 1:05 | S/O | Due to C/M work | 40 | 43.3333 | Power interruption
Mymensingh | 132/33 kV transformer T1 | 2021-08-10 09:36 | 2021-08-10 12:20 | 2:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T2 | 2021-08-10 12:25 | 2021-08-10 13:30 | 1:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensingh | 132/33 kV transformer T3 | 2021-08-10 13:35 | 2021-08-10 14:50 | 1:15 | S/O | Due to meter replacement | 0 | 0 | No interruption
Munshiganj | 33 kV Bus-2 | 2021-08-12 06:42 | 2021-08-12 08:15 | 1:33 | S/O | Due to C/M work | 34 | 52.7 | Power interruption
Nawabganj | 132/33 kV transformer T1 | 2021-08-16 07:43 | 2021-08-16 09:03 | 1:20 | S/O | Due to C/M work | 40 | 53.3333 | Power interruption
Aminbazar | 132/33 kV transformer T3 | 2021-08-18 09:41 | 2021-08-18 16:47 | 7:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T1 | 2021-08-18 10:31 | 2021-08-18 11:44 | 1:13 | S/O | Due to oil sample collection. | 0 | 0 | No interruption
Sherpur | 132/33 kV transformer T2 | 2021-08-18 10:31 | 2021-08-18 11:44 | 1:13 | S/O | Due to oil sample collection. | 0 | 0 | No interruption
Dhamrai | 132/33 kV transformer T2 | 2021-08-19 06:07 | 2021-08-19 10:04 | 3:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T1 | 2021-08-19 06:53 | 2021-08-19 10:02 | 3:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | 132/33 kV transformer T2 | 2021-08-22 07:17 | 2021-08-22 09:14 | 1:57 | S/O | Due to C/M work | 40 | 78 | Power interruption
Aminbazar | 400/230 kV transformer T-3 | 2021-08-24 10:15 | 2021-08-24 16:05 | 5:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 132 kV Bus -1 | 2021-08-24 10:10 | 2021-08-24 14:10 | 4:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | 133 kV Bus -2 | 2021-08-24 14:25 | 2021-08-24 16:35 | 2:10 | S/O | Due to D/W work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer ATR-03 | 2021-08-25 10:52 | 2021-08-25 16:37 | 5:45 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | 132/33 kV transformer T3 | 2021-08-26 07:41 | 2021-08-26 07:41 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T1 | 2021-08-27 10:10 | 2021-08-27 13:14 | 3:04 | S/O | Due to C/M work | 0 | 0 | No interruption
Narsingdi | 132/33 kV transformer T2 | 2021-08-27 14:24 | 2021-08-27 16:55 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer T1 | 2021-08-28 11:18 | 2021-08-28 12:29 | 1:11 | S/O | Due to C/M work | 0 | 0 | No interruption
Aminbazar | 400/230 kV transformer TR-2 | 2021-08-29 10:07 | 2021-08-29 16:57 | 6:50 | S/O | Due to D/W work | 0 | 0 | No interruption
Srinagar | 132/33 kV transformer T2 | 2021-08-29 10:07 | 2021-08-29 14:04 | 3:57 | S/O | Due to oil filling | 0 | 0 | No interruption
Tongi | 132/33 kV transformer T2 | 2021-08-29 10:02 | 2021-08-29 10:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T2 | 2021-08-30 11:10 | 2021-08-30 19:19 | 8:09 | S/O | Due to D/W work | 0 | 0 | No interruption
Nawabganj | 132/33 kV transformer T1 | 2021-08-30 13:25 | 2021-08-30 18:30 | 5:05 | S/O | Due to D/W work | 0 | 0 | No interruption
Tangail | 132/33 kV transformer T2 | 2021-08-31 12:06 | 2021-08-31 13:36 | 1:30 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 99:58 |  | Unserved Energy: |  | 289.1667
Dhaka (South) Grid Circle :
Hasnabad | 132/33 kv transformers T-1 | 2021-08-02 08:47 | 2021-08-02 11:52 | 3:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kv transformers T-5 | 2021-08-02 14:52 | 2021-08-02 16:45 | 1:53 | S/O | Due to protection test | 0 | 0 | No interruption
Hasnabad | 132/33 kv transformers T-1 |  | 2021-08-04 18:49 |  | S/O | After maintence | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformers T-1 |  | 2021-08-05 12:57 |  | S/O | After maintence | 0 | 0 | No interruption
Haripur | 230/132 kV transformers T-2 |  | 2021-08-05 12:57 |  | S/O | After maintence | 0 | 0 | No interruption
Hasnabad | 230/132 kV transformers T-1 | 2021-08-07 09:20 | 2021-08-07 11:36 | 2:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur SBU | 132/33 kV transformer T1 | 2021-08-07 13:23 | 2021-08-07 14:50 | 1:27 | S/O | Due to C/M work | 40 | 58 | Power interruption
Hasnabad | 230/132 kV transformers T-03 | 2021-08-10 11:45 | 2021-08-10 11:45 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kv transformers T-5 | 2021-08-10 20:58 | 2021-08-10 22:20 | 1:22 | S/O | Due to neutral grounding checking. | 0 | 0 | No interruption
Siddhirganj | 230/132 kV transformers T-2 | 2021-08-16 09:10 | 2021-08-16 16:54 | 7:44 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | 230/132 kV transformers MTR-2 | 2021-08-23 13:57 | 2021-08-23 18:13 | 4:16 | S/O | Due to C/M work | 0 | 0 | No interruption
Hasnabad | 132/33 kV transformer T1 | 2021-08-25 10:01 | 2021-08-25 10:59 | 0:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddirganj | 230/132 kV transformers T-2 | 2021-08-29 16:41 | 2021-08-29 17:59 | 1:18 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 3:05 |  | Unserved Energy: |  | 58
Chattogram Grid Circle :
Madunaghat | 132/33 kv transformers T-1 | 2021-08-01 09:50 | 2021-08-01 13:06 | 3:16 | S/O | Due to C/M work | 0 | 0 | No interruption
GK Project | 132/33 kv transformers T-1 | 2021-08-03 10:30 | 2021-08-03 17:24 | 6:54 | S/O | Due to D/W work | 0 | 0 | No interruption
GK Project | 132/33 kv transformers T-3 | 2021-08-04 09:10 | 2021-08-04 15:58 | 6:48 | S/O | Due to D/W work | 0 | 0 | No interruption
GK Project | 132/33 kv transformers T-1 | 2021-08-04 09:16 | 2021-08-04 15:12 | 5:56 | S/O | Due to D/W work | 0 | 0 | No interruption
Bakulia | 132/33 kv transformers T-3 | 2021-08-04 16:22 | 2021-08-04 17:55 | 1:33 | S/O | Due to C/M work | 25 | 38.75 | Power interruption
Chowmuhoni | 132/33 kv transformers T-2 | 2021-08-11 23:23 | 2021-08-12 01:50 | 2:27 | S/O | Due to C/M work | 35 | 85.75 | Power interruption
Madunaghat | 132/33 kv transformers T-1 | 2021-08-20 08:27 | 2021-08-20 10:53 | 2:26 | S/O | Due to C/M work | 22 | 53.5333 | Power interruption
Chowmuhoni | 132/33 kv transformers T-2 | 2021-08-21 07:20 | 2021-08-21 13:36 | 6:16 | S/O | Due to C/M work | 40 | 250.6667 | Power interruption
Baraulia | 132/33 kv transformers T-3 |  | 2021-08-22 12:45 |  | S/O | After maintence | 0 | 0 | No interruption
Halishar | 132/33 kv transformers T-2 | 2021-08-23 07:35 | 2021-08-23 07:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | 132/33 kv transformers T-1 | 2021-08-27 07:57 | 2021-08-27 08:57 | 1:00 | S/O | Due to C/M work | 24 | 24 | Power interruption
Madunaghat | 132/33 kv transformers T-1 and 33 kV bus | 2021-08-28 13:28 | 2021-08-28 17:56 | 4:28 | S/O | Due to C/M work | 34 | 151.8667 | Power interruption
Madunaghat | 132/33 kv transformers T-2 and 33 kV bus | 2021-08-28 15:56 | 2021-08-28 16:46 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Bakulia | 132/33 kv transformers T-3 | 2021-08-29 05:43 | 2021-08-29 07:44 | 2:01 | S/O | Due to C/M work | 0 | 0 | No interruption
Sikalbaha | 132/33 kv transformers T-4 | 2021-08-29 07:03 | 2021-08-29 08:03 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Hathazari | 230 kV Bus-1 | 2021-08-29 14:30 | 2021-08-29 16:58 | 2:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | 231 kV Bus-1 | 2021-08-30 09:19 | 2021-08-30 12:12 | 2:53 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 50:16 |  | Unserved Energy : |  | 604.5667
Cumilla Grid Circle :
Cumilla(N) | 132/33 kv transformers T4 | 2021-08-01 11:37 | 2021-08-01 15:50 | 4:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Chatak | 132/33 kv transformers T3 | 2021-08-08 08:43 | 2021-08-08 09:49 | 1:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kv transformers T4 | 2021-08-12 08:01 | 2021-08-12 09:27 | 1:26 | S/O | Due to C/M work | 20 | 28.6667 | Power interruption
Shahjibazar | 132/33 kv transformers T2 | 2021-08-13 10:32 | 2021-08-13 11:20 | 0:48 | S/O | Due to C/M work | 21 | 16.8 | Power interruption
B.Baria | 132/33 kv transformers T1,T2 | 2021-08-17 09:28 | 2021-08-17 11:05 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kv transformers T-1 | 2021-08-18 10:47 | 2021-08-18 17:31 | 6:44 | S/O | Due to C/M work | 10 | 67.3333 | Power interruption
Beanibazar | 33 kV Bus section-1 | 2021-08-18 15:50 | 2021-08-18 17:33 | 1:43 | S/O | Due to maintenance work | 10 | 17.1667 | Power interruption
Ramganj | 132/33 kv transformers T-1 | 2021-08-19 09:22 | 2021-08-19 15:46 | 6:24 | S/O | Due to D/W work | 20 | 128 | Power interruption
Cumilla(N) | 132/33 kv transformers T3 | 2021-08-19 10:50 | 2021-08-19 16:20 | 5:30 | S/O | Due to winding temperature meter work | 0 | 0 | No interruption
Ramganj | 132/33 kv transformers T-2 | 2021-08-20 10:07 | 2021-08-20 15:52 | 5:45 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | 132/33 kv transformers T-1 with 33 kV Bus | 2021-08-21 08:49 | 2021-08-21 14:24 | 5:35 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformers T-2 | 2021-08-24 15:35 | 2021-08-24 17:01 | 1:26 | S/O | Due to C/M work | 35 | 50.1667 | Power interruption
Beanibazar | 132/33 kv transformers T-2 | 2021-08-27 10:02 | 2021-08-27 10:02 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformers T-4 | 2021-08-27 12:06 | 2021-08-27 17:49 | 5:43 | S/O | Due to D/W work | 0 | 0 | No interruption
Shahjibazar | 132/33 kv transformers T-2 | 2021-08-28 10:21 | 2021-08-28 12:29 | 2:08 | S/O | Due to C/M work | 20 | 42.6667 | Power interruption
|  |  | Total : | 50:08 |  | Unserved Energy : |  | 350.8
Khulna Grid Circle :
Faridpur | 132/33 kv transformers T-1 | 2021-08-02 07:38 | 2021-08-02 08:45 | 1:07 | S/O | Due to C/M work | 21 | 23.45 | Power interruption
Barishal(N) | 132/33 kv transformers T-1 | 2021-08-02 08:45 | 2021-08-02 14:45 | 6:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Gollamari | 132/33 kv transformers T-2 | 2021-08-02 13:24 | 2021-08-02 14:48 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kv transformers T-2 | 2021-08-04 07:50 | 2021-08-04 08:25 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Patuakhali | 132/33 kv transformers T-1 | 2021-08-04 08:26 | 2021-08-04 09:40 | 1:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | 132/33 kv transformers T-3 | 2021-08-04 09:57 | 2021-08-04 15:15 | 5:18 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | 132/33 kV transformer T2 | 2021-08-11 07:06 | 2021-08-11 08:19 | 1:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Jashore | 132/33 kV transformer T1 | 2021-08-11 08:21 | 2021-08-11 10:57 | 2:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(New) | 230 kV Bus-1 | 2021-08-12 08:34 | 2021-08-12 16:36 | 8:02 | S/O | Due to D/W work | 0 | 0 | No interruption
Jhenaidah | 230 kV Bus-1 | 2021-08-14 07:56 | 2021-08-14 17:04 | 9:08 | S/O | Due to D/W work | 0 | 0 | No interruption
Faridpur | 132/33 kv transformers T-3 | 2021-08-19 08:52 | 2021-08-19 13:14 | 4:22 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | 132/33 kv transformers T-4 | 2021-08-23 14:51 | 2021-08-23 15:50 | 0:59 | S/O | Due to C/M work | 8 | 7.8667 | Power interruption
Noapara | 132/33 kv transformers T-3 | 2021-08-23 20:50 | 2021-08-23 21:15 | 0:25 | S/O | Due to C/M work | 0 | 0 | No interruption
Gopalganj | 132/33 kV transformer T1 | 2021-08-27 08:16 | 2021-08-27 10:08 | 1:52 | S/O | Due to C/M work | 0 | 0 | No interruption
Satkhira | 132/33 kV transformer T1 | 2021-08-27 09:38 | 2021-08-27 11:33 | 1:55 | S/O | Due to C/M work | 40 | 76.6667 | Power interruption
|  |  | Total : | 46:10 |  | Unserved Energy : |  | 107.9833
HVDC Grid Circle :Nil
HVDC Bheramara | HVDC Bheramara 20DF 22 filter | 2021-08-16 15:34 | 2021-08-16 20:24 | 4:50 | S/O | Due to maintenance work | 0 | 0 | No interruption
|  |  | Total : | 4:50 |  | Unserved Energy : |  | 0
Bogura Grid Circle:
Chapainawabganj | 132/33 kV Transformer-T1 | 2021-08-02 08:22 | 2021-08-02 08:22 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T2 | 2021-08-03 05:56 | 2021-08-03 05:56 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T1 | 2021-08-03 14:20 | 2021-08-03 17:05 | 2:45 | S/O | Due to C/M work | 20 | 55 | Power interruption
Natore | 132/33 kV Transformer-T4 | 2021-08-04 05:46 | 2021-08-04 05:46 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Purbasadipur | Purbasadipur 132 kV full Bus | 2021-08-06 05:54 | 2021-08-06 08:31 | 2:37 | S/O | Due to D/W work | 240 | 628 | Power interruption
Sirajganj | 132/33 kV Transformer-T1 | 2021-08-06 08:39 | 2021-08-06 09:19 | 0:40 | S/O | Due to C/M work | 15 | 10 | Power interruption
Bogura | 132/33 kV Transformer-T1 | 2021-08-08 16:12 | 2021-08-08 17:09 | 0:57 | S/O | Due to C/M work | 60 | 57 | Power interruption
Pabna | 132/33 kV Transformer-T2 | 2021-08-11 16:46 | 2021-08-11 17:46 | 1:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T4 |  | 2021-08-12 18:45 |  | S/O | After maintence | 0 | 0 | No interruption
Rangpur | 132/33 kV Transformer-T2 and 33 kV bus sec-2 | 2021-08-13 10:59 | 2021-08-13 11:45 | 0:46 | S/O | Due to C/M work | 60 | 46 | Power interruption
Sherpur(Bogura) | 132/33 kV Transformer-T1 | 2021-08-13 11:48 | 2021-08-13 11:58 | 0:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur(Bogura) | 132/33 kV Transformer-T2 | 2021-08-13 11:48 | 2021-08-13 11:58 | 0:10 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohastanghor | 132/33 kV Transformer-T2 | 2021-08-18 12:54 | 2021-08-18 13:16 | 0:22 | S/O | Due to D/W work | 0 | 0 | No interruption
Natore | 132/33 kV Transformer-T1 | 2021-08-19 06:54 | 2021-08-19 10:15 | 3:21 | S/O | Due to C/M work | 35 | 117.25 | Power interruption
Jaldhaka | 132/33 kV Transformer-T1 | 2021-08-20 10:30 | 2021-08-20 13:20 | 2:50 | S/O | Due to PT installation. | 36 | 102 | Power interruption
Rajshahi | 132/33 kV Transformer-T3 | 2021-08-21 07:09 | 2021-08-21 08:31 | 1:22 | S/O | Due to C/M work | 20 | 27.3333 | Power interruption
Ishwardi | 132/33 kV Transformer-T1 | 2021-08-21 10:42 | 2021-08-21 12:11 | 1:29 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | 132/33 kV Transformer-T2 | 2021-08-22 13:14 | 2021-08-22 14:04 | 0:50 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV Transformer-T1 | 2021-08-23 12:01 | 2021-08-23 13:35 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | 132/33 kV Transformer-T2 | 2021-08-23 11:45 | 2021-08-23 12:00 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Naogaon | 132/33 kV Transformer-T3 | 2021-08-25 12:50 | 2021-08-25 14:55 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Barapukuria | 230/132 kV Transformer- T01 | 2021-08-28 05:57 | 2021-08-28 05:57 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | 132/33 kV Transformer-T4 | 2021-08-28 20:19 | 2021-08-28 21:02 | 0:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjadpur | 132/33 kV Transformer-T3 | 2021-08-31 11:56 | 2021-08-31 12:58 | 1:02 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 24:58 |  | Unserved Energy : |  | 1042.5833
Others :Nil
|  |  | Total | 0:00 |  | Unserved Energy : |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 279:25 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance | [7 empty] | Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-26
Page: 1/5 | [8 empty] | QF-LDC-26
POWER GRID COMPANY OF BANGLADESH LTD
Information Management Division, LDC, Dhaka.
Outage of Transmission Lines due to Scheduled Maintenance/Project Work
Month:August 2021
Name of the | Equipment name | Start | Finish | Duration | Type of | Cause | Unserved | Unserved | Remarks
Sub-station |  | Date and Time | Date and Time |  | outage |  | Load (MW) | Energy (MWH)
Dhaka (North) Grid Circle :
Mymensing | Mymensing-Bhaluka 132 kV Ckt-1 | 2021-08-09 09:35 | 2021-08-09 13:36 | 4:01 | S/O | Due to D/W work | 0 | 0 | No interruption
Mymensing | Mymensing-Bhaluka 132 kV Ckt-2 | 2021-08-09 13:42 | 2021-08-09 16:02 | 2:20 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kodda 132 kV Ckt-2 | 2021-08-09 14:19 | 2021-08-09 17:34 | 3:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj GIS | Keraniganj GIS-Lalbagh 132 kV Ckt-1 | 2021-08-11 10:18 | 2021-08-11 16:43 | 6:25 | S/O | Due to project work | 0 | 0 | No interruption
Keraniganj GIS | Keraniganj GIS-Lalbagh 132 kV Ckt-2 | 2021-08-11 10:18 | 2021-08-11 16:44 | 6:26 | S/O | Due to project work | 0 | 0 | No interruption
Keraniganj GIS | Keraniganj GIS-Lalbagh 132 kV Ckt-3 | 2021-08-11 10:18 | 2021-08-11 10:18 | 0:00 | S/O | Due to project work | 0 | 0 | No interruption
Mymensingh RPCL P.P | Mymensingh RPCL P.P.-Mymensingh S/S 132 kV Ckt-2 | 2021-08-11 14:03 | 2021-08-11 17:16 | 3:13 | S/O | Due to C/M work | 0 | 0 | No interruption
Madanganj | Madanganj-Munshiganj 132 kV Ckt-2 | 2021-08-12 14:26 | 2021-08-12 17:34 | 3:08 | S/O | Due to relay protection test. | 0 | 0 | No interruption
Aminbazar | Aminbazar-Mirpur 132 kV Ckt-1 | 2021-08-16 10:07 | 2021-08-16 16:01 | 5:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-1 | 2021-08-17 07:32 | 2021-08-17 07:32 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Valuka 132 kV Ckt-1 | 2021-08-18 10:44 | 2021-08-18 12:50 | 2:06 | S/O | Due to C/M work | 0 | 0 | No interruption
Tongi | Tongi-New Tongi 132 kV Ckt-1 | 2021-08-18 11:16 | 2021-08-18 12:50 | 1:34 | S/O | Due to C/M work | 0 | 0 | No interruption
Mymensing | Mymensing-Valuka 132 kV Ckt-2 | 2021-08-18 13:00 | 2021-08-18 13:35 | 0:35 | S/O | Due to C/M work | 0 | 0 | No interruption
Kodda | Kodda-Rajendrapur 132 kV Ckt-2 | 2021-08-20 10:51 | 2021-08-20 10:51 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Kaliakoir 132 kV Ckt-2 | 2021-08-20 12:22 | 2021-08-20 12:58 | 0:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Norsingdi 132 kV Ckt-1 | 2021-08-23 08:57 | 2021-08-23 14:43 | 5:46 | S/O | Due to D/W work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Ashuganj 132 kV Ckt-1 | 2021-08-24 11:48 | 2021-08-24 17:08 | 5:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-1 | 2021-08-24 10:23 | 2021-08-24 18:00 | 7:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV Ckt-2 | 2021-08-25 07:19 | 2021-08-25 07:19 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Tongi | Tongi-Bashundhara 132 kV Ckt-2 | 2021-08-25 11:37 | 2021-08-25 17:34 | 5:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Ghorasal | Ghorasal-Narshingdi 132 kV Ckt-2 | 2021-08-25 15:05 | 2021-08-25 17:33 | 2:28 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-2 | 2021-08-26 10:44 | 2021-08-26 16:22 | 5:38 | S/O | Due to C/M work | 0 | 0 | No interruption
Keraniganj New | Keraniganj New-Kamrangirchar 132 kV Ckt | 2021-08-27 06:38 | 2021-08-27 06:38 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Keraniganj New | Keraniganj New-Lalbagh 132 kV Ckt-1,2&3 | 2021-08-27 06:42 | 2021-08-27 06:42 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kabirpur | Kabirpur-Manikganj 132 kV Ckt-1 | 2021-08-27 07:41 | 2021-08-27 07:41 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Keraniganj(new) 132 kV Ckt |  | 2021-08-27 13:17 |  | S/O | After maintenance | 0 | 0 | No interruption
Tongi | Tongi-Metro Rail 132 kV Ckt | 2021-08-27 10:30 | 2021-08-27 18:22 | 7:52 | S/O | Due to painting work | 0 | 0 | No interruption
Kamrangirchar | Kamrangirchar-Keraniganj(new) 132 kV Ckt | 2021-08-27 13:25 | 2021-08-27 13:25 | 0:00 | S/O | Due to phase correction | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV ckt-2 | 2021-08-30 07:31 | 2021-08-30 07:31 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Manikganj | Manikganj-Kabirpur 132 kV ckt-2 | 2021-08-31 08:21 | 2021-08-31 15:24 | 7:03 | S/O | Due to D/W work | 0 | 0 | No interruption
Bhulta | Bhulta-Rampura 230 kV Ckt-3 | 2021-08-31 09:48 | 2021-08-31 13:55 | 4:07 | S/O | Due to C/M work | 0 | 0 | No interruption
Rampura | Rampura-Bhulta 230 kV Ckt-4 | 2021-08-31 14:15 | 2021-08-31 16:02 | 1:47 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 93:08 |  | Unserved Energy: |  | 0
Dhaka (South) Grid Circle :
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-2 |  | 2021-08-05 10:32 |  | S/O | After maintenance | 0 | 0 | No interruption
Haripur S/S | Haripur S/S-Haripur 412 MW P.P. Ckt |  | 2021-08-05 08:26 |  | S/O | After maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Sitalakha 132 kV Ckt | 2021-08-07 10:12 | 2021-08-07 10:12 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Brammangaon 132 kV Ckt | 2021-08-07 10:28 | 2021-08-07 18:13 | 7:45 | S/O | Due to DPDC work. | 0 | 0 | No interruption
Haripur | Haripur-Sonargaon 132 kV Ckt-1 | 2021-08-10 09:06 | 2021-08-10 11:48 | 2:42 | S/O | Due to C/M work | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2021-08-11 12:32 | 2021-08-11 16:59 | 4:27 | S/O | Due to C/M work | 0 | 0 | No interruption
Siddhirganj | Siddhirganj-Haripur 132 kV Ckt-1 | 2021-08-17 09:38 | 2021-08-17 12:35 | 2:57 | S/O | Due to C/M work | 0 | 0 | No interruption
Haripur | Haripur-Siddirganj 132 kV Ckt-2 | 2021-08-18 09:41 | 2021-08-18 16:47 | 7:06 | S/O | Due to relay test | 0 | 0 | No interruption
Sonargaon | Sonargaon-Daudkandi 132 kV Ckt-2 | 2021-08-21 09:47 | 2021-08-21 17:25 | 7:38 | S/O | Due to CB inspection. | 0 | 0 | No interruption
Hasnabad | Hasnabad-Kamrangirchar 132 kV Ckt | 2021-08-27 05:54 | 2021-08-27 05:54 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hasnabad | Hasnabad-Aurahati 132 kV Ckt |  | 2021-08-27 12:53 |  | S/O | After maintenance | 0 | 0 | No interruption
Hasnabad | Hasnabad-Lalbag 132 kV Ckt | 2021-08-28 06:57 | 2021-08-28 06:57 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 32:35 |  | Unserved Energy: |  | 0
Chattogram Grid Circle :
Hathazari | Hathazari-GPH 2302 kV Ckt | 2021-08-01 08:52 | 2021-08-01 17:57 | 9:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulshi | Khulshi-Abul Khair 132 kV Ckt | 2021-08-03 08:27 | 2021-08-03 08:27 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Khulshi | Khulshi-Baraulia 132 kV Ckt | 2021-08-03 08:27 | 2021-08-03 08:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-08-06 06:36 | 2021-08-06 06:36 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Hathazari | Hathazari-Baroirhat 132 kV Ckt-2 | 2021-08-07 10:57 | 2021-08-07 13:37 | 2:40 | S/O | Due to tree trimming | 0 | 0 | No interruption
Haripur | Haripur-Rahim Steel 132 kV Ckt |  | 2021-08-07 16:57 |  | S/O | After maintenance | 0 | 0 | No interruption
Khulshi | Khulshi-AKS 132 kV Ckt |  | 2021-08-07 15:35 |  | S/O | After maintenance | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-08-12 06:40 | 2021-08-13 01:11 | 18:31 | S/O | Due to D/W work | 13 | 240.7167 | Power interruption
Madunaghat | Madunaghat-Hathazari 132 kV Ckt | 2021-08-14 07:03 | 2021-08-14 07:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Halishahar | Halishahar-Khulshi 132 kV Ckt-2 | 2021-08-19 07:12 | 2021-08-19 12:32 | 5:20 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-08-21 07:14 | 2021-08-27 17:27 | 154:13 | S/O | Due to D/W work | 10 | 1542.1667 | Power interruption
Chowmohani | Chowmohani-Husaf P/S 132 kV | 2021-08-24 09:08 | 2021-08-24 12:06 | 2:58 | S/O | Due to C/M work | 0 | 0 | No interruption
Julda | Julda-Julda #1 P/S 132 kV Ckt | 2021-08-24 06:42 | 2021-08-24 08:06 | 1:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-2 | 2021-08-28 07:05 | 2021-08-28 07:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Dohazari | Dohazari-Cox'sbazar 132 kV Ckt-1 | 2021-08-29 12:23 | 2021-08-29 15:09 | 2:46 | S/O | Due to D/W work | 0 | 0 | No interruption
|  |  | Total : | 196:57 |  | Unserved Energy: |  | 1782.8833
Cumilla Grid Circle :
B. Baria | B. Baria-Shahjibazar 132 kV Ckt-2 | 2021-08-06 06:56 | 2021-08-06 06:56 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Sylhet | Sylhet-Fenchuganj 132 kV Ckt | 2021-08-05 07:27 | 2021-08-05 07:27 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Ramganj | Ramganj-Chandpur Desh 132 kV Ckt-1 | 2021-08-09 07:53 | 2021-08-09 07:53 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-1 | 2021-08-10 11:54 | 2021-08-10 13:43 | 1:49 | S/O | Due to protection test | 0 | 0 | No interruption
Daudkandi | Daudkandi-Sonargaon 132 kV Ckt-2 | 2021-08-10 13:46 | 2021-08-10 18:43 | 4:57 | S/O | Due to protection test | 0 | 0 | No interruption
Cumilla(N) | Cumilla(N)-Kochua 132 kV Ckt | 2021-08-17 10:30 | 2021-08-17 17:09 | 6:39 | S/O | Due to C/M work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Sirajganj 230 kV Ckt-2 | 2021-08-21 10:14 | 2021-08-21 11:35 | 1:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Shahjibazar S/S | Shahjibazar S/S-Shahjibazar 86 MW P/P 132 kV Ckt | 2021-08-23 06:05 | 2021-08-23 06:05 | 0:00 | S/O | Due to D/W work | 0 | 0 | No interruption
Ashuganj | Ashuganj-Ghorasal 132 kV Ckt-2 | 2021-08-24 09:04 | 2021-08-24 14:58 | 5:54 | S/O | Due to D/W work | 0 | 0 | No interruption
Cumilla | Cumilla-Daudkandi 132 kV Ckt-2 | 2021-08-31 11:41 | 2021-08-31 14:16 | 2:35 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 23:15 |  | Unserved Energy: |  | 0
Khulna Grid Circle :
Khulna(S) | Khulna(S)-Satkhira 132 kV Ckt-2 | 2021-08-02 08:50 | 2021-08-02 09:59 | 1:09 | S/O | Due to C/M work | 0 | 0 | No interruption
Faridpur | Faridpur-(Rajbari)-Bheramara 132 kV Ckt | 2021-08-03 07:35 | 2021-08-03 07:35 | 0:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV Ckt-1 | 2021-08-11 11:20 | 2021-08-11 12:57 | 1:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Noapara | Noapara-Jashore 132 kV Ckt-2 | 2021-08-11 13:02 | 2021-08-11 15:32 | 2:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah(New) | Jhenaidah(New)-Khulna(S) 230kV Ckt-1 | 2021-08-12 08:30 | 2021-08-12 16:36 | 8:06 | S/O | Due to D/W work. | 0 | 0 | No interruption
Faridpur | Faridpur-Bheramara 132 kV Ckt-2 | 2021-08-13 07:08 | 2021-08-13 07:08 | 0:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
Faridpur | Faridpur-Rajbari 132 kV Ckt-1 | 2021-08-13 08:01 | 2021-08-13 08:01 | 0:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
Bottail | Bottail-Jhenaidah 132 kV Ckt-1 | 2021-08-13 08:43 | 2021-08-13 10:02 | 1:19 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna(S) | Khulna(S)-Jhenaidah 230 kV Ckt | 2021-08-14 08:05 | 2021-08-14 17:05 | 9:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
Khulna© | Khulna©-Goalpara 132 kV Ckt-1 | 2021-08-14 10:32 | 2021-08-14 12:26 | 1:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Jhenaidah | Jhenaidah-Khulna(S) 230 kV Ckt-1 | 2021-08-20 07:45 | 2021-08-20 20:23 | 12:38 | S/O | Due to D/W work. | 0 | 0 | No interruption
Jashore | Jashore-Jhenaidah 132 kV Ckt 1 & 2 | 2021-08-21 06:51 | 2021-08-21 06:51 | 0:00 | S/O | Due to D/W work. | 0 | 0 | No interruption
Jaldhaka | Jaldhaka-Saidpur 132 kV Ckt-1 | 2021-08-23 11:45 | 2021-08-23 12:00 | 0:15 | S/O | Due to C/M work | 0 | 0 | No interruption
Jaldhaka | Jaldhaka-Saidpur 132 kV Ckt-2 | 2021-08-23 11:31 | 2021-08-23 11:45 | 0:14 | S/O | Due to C/M work | 0 | 0 | No interruption
Khulna© | Khulna(C)-Khulna 225 MW Ckt | 2021-08-26 09:54 | 2021-08-26 12:05 | 2:11 | S/O | Due to C/M work | 0 | 0 | No interruption
|  |  | Total : | 39:44 |  | Unserved Energy: |  | 0
HVDC Grid Circle :
HVDC Bheramara | HVDC Bheramara-Bahrampur 400 kV Ckt-3 | 2021-08-11 09:58 | 2021-08-11 14:07 | 0:49 | S/O | Due to maintenance | 0 | 0 | No interruption
HVDC Bheramara | Jhenaidah(New)-HVDC 230 kV Ckt-1 | 2021-08-12 08:28 | 2021-08-12 16:47 | 1:49 | S/O | Due to maintenance | 0 | 0 | No interruption
HVDC Bheramara | Jhenaidah-HVDC 230 kV Ckt | 2021-08-14 08:09 | 2021-08-14 17:04 | 2:49 | S/O | Due to D/W work. | 0 | 0 | No interruption
HVDC Bheramara | Bheramara HVDC-Jhenaidah 230 kV Ckt-1 | 2021-08-20 08:04 | 2021-08-20 17:26 | 3:49 | S/O | Due to D/W work. | 0 | 0 | No interruption
HVDC Bheramara | Khulna(S)-Bheramara HVDC 230 kV Ckt-2 | 2021-08-20 08:36 | 2021-08-20 20:23 | 4:49 | S/O | Due to D/W work. | 0 | 0 | No interruption
HVDC Bheramara | Bheramara HVDC-Bahrampur 400 kV Ckt-4 | 2021-08-21 11:43 | 2021-08-21 11:43 | 5:49 | S/O | Due to SAS work at India part | 0 | 0 | No interruption
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Bogura Grid Circle :
Rangpur Conf. P.P. | Rangpur Conf. P.P.-Rangpur S/S 132 kV Ckt-1 | 2021-08-02 10:50 | 2021-08-02 13:21 | 2:31 | S/O | Due to C/M work | 0 | 0 | No interruption
Polashbari | Polashbari-Mohasthangarh 132 kV Ckt-2 | 2021-08-07 11:21 | 2021-08-07 15:09 | 3:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-2 | 2021-08-08 07:03 | 2021-08-08 07:03 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sirajganj 230 kV Ckt-1 | 2021-08-08 14:20 | 2021-08-08 17:03 | 2:43 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur Confi. | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-08-09 10:15 | 2021-08-09 12:20 | 2:05 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur Confi | Rangpur Confidence-Mithapukur 132 kV Ckt-1 | 2021-08-09 12:32 | 2021-08-09 13:22 | 0:50 | S/O | Due to gas filing | 0 | 0 | No interruption
Rangpur | Rangpur-Rangpur Confidence 132 kV Ckt-2 | 2021-08-09 14:43 | 2021-08-09 15:32 | 0:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Amnura | Amnura-Chapainawabganj 132 kV Ckt | 2021-08-11 12:20 | 2021-08-11 13:15 | 0:55 | S/O | Due to C/M work | 0 | 0 | No interruption
Mohasthangarh | Mohasthangarh-Polashbari 132 kV Ckt-1 | 2021-08-11 12:31 | 2021-08-11 17:20 | 4:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Mithapukur | Mithapukur-Rangpur confidence P/S 132 kV Ckt-2 | 2021-08-13 09:38 | 2021-08-13 09:38 | 0:00 | S/O | Due to PT maintenance | 0 | 0 | No interruption
Sherpur | Sherpur-Bogura 132 kV Ckt-1 | 2021-08-13 09:14 | 2021-08-13 09:44 | 0:30 | S/O | Due to C/M work | 0 | 0 | No interruption
Sherpur | Sherpur-Bogura 132 kV Ckt-2 | 2021-08-13 09:45 | 2021-08-13 10:06 | 0:21 | S/O | Due to C/M work | 0 | 0 | No interruption
Sirajganj | Sirajganj-Sherpur 132 kV Ckt-1 | 2021-08-13 10:09 | 2021-08-13 10:33 | 0:24 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Naogaon 132 kV Ckt-1 | 2021-08-21 07:35 | 2021-08-21 07:35 | 0:00 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur Confidence | Rangpur Confidence-Mithapukur 132 kV Ckt-2 | 2021-08-20 12:05 | 2021-08-20 17:33 | 5:28 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Jaldhaka 132 kV Ckt-1 | 2021-08-21 09:50 | 2021-08-21 14:26 | 4:36 | S/O | Due to D/W work. | 0 | 0 | No interruption
Bogura(N) | Bogura(N)-Naogaon 132 kV Ckt-1 |  | 2021-08-21 15:26 |  | S/O | After mainteneance | 0 | 0 | No interruption
Bogura(N) | Bogura-Sirajganj 230 kV Ckt-1 | 2021-08-21 15:39 | 2021-08-21 18:27 | 2:48 | S/O | Due to C/M work | 0 | 0 | No interruption
Bogura | Bogura-Sherpur 132 kV Ckt-1 | 2021-08-22 08:31 | 2021-08-22 12:08 | 3:37 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Mithapukukur 132 kV Ckt-2 | 2021-08-22 11:35 | 2021-08-22 14:29 | 2:54 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur | Rangpur-Saidpur 132 kV Ckt-2 | 2021-08-22 09:55 | 2021-08-22 11:44 | 1:49 | S/O | Due to C/M work | 0 | 0 | No interruption
Saidpur | Saidpur-Purbasadipur 132 kV Ckt-2 | 2021-08-22 15:23 | 2021-08-22 16:15 | 0:52 | S/O | Due to replace meter | 0 | 0 | No interruption
Barapukuria | Barapukuria-Saidpur 132 kV Ckt-2 | 2021-08-29 06:10 | 2021-08-29 09:46 | 3:36 | S/O | Due to C/M work | 0 | 0 | No interruption
Rangpur confidence | Rangpur confidence-Mithapukur 132 kV Ckt-2 | 2021-08-30 02:39 | 2021-08-30 08:02 | 5:23 | S/O | Due to SF6 filling at P/S end | 0 | 0 | No interruption
|  |  | Total : | 50:48 |  | Unserved Energy: |  | 0
Others :
Nill
|  |  | Total : | 0:00 |  | Unserved Energy: |  | 0
Total outage period of Sub-Station equipment due to schedule maintenance: |  |  |  | 436:27 | Hours
S/O=Schedule Outage, D/W= Development Work, A/M=Annual Maintenance , C/M=Corrective Maintenance
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-27
Page: 1/1 | [8 empty] | QF-LDC-27
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF TRIPPING AND OUTAGE ( EMERGENCY & SCHEDULED )
Month:August 2021
| Area | Previous Month (July' 2021 |  |  |  | Current Month (August 2021)
SL No. |  | Total number of |  |  |  | Total number of
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 34 | 25 | 95 | 154 | 34 | 9 | 69 | 112
2 | Dhaka (South) Grid Circle. | 2 | 2 | 3 | 7 | 11 | 0 | 25 | 36
3 | Chattogram Grid Circle. | 15 | 7 | 24 | 46 | 25 | 7 | 32 | 64
4 | Cumilla Grid Circle. | 16 | 4 | 19 | 39 | 25 | 4 | 25 | 54
5 | Khulna Grid Circle. | 15 | 10 | 36 | 61 | 17 | 8 | 30 | 55
6 | HVDC Grid Circle | 0 | 0 | 1 | 1 | 0 | 0 | 7 | 7
7 | Bogura Grid Circle. | 16 | 6 | 22 | 44 | 27 | 13 | 48 | 88
8 | Others | Total number of Total: 0; Total number of T: 0; Total number of Total: 0
9 | Total | 98 | 54 | 200 | 352 | 139 | 41 | 236 | 416
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-28
Page: 1/1 | [8 empty] | QF-LDC-28
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
SUMMARY OF UNSERVED ENERGY
Month:August 2021
| Area | Previous Month (July' 2021) |  |  |  | Current Month (August 2021)
SL No. |  | Energy unserved ( MWH ) due to |  |  |  | Energy unserved ( MWH ) due to
|  | T | E/O | S/O | Total | T | E/O | S/O | Total
1 | Dhaka (North) Grid Circle. | 513.84 | 181.98 | 566.43 | 1262.25 | 785.56 | 468.2 | 289.17 | 1542.93
2 | Dhaka (South) Grid Circle. | 15.8333 | 0 | 0 | 15.8333 | 360.1 | 0 | 58 | 418.1
3 | Chattogram Grid Circle. | 82.58 | 70.76 | 139.7333 | 293.0733 | 96.97 | 139.43 | 2387.45 | 2623.85
4 | Cumilla Grid Circle. | 161.15 | 23 | 242.57 | 426.72 | 127.18 | 79 | 350.8 | 556.98
5 | Khulna Grid Circle. | 141.8 | 204.57 | 748.67 | 1095.04 | 416.94 | 122.67 | 107.98 | 647.59
6 | HVDC Grid Circle | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Bogura Grid Circle. | 46.53 | 113.07 | 788.07 | 947.67 | 84.67 | 733.97 | 1042.58 | 1861.22
8 | Others | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | Total | 961.7333 | 593.38 | 2485.4733 | 4040.5867 | 1871.42 | 1543.27 | 4235.98 | 7650.67
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-29
Page: 1/1 | [9 empty] | QF-LDC-29
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Sub-Station performance
Month:August 2021
A) Power Interruption
SL. | Name of | Total Capacity | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of the Sub-Station |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | MVA | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11
1 | Dhaka (North) | 8801.6 | 10 | 6 | 16 | 2 | 2 | 12 | 1121.89
2 | Dhaka (South) | 5031.6 | 2 | 1 | 3 | 1 | 1 | 1 | 381.77
3 | Chattogram | 2042 | 7 | 6 | 13 | 4 | 2 | 7 | 810.27
4 | Khulna | 2434 | 9 | 3 | 12 | 5 | 3 | 4 | 346.61
5 | HVDC | 5954.3 | - | - | - | - | - | - | 0
6 | Bogura | 3145.6 | 8 | 8 | 16 | 2 | 4 | 10 | 1815.05
7 | Cumilla | 2981 | 8 | 7 | 15 | 4 | 2 | 9 | 556.98
8 | Others | - | - | - | - | - | - | - | 0
| Total | 30390.1 | [6 empty] | 5032.57
B) Availability of the Sub-Station
SL. | Name of | Availability
No | the Circle | of the S/S
1 | 2 | 3
1 | Dhaka (North) | 99.95%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.94%
4 | Khulna | 99.96%
5 | HVDC | 100% | [6 empty] | Executive Engineer
6 | Bogura | 99.86% | [6 empty] | Information Management Division
7 | Cumilla | 99.94% | [6 empty] | LDC, PGCB, Dhaka.

## QF-LDC-30
Page: 1/1 | [10 empty] | QF-LDC-30
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Consolidated Statement of Transmission line's performance
Month:August 2021
A) Power Interruption
SL. | Name of | Total length | No. of Section in | No of Power Interruption |  |  | Power | Power | Power | Amount of | Remarks
No | the Circle | of Transmission line | the Transmission |  |  |  | Interruption | Interruption | Interruption | Interrupted
|  | (Ckt-KM) | Line | Forced | Scheduled | Total | Up to 30Mins | Up to 01Hrs | Above 01Hour | Energy MWH
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12
1 | Dhaka (North) | 2254.4715 | - | 3 | - | 3 | 2 | - | 1 | 421.05
2 | Dhaka (South) | 990.29 |  | 2 | - | 2 | 1 | 1 | - | 36.33
3 | Chattogram | 917 | - | 2 | 2 | 4 | 2 | - | 2 | 1813.58
4 | Khulna | 1238.4 | - | 2 | - | 2 | 2 | - | - | 300.97 | -
5 | HVDC | 1325 | 501 | - | - | - | - | - | - | - | -
6 | Bogura | 1803.3 | - | 2 | - | 2 | 2 | - | - | 46.17
7 | Cumilla | 1648.16 | - | - | - | - | - | - | - | -
8 | Others | - |  | - | - | - | - | - | - | -
| Total | 10176.6215 | 501 | [6 empty] | 2618.1
B) Availability of theTransmission Line
SL. | Name of | Availability of the
No | the Circle | Transmission Line
1 | 2 | 3
1 | Dhaka (North) | 99.88%
2 | Dhaka (South) | 99.99%
3 | Chattogram | 99.95%
4 | Khulna | 99.99%
5 | Bheramara (HVDC) | 100% | [7 empty] | Executive Engineer
6 | Bogura | 99.98% | [7 empty] | Information Management Division
7 | Cumilla | 99.97% | [7 empty] | LDC, PGCB, Dhaka.

## QF-LDC-31
Page: 1/1 | [12 empty] | QF-LDC-31
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
| Consolidated Statement of Transmission line's performance | Power Interruption due to trouble in Transmission/Generation System
Month:August 2021
Type of | Power failure due to | [7 empty] | Partial |  | Total Grid failure
fault | Trouble In |  | Trouble In Grid S/S |  | Trouble In |  | Lightning in |  | Grid failure |  |  |  | Remarks
| Generation |  | Equipment |  | Transmission Line |  | Transmission Line/Thunder Storm
Period | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration | Total | Duration
| No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min. | No | Hour / Min.
2021-08-18 | 21 | - | 18 | 29hr 1 min | 1 | 2hr28 min | - | - | - | - | - | - | -
* Tripping of a generator is accounted in the category "Trouble in Generation ". Not all tripping cause power interruption.
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-32
Page: 1/1 |  |  |  |  | QF-LDC-32
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Overall Power Interruption report of the Systems
Month: August 2021
| Total Nos.of | Total | Unserved | Total | Remarks
Sub-station | Interruption | Duration of | Load | Unserved
|  | Interruption | (MW) | Energy
|  | Hrs./Mins. |  | (MWH)
Mymensingh | 3 | 8:56 | 35 | 312.6667 | Due to Tripping of 132/33 kv transformers T-3
|  | 3:31 | 30 | 105.5 | Due to high temperature feeder DS
|  | 0:11 | 120 | 22 | Due to Tripping of 132/33 kV Transformers-T1 & T2
Mirpur | 1 | 0:48 | 24 | 19.2 | Due to red-hot maint
Tangail | 5 | 0:20 | 100 | 33.3333 | Due to Tripping of 132/33 kV Transformers-T1 & T2
|  | 1:47 | 35 | 62.4167 | Due to Tripping of 132/33 kV transformer T2 with 33 kV Bus section
|  | 0:47 | 68 | 53.2667 | Due to Tripping of 132/33 kV Transformers-T1 & T2
|  | 1:57 | 24 | 46.8 | Due to S/D of 132/33 kV transformer T3
|  | 1:07 | 50 | 55.8333 | Due to red-hot maint
Kishoreganj | 1 | 1:25 | 90 | 127.5 | Due to Tripping of 132/33 kV Transformers-T1 & T2
Nawabganj | 3 | 2:03 | 20 | 41 | Due to red-hot maint
|  | 1:30 | 10 | 15 | Due to S/D of 132/33 kV transformer T2
|  | 1:20 | 40 | 53.3333 | Due to S/D of 132/33 kV transformer T1
Kabirpur | 3 | 1:05 | 40 | 43.3333 | Due to S/D of 132/33 kV transformer T3
|  | 1:57 | 40 | 78 | Due to S/D of 132/33 kV transformer T2
|  | 0:25 | 275 | 114.5833 | Due to Tripping of Kabirpur-Kodda 132 kV Ckt-1
Shyampur old | 1 | 0:23 | 156 | 59.8 | Due to Tripping of Shyampur old-Shyampur new 132 kV both Ckts
Mymensing RPCL | 1 | 2:28 | 100 | 246.6667 | Due to red hot maint
Munshiganj | 1 | 1:33 | 34 | 52.7 | Due to S/D of 33 kV Bus-2
Haripur SBU | 1 | 1:27 | 40 | 58 | Due to S/D of 132/33 kV transformer T1
Hasnabad | 1 | 0:27 | 48 | 21.6 | Due to Tripping of 132/33 kV Transformers- T1 & T5
Siddhirganj | 1 | 0:12 | 40 | 8 | Due to Tripping of Siddhirganj-Matuail 132 kV Ckt
Haripur | 2 | 0:34 | 50 | 28.3333 | Due to Tripping of Haripur-Norsingdi 132 kV Ckt
|  | 0:49 | 370 | 302.1667 | Due to Tripping of 132 kV Bus-1&2
Halishahar | 3 | 0:16 | 74 | 19.7333 | Due to Tripping of Halishahar-Khulsi 132 kV Ckt-2
|  | 1:19 | 34 | 44.7667 | Due to red-hot maint
|  | 0:10 | 45 | 7.5 | Due to Tripping of 132/33 kv transformers T-1 & T-3
Chowmuhoni | 5 | 0:13 | 100 | 21.6667 | Due to Tripping of 132/33 kv transformers T-1 & T-2
|  | 0:17 | 58 | 16.4333 | Due to Tripping of 132/33 kv transformers T3
|  | 2:22 | 40 | 94.6667 | Due to red-hot maint
|  | 2:27 | 35 | 85.75 | Due to S/D of 132/33 kv transformers T-2
|  | 6:16 | 40 | 250.6667 | Due to S/D of 132/33 kv transformers T-2
Bakulia | 2 | 0:32 | 30 | 16 | Due to Tripping of 132/33 kv transformers T4
|  | 1:33 | 25 | 38.75 | Due to S/D of 132/33 kv transformers T-3
Sikalbaha | 1 | 0:10 | 28 | 4.6667 | Due to Tripping of 132/33 kv transformers T3
Dohazari | 4 | 18:31 | 13 | 240.7167 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-1
|  | 154:13 | 10 | 1542.1667 | Due to S/D of Dohazari-Cox'sbazar 132 kV Ckt-1
|  | 0:07 | 94 | 10.9667 | Due to Tripping of Dohazari-Cox'sbazar 132 kV Ckt
|  | 1:00 | 24 | 24 | Due to S/D of 132/33 kv transformers T-1
Madunaghat | 2 | 2:26 | 22 | 53.5333 | Due to S/D of 132/33 kv transformers T-1
|  | 4:28 | 34 | 151.8667 | Due to S/D of 132/33 kv transformers T-1 and 33 kV bus
Comilla(N) | 3 | 0:28 | 95 | 44.3333 | Due to Tripping of 132/33 kv transformers T4
|  | 0:21 | 73 | 25.55 | Due to Tripping of 132/33 kv transformers T3 and T4
|  | 0:16 | 72 | 19.2 | Due to Tripping of 132/33 kv transformers T3 & T-4
Ashuganj | 1 | 1:06 | 30 | 33 | Due to Tripping of 230/132 kV Transformer OAT-12
Shahjibazar | 4 | 0:51 | 30 | 25.5 | Due to red-hot maint
|  | 0:48 | 21 | 16.8 | Due to S/D of 132/33 kv transformers T2
|  | 1:26 | 35 | 50.1667 | Due to S/D of 132/33 kv transformers T-2
|  | 2:08 | 20 | 42.6667 | Due to S/D of 132/33 kv transformers T-2
Sreemangal | 1 | 0:18 | 17 | 5.1 | Due to Tripping of 132/33 kv transformers T2 and T3
Biyanibazar | 3 | 1:06 | 30 | 33 | Due to red-hot maint
|  | 1:22 | 15 | 20.5 | Due to red-hot maint
|  | 1:43 | 10 | 17.1667 | Due to S/D of 33 kV Bus section-1
Ramganj | 3 | 1:26 | 20 | 28.6667 | Due to S/D of 132/33 kv transformers T4
|  | 6:44 | 10 | 67.3333 | Due to S/D of 132/33 kv transformers T-1
|  | 6:24 | 20 | 128 | Due to S/D of 132/33 kv transformers T-1
Jhenaidah | 1 | 0:08 | 71 | 9.4667 | Due to Tripping of 132/33 kv transformers T1 and T2
Gopalganj(Old) | 2 | 2:46 | 20 | 55.3333 | Due to 33 kV Fokirhat PBS feeder fault
|  | 0:42 | 75 | 52.5 | Due to Tripping of 132/33 kv transformers T1 and T2
Gallamari | 3 | 1:00 | 10 | 10 | Due to red-hot maint
|  | 0:22 | 36 | 13.2 | Due to Tripping of 132/33 kv transformers T1 and T2
|  | 0:27 | 24 | 10.8 | Due to Tripping of 132/33 kv transformers T1
Madaripur | 1 | 1:20 | 30 | 40 | Due to red-hot maint
Patuakhali | 1 | 0:13 | 80 | 17.3333 | Due to severe flashing at 33 kV feeder
Faridpur | 2 | 1:07 | 21 | 23.45 | Due to S/D of 132/33 kv transformers T-1
|  | 0:20 | 90 | 30 | Due to Tripping of 132/33 kv transformers T1 and T2
Jashore | 1 | 0:30 | 391 | 195.5 | Due to Tripping of Jashore-Noapara 132 kV Ckt-1
Kustia | 1 | 0:14 | 452 | 105.4667 | Due to Tripping of Kustia-Bheramara 132 kV Ckt-1 & 2
Noapara | 1 | 0:59 | 8 | 7.8667 | Due to S/D of 132/33 kv transformers T-4
Satkhira | 1 | 1:55 | 40 | 76.6667 | Due to S/D of 132/33 kV transformer T1
Rangpur | 5 | 2:45 | 20 | 55 | Due to S/D of 132/33 kV Transformer-T1
|  | 0:46 | 60 | 46 | Due to S/D of 132/33 kV Transformer-T2 and 33 kV bus sec-2
|  | 2:38 | 70 | 184.3333 | Due to red-hot maint
|  | 1:27 | 42 | 60.9 | Due to red-hot maint
|  | 0:10 | 70 | 11.6667 | Due to Tripping of 132/33 kV Transformer-T1 and T2
Purbasadipur | 2 | 2:37 | 240 | 628 | Due to S/D of Purbasadipur 132 kV full Bus
|  | 2:06 | 200 | 420 | Due to red-hot maint
Bogura | 2 | 0:57 | 60 | 57 | Due to S/D of 132/33 kV Transformer-T1
|  | 1:01 | 20 | 20.3333 | Due to red-hot maint
Ishwardi | 1 | 0:20 | 14 | 4.6667 | Due to Tripping of 132/33 kv transformers T1
Sherpur(Bogura) | 1 | 0:38 | 35 | 22.1667 | Due to Tripping of 132/33 kv transformers T-2
Bogura(O) | 1 | 2:01 | 24 | 48.4 | Due to red-hot maint
Palashbari | 1 | 0:30 | 80 | 40 | Due to Tripping of Palashbari-Mithapukur 132 kV Ckt-1 | 34.8
Thakurgaon | 1 | 0:10 | 37 | 6.1667 | Due to Tripping of Thakurgaon-Panchagar 132 kV Ckt
Sirajganj | 1 | 0:40 | 15 | 10 | Due to S/D of 132/33 kV Transformer-T1
Natore | 1 | 3:21 | 35 | 117.25 | Due to S/D of 132/33 kV Transformer-T1
Jaldhaka | 1 | 2:50 | 36 | 102 | Due to S/D of 132/33 kV Transformer-T1
Rajshahi | 1 | 1:22 | 20 | 27.3333 | Due to S/D of 132/33 kV Transformer-T3
| Total Unserved energy : |  |  | 7650.6667 | MWH
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-33
Page: 1/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD. | [7 empty] | Reporting Month
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station | [6 empty] | 2021-08-01
Month: August '2021 | [7 empty] | Don't Change Here. Change from Voltage Sheet.
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
1 | Siddhirganj | 134 | 22 | 2021-08-01 | 16:00
2 | Munsiganj | 112 | 22 | 2021-08-01 | 21:00 |  |  |  | 309 | Kodda
3 | Sonargaon | 224 | 23 | 2021-08-01 | 11:00 |  |  |  | 4 | Ruppur Paromanobik
4 | Shyampur | 218 | 23 | 2021-08-01 | 11:00
5 | Bhulta | 222 | 22 | 2021-08-01 | 12:00
6 | Madanganj | 112 | 23 | 2021-08-01 | 15:00
7 | Shitalakhya | 128 | 22 | 2021-08-01 | 12:00
8 | Rahim steel | 66 | 23 | 2021-08-01 | 11:00
9 | Matuail | 80 | 23 | 2021-08-01 | 1:00
10 | Ghorasal | 175 | 23 | 2021-08-01 | 1:00
11 | Narsingdi | 186 | 31 | 2021-08-01 | 19:30
12 | Haripur (SBU) | 125 | 25 | 2021-08-01 | 9:00
13 | Sreenagar | 65 | 23 | 2021-08-01 | 19:00
14 | Ullon | 90 | 31 | 2021-08-01 | 0:00
15 | Hasnabad | 106 | 23 | 2021-08-01 | 15:00
16 | Magbazar | 107 | 29 | 2021-08-01 | 13:00
17 | Maniknagar | 82 | 31 | 2021-08-01 | 13:00
18 | Bangabhaban | 42 | 23 | 2021-08-01 | 8:00
19 | Narinda | 83 | 23 | 2021-08-01 | 12:00
20 | Dhanmondi | 194 | 29 | 2021-08-01 | 13:00
21 | Lalbag | 100 | 12 | 2021-08-01 | 13:00
22 | Madartek | 79 | 5 | 2021-08-01 | 19:00
23 | Dhaka University | 37 | 29 | 2021-08-01 | 13:00
24 | Aftabnagar | 61 | 23 | 2021-08-01 | 12:00
25 | Fatullah | 62 | 25 | 2021-08-01 | 10:00
26 | Nawabganj | 66 | 23 | 2021-08-01 | 18:30
27 | Mirpur | 122 | 25 | 2021-08-01 | 19:00
28 | Kalyanpur | 108 | 5 | 2021-08-01 | 11:00
29 | Gulshan | 106 | 16 | 2021-08-01 | 11:00
30 | Uttara | 107 | 11 | 2021-08-01 | 16:00
31 | Uttara(new) | 95 | 23 | 2021-08-01 | 17:00
32 | Kamrangirchar | 175 | 23 | 2021-08-01 | 16:00
33 | Savar | 187 | 22 | 2021-08-01 | 15:00
34 | Bhasantec | 142 | 24 | 2021-08-01 | 14:00
35 | Agargaon | 96 | 23 | 2021-08-01 | 14:00
36 | Satmosjid | 145 | 23 | 2021-08-01 | 12:00
37 | Tongi | 251 | 23 | 2021-08-01 | 15:00
38 | Kabirpur | 254 | 25 | 2021-08-01 | 19:00
39 | Basundhara | 249 | 22 | 2021-08-01 | 14:00
40 | Manikganj | 175 | 23 | 2021-08-01 | 15:00
41 | Joydevpur | 177 | 29 | 2021-08-01 | 18:30
42 | New Tongi | 286 | 23 | 2021-08-01 | 10:00
43 | Kodda | 309 | 31 | 2021-08-01 | 14:00
44 | Dhamrai | 124 | 22 | 2021-08-01 | 19:30
45 | Rajendrapur | 124 | 23 | 2021-08-01 | 20:00
46 | Valuka | 206 | 23 | 2021-08-01 | 1:00
47 | Tangail | 226 | 22 | 2021-08-01 | 21:00
48 | Mymensing | 228 | 5 | 2021-08-01 | 19:30
49 | Kishorganj | 152 | 8 | 2021-08-01 | 19:00
50 | Netrokona | 136 | 23 | 2021-08-01 | 5:00
51 | Jamalpur | 160 | 5 | 2021-08-01 | 22:00
52 | Sherpur | 146 | 5 | 2021-08-01 | 19:30
53 | Srimongal | 100 | 23 | 2021-08-01 | 20:00
Page: 2/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
54 | Shahjibazar | 134 | 29 | 2021-08-01 | 21:00
56 | Fenchuganj | 49 | 4 | 2021-08-01 | 21:00
57 | Kulawara | 129 | 23 | 2021-08-01 | 18:30
58 | Sylhet | 139 | 30 | 2021-08-01 | 19:30
59 | Chatak | 45 | 23 | 2021-08-01 | 1:00
60 | Sunamganj | 57 | 23 | 2021-08-01 | 19:00
61 | Bianibazar | 71 | 3 | 2021-08-01 | 22:00
62 | Cumilla (S) | 168 | 29 | 2021-08-01 | 18:30
63 | Cumilla(N) | 145 | 31 | 2021-08-01 | 24:00
64 | Chandpur | 86 | 4 | 2021-08-01 | 23:00
65 | Feni | 130 | 22 | 2021-08-01 | 20:00
66 | Chowmuhani | 220 | 5 | 2021-08-01 | 22:00
67 | Ashuganj | 49 | 29 | 2021-08-01 | 23:00
68 | Daudkandi | 165 | 16 | 2021-08-01 | 21:00
69 | B.Baria | 173 | 31 | 2021-08-01 | 23:00
70 | Ramganj | 100 | 5 | 2021-08-01 | 23:00
71 | Chaddagram | 64 | 12 | 2021-08-01 | 21:00
72 | PHP | 12 | 12 | 2021-08-01 | 19:00
73 | Kochua | 86 | 27 | 2021-08-01 | 22:00
74 | Madanhat | 94 | 23 | 2021-08-01 | 19:00
75 | Hathazari | 98 | 14 | 2021-08-01 | 21:00
76 | Khulshi | 203 | 11 | 2021-08-01 | 17:00
77 | Halishahar | 100 | 5 | 2021-08-01 | 13:00
78 | Baraulia | 163 | 26 | 2021-08-01 | 16:00
79 | Sikalbaha | 41 | 5 | 2021-08-01 | 15:00
80 | Dohazari | 112 | 10 | 2021-08-01 | 20:00
81 | Cox'sbazar | 111 | 15 | 2021-08-01 | 19:00
82 | Chandraghona | 30 | 24 | 2021-08-01 | 19:00
83 | Kaptai | 12 | 18 | 2021-08-01 | 16:00
84 | A. Khaer Stl. | 13 | 29 | 2021-08-01 | 18:00
85 | Bakulia | 113 | 11 | 2021-08-01 | 19:00
86 | Julda | 28.7 | 23 | 2021-08-01 | 21:00
87 | TK chemical | 47.2 | 12 | 2021-08-01 | 6:00
88 | Modern Steel | 33 | 23 | 2021-08-01 | 23:00
89 | Shahmirpur | 36 | 31 | 2021-08-01 | 18:30
90 | Khagrachhari | 30 | 3 | 2021-08-01 | 5:00
91 | Matarbari | 48 | 23 | 2021-08-01 | 19:00
92 | Baroiar Hat | 56 | 31 | 2021-08-01 | 15:00
93 | Rangamati | 14 | 12 | 2021-08-01 | 20:00
94 | Abul Khair 230 | 217 | 24 | 2021-08-01 | 6:00
95 | BSRM | 163 | 7 | 2021-08-01 | 15:00
96 | GPH Ispat | 97 | 31 | 2021-08-01 | 19:00
97 | Goalpara | 36 | 23 | 2021-08-01 | 19:00
98 | Central s/s | 114 | 31 | 2021-08-01 | 20:00
99 | Noapara | 113 | 15 | 2021-08-01 | 20:00
100 | Jashore | 128 | 22 | 2021-08-01 | 21:00
101 | Benapol | 126 | 23 | 2021-08-01 | 19:00
101 | Jhenidah | 136 | 23 | 2021-08-01 | 19:00
102 | Bottail | 142 | 8 | 2021-08-01 | 19:30
Page: 3/3 | [5 empty] | QF-LDC-33
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum Load recorded at different Sub-Station
Month: August '2021
Sl. No | Name of the Sub-station | MW | DATE |  | Time | Remarks
103 | G.K Project | 63 | 10 | 2021-08-01 | 19:00
104 | Faridpur | 158 | 25 | 2021-08-01 | 20:00
105 | Madaripur | 113 | 11 | 2021-08-01 | 22:00
106 | Sariatpur | 97 | 23 | 2021-08-01 | 19:30
107 | Gopalganj | 104 | 23 | 2021-08-01 | 22:00
108 | Bagerhat | 110 | 5 | 2021-08-01 | 19:30
109 | Mongla | 50 | 29 | 2021-08-01 | 12:00
110 | Satkhira | 118 | 25 | 2021-08-01 | 21:00
111 | Gallamari | 60 | 23 | 2021-08-01 | 22:00
112 | Magura | 64 | 15 | 2021-08-01 | 20:00
113 | Norail | 50 | 27 | 2021-08-01 | 19:00
114 | Chuadanga | 109 | 11 | 2021-08-01 | 21:00
115 | Borguna | 48 | 23 | 2021-08-01 | 21:00
116 | Barsal(N) | 52 | 5 | 2021-08-01 | 22:00
117 | Barsal(S) | 118 | 25 | 2021-08-01 | 22:00
118 | Patuakhali | 126 | 28 | 2021-08-01 | 23:00
119 | Bhandaria | 58 | 5 | 2021-08-01 | 22:00
120 | Borhan Uddin | 68 | 23 | 2021-08-01 | 21:00
121 | Ishurdi | 74 | 22 | 2021-08-01 | 19:30
122 | Ruppur Paromanobik | 4 | 4 | 2021-08-01 | 9:00
123 | Natore | 158 | 23 | 2021-08-01 | 1:00
124 | Bogura | 170 | 5 | 2021-08-01 | 23:00
125 | Naogaon | 150 | 23 | 2021-08-01 | 21:00
126 | Rajshahi | 160 | 9 | 2021-08-01 | 21:00
127 | Rajshahi New | 19 | 31 | 2021-08-01 | 19:30
128 | C.Nawabganj | 66 | 9 | 2021-08-01 | 22:00
129 | Amnura | 56 | 26 | 2021-08-01 | 21:0
130 | Pabna | 113 | 22 | 2021-08-01 | 21:00
131 | Shahjadpur | 104 | 30 | 2021-08-01 | 20:00
132 | Serajganj | 112 | 22 | 2021-08-01 | 20:00
133 | Niyamatpur | 79 | 5 | 2021-08-01 | 21:00
134 | Joypurhat | 65 | 13 | 2021-08-01 | 21:00
135 | Sherpur(Bogura) | 70 | 10 | 2021-08-01 | 21:00
136 | Mohastangar | 74 | 30 | 2021-08-01 | 1:00
137 | Bangura | 40 | 3 | 2021-08-01 | 19:30
138 | Rangpur | 149 | 6 | 2021-08-01 | 19:00
139 | Lalmonirhat | 50 | 8 | 2021-08-01 | 19:30
140 | Saidpur | 114 | 11 | 2021-08-01 | 20:00
141 | Purbasadipur | 118 | 4 | 2021-08-01 | 21:00
142 | Thakurgaon | 117 | 23 | 2021-08-01 | 1:00
143 | Palshbari | 130 | 9 | 2021-08-01 | 20:00
144 | Barapukuria | 57 | 3 | 2021-08-01 | 21:00
145 | Panchugar | 64 | 5 | 2021-08-01 | 19:30
146 | Joldhaka | 70 | 4 | 2021-08-01 | 22:00
147 | Kurigram | 66 | 6 | 2021-08-01 | 19:30
148 | Mitha Pukur | 50 | 30 | 2021-08-01 | 1:00
Executive Engineer
Information Management Division
LDC, PGCB, Dhaka.

## QF-LDC-34
Page: 1/1 |  |  |  |  | QF-LDC-34
POWER GRID COMPANY OF BANGLADESH LTD. Page 1 of 1
Information Management Division, LDC, Dhaka.
Area wise maximum load served
Month:August 2021
Area | MW | Date | Hour | Remarks
Dhaka | 5624 | 26.08.2021 | 10:00
Chattogram | 1513 | 26.08.2021 | 24:00'
Khulna | 1685 | 22.08.2021 | 20:00
Rajshahi | 1359 | 10.08.2021 | 21:00
Cumilla | 1269 | 31.08.2021 | 23:00
Mymensingh | 1065 | 05.08.2021 | 21:00
Sylhet | 562 | 28.08.2021 | 20:00
Barisal | 410 | 25.08.2021 | 22:00
Rangpur | 859 | 11.08.2021 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-35
| Page: 1/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
SL. | 400 KV Substation | Rated | Maxm | Date |  |  | Minm | Date
No. |  | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
|  | kV | kV |  |  |  | kV
1 | Bibiyana | 400 | 411 | 6 | 2021-08-01 | 18:30 | 399 | 1 | 2021-08-01 | 9:00
2 | Bheramara | 400 | 408 | 7 | 2021-08-01 | 20:00 | 391 | 27 | 2021-08-01 | 21:00
3 | Ashuganj(N) | 400 | 399 | 10 | 2021-08-01 | 1:00 | 325 | 30 | 2021-08-01 | 10:00
4 | Payra | 400 | 415 | 3 | 2021-08-01 | 20:00 | 388 | 13 | 2021-08-01 | 1:00
5 | Kaliakoir | 400 | 403 | 6 | 2021-08-01 | 4:00 | 380 | 29 | 2021-08-01 | 12:00
6 | Bhulta | 400 | 393 | 6 | 2021-08-01 | 18:00 | 363 | 29 | 2021-08-01 | 12:00
7 | Gopalganj | 400 | 413 | 13 | 2021-08-01 | 15:00 | 383 | 7 | 2021-08-01 | 21:00
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 230 KV Substation | kV | kV |  |  |  | kV
1 | Ghorasal | 230 | 244 | 25 | 2021-08-01 | 20:00 | 227 | 2 | 2021-08-01 | 10:00
2 | Ishurdi | 230 | 236 | 9 | 2021-08-01 | 10:00 | 222 | 10 | 2021-08-01 | 21:00
3 | Ashuganj | 230 | 256 | 31 | 2021-08-01 | 11:00 | 230 | 29 | 2021-08-01 | 12:00
4 | Serajganj | 230 | 235 | 28 | 2021-08-01 | 16:00 | 223 | 2 | 2021-08-01 | 21:00
5 | Baghabari | 230 | 237 | 31 | 2021-08-01 | 18:00 | 215 | 15 | 2021-08-01 | 21:00
6 | Barapukuria | 230 | 239 | 27 | 2021-08-01 | 15:00 | 222 | 9 | 2021-08-01 | 24:00
7 | Bogura | 230 | 229 | 28 | 2021-08-01 | 6:00 | 211 | 5 | 2021-08-01 | 21:00
8 | Rajshahi | 230 | 232 | 15 | 2021-08-01 | 18:00 | 218 | 14 | 2021-08-01 | 21:00
9 | Khulna South | 230 | 230 | 1 | 2021-08-01 | 17:00 | 0 | 20 | 2021-08-01 | 11:00
10 | Rampura | 230 | 232 | 6 | 2021-08-01 | 18:30 | 220 | 29 | 2021-08-01 | 12:00
11 | Haripur | 230 | 233 | 6 | 2021-08-01 | 19:30 | 217 | 29 | 2021-08-01 | 11:00
12 | Hasnabad | 230 | 234 | 3 | 2021-08-01 | 21:00 | 219 | 26 | 2021-08-01 | 7:00
13 | Shyampur | 230 | 229 | 4 | 2021-08-01 | 21:00 | 220 | 1 | 2021-08-01 | 12:00
14 | Aminbazar | 230 | 236 | 11 | 2021-08-01 | 1:00 | 221 | 17 | 2021-08-01 | 2:00
15 | Tongi | 230 | 235 | 5 | 2021-08-01 | 19:30 | 218 | 17 | 2021-08-01 | 9:00
16 | Comilla (N) | 230 | 235 | 9 | 2021-08-01 | 18:30 | 224 | 13 | 2021-08-01 | 5:00
17 | Hathazari | 230 | 232 | 12 | 2021-08-01 | 10:00 | 215 | 13 | 2021-08-01 | 7:00
18 | Megnaghat | 230 | 238 | 1 | 2021-08-01 | 4:00 | 223 | 16 | 2021-08-01 | 23:00
19 | Fenchuganj | 230 | 245 | 19 | 2021-08-01 | 2:00 | 234 | 2 | 2021-08-01 | 19:30
20 | Siddhirganj | 230 | 236 | 9 | 2021-08-01 | 1:00 | 221 | 29 | 2021-08-01 | 11:00
21 | Maniknagar | 230 | 234 | 10 | 2021-08-01 | 1:00 | 220 | 29 | 2021-08-01 | 12:00
22 | Old Airport | 230 | 233 | 8 | 2021-08-01 | 8:00 | 218 | 29 | 2021-08-01 | 12:00
23 | Barisal | 230 | 251 | 23 | 2021-08-01 | 2:00 | 229 | 11 | 2021-08-01 | 19:00
24 | Bhola 225 MW | 230 | 251 | 23 | 2021-08-01 | 3:00 | 232 | 17 | 2021-08-01 | 15:00
25 | AKSML | 230 | 232 | 18 | 2021-08-01 | 22:00 | 209 | 13 | 2021-08-01 | 7:00
26 | BSRM | 230 | 232 | 9 | 2021-08-01 | 20:00 | 213 | 6 | 2021-08-01 | 16:00
27 | Bibiyana | 230 | 244 | 6 | 2021-08-01 | 5:00 | 233 | 1 | 2021-08-01 | 16:00
28 | Bhulta | 230 | 266 | 17 | 2021-08-01 | 13:00 | 221 | 29 | 2021-08-01 | 11:00
29 | Ashuganj (S) | 230 | 232 | 0 | 2021-08-01 | 1:00 | 230 | 29 | 2021-08-01 | 11:00
30 | Kaliakoir | 230 | 235 | 11 | 2021-08-01 | 3:00 | 207 | 16 | 2021-08-01 | 11:00
31 | GPH | 230 | 230 | 5 | 2021-08-01 | 20:00 | 210 | 13 | 2021-08-01 | 7:00
132 kV Substation
1 | Siddhirganj | 132 | 136 | 3 | 2021-08-01 | 0.79167 | 126 | 29 | 2021-08-01 | 0.5
2 | Munsiganj | 132 | 141 | 11 | 2021-08-01 | 0.8125 | 126 | 29 | 2021-08-01 | 0.45833
3 | Sonargaon | 132 | 143 | 4 | 2021-08-01 | 0.875 | 127 | 17 | 2021-08-01 | 0.375
4 | Shyampur | 132 | 140 | 4 | 2021-08-01 | 0.83333 | 129 | 29 | 2021-08-01 | 0.5
5 | Bhulta | 132 | 133 | 6 | 2021-08-01 | 0.8125 | 118 | 30 | 2021-08-01 | 0.45833
6 | Madanganj | 132 | 138 | 8 | 2021-08-01 | 0.8125 | 126 | 30 | 2021-08-01 | 0.5
7 | Shitalakhya | 132 | 142 | 3 | 2021-08-01 | 0.8125 | 121 | 1 | 2021-08-01 | 0.375
8 | Rahim Steal | 132 | 137 | 11 | 2021-08-01 | 0.79167 | 0 | 5 | 2021-08-01 | 0.041667
9 | Matuail | 132 | 136 | 3 | 2021-08-01 | 0.79167 | 126 | 29 | 2021-08-01 | 0.5
10 | Ghorasal | 132 | 140 | 1 | 2021-08-01 | 0.041667 | 132 | 3 | 2021-08-01 | 0.041667
11 | Narsinghdi | 132 | 136 | 6 | 2021-08-01 | 0.25 | 118 | 22 | 2021-08-01 | 0.70833
12 | Haripur (SBU) | 132 | 137 | 6 | 2021-08-01 | 0.8125 | 127 | 29 | 2021-08-01 | 0.45833
13 | Sreenagar | 132 | - |  | - | - | - | - | - | -
14 | Ullon | 132 | 136 | 6 | 2021-08-01 | 0.16667 | 123 | 29 | 2021-08-01 | 0.5
15 | Hasnabad | 132 | 138 | 3 | 2021-08-01 | 0.8125 | 127 | 17 | 2021-08-01 | 0.375
16 | Magbazar | 132 | 135 | 1 | 2021-08-01 | 0.25 | 123 | 3 | 2021-08-01 | 0.33333
17 | Maniknagar | 132 | 136 | 3 | 2021-08-01 | 0.33333 | 126 | 29 | 2021-08-01 | 0.5
18 | Bangabhaban | 132 | 136 | 3 | 2021-08-01 | 0.33333 | 126 | 29 | 2021-08-01 | 0.5
| Page: 2/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
19 | Narinda | 132 | 136 | 3 | 2021-08-01 | 0.33333 | 126 | 29 | 2021-08-01 | 0.5
20 | Dhanmondi | 132 | 136 | 1 | 2021-08-01 | 0.8125 | 125 | 29 | 2021-08-01 | 0.5
21 | Lalbag | 132 | 139 | 3 | 2021-08-01 | 0.8125 | 122 | 30 | 2021-08-01 | 0.5
22 | Madartek | 132 | 136 | 5 | 2021-08-01 | 0.20833 | 123 | 29 | 2021-08-01 | 0.5
23 | Dhaka University | 132 | - | - | - | - | - | - | - | -
24 | Aftabnagar | 132 | 137 | 11 | 2021-08-01 | 0.16667 | 123 | 29 | 2021-08-01 | 0.45833
25 | Fatullah | 132 | 141 | 4 | 2021-08-01 | 0.95833 | 129 | 29 | 2021-08-01 | 0.45833
26 | Nawabganj | 133 | 134 | 3 | 2021-08-01 | 0.8125 | 122 | 30 | 2021-08-01 | 0.5
27 | Mirpur | 132 | 140 | 2 | 2021-08-01 | 03;00 | 123 | 10 | 2021-08-01 | 0.70833
28 | Kalyanpur | 132 | 141 | 2 | 2021-08-01 | 20;00 | 126 | 20 | 2021-08-01 | 0.5
29 | Gulshan | 132 | 136 | 11 | 2021-08-01 | 0.25 | 123 | 29 | 2021-08-01 | 0.45833
30 | Uttara | 132 | 140 | 2 | 2021-08-01 | 0.20833 | 123 | 29 | 2021-08-01 | 0.5
31 | Uttara(New) | 132 | 140 | 1 | 2021-08-01 | 0.45833 | 125 | 17 | 2021-08-01 | 0.45833
32 | Kamrangirchar | 132 | 139 | 3 | 2021-08-01 | 0.83333 | 123 | 29 | 2021-08-01 | 0.5
33 | Savar | 132 | 141 | 3 | 2021-08-01 | 0.83333 | 125 | 20 | 2021-08-01 | 0.45833
34 | Bhasantec | 132 | 139 | 9 | 2021-08-01 | 0.041667 | 128 | 29 | 2021-08-01 | 0.5
35 | Agargaon | 132 | 142 | 2 | 2021-08-01 | 01;00 | 130 | 17 | 2021-08-01 | 0.41667
36 | Satmosjid | 132 | 139 | 9 | 2021-08-01 | 0.041667 | 129 | 29 | 2021-08-01 | 0.45833
37 | Tongi | 132 | 141 | 1 | 2021-08-01 | 23:00 | 127 | 17 | 2021-08-01 | 0.45833
38 | Kabirpur | 132 | 139 | 25 | 2021-08-01 | 23:00 | 126 | 8 | 2021-08-01 | 0.375
39 | Basundhara | 132 | 140 | 5 | 2021-08-01 | 0.77083 | 124 | 17 | 2021-08-01 | 10:00
40 | Manikganj | 132 | 144 | 2 | 2021-08-01 | 17:00 | 129 | 7 | 2021-08-01 | 0.41667
41 | Joydevpur | 132 | 141 | 6 | 2021-08-01 | 0.75 | 128 | 17 | 2021-08-01 | 10:00
42 | New Tongi | 132 | 141 | 4 | 2021-08-01 | 18:00 | 126 | 14 | 2021-08-01 | 0.33333
43 | Kodda | 132 | 140 | 11 | 2021-08-01 | 1:00 | 120 | 14 | 2021-08-01 | 0.33333
44 | Dhamrai | 132 | 137 | 5 | 2021-08-01 | 0.91667 | 125 | 31 | 2021-08-01 | 16:00
45 | Rajendrapur | 132 | 141 | 11 | 2021-08-01 | 18:00 | 118 | 29 | 2021-08-01 | 12:00
46 | Valuka | 132 | 130 | 7 | 2021-08-01 | 0.375 | 107 | 1 | 2021-08-01 | 0.875
47 | Tangail | 132 | 141 | 23 | 2021-08-01 | 0.45833 | 121 | 22 | 2021-08-01 | 0.83333
48 | Mymensing | 132 | 133 | 8 | 2021-08-01 | 0.54167 | 112 | 27 | 2021-08-01 | 0.041667
49 | Kishorganj | 132 | 133 | 7 | 2021-08-01 | 0.375 | 110 | 25 | 2021-08-01 | 0.79167
50 | Netrokona | 132 | 132 | 9 | 2021-08-01 | 0.75 | 108 | 3 | 2021-08-01 | 1899-12-31
51 | Jamalpur | 132 | 139 | 9 | 2021-08-01 | 0.75 | 108 | 30 | 2021-08-01 | 0
52 | Sherpur | 132 | 139 | 25 | 2021-08-01 | 0.95833 | 104 | 30 | 2021-08-01 | 0
53 | Srimongal | 132 | 141 | 6 | 2021-08-01 | 0.33333 | 128 | 24 | 2021-08-01 | 0.91667
54 | Shahjibazar | 132 | 139 | 6 | 2021-08-01 | 0.29167 | 127 | 23 | 2021-08-01 | 0.625
55 | Fenchuganj | 132 | 139 | 3 | 2021-08-01 | 0.33333 | 129 | 23 | 2021-08-01 | 0.77083
56 | Khulawara | 132 | 138 | 7 | 2021-08-01 | 0.375 | 128 | 25 | 2021-08-01 | 0.77083
57 | Sylhet | 132 | 135 | 7 | 2021-08-01 | 0.33333 | 124 | 24 | 2021-08-01 | 0.79167
58 | Chattak | 132 | 135 | 7 | 2021-08-01 | 0.375 | 122 | 24 | 2021-08-01 | 0.77083
59 | Sunamganj | 132 | 135 | 11 | 2021-08-01 | 0.20833 | 118 | 24 | 2021-08-01 | 0.91667
60 | Biani Bazar | 132 | 137 | 9 | 2021-08-01 | 0.625 | 121 | 25 | 2021-08-01 | 0.77083
61 | Comilla(South) | 132 | 130 | 25 | 2021-08-01 | 0.25 | 120 | 10 | 2021-08-01 | 0.79167
62 | Comilla (North) | 132 | 141 | 3 | 2021-08-01 | 0.375 | 133 | 13 | 2021-08-01 | 0.20833
63 | Chandpur | 132 | 143 | 12 | 2021-08-01 | 0.77083 | 130 | 1 | 2021-08-01 | 0.041667
64 | Feni | 132 | 139 | 3 | 2021-08-01 | 0.375 | 123 | 4 | 2021-08-01 | 0.25
65 | Chowmuhani | 132 | 137 | 14 | 2021-08-01 | 0.91667 | 126 | 20 | 2021-08-01 | 0.5
66 | Ashuganj | 132 | 141 | 6 | 2021-08-01 | 0.75 | 131 | 18 | 2021-08-01 | 0.20833
67 | Daudkandi | 132 | 143 | 4 | 2021-08-01 | 0.875 | 128 | 15 | 2021-08-01 | 0.45833
68 | Brahminbaria | 132 | 137 | 6 | 2021-08-01 | 0.75 | 125 | 1 | 2021-08-01 | 0.79167
69 | Ramganj | 132 | 139 | 19 | 2021-08-01 | 0.54167 | 125 | 13 | 2021-08-01 | 0.25
70 | Chaddagram | 132 | 140 | 28 | 2021-08-01 | 0.75 | 126 | 13 | 2021-08-01 | 0.29167
71 | PHP | 132 | 137 | 3 | 2021-08-01 | 0.375 | 122 | 13 | 2021-08-01 | 0.29167
72 | Kochua | 132 | 140 | 12 | 2021-08-01 | 0.79167 | 130 | 1 | 2021-08-01 | 0.041667
73 | Madanhat | 132 | 138 | 5 | 2021-08-01 | 0.8125 | 127 | 13 | 2021-08-01 | 0.25
74 | Hathazari | 132 | 137 | 7 | 2021-08-01 | 0.8125 | 126 | 13 | 2021-08-01 | 0.29167
75 | Khulshi | 132 | 148 | 27 | 2021-08-01 | 0 | 122 | 13 | 2021-08-01 | 0.29167
76 | Halishahar | 132 | 138 | 11 | 2021-08-01 | 0.875 | 122 | 13 | 2021-08-01 | 0.29167
77 | Baraulia | 132 | 136 | 5 | 2021-08-01 | 0.75 | 125 | 13 | 2021-08-01 | 0.25
78 | Sikalbaha | 132 | 139 | 5 | 2021-08-01 | 0.83333 | 113 | 13 | 2021-08-01 | 0.33333
79 | Dohazari | 132 | 134 | 9 | 2021-08-01 | 0.54167 | 120 | 25 | 2021-08-01 | 0.041667
| Page: 3/3 | [9 empty] | QF-LDC-35
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Maximum & Minimum Voltages of Grid Sub-Stations.
Month: July'2021
|  | Rated | Maxm | Date |  |  | Minm | Date
SL. | Substation | Voltage | Voltage |  |  | Hour | Voltage |  |  | Hour | Remarks
No. | 132 KV Substation | kV | kV |  |  |  | kV
80 | Cox'sbazar | 132 | 127 | 2 | 2021-08-01 | 0.70833 | 100 | 21 | 2021-08-01 | 0.77083
81 | Chandraghona | 132 | 137 | 7 | 2021-08-01 | 0.83333 | 126 | 13 | 2021-08-01 | 0.29167
82 | Kaptai | 132 | 143 | 15 | 2021-08-01 | 0.75 | 132 | 5 | 2021-08-01 | 0.54167
83 | A. Khaer Stl. | 132 | 138 | 24 | 2021-08-01 | 0 | 125 | 20 | 2021-08-01 | 0.41667
84 | Bakulia | 132 | 138 | 5 | 2021-08-01 | 0.83333 | 124 | 13 | 2021-08-01 | 0.375
85 | Julda | 132 | 138 | 5 | 2021-08-01 | 0.54167 | 124 | 13 | 2021-08-01 | 0.33333
86 | TK Chemical | 132 | 138 | 9 | 2021-08-01 | 0.83333 | 127 | 13 | 2021-08-01 | 0.70833
87 | Modern Steel | 132 | #N/A | #N/A | 2021-08-01 | #N/A | 0 | #VALUE! | 2021-08-01 | #N/A
88 | Shahmirpur | 132 | 139 | 7 | 2021-08-01 | 0.83333 | 124 | 13 | 2021-08-01 | 0.33333
89 | Khagrachhari | 132 | 136 | 9 | 2021-08-01 | 0.041667 | 125 | 13 | 2021-08-01 | 0.29167
90 | Matarbari | 132 | 130 | 2 | 2021-08-01 | 0.70833 | 100 | 21 | 2021-08-01 | 0.8125
91 | Baroiar Hat | 132 | 137 | 18 | 2021-08-01 | 0.77083 | 123 | 13 | 2021-08-01 | 0.29167
92 | Rangamati | 132 | 136 | 7 | 2021-08-01 | 0.83333 | 127 | 13 | 2021-08-01 | 0.33333
93 | Goalpara | 132 | 140 | 2 | 2021-08-01 | 0.77083 | 120 | 13 | 2021-08-01 | 0.95833
94 | Khulna Central | 132 | 140 | 3 | 2021-08-01 | 0.77083 | 122 | 12 | 2021-08-01 | 0.45833
95 | Noapara | 132 | 139 | 3 | 2021-08-01 | 0.77083 | 116 | 14 | 2021-08-01 | 0.33333
96 | Jessore | 132 | 135 | 20 | 2021-08-01 | 0.33333 | 113 | 13 | 2021-08-01 | 0.95833
97 | Benapol | 132 | 135 | 4 | 2021-08-01 | 0.70833 | 113 | 13 | 2021-08-01 | 0.95833
98 | Jhenida | 132 | 134 | 22 | 2021-08-01 | 0.41667 | 111 | 13 | 2021-08-01 | 0.95833
99 | Bottail | 132 | 135 | 13 | 2021-08-01 | 0.29167 | 121 | 1 | 2021-08-01 | 0.041667
100 | G.K Project | 132 | 140 | 2 | 2021-08-01 | 0.77083 | 129 | 1 | 2021-08-01 | 0.041667
101 | Faridpur | 132 | 140 | 13 | 2021-08-01 | 0.33333 | 127 | 1 | 2021-08-01 | 0.875
102 | Madaripur | 132 | 142 | 1 | 2021-08-01 | 0.54167 | 130 | 5 | 2021-08-01 | 0.91667
103 | Sariatpur | 132 | 142 | 13 | 2021-08-01 | 0.33333 | 128 | 1 | 2021-08-01 | 0.91667
104 | Gopalganj | 132 | 145 | 10 | 2021-08-01 | 0.33333 | 130 | 1 | 2021-08-01 | 0.91667
105 | Bagerhat | 132 | 140 | 18 | 2021-08-01 | 0.77083 | 112 | 13 | 2021-08-01 | 0.95833
106 | Mongla | 132 | 138 | 12 | 2021-08-01 | 0.75 | 113 | 13 | 2021-08-01 | 0.95833
107 | Satkhira | 132 | 138 | 12 | 2021-08-01 | 0.75 | 114 | 13 | 2021-08-01 | 0.95833
108 | Gallamari | 132 | 142 | 18 | 2021-08-01 | 0.77083 | 120 | 13 | 2021-08-01 | 0.95833
109 | Magura | 132 | 134 | 13 | 2021-08-01 | 0.41667 | 109 | 5 | 2021-08-01 | 0.95833
110 | Norail | 132 | 131 | 2 | 2021-08-01 | 0.77083 | 109 | 5 | 2021-08-01 | 0.875
111 | Chuadanga | 132 | 137 | 4 | 2021-08-01 | 0.75 | 107 | 12 | 2021-08-01 | 0.45833
112 | Borguna | 132 | 141 | 18 | 2021-08-01 | 0.33333 | 125 | 23 | 2021-08-01 | 0.83333
113 | Barisal(N) | 132 | 143 | 20 | 2021-08-01 | 0.33333 | 128 | 22 | 2021-08-01 | 0.91667
114 | Barisal(S) | 132 | 140 | 13 | 2021-08-01 | 0.375 | 127 | 14 | 2021-08-01 | 0.91667
115 | Patuakhali | 132 | 139 | 13 | 2021-08-01 | 0.33333 | 122 | 22 | 2021-08-01 | 0.95833
116 | Bhandaria | 132 | 140 | 18 | 2021-08-01 | 0.29167 | 120 | 12 | 2021-08-01 | 0.83333
117 | Ishurdi | 132 | 137 | 2 | 2021-08-01 | 0.66667 | 129 | 3 | 2021-08-01 | 0.875
118 | Ruppur paromanobik | 132 | 137 | 11 | 2021-08-01 | 0.70833 | 128 | 9 | 2021-08-01 | 0.875
118 | Natore | 132 | 138 | 24 | 2021-08-01 | 0.77083 | 125 | 9 | 2021-08-01 | 0.875
119 | Bogra | 132 | 140 | 12 | 2021-08-01 | 0.75 | 124 | 3 | 2021-08-01 | 0.875
120 | Noagaon | 132 | 134 | 23 | 2021-08-01 | 0.70833 | 117 | 5 | 2021-08-01 | 0.91667
121 | Rajshahi | 132 | 136 | 5 | 2021-08-01 | 0.77083 | 120 | 5 | 2021-08-01 | 0.58333
122 | Rajshahi New | 132 | 138 | 23 | 2021-08-01 | 0.70833 | 127 | 7 | 2021-08-01 | 0.875
123 | C.Nawabganj | 132 | 137 | 4 | 2021-08-01 | 0.75 | 125 | 15 | 2021-08-01 | 0.54167
124 | Amnura | 132 | 138 | 22 | 2021-08-01 | 0.75 | 123 | 8 | 2021-08-01 | 0.083333
125 | Pabna | 132 | 137 | 25 | 2021-08-01 | 0.875 | 127 | 5 | 2021-08-01 | 0.91667
126 | Shahjadpur | 132 | 140 | 3 | 2021-08-01 | 0.20833 | 132 | 9 | 2021-08-01 | 0.875
127 | Serajganj | 132 | 135 | 2 | 2021-08-01 | 0.29167 | 125 | 5 | 2021-08-01 | 0.91667
128 | Niyamatpur | 132 | 133 | 23 | 2021-08-01 | 0.70833 | 113 | 10 | 2021-08-01 | 0.875
129 | Joypurhat | 132 | 135 | 23 | 2021-08-01 | 0.70833 | 115 | 5 | 2021-08-01 | 0.91667
130 | Sherpur(Bogura) | 132 | 138 | 28 | 2021-08-01 | 0.70833 | 124 | 5 | 2021-08-01 | 0.875
132 | Mohastangor | 132 | 139 | 23 | 2021-08-01 | 0.70833 | 121 | 5 | 2021-08-01 | 0.91667
133 | Bangura | 132 | 138 | 26 | 2021-08-01 | 0.041667 | 130 | 1 | 2021-08-01 | 0.8125
134 | Rangpur | 132 | 136 | 1 | 2021-08-01 | 0.8125 | 109 | 6 | 2021-08-01 | 0.083333
135 | Lalmonirhat | 132 | 135 | 12 | 2021-08-01 | 0.58333 | 112 | 6 | 2021-08-01 | 0.41667
136 | Saidpur | 132 | 134 | 26 | 2021-08-01 | 0.58333 | 110 | 10 | 2021-08-01 | 0.875
137 | Purbasadipur | 132 | 133 | 2 | 2021-08-01 | 0.041667 | 104 | 9 | 2021-08-01 | 1899-12-31
138 | Thakurgaon | 132 | 133 | 19 | 2021-08-01 | 0.33333 | 102 | 9 | 2021-08-01 | 1899-12-31
139 | Palashbari | 132 | 136 | 23 | 2021-08-01 | 0.70833 | 112 | 7 | 2021-08-01 | 0.5
140 | Barapukuria | 132 | 139 | 27 | 2021-08-01 | 0.625 | 122 | 9 | 2021-08-01 | 1899-12-31
141 | Panchagar | 132 | 133 | 12 | 2021-08-01 | 0.54167 | 101 | 9 | 2021-08-01 | 1899-12-31
142 | Joldhaka | 132 | 133 | 23 | 2021-08-01 | 0.70833 | 105 | 9 | 2021-08-01 | 1899-12-31
143 | Kurigram | 132 | 137 | 26 | 2021-08-01 | 0.58333 | 110 | 6 | 2021-08-01 | 0.041667
144 | Mithapukur | 132 | 137 | 23 | 2021-08-01 | 0.70833 | 112 | 9 | 2021-08-01 | 1899-12-31
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-36
Page: 1/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 230/132 kV Auto Transformer
Month:August 2021
Name of the | Auto transformer |  | Recorded maximum load
sub-station | Name | Capacity ( MVA ) | MW | Amps ( 230kV side ) | Date | Time | Remarks
| TR1 | 225 | 0 | 0 | S/D
Hasnabad | TR2 | 225 | 142 | 420 | 16/07/21 | 9:00
| TR3 | 225 | 140 | 420
| TR1 | 225 | 150 | 460
Tongi | TR2 | 225 | 150 | 460 | 13/07/21 | 11:00
| TR3 | 225 | 150 | 460
Haripur | TR1 | 225 | 82 | 220
| TR2 | 225 | 82 | 220 | 13/07/21 | 4:00
| TR3 | 225 | 82 | 220
| TR1 | 225 | 179 | 480
Rampura | TR2 | 225 | 179 | 480 | 15/07/2021 | 15:00
| TR3 | 225 | 179 | 480
Keraniganj | ATR1 | 300 | 51 | 144 |  | 23:00
| ATR2 | 300 | 51 | 144 | 21/07/2021
| ATR3 | 300 | 51 | 144
| TR1 | 225 | 134 | 390
Aminbazar | TR2 | 225 | 134 | 390 | 2021-03-07 | 15:00
| TR3 | 225 | 142 | 406
Agargaon | TR1 | 300 | 155 | 438 | 18/07/21 | 13:00
| TR2 | 300 | 155 | 438
Maniknagar | TR1 | 300 | 123 | 350 | 15/07/21 | 16:00
| TR2 | 300 | 123 | 350
Cumilla (N) | TR1 | 225 | 178 | 507 | 2021-01-07 | 11:00
| TR2 | 225 | 174 | 493
Fenchuganj | AT2 | 300 | 233 | 615 | 2021-09-06 | 21:00
| MT1 | 150 | 92 | 250 | 25/07/21
Hathazari | MT2 | 150 | 92 | 250 |  | 18:00
| MT3 | 150 | 92 | 250
| MT4 | 150 | 92 | 250
| TR1 | 225 | 118 | 310
Ishurdi | TR2 | 225 | 118 | 310 | 29/07/21 | 23:00
| TR3 | 225 | 118 | 310
Khulna(S) | TR1 | 225 | 124 | 340
| TR2 | 225 | 124 | 340 | 18/07/21 | 19:30
| TR3 | 300 | 158 | 440
Bogura | TR1 | 225 | 121 | 366
| TR2 | 225 | 121 | 366 | 17/07/21 | 7:00
| TR3 | 225 | 166 | 482
Baghabari | TR1 | 300 | 170 | 460 | 14/07/21 | 21:00
| TR2 | 225 | 128 | 350
Rajshahi | ATR-01 | 300 | 114 | 306 | 27/07/21 | 14:00
| ATR-02 | 300 | 114 | 306
Barapukuria | TR1 | 225 | 162 | 800 |  |  | Due to unavailability of 230 kV side meters
| TR2 | 225 | 171 | 850 | 25/07/21 | 21:00 | 132 kV current is being provided
| TR6 | 300 | 222 | 1115
Bheramara | Transformer-1 | 225 | 132 | 346 | 29/07/21 | 23:00
| Transformer-2 | 225 | 132 | 346
Shyampur | ATR-01 | 300 | 103 | 338 | 17/07/21 | 10:00
| ATR-02 | 300 | 103 | 338
Kaliakoir | TR1 | 300 | 120 | 340 | 2021-07-15 | 21:00
Jhenaidah | TR1 | 300 | 110 | 300 | 2021-08-11 | 21:00 | T-2 not comissioned yet
Page: 2/2 | [6 empty] | QF-LDC-36
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka
Maximum load of 400/230 & 400/132 kV Transformer
Month:July 2021
Name of the | Transformer |  | Recorded maximum load |  |  |  | Remarks
sub-station | Name | Capacity ( MVA ) | MW | Amps (400 kV side) | Date | Time
Kaliakoir | TR1(400/230 kV) | 520 | 276 | 420 | 19/07/21 | 9:15
| TR2(400/230 kV) | 520 | 279.5 | 424
| TR1(400/132 kV) | 325 | 278.3 | 469 | 2021-08-07 | 19:30
| TR2(400/132 kV) | 325 | 277.3 | 466
Bibiyana | ICT1(400/230 kV) | 520 | 190 | 275 | 24/07/21 | 21:13
| ICT2(400/230kV) | 520 | 185 | 277
Bhulta | ATR1(400/230 kV) | 520 | 184 | 346 | 13/07/21 | 17:23
| ATR2(400/230kV) | 520 | 184 | 346
Ashuganj(N) | GSUT1 | 567 | 371 | 609 | 17/07/21 | 7:59
Gopalganj | ATR1(400/138 kV) | 325 | 299 | 458 | 2021-09-07 | 22:00
| ATR2(400/138kV) | 325 | 299 | 458
Payra | GSUT1 | 270 | 202 | 906 | 2021-09-07 | 22:27
| GSUT2 | 270 | 201 | 887
| GSUT3 | 270 | 202 | 889
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.

## QF-LDC-37
Page: 1/2 |  |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [9 empty] | QF-LDC-37 | Page: 2/2 |  |  | POWER GRID COMPANY OF BANGLADESH LTD. | [10 empty] | QF-LDC-37
|  |  |  | Information Management Division, LDC, Dhaka. | [13 empty] | Information Management Division, LDC, Dhaka.
[6 empty] | Report on load shedding | [13 empty] | Report on load shedding
Month:August 2021 | [6 empty] | (For Evening Peak) | [7 empty] | Month:August 2021 | [6 empty] | (For Day Peak)
| Peak Hour |  | Total load shed | [12 empty] | Peak Hour |  | Total load shed
Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks | Date | Generation | Demand |  |  |  |  | Areawise load shed (MW) | [6 empty] | Remarks
| (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur |  |  | (MW) | (MW) | MW | Time | Dhaka | Chitta-gong | Khulna | Rajshahi | Comilla | Mymen-singh | Sylhet | Barisal | Rangpur
2021-08-01 | 11508 | 11508 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-01 | 9171 | 9171 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-02 | 11788 | 11788 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-02 | 9739 | 9739 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-03 | 12060 | 12060 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-03 | 10153 | 10153 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-04 | 11997 | 11997 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-04 | 10077 | 10077 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-05 | 12438 | 12438 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-05 | 10725 | 10725 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-06 | 12179 | 12179 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-06 | 9711 | 9711 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-07 | 12159 | 12159 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-07 | 10128 | 10128 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-08 | 12290 | 12290 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-08 | 10130 | 10130 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-09 | 12524 | 12524 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-09 | 10702 | 10702 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-10 | 12673 | 12673 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-10 | 10905 | 10905 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-11 | 12768 | 12768 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-11 | 11012 | 11012 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-12 | 12748 | 12748 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-12 | 11313 | 11313 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-13 | 11840 | 11840 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-13 | 9304 | 9304 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-14 | 12706 | 12706 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-14 | 10835 | 10835 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-15 | 12487 | 12487 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-15 | 261.7463 | 261.7463 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-16 | 12987 | 12987 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-16 | 10707 | 10707 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-17 | 12675 | 12675 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-17 | 10648 | 10648 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-18 | 12526 | 12526 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-18 | 10515 | 10515 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-19 | 12531 | 12531 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-19 | 10634 | 10634 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-20 | 11651 | 11651 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-20 | 8811 | 8811 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-21 | 12686 | 12686 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-21 | 10166 | 10166 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-22 | 13271 | 13271 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-22 | 11340 | 11340 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-23 | 12491 | 12491 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-23 | 11327 | 11327 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-24 | 12864 | 12864 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-24 | 11120 | 11120 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-25 | 12919 | 12919 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-25 | 11048 | 11048 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-26 | 12416 | 12416 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-26 | 11031 | 11031 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-27 | 12120 | 12120 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-27 | 9423 | 9423 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-28 | 12743 | 12743 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-28 | 10251 | 10251 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-29 | 12893 | 12893 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-29 | 10869 | 10869 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-30 | 12868 | 12868 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-30 | 10470 | 10470 | - | - | - | - | - | - | - | - | - | - | - | -
2021-08-31 | 13185 | 13185 | - | - | - | - | - | - | - | - | - | - | - | - | 2021-08-31 | 11410 | 11410 | - | - | - | - | - | - | - | - | - | - | - | -

## QF-LDC-38
Page: 1/1 |  |  |  |  | QF-LDC-38
POWER GRID COMPANY OF BANGLADESH LTD.
Information Management Division, LDC, Dhaka.
Report on Generation System
Month:August 2021
Sl.No | Description of Item | Unit | Quantity | Date | Time
1 | Peak Genaration | MW | 13271 | 2021-08-22 | 21:00
2 | Maximum Day Peak Genaration | MW | 11410 | 2021-08-31 | 12:00
3 | Maximum Evening Peak Demand | MW | 13271 | 2021-08-22 | 21:00
4 | Minimum Generation | MW | 8249 | 2021-08-01 | 22:00
5 | Average of the daily evening peak Genaration | MW | 12483.5806
6 | Average of the daily day peak Genaration | MW | 10126.9918
7 | Maximum load shed | MW | 0 | - | -
8 | Minimum load shed | MW | 0 | - | -
9 | Total nos. of load shed days | Day | 0
10 | Average load shed ( Avg. of the 31 days in the month) | MW/Day | 0
11 | Total Generation | MkWh | 8168.2362
12 | Total Generation by BPDB | MkWh | 1762.3785 | % of total Gen. | 21.58%
13 | Total Generation by IPP | MkWh | 2800.7553 | '' | 34.29%
14 | A) Total Generation by Generation Companies | MkWh | 2356.5329 | '' | 28.85%
| B) Total Generation by REB | MkWh | 144.3267 | " | 1.767%
| C) Total Generation by RENTAL | MkWh | 511.1298 | " | 6.258%
| D) Total Imported from India (BIPTC) | MkWh | 502.0349 | " | 6.146%
| E) Total Imported from Tripura, India (A.C) | MkWh | 91.0781 | " | 1.115%
15 | Fuel wise Generation.
| A) Gas | MkWh | 4736.6321 | % of total Gen. | 57.99%
| B) Oil | MkWh | 2245.4531 | '' | 27.49%
| C) Hydro | MkWh | 86.881 | '' | 1.064%
| D) Solar | MkWh | 30.5606 | '' | 0.3741%
| E) Coal | MkWh | 475.5964 | '' | 5.823%
| F) BIPTC (Import from India) | MkWh | 502.0349 | '' | 6.146%
| G) A.C (Import from Tripura, India) | MkWh | 91.0781 | '' | 1.115%
16 | Maximun of the daily total Generation . | MkWh | 281.7136 | 2021-08-10
17 | Monthly Load factor | % | 82.7278
18 | Total fuel cost ( BPDB + PVT. ) ( Calculated) | M.Taka | 27858.7295
| A) Gas | M.Taka | 4786.7389
| B) Liquid fuel | M.Taka | 17731.1657
| C) Coal | M.Taka | 2208.5145
| D) BIPTC (Import from India) | M.Taka | 2472.5096
| E) Tripura(Import from India) | M.Taka | 659.8008
19 | Maximum of the daily fuel cost (PDB+PVT.)( Calculated) | M.Taka | 1031.5495 | 2021-08-24
| A) Gas | M.Taka | 176.0039 | 2021-08-03
| B) Liquid fuel | M.Taka | 808.6182 | 2021-08-24
| C) Coal | M.Taka | 77.0091 | 2021-08-24
| D) BIPTC (Import from India) | M.Taka | 86.5887 | 2021-08-23
20 | Average fuel cost of per unit Generation
| A) Including Hydro & Solar | Taka/kWhR | 3.5652
| B) Excluding Hydro & Solar | Taka/kWhR | 3.6169
21 | Head water level of Kaptai lake on the last day of the month
a) | As per Rule curve | FT (MSL) | 98.34 | 31/8/2021 | 06:00
b) | Actual | FT (MSL) | 97.78 | 31/8/2021 | 06:00
22 | Peak Genaration of August 2020 | MW | 12577 | 31/08/20 | 19:30
23 | Peak Demand of August 2020 | MW | 10843.5 | 31/08/20 | 12:00
24 | Maximum peak Generation recorded upto 31/08/2021 | MW | 13792 | 27/04/21 | 20:00
25 | Maximum peak Demand recorded upto 31/08/2021 | MW | 14097 | 27/04/21 | 21:00
26 | Maximum load shed recorded upto 31/08/2021 | MW | 1459 | 04/05/2010 | 20:00
Executive Engineer
Information Management Division
LDC,PGCB, Dhaka.