## Forecast
9 | [5 empty] | Power Grid Company of Bangladesh Ltd. | [10 empty] | QF-LDC-07
|  |  |  | Report on Forecasted Generation & Demand of national grid on | [6 empty] | 2021-09-28 | Tuesday
|  |  | Date (day): | 2021-09-28 |  | Tuesday
|  | Probable Maximum |  | Generation : |  | (a) At Day Peak Hour : | 13739.6 | MW |  |  | (b) At Evening Peak Hour : |  | 14934 | MW
| Sl. | [6 empty] | Present | Actual Generation |  | Forecasted Available Gen. on |  | Ev. Peak Gen.Shortage |  | Plants under |  | Probable
| No. | Name of the Power Station |  | Fuel | Producer | Installed Capacity |  | Capacity | On | 2021-09-27 | 2021-09-28 | during | for Fuel | for plant. S/D | Shut down (date)/ |  | Start up
[9 empty] | Day Peak | Ev. Peak | Day Peak | Ev. Peak | Limitation | M/C Problem | Remarks |  | Date
[6 empty] | Unit No. X Capacity | MW | MW | MW | MW | MW | MW | MW | MW
| 1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | Gas | PDB | 1*260 | 260 | 260 | 0 | 0 | 0 | 0 |  | 260 | Under maint.
| 2 | Ghorasal Repowered CCPP Unit-4 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maint.
|  | Ghorasal TPP Unit-5 |  | Gas | PDB | 1*210 | 210 | 190 | 0 | 0 | 0 | 0 | 190 |  | Gas shortage
| 3 | Ghorasal 365 MW CCPP Unit-7 |  | Gas | PDB | 1*243+1*122 | 365 | 365 | 310 | 300 | 310 | 310 |  | 55 | Machine problem.
|  | Ghorashal 78.5 MW PP(MAX) |  | Gas | QRPP | 2*40 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 4 | Ghorashal 108MW PP (Regent) |  | Gas | IPP | 34*3.35 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Gas shortage
| 5 | Haripur GTPP |  | Gas | SBU, PDB | 2*32 | 32 | 20 | 0 | 0 | 0 | 0 |  | 20 | Under maint.
| 6 | Haripur 412 MW CCPP |  | Gas | EGCB | 1*273+1*139 | 412 | 412 | 411 | 378 | 412 | 412
| 7 | Haripur 360MW CCPP(HPL) |  | Gas | IPP | 1*235+1*125 | 360 | 360 | 320 | 320 | 325 | 325 | 35 |  | Gas shortage
| 8 | Meghnaghat 450 MW CCPP(MPL) |  | Gas | IPP | 2*150+1*150 | 450 | 450 | 280 | 280 | 280 | 280 | 170 |  | Dirty Gas
| 9 | Meghnaghat 100 MW(IEL) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 10 | Meghnaghat CCPP(Summit) |  | Gas | IPP | 2*110+1*110 | 305 | 305 | 265 | 285 | 305 | 305 |  |  | FGMO
| 11 | Madanganj 102 PP(Summit) |  | HFO | QRPP | 6*17 | 102 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 12 | Madanganj-55 MW PP(Summit) |  | HFO | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 40 | 55 | 55 | 55
| 13 | Keraniganj 100 MW PP (Powerpac) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 50 | 54 | 63 | 63 |  | 37 | Engine problem
| 14 | Narshingdi 22 MW PP (Doreen) |  | Gas | SIPP, REB | 8*2.90 | 22 | 22 | 19 | 21 | 22 | 22
| 15 | 210 MW Siddhirgonj TPP |  | Gas | PDB | 1*210 | 210 | 115 | 0 | 0 | 0 | 0 |  | 115 | Under maint.
| 16 | Siddhirgonj 2*120 MW GTPP |  | Gas | EGCB | 2*105 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 17 | Siddhirganj 100 PP(Dutch Bangla) |  | HFO | QRPP | 12*8.9 | 100 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 18 | Siddhirganj 335 MW CCPP |  | Gas | EGCB | 1*217+118 | 335 | 335 | 250 | 250 | 280 | 300 | 35 |  | Gas shortage
| 19 | Gagnagar 102 MW PP (Digital Power) |  | HFO | IPP | 12*8.924 | 102 | 102 | 102 | 102 | 102 | 102
| 20 | Katpotti 52 MW PP (Sinha) |  | HFO | IPP | 7*7.9 | 51 | 51 | 0 | 0 | 0 | 0 | 51 |  | Fuel shortage
| 21 | Kamalaghat 54 MW PP(Banco Energy) |  | HFO | IPP | 3*18 | 54 | 54 | 17 | 17 | 17 | 54 |  |  | Engine problem
| 22 | Kodda 150MW PP |  | HFO | BPDB-RPCL | 9*17.06 | 149 | 149 | 48 | 150 | 149 | 149
| 23 | Manikganj 55 MW PP (Northern) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 55 | 17 | 55
| 24 | Nababganj 55 MW PP (Southern power ) |  | HFO | IPP | 3*19.3 | 55 | 55 | 17 | 35 | 55 | 55
| 25 | Bosila 108MW PP(CLC) |  | HFO | IPP | 12*8.775+1*3.5 | 108 | 108 | 0 | 0 | 0 | 0 | 108 |  | Fuel shortage
| 26 | Summit Power,(Madhabdi+Ashulia) |  | Gas | SIPP,REB | 3*3.67+4*8.73 | 80 | 80 | 46 | 54 | 55 | 55 |  | 25 | Engine problem
| 27 | Maona 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 28 | Rupganj 33 MW PP(Summit) |  | Gas | SIPP,REB | 4*8.73 | 33 | 33 | 25 | 33 | 33 | 33
| 29 | Gazipur 52 MW PP |  | HFO | IPP | 6*8.9 | 52 | 52 | 51 | 51 | 51 | 51
| 30 | Tongi 80 MW GTPP |  | Gas | PDB | 1* 105 | 105 | 105 | 0 | 0 | 0 | 0 |  | 105 | Under maint.
| 31 | Kodda 300 MW PP Unit-2 (Summit) |  | HFO | IPP | 18*17.076 | 300 | 300 | 258 | 281 | 250 | 300
| 32 | Keranigonj 300 MW PP (APR) |  | HSD | IPP | 256*1.4 | 300 | 300 | 0 | 0 | 100 | 300
| 33 | Bramhangoan 100 MW PP (Aggreko) |  | HSD | IPP | 100 | 100 | 100 | 0 | 0 | 100 | 100
| 34 | Aurahati 100MW PP (Aggreko) |  | HSD | IPP | 0.85*23+0.95*91 | 100 | 100 | 0 | 50 | 50 | 100
| 35 | Kodda 149 MW PP Unit-1 (Summit) |  | HFO | IPP | 149 | 149 | 149 | 149 | 149 | 149 | 149
| 36 | Gazipur 100 MW PP |  | HFO | RPCL | 100 MW | 105 | 105 | 105 | 105 | 100 | 100
| 37 | Meghnaghat 104 MW PP (OPCL) |  | HFO | IPP | 18.5*6 | 104 | 104 | 94 | 94 | 94 | 94 |  | 10 | Engine problem
| 38 | Manikgonj 162MW PP(MPGL) |  | HFO | IPP | 9*18 | 162 | 162 | 108 | 162 | 162 | 162
| 39 | Spectra Solar Plant Ltd. |  | Solar | IPP | 35 | 35 | 35 | 24 | 0 | 30 | 0
|  | Dhaka area Total |  |  |  |  | 6178 | 5719 | 3039 | 3314 | 3599 | 3964 | 907 | 807
| 40 | Chattogram TPP-1 |  | Gas | PDB | 1*210 | 210 | 180 | 115 | 115 | 115 | 115 | 65 |  | Gas shortage
|  | Chattogram TPP-2 |  | Gas | PDB | 1*210 | 210 | 180 | 0 | 0 | 0 | 0 |  | 180 | Under maintenance.
| 41 | Raozan 25 MW PP |  | HFO | IPP | 3*8.9 | 25 | 25 | 9 | 25 | 25 | 25
| 42 | Teknaf 20MW PP (Solartech) |  | Solar | Teknaf Solartech Energy Ltd. | 20 | 20 | 20 | 16 | 0 | 20 | 0
| 43 | Patenga 50MW PP (Baraka) |  | HFO | IPP | 8*6.98 | 50 | 50 | 50 | 50 | 50 | 50
| 44 | Karnaphuli Hydro PP Unit-1,2,3,4, 5 |  | Hydro | PDB | 2*40+3*50 | 230 | 230 | 118 | 120 | 119 | 120 | 110 |  | Low water level & Unit-2 S/D
| 45 | Sikalbaha 225MW CCPP |  | Gas/HSD | PDB | 1*150+1*175 | 225 | 225 | 0 | 0 | 0 | 0 |  | 225 | Under maint
| 46 | Sikalbaha Peaking GT |  | Gas/HSD | PDB | 1*150 | 150 | 150 | 0 | 0 | 0 | 0 |  | 150 | Under maint
| 47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | HFO | IPP | 105 MW | 105 | 105 | 105 | 105 | 105 | 105
| 48 | Hathazari 100 MW peaking PP |  | HFO | PDB | 11*8.9 | 98 | 98 | 0 | 0 | 0 | 0 |  | 98 | Under S/D.
| 49 | Dohazari -Kalaish 100 MW Peaking |  | HFO | PDB | 6*17 | 102 | 102 | 0 | 102 | 0 | 102
| 50 | Juldah 100 MW Unit-1 (Acorn) |  | HFO | QRPP | 8*13.45 | 100 | 100 | 85 | 50 | 100 | 100
| 51 | Juldah 100 MW PP Unit-3 (Acorn) |  | HFO | IPP | 0 | 100 | 100 | 90 | 100 | 100 | 100
| 52 | Barabkunda 22 MW PP (Regent) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 21 | 21 | 21 | 21
| * | Malancha, Ctg. EPZ (United) |  | Gas |  | 5*8.73+3*9.34 |  | 0 | 2 | 2 | 5 | 15
| 53 | Chattogram 108 MW PP (ECPV) |  | HFO | IPP | 16*7 | 108 | 108 | 35 | 85 | 85 | 86 |  | 22 | Engine problem
| 54 | Kaptai 7 MW Solar PP |  | Solar | PDB | 7.4 MW | 7 | 7 | 3 | 0 | 5 | 0
| 55 | Anwara 300 MW PP (United) |  | HFO | IPP | 300 MW | 300 | 300 | 304 | 305 | 300 | 300
| 56 | Jodiac Power |  | HFO | IPP | 3*18.55+1*3.6 | 54 | 54 | 54 | 54 | 54 | 54
| 57 | Karnaphuli Power Ltd. |  | HFO | IPP | 110 | 110 | 110 | 108 | 110 | 110 | 110
| 58 | Juldah unit-2 (Acorn) |  | HFO | IPP | 8*13.6 | 100 | 100 | 90 | 100 | 100 | 100
| 59 | Anlima Energy Ltd. |  | HFO | IPP | 6*21.2 | 116 | 116 | 108 | 108 | 116 | 116
|  | Chattogram area Total |  |  |  |  | 2442 | 2382 | 1313 | 1452 | 1430 | 1519 | 175 | 675
| 60 | Ashuganj TPP Unit- 3 |  | Gas | APSCL | 1*150 | 150 | 135 | 0 | 0 | 0 | 0 | 135 |  | Gas shortage
|  | Ashuganj TPP Unit- 4 |  | Gas | APSCL | 1*150 | 150 | 129 | 0 | 0 | 0 | 0 | 129 |  | Gas shortage
|  | Ashuganj TPP Unit- 5 |  | Gas | APSCL | 1*150 | 150 | 134 | 0 | 0 | 0 | 0 | 134 |  | Gas shortage
| 61 | Ashuganj 225 MW CCPP |  | Gas | APSCL | 1*142+1*75 | 221 | 221 | 205 | 208 | 210 | 210 |  |  | Gas shortage
| 62 | Ashuganj 450 MW CCPP(North) |  | Gas | APSCL | 1*360 | 360 | 360 | 320 | 315 | 150 | 330 | 30 |  | Gas shortage
| 63 | Ashuganj 450 MW CCPP(South) |  | Gas | APSCL | 1*360 | 360 | 360 | 305 | 295 | 300 | 300 | 60 |  | Gas shortage
| 64 | Ashuganj 50 MW PP |  | Gas | APSCL | 14*3.968 | 53 | 45 | 23 | 23 | 23 | 23 |  | 22 | Engine problem
| 65 | Ashuganj 55 MW PP (Precision) |  | Gas | RPP | 15*4 | 55 | 55 | 52 | 52 | 51 | 51
| 66 | Ashuganj 195MW PP (APSCL-United) |  | Gas | IPP | 20*9.73+1*16 | 195 | 195 | 36 | 36 | 63 | 63 | 132 |  | Gas shortage
| 67 | Ashuganj 51 MW PP (Midland) |  | Gas | IPP | 6*9.34 | 51 | 51 | 35 | 35 | 43 | 43 |  | 8 | Engine problem
| 68 | Ashuganj 150MW PP (Midland) |  | HFO | IPP | 23*7.015 | 150 | 150 | 110 | 123 | 135 | 135 |  | 15 | Engine problem
| 69 | Titas 50 MW Peaking PP |  | HFO | PDB | 6*8.92 | 52 | 52 | 0 | 48 | 0 | 50
| 70 | Chandpur 150 MW CCPP |  | Gas | PDB | 1*106+1*57 | 163 | 163 | 139 | 138 | 140 | 140 |  | 23 | Engine problem
| 71 | Chandpur 200MW (Desh energy) |  | HFO | IPP | 0 | 200 | 200 | 193 | 197 | 200 | 200
| 72 | Feni 22MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 0 | 22 | 22 | 22
| 73 | Feni 11 MW PP (Doreen) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| ** | Impoprt (Tripura) |  |  | Imported power | 0 | 160 | 160 | 140 | 128 | 138 | 164
| 74 | Jangalia 33MW PP (Summit) |  | Gas | SIPP, PDB | 4*8.73 | 33 | 33 | 33 | 33 | 33 | 33
| 75 | Jangalia 52 MW PP (Lakdanavi) |  | HFO | IPP | 6*8.92 | 52 | 52 | 8 | 16 | 8 | 8
| 76 | Cumilla 25 MW PP (Summit) |  | Gas | SIPP, PDB | 3*3.67+2*6.97 | 25 | 25 | 12 | 20 | 20 | 20
| 77 | Daudkandi 200 MW PP (B.Trac) |  | HSD | IPP | 154*1.4 | 200 | 200 | 0 | 0 | 150 | 200
| 78 | Feni Lanka Power |  | HFO | IPP | 7*18.415+1*9.78 | 114 | 114 | 17 | 34 | 114 | 114
| 79 | Chowmuhani 113 MW |  | HFO | IPP | 12*9.78+2*3.1 | 113 | 113 | 47 | 95 | 90 | 95 |  | 18 | Engine problem
| 80 | Bhairob 54.5 MW |  | HFO | IPP | 3*18.2 | 54 | 54 | 17 | 17 | 17 | 17 |  | 37 | 33 kV feeder fault
|  | Cumilla Area Total |  |  |  |  | 3094 | 3034 | 1700 | 1843 | 1918 | 2229 | 620 | 123
| 81 | RPCL 210MW CCPP |  | Gas | IPP | 4*35+1*70 | 210 | 202 | 152 | 162 | 170 | 170 | 32 |  | Gas shortage
| 82 | Tangail 22 MW PP (Doreen) |  | Gas | SIPP, PDB | 8*2.90 | 22 | 22 | 18 | 14 | 22 | 22
| 83 | Jamalpur 95 MW PP(Powerpac) |  | HFO | IPP | 12*8.924 | 95 | 95 | 0 | 0 | 8 | 8 |  | 87 | Engine problem
| 84 | Sarishabari 3 MW Solar Plant |  | Solar | IPP | 1*3 | 3 | 3 | 2 | 0 | 1.6 | 0
| 85 | Mymensingh 200 MW PP (United) |  | HFO | IPP | 200 | 200 | 200 | 168 | 170 | 170 | 170 |  | 30 | Engine problem
| 86 | Jamalpur 115 MW PP (United) |  | HFO | IPP | 115 MW | 115 | 115 | 115 | 115 | 115 | 115
| 87 | Sutiakhali 50 MW Solar PP |  | Solar | IPP | 50 | 50 | 50 | 57 | 0 | 50 | 0
| 88 | Tangail Palli Power Gen 22 MW |  | HFO | IPP | 4*6.7 | 22 | 22 | 19 | 16 | 22 | 22
|  | Mymensingh Area Total |  |  |  |  | 717 | 709 | 531 | 477 | 558.6 | 507 | 32 | 87
| 89 | Fenchugonj CCPP Phase-1 |  | Gas | PDB | 2*32+1*33 | 97 | 70 | 43 | 44 | 43 | 43 |  | 27 | Machine problem.
| 90 | Fenchugonj CCPP Phase-2 |  | Gas | PDB | 2*35+1*35 | 104 | 90 | 0 | 0 | 0 | 0 |  | 90 | Under maint.
| 91 | Kushiara 163 MW CCPP (KP) |  | Gas | IPP | 1*109+1*54 | 163 | 163 | 110 | 163 | 163 | 163
| 92 | Shajibazar 330 MW CCPP |  | Gas | PDB | 3*110 | 330 | 330 | 162 | 160 | 160 | 160 | 170 |  | Gas shortage
| 93 | Fenchugonj 51 MW PP (Barakatullah) |  | Gas | RPP | 19*2.90 | 51 | 51 | 50 | 50 | 50 | 50
|  | Fenchuganj 44MW (Energyprima) |  | Gas | RPP | 12*3.3+5*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 94 | Hobiganj 11MW PP Cofidence-E |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 8 | 11 | 11
| 95 | Shahjibazar GTPP Unit- 8 & 9 |  | Gas | PDB | 2*35 | 70 | 66 | 25 | 25 | 30 | 30 | 36 |  | Gas shortage
| 96 | Shahjibazar 86MW PP (Shahjibazar) |  | Gas | RPP | 32*2.90 | 86 | 86 | 70 | 78 | 78 | 78 |  | 8 | Engine problem
| 97 | Shahjibazar 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 |  | 100 | Under maint
| 98 | Sylhet 225 MW CCPP |  | Gas | PDB | 1*142+1*89 | 231 | 231 | 220 | 221 | 220 | 220
| 99 | Sylhet 20 MW GTPP |  | Gas | PDB | 1*20 | 20 | 20 | 18 | 18 | 18 | 18
|  | Sylhet 50MW PP (EPL) |  | Gas | RPP | 27*2 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 100 | Shahjahanulla 25 MW PP |  | Gas | SIPP, REB | 3*9.34 | 25 | 25 | 24 | 16 | 24 | 24
| 101 | Bibiana-II 341 MW CCPP (Summit) |  | Gas | IPP | 1*222+1*119 | 341 | 341 | 290 | 280 | 341 | 341 |  |  | FGMO
| 102 | Bibiyana-III 400 MW CCPP |  | Gas | PDB | 400 MW | 400 | 400 | 316 | 316 | 316 | 316 | 84 |  | Gas shortage
| 103 | Sylhet 10MW PP (Desh) |  | Gas | RPP | 6*1.95 | 10 | 10 | 0 | 8 | 0 | 0 | 10 |  | Gas shortage
| 104 | Bibiyana South 400 MW |  | Gas | PDB | 400 MW | 383 | 383 | 320 | 320 | 320 | 320 | 63 |  | Gas shortage
|  | Sylhet Area Total |  |  |  |  | 2422 | 2377 | 1656 | 1707 | 1774 | 1774 | 363 | 225
| 105 | Bheramara GTPP Unit-3 |  | HSD | PDB | 1*20 | 20 | 16 | 0 | 0 | 0 | 0
| ** | Bheramara (HVDC ) |  | 0 | Imported power | 2*500 | 1000 | 1000 | 709 | 709 | 721 | 721
| 106 | Khulna 115 PP MW (KPCL-2) |  | HFO | QRPP | 7*17 | 115 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 107 | Faridpur 50 MW Peaking PP |  | HFO | PDB | 8*6.89 | 54 | 54 | 0 | 30 | 4 | 32 |  | 22 | Engine problem
| 108 | Khulna 225 MW CCPP |  | HSD | NWPGCL | 1*150+1*75 | 230 | 230 | 120 | 170 | 225 | 225
| 109 | Gopalganj 100 MW Peaking PP |  | HFO | PDB | 16*6.98 | 109 | 109 | 0 | 0 | 0 | 40 |  | 69 | Engine problem
| 110 | Bheramara 410 MW CCPP |  | Gas | NWPGCL | 1*278+1*132 | 410 | 410 | 395 | 410 | 400 | 410
|  | Noapara 40 MW PP (Khanjahan Ali) |  | HFO | QRPP | 5*8.5 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 111 | Noapara 100 MW PP (Bangla Trac) |  | HSD | IPP | 70*1.4 | 100 | 100 | 0 | 50 | 50 | 100
| 112 | Rupsha 105 MW PP (Orion rupsha) |  | HFO | IPP | 6*18.445 | 105 | 105 | 85 | 98 | 88 | 105
| 113 | Madhumati 100 MW PP |  | HFO | NWPGCL | 100 MW | 105 | 105 | 0 | 0 | 100 | 100
|  | Khulna Area Total |  |  |  |  | 2248 | 2129 | 1309 | 1467 | 1588 | 1733 | 0 | 91
| 114 | Barisal 110 MW PP (Summit ) |  | HFO | IPP | 7*17.076 | 110 | 110 | 0 | 0 | 110 | 110
| 115 | Bhola 33 MW PP (Venture) |  | Gas | RPP | 1*34.50 | 33 | 33 | 21 | 33 | 33 | 33
| 116 | Bhola 225 MW CCPP |  | Gas | PDB | 2*63+1*68 | 194 | 194 | 86 | 86 | 87 | 87 |  | 107 | Machine problem.
| 117 | Bhola 95 MW PP (Aggreko) |  | Gas | QRPP | 96*1.10 | 95 | 95 | 50 | 11 | 81 | 91 | 4 |  | Gas shortage
| 118 | Payra 1320 MW |  | Coal | BCPCL | 2*622 | 1244 | 1244 | 460 | 500 | 622 | 622
| 119 | Bhola Nutan Biddut BD LTD |  | Gas | IPP | 220 | 220 | 220 | 132 | 223 | 220 | 220
| 120 | United Payra Power Ltd. |  | HFO | IPP | 8*18.5+1*9.5 | 150 | 150 | 0 | 35 | 0 | 150
|  | Barisal Area Total |  |  |  |  | 2046 | 2046 | 749 | 888 | 1153 | 1313 | 4 | 107
| 121 | Baghabari 71 MW GTPP |  | Gas | PDB | 1*71 | 71 | 71 | 0 | 0 | 0 | 0 | 70 |  | Gas shortage
|  | Baghabari 100 MW GTPP |  | Gas | PDB | 1*100 | 100 | 100 | 0 | 0 | 0 | 0 | 100 |  | Gas shortage
| 122 | Baghabari 50 MW Peaking PP |  | HFO | PDB | 6*8.9 | 52 | 52 | 0 | 50 | 50 | 50
| 123 | Bera 70 MW Peaking PP |  | HFO | PDB | 9*8.29 | 71 | 71 | 0 | 33 | 34 | 36 |  | 35 | Engine problem
| 124 | Amnura 50 MW PP(Sinha) |  | HFO | QRPP | 7*7.79 | 50 | 50 | 27 | 27 | 27 | 27 | 23 |  | Fuel shortage
| 125 | Katakhali 50 MW PP (Northern) |  | HFO | QRPP | 6*8.9 | 50 | 50 | 0 | 50 | 0 | 50 |  | 0
| 126 | Katakhali 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 35 | 0 | 35 |  | 15 | Engine problem
| 127 | Sirajgonj 225MW CCPP Unit-1 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 210 | 210 | 0 | 0 | 0 | 0 | 210 |  | Gas shortage
| 128 | Sirajgonj 225MW CCPP Unit-2 |  | Gas/HSD | NWPGCL | 1*150+1*75 | 220 | 220 | 170 | 184 | 200 | 220 |  |  | FGMO
| 129 | Sirajgonj 225MW CCPP Unit-3 |  | Gas/HSD | NWPGCL | 1*141 | 220 | 220 | 173 | 187 | 200 | 220 |  |  | FGMO
| 130 | Sirajgonj 400 MW CCPP Unit-4 |  | Gas/HSD | SNWPGCL | 1*282+1*132 | 414 | 414 | 356 | 402 | 400 | 400 |  |  | FGMO
| 131 | Santahar 50 MW Peaking PP |  | HFO | PDB | 6*8.7 | 50 | 50 | 0 | 29 | 0 | 34 |  | 16 | Engine problem
| 132 | Bogra 22 MW PP (GBB) |  | Gas | RPP | 6*4 | 22 | 22 | 16 | 21 | 22 | 22
| 133 | Bogura 20 MW PP (Energyprima) |  | Gas | RPP | 5*3.3+5*2 | 20 | 0 | 0 | 0 | 0 | 0 |  |  | Contract Expired
| 134 | Ullapara 11 MW PP (Summit) |  | Gas | SIPP, REB | 4*2.90 | 11 | 11 | 8 | 11 | 11 | 11
| 135 | Natore 52 MW PP (Rajlanka) |  | HFO | IPP | 52 | 52 | 52 | 8 | 43 | 52 | 52
| 136 | Chapainawabganj 100 MW Peaking PP |  | HFO | PDB | 104 | 104 | 104 | 0 | 94 | 90 | 94 |  | 10 | Engine problem
| 137 | Baghabari 200 MW PP (Paramount) |  | HSD | IPP | 200 MW | 200 | 200 | 0 | 0 | 200 | 200
| 138 | Bagura 113 MW PP (Confidence)-2 |  | HFO | IPP | 113 MW | 113 | 113 | 94 | 113 | 113 | 113
| 139 | Confidence Power Bogura Unit-1 113 MW |  | HFO | IPP | 6*18.55 | 113 | 113 | 113 | 113 | 113 | 113
| 140 | Sirajgonj 6.55 MW Solar |  | Solar | NWPGCL | 1*6 | 6 | 6 | 5 | 0 | 6 | 0
|  | Rajshahi Area Total |  |  |  |  | 2199 | 2179 | 970 | 1392 | 1518 | 1677 | 403 | 76
| 141 | Barapukuria TPP Unit-1 |  | Coal | PDB | 1*125 | 125 | 85 | 80 | 72 | 80 | 80
|  | Barapukuria TPP Unit-2 |  | Coal | PDB | 1*125 | 125 | 85 | 0 | 0 | 0 | 0 |  | 85 | Under maint.
| 142 | Barapukuria 275 MW TPP Unit-3 |  | Coal | PDB | 1*275 | 274 | 274 | 0 | 0 | 0 | 0 |  | 274 | Under maint.
| 143 | Rangpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 15 |  | 5 | Engine problem
| 144 | Saidpur 20 MW GTPP |  | HSD | PDB | 1*20 | 20 | 20 | 0 | 0 | 0 | 10 |  | 10 | Engine problem
| 145 | Rangpur 113 MW PP (Confidence) |  | HFO | IPP | 113 MW | 113 | 113 | 104 | 104 | 113 | 113
| 146 | Sympa Solar Power 8MW |  | Solar | IPP | 8 MW | 8 | 8 | 7 | 0 | 8 | 0
|  | Rangpur Area Total |  |  |  |  | 685 | 605 | 191 | 176 | 201 | 218 | 0 | 374
|  | Total |  |  |  |  | 22031 | 21180 | 11458 | 12716 | 13739.6 | 14934 | 2504 | 2565
|  | Usable load at Substation end after deducting Auxiliary use & Transmission loss | [6 empty] | 10964.2139 | 12168 | 13147.4876 | 14290.4146
| A. |  | 2021-09-27 | (Yesterday) |  |  |  |  | Monday
| 1 | Highest Generation : |  |  | 12716 | MW at | 19:00 | hrs | 11 Evening Peak Hour : | [5 empty] | 19:00 | hrs.
| 2 | Minimum Generation : |  |  | 9805 | MW at | 8:00 | hrs | 12 Max. Demand (Generation end) at evening peak hour : | [5 empty] | 12716 | MW
| 3 | Day peak Generation : |  |  | 11458 | MW at | 12:00 | hrs | 13 Max. Demand (Substation end) at evening peak hour : | [5 empty] | 12168 | MW
| 4 | Evening peak Generation : |  |  | 12716 | MW at | 19:00 | hrs | 14 Load Shed (Substation end) at evening peak hour : | [5 empty] | 0 | MW
| 5 | Total Energy Generation : |  | 276.366 | MKWHr | By Solar | 0.84755 | MKWHr | 15. Area wise Demand (S/S end), Supply (S/S end) & | [5 empty] | 16 Hourly Load Shed during
|  | By Gas : | 153.3058 | MKWHr |  | By Oil: | 85.4221 | MKWHr | Load Shed (S/S end) at Evening peak hour in MW : | [5 empty] | Evening Peak hours :
|  | By Coal : | 13.7723 | MKWHr |  | By Hydro: | 2.7759 | MKWHr | Area | Demand | Supply |  | Loadshed |  | Time |  | Loadshed
| 6 | Generation Shortfall : |  | For Fuel Limitation = |  |  | 2504 | MW | Dhaka | 4560 | 4560 |  | 0
|  |  |  | For Plants S/D or M/C prob = |  |  | 2565 | MW | Chittagong | 1316 | 1316 |  | 0 |  | 18:00 |  | 0
|  |  |  | Total = |  |  | 5069 | MW | Khulna | 1358 | 1358 |  | 0 |  | 18:30 |  | 0
| 7 | Total Gas Supplied : |  |  | 1160.49 | MMCFD |  |  | Rajshahi | 1162 | 1162 |  | 0 |  | 19:00 |  | 0
| 8 | Fuel Cost : | i) Gas : | Taka | 155236664.992 | ii) Oil : | Taka | 625441529.81 | Comilla | 1193 | 1193 |  | 0 |  | 19:30 |  | 0
|  |  | iii) Coal : |  | 63505547.81 | Total | Taka | 844183742.612 | Mymensingh | 962 | 962 |  | 0 |  | 20:00 |  | 0
| 9 | Power flow through E-W Interconnectors : |  | Taka |  | i) Energy | 1.93 | MKWHr. | Sylhet | 557 | 557 |  | 0 |  | 21:00 |  | 0
|  | ii) During Peak Demand : |  |  | 178 | MW (E to W) at | 19:00 | hrs | Barisal | 365 | 365 |  | 0 |  | 22:00 |  | 0
|  | iii) Maximum : |  |  | -296 | MW at | 2:00 | hrs | Rangpur | 695 | 695 |  | 0 |  | 23:00 |  | 0
| 10 | Maximum Temperature in Dhaka was |  |  |  | 35.9° C |  |  | Total | 12168 | 12168 |  | 0
| B. |  | 2021-09-28 | (Today) |  |  |  | Tuesday |  |  | Probable max. temperature in Dhaka |  |  | 32.1° C
Forecast
| 1 | Maximum Demand* Evening (Generation end) |  |  |  | 13200 | MW |  | 6 Total Load Shed forecast (Substation end) : |  |  |  |  | 0 | MW
| 2 | Maximum Generation (Generation end) |  |  |  | 14934 | MW |  | 7 Area wise Load Shed forecast (Substation end) :
| 3 | Maximum Demand* Day (Generation end) |  |  |  | 10800 | MW
| 4 | Reserve(Generation end) |  |  |  | 1734 | MW |  | Dhaka | Chittagong | Khulna | Rajshahi | Comilla | Mymensingh | Sylhet | Barisal | Rangpur
| 5 | Total Energy Generation |  |  |  | 286.8851 | MKWHr |  | MW | MW | MW | MW | MW | MW | MW | MW | MW
| 6 | Actual Minimum Generation up to 8:00 hrs. |  |  |  | 9181 | MW at | 8:00 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| * Import Through HVDC C/B Interconnector : |  |  |  |  | i) Energy | 17.2058 | MKWHr. | ii) HVDC Flow at Peak Time |  | 709 | MW at | 19:00 | hrs.
| * Import Through Comilla C/B Interconnector : |  |  |  |  | i) Energy | 3.0365 | MKWHr. | iii) Maximum HVDC Flow : |  | 720 | MW at | 2:00 | hrs.
*Cost for HVDC, Tripura & Solar energy is not usually included in the total fuel cost.
| Water Level of Kaptai Lake at 06:00 hr (ft): |  |  |  |  | (a) Yesterday : | 106.41 |  | (b) Today: | 106.44 |  | (c) Rule Curve: |  | 105.28
.
[5 empty] | Sub Divisional Engineer | [6 empty] | Executive Engineer
[5 empty] | Network Operation Division | [6 empty] | Network Operation Division

## YesterdayGen
2021-09-27
Plant Name | Ghorasal TPP (Unit-1&2) | Ghorasal Repowered CCPP:Unit-3 (GT | Ghorasal Repowered CCPP Unit-4 | Ghorasal TPP Unit-5 | Ghorasal 365 MW CCPP Unit-7 | Ghorashal 108MW PP (Regent) | Ghorashal 78.5 MW PP(MAX) | Haripur 412 MW CCPP | Haripur 360MW CCPP(HPL) | Plant Removed | Haripur GTPP | Meghnaghat 450 MW CCPP(MPL) | Meghnaghat CCPP(Summit) | Meghnaghat 100 MW(IEL) | Madanganj 102 PP(Summit) | Madanganj-55 MW PP(Summit) | Siddhirganj 335 MW CCPP | 210 MW Siddhirgonj TPP | Siddhirgonj 2*120 MW GTPP | Siddhirganj 100 PP(Dutch Bangla) | Gagnagar 102 MW PP (Digital Power) | Kodda 150MW PP | Keraniganj 100 MW PP (Powerpac) | Bosila 108MW PP(CLC) | Pagla (DPA ) | Katpotti 52 MW PP (Sinha) | Kamalaghat 54 MW PP(Banco Energy) | Manikganj 55 MW PP (Northern) | Nababganj 55 MW PP (Southern power ) | Narshingdi 22 MW PP (Doreen) | Summit Ashulia | Summit Madhabdi | Maona 33 MW PP(Summit) | Rupganj 33 MW PP(Summit) | Gazipur 52 MW PP | Tongi 80 MW GTPP | Karnaphuli Hydro PP Unit-1, 2 & 3 | Karnaphuli Hydro PP Unit-4 & 5 | Chattogram TPP-1 | Chattogram TPP-2 | Raozan 25 MW PP | Sikalbaha 225MW CCPP (Gas) | Sikalbaha 225MW CCPP(Oil) | Sikalbaha 150MW GTPP | Sikalbaha 150MW GTPP(Oil) | Plant Removed | Tangail Palli Power Gen 22 MW | Hathazari 100 MW peaking PP | Dohazari -Kalaish 100 MW Peaking | Juldah 100 MW Unit-1 (Acorn) | Chattogram 108 MW PP (ECPV) | Patenga 50MW PP (Baraka) | Barabkunda 22 MW PP (Regent) | Malancha, Ctg. EPZ (United) | Ashuganj TPP Unit- 3 | Ashuganj TPP Unit- 4 | Ashuganj TPP Unit- 5 | Ashuganj 450 MW CCPP(North) | Ashuganj 450 MW CCPP(South) | Ashuganj 225 MW CCPP | Ashuganj 195MW PP (APSCL-United) | Chandpur 150 MW CCPP | Ashuganj 50 MW PP | Ashuganj 55 MW PP (Precision) | Ashuganj 53MW PP (United) | Ashuganj 51 MW PP (Midland) | B.Baria (Aggreko) 85MW | Titas 50 MW Peaking PP | Jangalia 52 MW PP (Lakdanavi) | Feni 22MW PP (Doreen) | Feni 11 MW PP (Doreen) | Jangalia 33MW PP (Summit) | Cumilla 25 MW PP (Summit) | Impoprt (Tripura) | RPCL 210MW CCPP | Jamalpur 95 MW PP(Powerpac) | Tangail 22 MW PP (Doreen) | Sarishabari 3 MW Solar Plant | Fenchugonj CCPP Phase-1 | Fenchugonj CCPP Phase-2 | Fenchugonj 51 MW PP (Barakatullah) | Fenchuganj 44MW (Energyprima) | Kushiara 163 MW CCPP (KP) | Shajibazar 330 MW CCPP | Shahjibazar GTPP Unit- 8 & 9 | Shahjibazar 86MW PP (Shahjibazar) | Shahjibazar 50MW PP (EPL) | Sylhet 225 MW CCPP | Sylhet 20 MW GTPP | Sylhet 50MW PP (EPL) | Sylhet 10MW PP (Desh) | Bibiana-II 341 MW CCPP (Summit) | Shahjahanulla 25 MW PP | Hobiganj 11MW PP Cofidence-E | Daudkandi 200 MW PP (B.Trac) | Kodda 300 MW PP Unit-2 (Summit) | Keranigonj 300 MW PP (APR) | Bramhangoan 100 MW PP (Aggreko) | Mymensingh 200 MW PP (United) | Aurahati 100MW PP (Aggreko) | Kodda 149 MW PP Unit-1 (Summit) | Teknaf 20MW PP (Solartech) | Juldah 100 MW PP Unit-3 (Acorn) | Chandpur 200MW (Desh energy) | Ashuganj 150MW PP (Midland) | Bibiyana-III 400 MW CCPP | Jamalpur 115 MW PP (United) | Gazipur 100 MW PP | Sikalbaha 105 MW PP (Baraka Sikalbaha) | Kaptai 7 MW Solar PP | Anwara 300 MW PP (United) | Jodiac Power | Karnaphuli Power Ltd. | Feni Lanka Power | Chowmuhani 113 MW | Juldah unit-2 (Acorn) | Bibiyana South 400 MW | Meghnaghat 104 MW PP (OPCL) | Sutiakhali 50 MW Solar PP | Manikgonj 162MW PP(MPGL) | Anlima Energy Ltd. | Shahjibazar 100 MW GTPP | Bhairob 54.5 MW | Spectra Solar Plant Ltd. | EasternBlank | Bheramara (HVDC ) | Bheramara GTPP Unit-3 | Bheramara 410 MW CCPP | Khulna 115 MW PP (KPCL-1 & 3) | Khulna 115 PP MW (KPCL-2) | Khulna 225 MW CCPP | Khulna 60MW | Khulna (Aggreeco) 55MW | Faridpur 50 MW Peaking PP | Gopalganj 100 MW Peaking PP | Noapara 40 MW PP (Khanjahan Ali) | Bhola 225 MW CCPP | Bhola 33 MW PP (Venture) | Barisal 110 MW PP (Summit ) | Barisal GT PP Unit-1& 2 | Baghabari 100 MW GTPP | Baghabari 71 MW GTPP | Baghabari 50 MW Peaking PP | Bera 70 MW Peaking PP | Chapainawabganj 100 MW Peaking PP | Amnura 50 MW PP(Sinha) | Katakhali 50 MW PP (Northern) | Katakhali 50 MW Peaking PP | Natore 52 MW PP (Rajlanka) | Santahar 50 MW Peaking PP | Bogra 22 MW PP (GBB) | Bogura 20 MW PP (Energyprima) | Ullapara 11 MW PP (Summit) | Barapukuria TPP Unit-1 | Barapukuria TPP Unit-2 | Barapukuria 275 MW TPP Unit-3 | Rangpur 20 MW GTPP | Saidpur 20 MW GTPP | Sirajgonj 225MW CCPP Unit-1 (Gas) | Sirajgonj 225MW CCPP Unit-1(Oil) | Sirajgonj 225 MW CCPP Unit-2 (Gas) | Sirajgonj 225 MW CCPP Unit-2 (Oil) | Bhola 95 MW PP (Aggreko) | Noapara 100 MW PP (Bangla Trac) | Sirajgonj 225MW CCPP Unit-3 (Gas) | Sirajgonj 225MW CCPP Unit-3 (Oil) | Sirajgonj 400 MW CCPP Unit-4 | Rupsha 105 MW PP (Orion rupsha) | Baghabari 200 MW PP (Paramount) | Bagura 113 MW PP (Confidence)-2 | Madhumati 100 MW PP | Rangpur 113 MW PP (Confidence) | Sirajgonj 400MW CCPP Unit-4 (Oil) | Sympa Solar Power 8MW | Confidence Power Bogura Unit-1 113 MW | Payra 1320 MW | Bhola Nutan Biddut BD LTD (GAS) | Bhola Nutan Biddut BD LTD (OIL) | United Payra Power Ltd. | Sirajgonj 6.55 MW Solar | WesternBlank | Eastern Grid Total | Western Grid Total | Total (MW) | Gas (Public) | HVDC | Gas (Private) | Oil (Private) | Coal | Hydro | Oil (Public) | Tripura | Solar | Shortage | Water Level
1:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 328 |  | 0 | 280 | 260 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 100 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 30 | 33 | 16 | 0 | 44 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 34 | 40 | 0 | 25 | 21 | 36 | 0 | 0 | 0 | 335 | 300 | 210 | 36 | 141 | 23 | 56 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 124 | 188 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 245 | 0 | 0 | 182 | 0 | 149 | 0 | 100 | 155 | 130 | 316 | 115 | 0 | 105 | 0 | 305 | 54 | 68 | 34 | 74 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 155 | 0 | 0 | 0 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 62 | 0 | 190 | 0 | 415 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 520 | 118 | 0 | 17 | 0 |  | 8164 | 3457 | 11621 | 4569 | 710 | 1982 | 3229 | 599 | 119 | 289 | 124 | 0 | 0 | 106.41
2:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 329 |  | 0 | 280 | 280 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 43 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 17 | 10 | 0 | 25 | 21 | 8 | 0 | 0 | 0 | 355 | 320 | 210 | 36 | 134 | 23 | 56 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 124 | 200 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 130 | 163 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 285 | 24 | 8 | 0 | 245 | 0 | 0 | 165 | 0 | 123 | 0 | 100 | 155 | 123 | 316 | 115 | 0 | 105 | 0 | 304 | 54 | 68 | 17 | 63 | 100 | 320 | 94 | 0 | 126 | 108 | 0 | 17 | 0 |  | 720 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 32 | 0 | 197 | 0 | 420 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 500 | 193 | 0 | 0 | 0 |  | 7884 | 3444 | 11328 | 4628 | 720 | 1979 | 3011 | 579 | 118 | 169 | 124 | 0 | 0 | 106.41
3:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 329 |  | 0 | 280 | 260 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 58 | 32 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 28 | 33 | 0 | 0 | 43 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 10 | 0 | 25 | 21 | 38 | 0 | 0 | 0 | 340 | 305 | 210 | 36 | 137 | 20 | 55 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 120 | 202 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 130 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 295 | 24 | 8 | 0 | 245 | 0 | 0 | 164 | 0 | 117 | 0 | 100 | 155 | 127 | 316 | 115 | 0 | 105 | 0 | 304 | 54 | 68 | 17 | 58 | 100 | 320 | 94 | 0 | 108 | 108 | 0 | 17 | 0 |  | 715 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 195 | 0 | 394 | 105 | 0 | 113 | 0 | 111 | 0 | 0 | 113 | 500 | 193 | 0 | 0 | 0 |  | 7825 | 3389 | 11214 | 4590 | 715 | 1975 | 2965 | 579 | 118 | 152 | 120 | 0 | 0 | 106.41
4:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 329 |  | 0 | 280 | 255 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 42 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 39 | 0 | 0 | 0 | 340 | 305 | 212 | 36 | 141 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 116 | 210 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 130 | 161 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 195 | 0 | 0 | 140 | 0 | 98 | 0 | 100 | 120 | 125 | 316 | 115 | 0 | 68 | 0 | 306 | 54 | 68 | 17 | 58 | 100 | 320 | 94 | 0 | 90 | 108 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 0 | 188 | 0 | 404 | 35 | 0 | 113 | 0 | 111 | 0 | 0 | 35 | 470 | 223 | 0 | 0 | 0 |  | 7588 | 3239 | 10827 | 4602 | 710 | 2002 | 2594 | 550 | 117 | 136 | 116 | 0 | 0 | 106.41
5:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 330 |  | 0 | 280 | 275 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 41 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 39 | 0 | 0 | 0 | 355 | 320 | 212 | 36 | 141 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 112 | 210 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 130 | 159 | 25 | 78 | 0 | 220 | 18 | 0 | 0 | 285 | 24 | 8 | 0 | 165 | 0 | 0 | 100 | 0 | 85 | 0 | 100 | 100 | 127 | 316 | 115 | 0 | 68 | 0 | 305 | 54 | 68 | 17 | 58 | 100 | 320 | 94 | 0 | 90 | 108 | 0 | 17 | 0 |  | 709 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 0 | 191 | 0 | 414 | 0 | 0 | 35 | 0 | 111 | 0 | 0 | 35 | 430 | 226 | 0 | 0 | 0 |  | 7535 | 3100 | 10635 | 4631 | 709 | 2022 | 2399 | 510 | 116 | 136 | 112 | 0 | 0 | 106.41
6:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 330 |  | 0 | 280 | 235 | 0 | 0 | 55 | 290 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 33 | 33 | 0 | 0 | 40 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 39 | 0 | 0 | 0 | 335 | 305 | 212 | 36 | 138 | 20 | 56 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 106 | 212 | 0 | 19 | 0 | 43 | 0 | 53 | 0 | 130 | 160 | 25 | 78 | 0 | 159 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 165 | 0 | 0 | 60 | 0 | 85 | 0 | 100 | 70 | 127 | 316 | 112 | 0 | 17 | 0 | 305 | 54 | 17 | 17 | 58 | 100 | 320 | 94 | 0 | 90 | 90 | 0 | 17 | 0 |  | 710 | 0 | 410 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 0 | 11 | 0 | 190 | 0 | 341 | 0 | 0 | 35 | 0 | 95 | 0 | 0 | 35 | 410 | 197 | 0 | 0 | 0 |  | 7184 | 2963 | 10147 | 4526 | 710 | 1915 | 2150 | 489 | 115 | 136 | 106 | 0 | 0 | 106.41
7:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 394 | 293 |  | 0 | 280 | 280 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 58 | 16 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 23 | 33 | 33 | 0 | 0 | 40 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 1 | 21 | 37 | 0 | 0 | 0 | 280 | 305 | 212 | 36 | 141 | 20 | 55 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 98 | 211 | 0 | 19 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 25 | 78 | 0 | 159 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 165 | 0 | 0 | 60 | 0 | 85 | 2 | 70 | 70 | 123 | 316 | 112 | 0 | 17 | 1 | 253 | 54 | 17 | 17 | 57 | 70 | 320 | 62 | 10 | 90 | 72 | 0 | 17 | 3 |  | 709 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 158 | 0 | 11 | 0 | 169 | 0 | 347 | 0 | 0 | 35 | 0 | 90 | 0 | 1 | 35 | 400 | 182 | 0 | 0 | 1 |  | 6958 | 2850 | 9808 | 4367 | 709 | 1859 | 2024 | 482 | 115 | 136 | 98 | 18 | 0 | 106.41
8:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 406 | 293 |  | 0 | 280 | 260 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 23 | 33 | 33 | 0 | 0 | 40 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 21 | 7 | 0 | 0 | 0 | 265 | 305 | 212 | 36 | 139 | 23 | 52 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 104 | 201 | 0 | 18 | 1 | 43 | 0 | 47 | 0 | 130 | 160 | 25 | 75 | 0 | 159 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 178 | 0 | 0 | 60 | 0 | 105 | 10 | 70 | 70 | 117 | 316 | 112 | 35 | 24 | 2 | 252 | 54 | 23 | 17 | 58 | 70 | 320 | 54 | 25 | 90 | 72 | 0 | 17 | 18 |  | 710 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 0 | 11 | 0 | 168 | 0 | 308 | 0 | 0 | 35 | 0 | 90 | 0 | 2 | 35 | 400 | 182 | 0 | 0 | 1 |  | 6992 | 2813 | 9805 | 4356 | 710 | 1779 | 2082 | 480 | 115 | 120 | 104 | 59 | 0 | 106.4
9:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 413 | 314 |  | 0 | 280 | 260 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 23 | 33 | 33 | 8 | 0 | 42 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 2 | 0 | 0 | 0 | 330 | 305 | 212 | 36 | 138 | 23 | 54 | 0 | 35 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 110 | 183 | 0 | 18 | 1 | 44 | 0 | 47 | 0 | 130 | 161 | 25 | 75 | 0 | 187 | 18 | 0 | 0 | 280 | 24 | 8 | 0 | 245 | 0 | 0 | 60 | 0 | 132 | 14 | 100 | 70 | 117 | 316 | 111 | 105 | 34 | 4 | 303 | 54 | 34 | 17 | 58 | 100 | 321 | 62 | 43 | 90 | 72 | 0 | 17 | 22 |  | 710 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 87 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 0 | 11 | 0 | 173 | 0 | 390 | 0 | 0 | 35 | 0 | 90 | 0 | 4 | 35 | 390 | 132 | 0 | 0 | 4 |  | 7434 | 2847 | 10281 | 4429 | 710 | 1826 | 2407 | 470 | 117 | 120 | 110 | 92 | 0 | 106.4
10:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 413 | 320 |  | 0 | 280 | 300 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 22 | 33 | 33 | 51 | 0 | 42 | 75 | 115 | 0 | 2 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 13 | 21 | 2 | 0 | 0 | 0 | 300 | 340 | 206 | 36 | 140 | 23 | 52 | 0 | 0 | 0 | 0 | 8 | 0 | 11 | 33 | 15 | 112 | 168 | 0 | 18 | 2 | 44 | 0 | 47 | 0 | 110 | 162 | 25 | 75 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 8 | 0 | 262 | 0 | 0 | 60 | 0 | 149 | 10 | 100 | 74 | 117 | 315 | 115 | 105 | 34 | 2 | 306 | 54 | 34 | 17 | 58 | 100 | 320 | 93 | 54 | 90 | 105 | 0 | 17 | 21 |  | 710 | 0 | 400 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 0 | 11 | 0 | 188 | 0 | 383 | 0 | 0 | 38 | 0 | 100 | 0 | 6 | 50 | 410 | 132 | 0 | 0 | 4 |  | 7624 | 2955 | 10579 | 4503 | 710 | 1777 | 2651 | 490 | 117 | 120 | 112 | 99 | 0 | 106.4
11:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 413 | 320 |  | 0 | 280 | 265 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 102 | 48 | 20 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 22 | 33 | 33 | 51 | 0 | 43 | 75 | 115 | 0 | 8 | 0 | 0 | 0 | 0 |  | 4 | 0 | 0 | 70 | 8 | 38 | 21 | 2 | 0 | 0 | 0 | 315 | 300 | 207 | 36 | 140 | 20 | 52 | 0 | 17 | 0 | 0 | 8 | 0 | 11 | 33 | 12 | 132 | 168 | 0 | 18 | 1 | 44 | 0 | 50 | 0 | 110 | 161 | 25 | 71 | 0 | 220 | 18 | 0 | 0 | 270 | 24 | 8 | 0 | 258 | 0 | 0 | 125 | 0 | 149 | 11 | 90 | 121 | 110 | 318 | 115 | 90 | 91 | 6 | 287 | 54 | 65 | 17 | 50 | 90 | 320 | 94 | 57 | 90 | 108 | 0 | 17 | 18 |  | 709 | 0 | 370 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 16 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 189 | 0 | 11 | 0 | 187 | 0 | 341 | 35 | 0 | 80 | 0 | 104 | 0 | 7 | 100 | 450 | 132 | 0 | 0 | 4 |  | 7888 | 3054 | 10942 | 4443 | 709 | 1729 | 3009 | 530 | 118 | 168 | 132 | 104 | 0 | 106.4
12:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 411 | 320 |  | 0 | 280 | 265 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 102 | 48 | 50 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 21 | 33 | 25 | 51 | 0 | 43 | 75 | 115 | 0 | 9 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 85 | 35 | 50 | 21 | 2 | 0 | 0 | 0 | 320 | 305 | 205 | 36 | 139 | 23 | 52 | 0 | 35 | 0 | 0 | 8 | 0 | 8 | 33 | 12 | 140 | 152 | 0 | 18 | 2 | 43 | 0 | 50 | 0 | 110 | 162 | 25 | 70 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 8 | 0 | 258 | 0 | 0 | 168 | 0 | 149 | 16 | 90 | 193 | 110 | 316 | 115 | 105 | 105 | 3 | 304 | 54 | 108 | 17 | 47 | 90 | 320 | 94 | 57 | 108 | 108 | 0 | 17 | 24 |  | 709 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 8 | 0 | 16 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 50 | 0 | 173 | 0 | 356 | 85 | 0 | 94 | 0 | 104 | 0 | 7 | 113 | 460 | 132 | 0 | 0 | 5 |  | 8239 | 3219 | 11458 | 4413 | 709 | 1820 | 3436 | 540 | 118 | 168 | 140 | 114 | 0 | 106.4
13:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 409 | 315 |  | 0 | 280 | 245 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 45 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 21 | 33 | 33 | 51 | 0 | 43 | 75 | 115 | 0 | 24 | 0 | 0 | 0 | 0 |  | 0 | 0 | 85 | 92 | 70 | 50 | 21 | 6 | 0 | 0 | 0 | 315 | 300 | 208 | 36 | 134 | 23 | 51 | 0 | 35 | 0 | 0 | 8 | 0 | 8 | 33 | 12 | 140 | 141 | 0 | 0 | 2 | 44 | 0 | 50 | 0 | 110 | 162 | 25 | 77 | 0 | 180 | 18 | 0 | 0 | 260 | 21 | 8 | 0 | 245 | 0 | 0 | 167 | 0 | 149 | 17 | 100 | 200 | 113 | 318 | 106 | 105 | 105 | 6 | 304 | 54 | 110 | 34 | 48 | 90 | 320 | 94 | 56 | 108 | 108 | 0 | 17 | 34 |  | 709 | 0 | 320 | 0 | 0 | 160 | 0 | 0 | 3 | 0 | 0 | 86 | 23 | 0 | 0 | 0 | 0 | 43 | 0 | 0 | 27 | 0 | 0 | 27 | 0 | 19 | 0 | 8 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 176 | 0 | 0 | 0 | 193 | 0 | 295 | 105 | 0 | 94 | 0 | 103 | 0 | 7 | 113 | 450 | 174 | 0 | 0 | 4 |  | 8384 | 3220 | 11604 | 4289 | 709 | 1731 | 3519 | 531 | 118 | 441 | 140 | 126 | 0 | 106.39
14:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 408 | 315 |  | 0 | 280 | 265 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 10 | 0 | 0 | 0 | 17 | 17 | 17 | 18 | 25 | 28 | 33 | 33 | 51 | 0 | 39 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 50 | 83 | 50 | 21 | 4 | 0 | 0 | 0 | 320 | 310 | 203 | 36 | 137 | 23 | 53 | 0 | 35 | 0 | 48 | 16 | 0 | 8 | 33 | 12 | 146 | 139 | 0 | 0 | 2 | 44 | 0 | 49 | 0 | 110 | 160 | 25 | 76 | 0 | 213 | 18 | 0 | 0 | 280 | 16 | 8 | 0 | 260 | 0 | 0 | 165 | 0 | 149 | 8 | 100 | 200 | 117 | 316 | 115 | 105 | 105 | 4 | 305 | 54 | 105 | 34 | 49 | 100 | 320 | 94 | 45 | 126 | 108 | 0 | 17 | 29 |  | 709 | 0 | 320 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 84 | 24 | 0 | 0 | 0 | 0 | 50 | 5 | 0 | 27 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 174 | 0 | 40 | 0 | 171 | 0 | 402 | 105 | 0 | 96 | 0 | 103 | 0 | 7 | 113 | 420 | 176 | 0 | 0 | 4 |  | 8498 | 3266 | 11764 | 4303 | 709 | 1898 | 3518 | 498 | 114 | 479 | 146 | 99 | 0 | 106.39
15:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 406 | 314 |  | 0 | 280 | 280 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 34 | 0 | 0 | 0 | 17 | 17 | 17 | 18 | 25 | 28 | 33 | 33 | 51 | 0 | 40 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 11 | 0 | 101 | 50 | 85 | 50 | 21 | 3 | 0 | 0 | 0 | 320 | 310 | 202 | 36 | 142 | 23 | 52 | 0 | 35 | 0 | 48 | 16 | 19 | 8 | 33 | 12 | 154 | 154 | 0 | 18 | 1 | 43 | 0 | 50 | 0 | 110 | 160 | 25 | 71 | 0 | 221 | 18 | 0 | 0 | 300 | 16 | 8 | 0 | 260 | 0 | 0 | 167 | 0 | 149 | 4 | 90 | 200 | 118 | 316 | 115 | 105 | 105 | 1 | 304 | 54 | 110 | 34 | 48 | 100 | 320 | 94 | 38 | 139 | 108 | 0 | 17 | 22 |  | 709 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 85 | 20 | 0 | 0 | 0 | 0 | 50 | 7 | 0 | 27 | 0 | 0 | 8 | 0 | 18 | 0 | 8 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 177 | 0 | 43 | 0 | 169 | 0 | 407 | 105 | 0 | 113 | 0 | 105 | 0 | 6 | 113 | 450 | 176 | 0 | 0 | 4 |  | 8619 | 3407 | 12026 | 4451 | 709 | 1915 | 3598 | 528 | 115 | 480 | 154 | 76 | 0 | 106.4
16:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 410 | 314 |  | 0 | 280 | 265 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 72 | 98 | 50 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 28 | 33 | 33 | 41 | 0 | 40 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 10 | 50 | 50 | 21 | 3 | 0 | 0 | 0 | 310 | 305 | 203 | 36 | 139 | 23 | 47 | 0 | 35 | 0 | 48 | 16 | 19 | 8 | 33 | 12 | 150 | 154 | 0 | 18 | 1 | 43 | 0 | 50 | 0 | 110 | 161 | 25 | 72 | 0 | 221 | 18 | 0 | 5 | 280 | 16 | 8 | 0 | 260 | 0 | 0 | 100 | 0 | 149 | 2 | 90 | 180 | 118 | 316 | 115 | 70 | 105 | 0 | 287 | 54 | 110 | 34 | 47 | 100 | 320 | 93 | 15 | 144 | 108 | 0 | 17 | 6 |  | 709 | 0 | 405 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 8 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 41 | 0 | 164 | 0 | 340 | 35 | 0 | 113 | 0 | 101 | 0 | 5 | 113 | 430 | 176 | 0 | 0 | 2 |  | 8245 | 3219 | 11464 | 4421 | 709 | 1829 | 3252 | 502 | 115 | 455 | 150 | 31 | 0 | 106.4
17:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 408 | 314 |  | 0 | 280 | 245 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 48 | 82 | 50 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 28 | 33 | 33 | 25 | 0 | 40 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 0 | 0 | 102 | 10 | 11 | 25 | 21 | 6 | 0 | 0 | 0 | 315 | 305 | 208 | 36 | 137 | 23 | 48 | 0 | 35 | 0 | 48 | 16 | 19 | 8 | 33 | 19 | 140 | 167 | 0 | 0 | 0 | 44 | 0 | 50 | 0 | 110 | 160 | 25 | 77 | 0 | 220 | 18 | 0 | 6 | 290 | 16 | 8 | 0 | 260 | 0 | 0 | 100 | 0 | 149 | 1 | 90 | 136 | 118 | 316 | 115 | 70 | 68 | 0 | 304 | 54 | 51 | 34 | 50 | 100 | 321 | 94 | 8 | 151 | 108 | 0 | 17 | 1 |  | 709 | 0 | 340 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 86 | 22 | 0 | 0 | 0 | 0 | 50 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 173 | 0 | 10 | 0 | 164 | 0 | 320 | 17 | 0 | 70 | 0 | 54 | 0 | 3 | 50 | 370 | 199 | 0 | 0 | 0 |  | 7973 | 2894 | 10867 | 4365 | 709 | 1822 | 2821 | 443 | 115 | 439 | 140 | 13 | 0 | 106.41
18:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 339 | 320 |  | 0 | 280 | 285 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 72 | 150 | 55 | 0 | 0 | 0 | 17 | 17 | 35 | 19 | 25 | 17 | 33 | 33 | 51 | 0 | 40 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 1 | 0 | 102 | 50 | 42 | 30 | 21 | 5 | 0 | 0 | 0 | 290 | 290 | 204 | 36 | 140 | 23 | 50 | 0 | 35 | 0 | 48 | 16 | 19 | 8 | 33 | 20 | 164 | 165 | 0 | 0 | 0 | 44 | 0 | 50 | 0 | 110 | 161 | 25 | 78 | 0 | 195 | 18 | 0 | 8 | 290 | 16 | 8 | 0 | 275 | 0 | 0 | 108 | 0 | 149 | 0 | 55 | 147 | 118 | 317 | 115 | 80 | 84 | 0 | 304 | 54 | 65 | 34 | 95 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 710 | 0 | 335 | 0 | 0 | 150 | 0 | 0 | 23 | 0 | 0 | 85 | 26 | 0 | 0 | 0 | 0 | 50 | 33 | 93 | 27 | 0 | 24 | 0 | 28 | 21 | 0 | 8 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 0 | 11 | 0 | 148 | 0 | 383 | 35 | 0 | 75 | 0 | 88 | 0 | 0 | 95 | 380 | 222 | 0 | 1 | 0 |  | 8204 | 3285 | 11489 | 4185 | 710 | 1925 | 3236 | 453 | 115 | 701 | 164 | 0 | 0 | 106.41
18:30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19:00 | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 378 | 320 |  | 0 | 280 | 285 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 54 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 0 | 102 | 50 | 85 | 50 | 21 | 2 | 0 | 0 | 0 | 315 | 295 | 208 | 36 | 138 | 23 | 52 | 0 | 35 | 0 | 48 | 16 | 22 | 8 | 33 | 20 | 128 | 162 | 0 | 14 | 0 | 44 | 0 | 50 | 0 | 163 | 160 | 25 | 78 | 0 | 221 | 18 | 0 | 8 | 280 | 16 | 8 | 0 | 281 | 0 | 0 | 170 | 50 | 149 | 0 | 100 | 197 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 34 | 95 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 86 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 94 | 27 | 50 | 35 | 43 | 29 | 21 | 0 | 11 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 50 | 187 | 0 | 402 | 98 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 500 | 223 | 0 | 35 | 0 |  | 8793 | 3923 | 12716 | 4449 | 709 | 1994 | 4003 | 572 | 120 | 741 | 128 | 0 | 0 | 106.42
19:30 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 379 | 320 |  | 0 | 280 | 300 | 0 | 0 | 55 | 255 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 50 | 85 | 50 | 21 | 5 | 0 | 0 | 0 | 310 | 295 | 206 | 36 | 140 | 23 | 52 | 0 | 35 | 0 | 48 | 16 | 22 | 11 | 33 | 20 | 130 | 163 | 0 | 21 | 0 | 44 | 0 | 50 | 0 | 163 | 160 | 25 | 78 | 0 | 221 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 281 | 0 | 0 | 189 | 0 | 149 | 0 | 100 | 200 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 34 | 95 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 716 | 0 | 390 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 94 | 27 | 50 | 38 | 43 | 29 | 21 | 0 | 11 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 30 | 191 | 0 | 339 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 530 | 222 | 0 | 17 | 0 |  | 8815 | 3853 | 12668 | 4460 | 716 | 1933 | 3963 | 602 | 120 | 744 | 130 | 0 | 0 | 0
20:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 379 | 320 |  | 0 | 280 | 295 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 50 | 85 | 50 | 21 | 8 | 0 | 0 | 0 | 310 | 295 | 206 | 36 | 140 | 23 | 54 | 0 | 35 | 0 | 41 | 16 | 22 | 11 | 33 | 20 | 128 | 170 | 0 | 21 | 0 | 44 | 0 | 50 | 0 | 163 | 161 | 25 | 78 | 0 | 221 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 281 | 0 | 0 | 189 | 0 | 149 | 0 | 100 | 200 | 120 | 316 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 34 | 95 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 716 | 0 | 390 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 87 | 33 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 27 | 50 | 40 | 43 | 28 | 21 | 0 | 11 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 30 | 192 | 0 | 351 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 530 | 221 | 0 | 17 | 0 |  | 8816 | 3832 | 12648 | 4464 | 716 | 1959 | 3955 | 601 | 120 | 705 | 128 | 0 | 0 | 106.41
21:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 398 | 321 |  | 0 | 305 | 270 | 0 | 0 | 55 | 269 | 0 | 0 | 0 | 102 | 150 | 50 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 24 | 0 | 102 | 70 | 85 | 50 | 21 | 17 | 0 | 0 | 0 | 315 | 295 | 208 | 36 | 138 | 23 | 55 | 0 | 35 | 0 | 48 | 16 | 22 | 11 | 33 | 20 | 130 | 171 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 161 | 25 | 78 | 0 | 221 | 18 | 0 | 8 | 280 | 16 | 11 | 0 | 281 | 0 | 0 | 190 | 0 | 149 | 0 | 100 | 200 | 122 | 316 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 52 | 96 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 716 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 10 | 0 | 38 | 43 | 28 | 21 | 0 | 11 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 30 | 193 | 0 | 326 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 530 | 221 | 0 | 17 | 0 |  | 8910 | 3760 | 12670 | 4527 | 716 | 1961 | 3904 | 602 | 120 | 710 | 130 | 0 | 0 | 106.42
22:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 317 |  | 0 | 305 | 283 | 0 | 0 | 55 | 275 | 0 | 0 | 0 | 102 | 150 | 51 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 30 | 33 | 33 | 25 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 7 | 0 | 34 | 100 | 85 | 50 | 0 | 32 | 0 | 0 | 0 | 330 | 315 | 206 | 36 | 139 | 23 | 55 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 20 | 132 | 167 | 0 | 0 | 0 | 43 | 0 | 50 | 0 | 163 | 162 | 25 | 78 | 0 | 220 | 18 | 0 | 8 | 290 | 16 | 11 | 0 | 281 | 0 | 0 | 191 | 0 | 149 | 0 | 90 | 200 | 127 | 317 | 115 | 105 | 105 | 0 | 304 | 54 | 110 | 52 | 92 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 716 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 87 | 34 | 0 | 0 | 0 | 0 | 50 | 0 | 94 | 0 | 0 | 0 | 52 | 28 | 21 | 0 | 11 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 30 | 188 | 0 | 360 | 105 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 530 | 223 | 0 | 17 | 0 |  | 8805 | 3752 | 12557 | 4518 | 716 | 2018 | 3895 | 602 | 120 | 556 | 132 | 0 | 0 | 106.42
23:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 327 |  | 0 | 305 | 260 | 0 | 0 | 55 | 275 | 0 | 0 | 0 | 102 | 150 | 10 | 0 | 0 | 0 | 17 | 17 | 17 | 21 | 25 | 30 | 33 | 33 | 25 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 |  | 16 | 0 | 34 | 100 | 85 | 50 | 21 | 34 | 0 | 0 | 0 | 340 | 300 | 209 | 36 | 137 | 23 | 56 | 0 | 35 | 0 | 0 | 16 | 22 | 11 | 33 | 20 | 132 | 167 | 0 | 21 | 0 | 44 | 0 | 50 | 0 | 163 | 161 | 25 | 78 | 0 | 220 | 17 | 0 | 9 | 280 | 16 | 11 | 70 | 281 | 0 | 0 | 192 | 0 | 149 | 0 | 90 | 200 | 123 | 316 | 115 | 52 | 105 | 0 | 305 | 54 | 110 | 52 | 83 | 100 | 320 | 93 | 0 | 162 | 108 | 0 | 17 | 0 |  | 716 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 14 | 0 | 0 | 87 | 24 | 0 | 0 | 0 | 0 | 50 | 0 | 91 | 0 | 0 | 0 | 52 | 27 | 21 | 0 | 11 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 183 | 0 | 11 | 30 | 185 | 0 | 314 | 105 | 0 | 113 | 0 | 106 | 0 | 0 | 113 | 520 | 225 | 0 | 0 | 0 |  | 8740 | 3651 | 12391 | 4551 | 716 | 1968 | 3775 | 593 | 120 | 536 | 132 | 0 | 0 | 106.42
24:00 | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 399 | 327 |  | 0 | 305 | 260 | 0 | 0 | 55 | 275 | 0 | 0 | 0 | 102 | 150 | 10 | 0 | 0 | 0 | 17 | 17 | 17 | 22 | 25 | 30 | 33 | 33 | 25 | 0 | 44 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 24 | 0 | 17 | 100 | 46 | 50 | 21 | 33 | 0 | 0 | 0 | 335 | 300 | 207 | 36 | 140 | 23 | 56 | 0 | 35 | 0 | 0 | 23 | 22 | 11 | 33 | 20 | 128 | 171 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 9 | 280 | 16 | 11 | 70 | 281 | 0 | 0 | 192 | 0 | 149 | 0 | 100 | 200 | 128 | 316 | 115 | 17 | 105 | 0 | 303 | 54 | 110 | 52 | 60 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 717 | 0 | 410 | 0 | 0 | 140 | 0 | 0 | 4 | 0 | 0 | 87 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 0 | 0 | 0 | 52 | 0 | 21 | 0 | 11 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 0 | 12 | 0 | 188 | 0 | 365 | 105 | 0 | 113 | 0 | 113 | 0 | 0 | 113 | 520 | 225 | 0 | 0 | 0 |  | 8624 | 3535 | 12159 | 4558 | 717 | 2027 | 3659 | 593 | 119 | 358 | 128 | 0 | 0 | 106.42
KWH | 0 | 0 | 0 | 0 | 7382709 | 0 | 0 | 9666560 | 7606000 |  | 0 | 6795000 | 6474124 | 0 | 0 | 1323073 | 6614803 | 0 | 0 | 0 | 1996704 | 1968000 | 591427 | 0 | 0 | 0 | 436680 | 555036 | 523595 | 461196 | 600000 | 616680 | 805000 | 791200 | 667200 | 0 | 967920 | 1808000 | 2800000 | 0 | 316935 | 0 | 0 | 0 | 0 |  | 233040 | 0 | 1053673 | 935760 | 866880 | 781920 | 478176 | 409920 | 0 | 0 | 0 | 7896000 | 7414000 | 5021000 | 903272 | 3252490 | 496368 | 1277280 | 0 | 790236 | 0 | 379064 | 318398 | 192780 | 234900 | 802100 | 396090 | 3036480 | 4144080 | 0 | 341208 | 14750 | 1026000 | 0 | 1209000 | 0 | 3355281 | 3657000 | 594528 | 1835520 | 0 | 3933750 | 386000 | 0 | 70740 | 7037000 | 480500 | 201264 | 113472 | 5928980 | 68889 | 27070 | 3446400 | 60336 | 3241730 | 96795 | 2223360 | 3719040 | 2898836 | 7598000 | 2727600 | 1621200 | 2093418 | 26281 | 7118291 | 1300159 | 1997227 | 710220 | 1571640 | 2292480 | 7679700 | 2160000 | 421150 | 3136320 | 2492782 | 0 | 432360 | 203103 |  | 17205818 | 0 | 9704736 | 0 | 0 | 3378240 | 0 | 0 | 167040 | 0 | 0 | 2083690 | 594393 | 0 | 0 | 0 | 0 | 525003 | 142019 | 615304 | 218380 | 90165 | 124672 | 380160 | 177373 | 463920 | 0 | 203526 | 1856727 | 0 | 0 | 0 | 0 | 0 | 0 | 4498418 | 0 | 501977 | 230400 | 4615009 | 0 | 8910618 | 1657440 | 0 | 2226048 | 0 | 2414332 | 0 | 46535 | 2158176 | 11915600 | 4476218 | 0 | 114000 | 38940 |  | 194631129 | 81734877 | 276366006 | 107069461 | 17205818 | 46236375 | 76891683 | 13772327 | 2775920 | 8530388 | 3036480 | 847554 | 0
Fuel Cost | 0 | 0 | 0 | 0 | 8194806.99 | 0 | 0 | 9763225.6 | 7834180 |  | 0 | 7406550 | 7186277.64 | 0 | 0 | 11193197.58 | 6879395.12 | 0 | 0 | 0 | 18209940.48 | 19365120 | 5452956.94 | 0 | 0 | 0 | 3187764 | 4290428.28 | 5162646.7 | 345897 | 450000 | 0 | 0 | 0 | 6451824 | 0 | 261338.4 | 488160 | 5068000 | 0 | 2944326.15 | 0 | 0 | 0 | 0 |  | 0 | 0 | 10220628.1 | 8936508 | 7541856 | 6192806.4 | 602501.76 | 1217462.4 | 0 | 0 | 0 | 5843040 | 7414000 | 4619320 | 1165220.88 | 3740363.5 | 560895.84 | 1788192 | 0 | 1351303.56 | 0 | 3828546.4 | 3040700.9 | 244830.6 | 176175 | 1403675 | 297067.5 | 22773600 | 4392724.8 | 0 | 433334.16 | 235115 | 1682640 | 0 | 2152020 | 0 | 3825020.34 | 3803280 | 1171220.16 | 3505843.2 | 0 | 6805387.5 | 845340 | 0 | 144309.6 | 7107370 | 360375 | 152960.64 | 1930158.72 | 44823088.8 | 1169735.22 | 452610.4 | 17921280 | 1008817.92 | 31898623.2 | 1131533.55 | 18120384 | 40351584 | 20436793.8 | 7066140 | 24875712 | 15320340 | 18233670.78 | 0 | 53814279.96 | 11324384.89 | 17555625.33 | 7087995.6 | 13468954.8 | 15267916.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99105511.68 | 0 | 10189972.8 | 0 | 0 | 46822406.4 | 0 | 0 | 1752249.6 | 0 | 0 | 2354569.7 | 921309.15 | 0 | 0 | 0 | 0 | 5166029.52 | 1442913.04 | 5445440.4 | 1681526 | 1219030.8 | 1208071.68 | 3683750.4 | 1720518.1 | 890726.4 | 0 | 154069.182 | 11196063.81 | 0 | 0 | 0 | 0 | 0 | 0 | 5937911.76 | 0 | 752965.5 | 3919104 | 5399560.53 | 0 | 8821511.82 | 17303673.6 | 0 | 21125195.52 | 0 | 18735216.32 | 0 | 514211.75 | 15948920.64 | 52309484 | 0 | 0 | 0 | 0 |  | 622971298.89 | 345721914.102 | 968693212.992 | 106352680.142 | 99105511.68 | 48883984.85 | 528469606.57 | 63505547.81 | 749498.4 | 96971923.24 | 22773600 | 1880860.3 | 0
Yesterday Day Peak | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 411 | 320 |  | 0 | 280 | 265 | 0 | 0 | 40 | 250 | 0 | 0 | 0 | 102 | 48 | 50 | 0 | 0 | 0 | 17 | 17 | 17 | 19 | 25 | 21 | 33 | 25 | 51 | 0 | 43 | 75 | 115 | 0 | 9 | 0 | 0 | 0 | 0 |  | 19 | 0 | 0 | 85 | 35 | 50 | 21 | 2 | 0 | 0 | 0 | 320 | 305 | 205 | 36 | 139 | 23 | 52 | 0 | 35 | 0 | 0 | 8 | 0 | 8 | 33 | 12 | 140 | 152 | 0 | 18 | 2 | 43 | 0 | 50 | 0 | 110 | 162 | 25 | 70 | 0 | 220 | 18 | 0 | 0 | 290 | 24 | 8 | 0 | 258 | 0 | 0 | 168 | 0 | 149 | 16 | 90 | 193 | 110 | 316 | 115 | 105 | 105 | 3 | 304 | 54 | 108 | 17 | 47 | 90 | 320 | 94 | 57 | 108 | 108 | 0 | 17 | 24 |  | 709 | 0 | 395 | 0 | 0 | 120 | 0 | 0 | 0 | 0 | 0 | 86 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 0 | 0 | 8 | 0 | 16 | 0 | 8 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 0 | 50 | 0 | 173 | 0 | 356 | 85 | 0 | 94 | 0 | 104 | 0 | 7 | 113 | 460 | 132 | 0 | 0 | 5 |  | 11458 | DayPeak
Yesterday Evening Peak | 0 | 0 | 0 | 0 | 300 | 0 | 0 | 378 | 320 | 0 | 0 | 280 | 285 | 0 | 0 | 55 | 250 | 0 | 0 | 0 | 102 | 150 | 54 | 0 | 0 | 0 | 17 | 55 | 35 | 21 | 25 | 29 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 16 | 0 | 102 | 50 | 85 | 50 | 21 | 2 | 0 | 0 | 0 | 315 | 295 | 208 | 36 | 138 | 23 | 52 | 0 | 35 | 0 | 48 | 16 | 22 | 8 | 33 | 20 | 128 | 162 | 0 | 14 | 0 | 44 | 0 | 50 | 0 | 163 | 160 | 25 | 78 | 0 | 221 | 18 | 0 | 8 | 280 | 16 | 8 | 0 | 281 | 0 | 0 | 170 | 50 | 149 | 0 | 100 | 197 | 123 | 316 | 115 | 105 | 105 | 0 | 305 | 54 | 110 | 34 | 95 | 100 | 320 | 94 | 0 | 162 | 108 | 0 | 17 | 0 |  | 709 | 0 | 410 | 0 | 0 | 170 | 0 | 0 | 30 | 0 | 0 | 86 | 33 | 0 | 0 | 0 | 0 | 50 | 33 | 94 | 27 | 50 | 35 | 43 | 29 | 21 | 0 | 11 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 0 | 11 | 50 | 187 | 0 | 402 | 98 | 0 | 113 | 0 | 104 | 0 | 0 | 113 | 500 | 223 | 0 | 35 | 0 |  | 12716 | EvPeak
Forecast for Evening | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 325 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 300 | 0 | 0 | 0 | 102 | 149 | 63 | 0 | 0 | 0 | 54 | 55 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 45 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 102 | 100 | 86 | 50 | 21 | 15 | 0 | 0 | 0 | 330 | 300 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 50 | 8 | 22 | 11 | 33 | 20 | 164 | 170 | 8 | 22 | 0 | 43 | 0 | 50 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 341 | 24 | 11 | 200 | 300 | 300 | 100 | 170 | 100 | 149 | 0 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 0 | 300 | 54 | 110 | 114 | 95 | 100 | 320 | 94 | 0 | 162 | 116 | 0 | 17 |  |  | 721 | 0 | 410 | 0 | 0 | 225 | 0 | 0 | 32 | 40 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 36 | 94 | 27 | 50 | 35 | 52 | 34 | 22 | 0 | 11 | 80 | 0 | 0 | 15 | 10 | 0 | 0 | 220 | 0 | 91 | 100 | 220 | 0 | 400 | 105 | 180 | 113 | 100 | 113 | 0 | 0 | 113 | 622 | 220 |  | 150
Forecast for Day | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 412 | 325 | 0 | 0 | 280 | 305 | 0 | 0 | 55 | 280 | 0 | 0 | 0 | 102 | 149 | 63 | 0 | 0 | 0 | 17 | 17 | 55 | 22 | 25 | 30 | 33 | 33 | 51 | 0 | 44 | 75 | 115 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 22 |  | 0 | 100 | 85 | 50 | 21 | 5 | 0 | 0 | 0 | 150 | 300 | 210 | 63 | 140 | 23 | 51 | 0 | 43 | 0 | 0 | 8 | 22 | 11 | 33 | 20 | 138 | 170 | 8 | 22 | 1.6 | 43 | 0 | 50 | 0 | 163 | 160 | 30 | 78 | 0 | 220 | 18 | 0 | 0 | 341 | 24 | 11 | 150 | 250 | 100 | 100 | 170 | 50 | 149 | 20 | 100 | 200 | 135 | 316 | 115 | 100 | 105 | 5 | 300 | 54 | 110 | 114 | 90 | 100 | 320 | 94 | 50 | 162 | 116 | 0 | 17 | 30 |  | 721 | 0 | 400 | 0 | 0 | 225 | 0 | 0 | 4 | 0 | 0 | 87 | 33 | 110 | 0 | 0 | 0 | 50 | 34 | 90 | 27 | 0 | 0 | 52 | 0 | 22 | 0 | 11 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 81 | 50 | 200 | 0 | 400 | 88 | 100 | 113 | 100 | 113 | 0 | 8 | 113 | 622 | 220 |  | 0 | 6
Generation at 08:00(Today) | 0 | 0 | 0 | 0 | 310 | 0 | 0 | 361 | 293 | 0 | 0 | 305 | 260 | 0 | 0 | 55 | 254 | 0 | 0 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 17 | 17 | 17 | 0 | 25 | 30 | 33 |  | 0 | 0 | 40 | 75 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 7 | 0 | 0 | 0 | 0 | 305 | 180 | 80 | 137 | 20 | 56 | 0 | 35 | 0 | 0 | 0 | 19 | 8 | 33 | 20 | 84 | 198 | 0 | 21 | 0 | 43 | 0 | 50 | 0 | 130 | 160 | 25 | 78 | 0 | 220 | 18 | 0 | 9 | 270 | 14 | 8 | 0 | 170 | 0 | 0 | 50 | 0 | 105 | 9 | 100 | 120 | 120 | 317 | 115 | 5 | 51 | 2 | 25 | 54 | 17 | 0 | 47 | 100 | 320 | 35 | 7 | 35 | 53 | 0 | 17 | 3 | 0 | 709 | 0 | 350 | 0 | 0 | 120 | 0 | 0 | 4 | 0 | 0 | 87 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 11 | 79 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 11 | 0 | 188 | 0 | 391 | 0 | 0 | 35 | 0 | 0 | 0 | 3 | 35 | 330 | 224 | 0 | 0 | 0 | 0
199
| Minimum Generation |  | 9805 | 8:00
| Highest Generation |  | 12716 | 19:00
| Day Peak Generation |  | 11458 | 12:00
| Evening Peak Generation |  | 12716 | 19:00
| HVDC Max Flow |  | 720 | 2:00
| HVDC EvPeak Flow |  | 709 | 19:00
| Load factor L.F |  | 90.56%

## P1
POWER GRID COMPANY OF BANGLADESH LTD.
|  |  | NATIONAL LOAD DESPATCH CENTER |  |  |  |  | QF-LDC-08
|  |  | DAILY REPORT |  |  |  |  | Page -1
[6 empty] | Reporting Date : | 2021-09-28
Till now the maximum generation is : - |  |  | 13792 | 20:00 | Hrs on | 2021-04-27
The Summary of Yesterday's |  | 2021-09-27 | Generation & Demand |  | Today's Actual Min Gen. & Probable Gen. & Demand
Day Peak Generation : |  | 11458 | MW Hour : | 12:00 | Min. Gen. at | 8:00 | 9181 | MW
Evening Peak Generation : |  | 12716 | MW Hour : | 19:00 | Available Max Generation : |  | 14934 | MW
E.P. Demand (at gen end) : |  | 12716 | MW Hour : | 19:00 | Max Demand (Evening) : |  | 13200 | MW
Maximum Generation : |  | 12716 | MW Hour : | 19:00 | Reserve(Generation end) |  | 1734 | MW
Total Gen. (MKWH) : |  | 276.366 | System Load Factor : | 90.56% | Load Shed : |  | 0 | MW
EXPORT / IMPORT THROUGH EAST-WEST INTERCONNECTOR
Export from East grid to West grid :- Maximum |  |  | -296 | MW at | 2:00 | Energy |  | MKWHR.
Import from West grid to East grid :- Maximum |  |  | - | MW at | - | Energy | - | MKWHR.
| Water Level of Kaptai Lake at 6:00 A M on |  | 2021-09-28
Actual : | 106.44 | Ft.(MSL) , | Rule curve : | 105.28 | Ft.( MSL )
Gas Consumed : | Total = | 1160.49 | MMCFD. | Oil Consumed (PDB) :
[6 empty] | HSD : |  | Liter
[6 empty] | FO : |  | Liter
Cost of the Consumed Fuel (PDB+Pvt) : |  | Gas : | 155236664.992
: |  | Coal : | 63505547.81 | Oil : | 625441529.81 | Total : | 844183742.612
Load Shedding & Other Information
Area | Yesterday |  |  |  | Today
|  |  | Estimated Demand (S/S end) |  | Estimated Shedding (S/S end) |  | Rates of Shedding
| MW |  | MW |  |  | MW | (On Estimated Demand)
Dhaka | 0 | 0:00 | 4692.7898 |  |  | 0 | 0%
Chittagong Area | 0 | 0:00 | 1601.2084 |  |  | 0 | 0%
Khulna Area | 0 | 0:00 | 1435.5919 |  |  | 0 | 0%
Rajshahi Area | 0 | 0:00 | 1297.52 |  |  | 0 | 0%
Cumilla Area | 0 | 0:00 | 1172.3617 |  |  | 0 | 0%
Mymensingh Area | 0 | 0:00 | 946.068 |  |  | 0 | 0%
Sylhet Area | 0 | 0:00 | 522.0455 |  |  | 0 | 0%
Barisal Area | 0 | 0:00 | 243.4032 |  |  | 0 | 0%
Rangpur Area | 0 | 0:00 | 729.6879 |  |  | 0 | 0%
Total | 0 |  | 12640.6765 |  |  | 0
Information of the Generating Units under shut down.
| Planned Shut- Down |  |  | Forced Shut- Down
1) Barapukuria ST: Unit-2 ,3
2) Ghorasal-3,4,5
3) Ashuganj-3,4,5
4) Baghabari-71 MW & 100 MW
5) Bhola 225 MW GT-2
6) Shahjinazar 8 & 9
7) Raozan #02
8) Fenchuganj 3,4
Additional Information of Machines, lines, Interruption / Forced Load shed etc.
a) Barisal(N)-Bhola P/P 230 kV Ckt-2 tripped at 12:24 from both end showing Dist. Z1 R,Y-phase
relays and was switched on at 12:54.
b) Aminbazar 230 kV Bus-2 was shutdown at 11:17 for C/M.
c) Aminbazar 230/132 T2 transformer was under shut down from 11:22 to 15:30 for C/M.
d) Chowmuhoni 132/33 T1 transformer was under shut down from 09:06 to 11:36 for C/M.
e) Chowmuhoni 132/33 T2 transformer was under shut down from 12:55 to 14:56 for C/M.
f) Haripur-Fatulla 132 kV Ckt was switched on at 11:07.
g) Mirpur 132 kV reserve Bus was under shut down from 08:20 to 17:28 for C/M.
h) 33 kV end of Tangail 132/33 kV T-1 & T2 transformers tripped at 12:40 showing O/C, E/F relays & 33 kV
new REB feeder fault and was switched on at 13:40.
i) Tangail-Kaliakoir 132 kV Ckt-1 tripped at 16:58 from both end showing Dist. Z1 relay and was
switched on at 17:56.
j) 33 kV end of Barapukuria 132/33 kV T-4 transformer tripped at 16:36 due to R/H maintenance at 33 kV |  |  |  |  | About 25 MW power interruption occurred under Barapukuria S/S area
breaker and was switched on at 17:55. |  |  |  |  | from 16:36 to 17:56.
k) Satkhira 132/33 kV T-1 & T2 transformers tripped at 19:25 showing O/C, E/F relays at 33 kV end and
l) 33 kV end of B.Baria 132/33 kV T-1 & T2 transformers tripped at 05:18(28-09-2021) showing O/C, E/F
relays at 33 kV end and was switched on at 05:36(28-09-2021).
m) Bhulta132/33 kV T-1 transformer tripped at 05:38(28-09-2021) by 132 kV mechanical protection.
n) Kodda-Rajendrapur 132 kV Ckt-1 & 2 tripped at 06:09(28-09-2021) showing Dist. Z1 & main protection |  |  |  |  | About 82 MW power interruption occurred under Kodda S/S area
relays at Kodda end and were switched on at 06:24, 06:31(28-09-2021) respectively. |  |  |  |  | from 06:09 to 06:24.
o) Cumilla(N)-Choddagram 132 kV Ckt-1 tripped at 03:20(28-09-20210 showing Dist. A-phase at
Cumilla(N) end and was switched on at 03:33(28-09-2021).
p) UMPL-Sherpur 132 kV Ckt-1 was shut down at 07:12(28-09-20210 for C/M.
q) Kabirpur 132/33 kV T-2 & T3 transformers were shut down at 07:22(28-09-2021) due to 33 kV |  |  |  |  | About 80 MW power interruption occurred under Kabirpur S/S area
Bus maintenance. |  |  |  |  | from 07:22(28-09-2021) to till.
r) Norail 132/33 kV T-2 transformer was shut down at 06:45(28-09-2021) due to R/H maintenance at 33 kV |  |  |  |  | About 14 MW power interruption occurred under Norail S/S area
end. |  |  |  |  | from 06:45(28-09-2021) to till.
s) Ashuganj-Sirajganj 230 kV Ckt-1 tripped at 07:01(28-09-2021) showing Dist. Z1, RST at Ashuganj end
and was switched on at 07:34(28-09-2021).

## P2
EVENING PEAK GENERATION AND DAY LONG ENERGY DATA OF POWER STATIONS
| Date : | 2021-09-27 | [5 empty] | Page -2
Sl. |  |  |  |  | Present | Peak | Energy
No. | Name of the Power Stations |  | Producer | Installed Capacity | Capacity | Hour | Generated | Remarks
Generation
|  |  |  | Unit No. X Capacity | MW | MW | KWH
1 | Ghorasal Repowered CCPP:Unit-3 (GT |  | PDB | 1*260 | 260 | 0 | 0 | Under maint.
2 | Ghorasal Repowered CCPP Unit-4 |  | PDB | 1*210 | 180 | 0 | 0 | Under maint.
| Ghorasal TPP Unit-5 |  | PDB | 1*210 | 190 | 0 | 0 | Gas shortage
3 | Ghorasal 365 MW CCPP Unit-7 |  | PDB | 1*243+1*122 | 365 | 300 | 7382709 | Machine problem
| Ghorashal 78.5 MW PP(MAX) |  | QRPP | 2*40 | 0 | 0 | 0 | Contract Expired
4 | Ghorashal 108MW PP (Regent) |  | IPP | 34*3.35 | 108 | 0 | 0 | Gas shortage
5 | Haripur GTPP |  | SBU, PDB | 2*32 | 20 | 0 | 0 | Under maint.
6 | Haripur 412 MW CCPP |  | EGCB | 1*273+1*139 | 412 | 378 | 9666560 | Gas shortage
7 | Haripur 360MW CCPP(HPL) |  | IPP | 1*235+1*125 | 360 | 320 | 7606000 | Gas shortage
8 | Meghnaghat 450 MW CCPP(MPL) |  | IPP | 2*150+1*150 | 450 | 280 | 6795000 | Dirty Gas
9 | Meghnaghat 100 MW(IEL) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
10 | Meghnaghat CCPP(Summit) |  | IPP | 2*110+1*110 | 305 | 285 | 6474124 | FGMO
11 | Madanganj 102 PP(Summit) |  | QRPP | 6*17 | 0 | 0 | 0 | Contract Expired
12 | Madanganj-55 MW PP(Summit) |  | (IPP) | 3*17.08+1*11.3 | 55 | 55 | 1323073
13 | Keraniganj 100 MW PP (Powerpac) |  | QRPP | 8*13.45 | 100 | 54 | 591427 | Engine problem
14 | Narshingdi 22 MW PP (Doreen) |  | SIPP, REB | 8*2.90 | 22 | 21 | 461196
15 | 210 MW Siddhirgonj TPP |  | PDB | 1*210 | 115 | 0 | 0 | Under maint.
16 | Siddhirgonj 2*120 MW GTPP |  | EGCB | 2*105 | 210 | 0 | 0 | Gas shortage
17 | Siddhirganj 100 PP(Dutch Bangla) |  | QRPP | 12*8.9 | 0 | 0 | 0 | Contract Expired
18 | Siddhirganj 335 MW CCPP |  | EGCB | 1*217+118 | 335 | 250 | 6614803 | Gas shortage
19 | Gagnagar 102 MW PP (Digital Power) |  | IPP | 12*8.924 | 102 | 102 | 1996704
20 | Katpotti 52 MW PP (Sinha) |  | IPP | 7*7.9 | 51 | 0 | 0 | Fuel shortage
21 | Kamalaghat 54 MW PP(Banco Energy) |  | IPP | 3*18 | 54 | 17 | 436680 | Engine problem
22 | Kodda 150MW PP |  | BPDB-RPCL | 9*17.06 | 149 | 150 | 1968000
23 | Manikganj 55 MW PP (Northern) |  | IPP | 3*19.3 | 55 | 55 | 555036
24 | Nababganj 55 MW PP (Southern power ) |  | IPP | 3*19.3 | 55 | 35 | 523595 | Engine problem
25 | Bosila 108MW PP(CLC) |  | IPP | 12*8.775+1*3.5 | 108 | 0 | 0 | Fuel shortage
26 | Summit Power,(Madhabdi+Ashulia) |  | SIPP,REB | 3*3.67+4*8.73 | 80 | 54 | 1216680 | Engine problem
27 | Maona 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 805000
28 | Rupganj 33 MW PP(Summit) |  | SIPP,REB | 4*8.73 | 33 | 33 | 791200
29 | Gazipur 52 MW PP |  | IPP | 6*8.9 | 52 | 51 | 667200
30 | Tongi 80 MW GTPP |  | PDB | 1* 105 | 105 | 0 | 0 | Under maint.
31 | Kodda 300 MW PP Unit-2 (Summit) |  | IPP | 18*17.076 | 300 | 281 | 5928980 | Engine problem
32 | Keranigonj 300 MW PP (APR) |  | IPP | 256*1.4 | 300 | 0 | 68889 | Reserve.
33 | Bramhangoan 100 MW PP (Aggreko) |  | IPP | 100 | 100 | 0 | 27070 | Reserve.
34 | Aurahati 100MW PP (Aggreko) |  | IPP | 0.85*23+0.95*91 | 100 | 50 | 60336 | Low demand
35 | Kodda 149 MW PP Unit-1 (Summit) |  | IPP | 149 | 149 | 149 | 3241730
36 | Gazipur 100 MW PP |  | RPCL | 100 MW | 105 | 105 | 1621200
37 | Meghnaghat 104 MW PP (OPCL) |  | IPP | 18.5*6 | 104 | 94 | 2160000 | Engine problem
38 | Manikgonj 162MW PP(MPGL) |  | IPP | 9*18 | 162 | 162 | 3136320
39 | Spectra Solar Plant Ltd. |  | IPP | 35 | 35 | 0 | 203103
| Dhaka area Total |  |  |  | 5719 | 3314 | 72322615
40 | Chattogram TPP-1 |  | PDB | 1*210 | 180 | 115 | 2800000 | Gas shortage
| Chattogram TPP-2 |  | PDB | 1*210 | 180 | 0 | 0 | Gas shortage
41 | Raozan 25 MW PP |  | IPP | 3*8.9 | 25 | 25 | 316935
42 | Teknaf 20MW PP (Solartech) |  | Teknaf Solartech Energy Ltd. | 20 | 20 | 0 | 96795
43 | Patenga 50MW PP (Baraka) |  | IPP | 8*6.98 | 50 | 50 | 781920
44 | Kaptai Hydro: Unit-1,2,3,4, 5 |  | PDB | 2*40+3*50 | 230 | 120 | 2775920 | Low water level
45 | Sikalbaha 225MW |  | PDB | 1*150+1*175 | 225 | 0 | 0 | Under maint.
46 | Sikalbaha Peaking GT |  | PDB | 1*150 | 150 | 0 | 0 | Under maint.
47 | Sikalbaha 105 MW PP (Baraka Sikalbaha) |  | IPP | 105 MW | 105 | 105 | 2093418
48 | Hathazari 100 MW peaking PP |  | PDB | 11*8.9 | 98 | 0 | 0 | Under S/D
49 | Dohazari -Kalaish 100 MW Peaking |  | PDB | 6*17 | 102 | 102 | 1053673
50 | Juldah 100 MW Unit-1 (Acorn) |  | QRPP | 8*13.45 | 100 | 50 | 935760 | Low demand
51 | Juldah 100 MW PP Unit-3 (Acorn) |  | IPP | 0 | 100 | 100 | 2223360
52 | Barabkunda 22 MW PP (Regent) |  | SIPP, PDB | 8*2.90 | 22 | 21 | 478176
* | Malancha, Ctg. EPZ (United) |  |  | 5*8.73+3*9.34 | 0 | 2 | 409920
53 | Chattogram 108 MW PP (ECPV) |  | IPP | 16*7 | 108 | 85 | 866880 | Engine problem
54 | Kaptai 7 MW Solar PP |  | PDB | 7.4 MW | 7 | 0 | 26281
55 | Anwara 300 MW PP (United) |  | IPP | 300 MW | 300 | 305 | 7118291
56 | Jodiac Power |  | IPP | 3*18.55+1*3.6 | 54 | 54 | 1300159
57 | Karnaphuli Power Ltd. |  | IPP | 110 | 110 | 110 | 1997227
58 | Juldah unit-2 (Acorn) |  | IPP | 8*13.6 | 100 | 100 | 2292480
59 | Anlima Energy Ltd. |  | IPP | 6*21.2 | 116 | 108 | 2492782 | Engine problem
| Chattogram area Total |  |  |  | 2382 | 1452 | 30059977
60 | Ashuganj TPP Unit- 3 |  | APSCL | 1*150 | 135 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 4 |  | APSCL | 1*150 | 129 | 0 | 0 | Gas shortage
| Ashuganj TPP Unit- 5 |  | APSCL | 1*150 | 134 | 0 | 0 | Gas shortage
61 | Ashuganj 225 MW CCPP |  | APSCL | 1*142+1*75 | 221 | 208 | 5021000 | FGMO
62 | Ashuganj 450 MW CCPP(North) |  | APSCL | 1*360 | 360 | 315 | 7896000 | FGMO
63 | Ashuganj 450 MW CCPP(South) |  | APSCL | 1*360 | 360 | 295 | 7414000 | FGMO
64 | Ashuganj 50 MW PP |  | APSCL | 14*3.968 | 45 | 23 | 496368 | Engine problem
65 | Ashuganj 55 MW PP (Precision) |  | RPP | 15*4 | 55 | 52 | 1277280
66 | Ashuganj 195MW PP (APSCL-United) |  | IPP | 20*9.73+1*16 | 195 | 36 | 903272 | Gas shortage
67 | Ashuganj 51 MW PP (Midland) |  | IPP | 6*9.34 | 51 | 35 | 790236 | Engine problem
68 | Ashuganj 150MW PP (Midland) |  | IPP | 23*7.015 | 150 | 123 | 2898836 | Engine problem
69 | Titas 50 MW Peaking PP |  | PDB | 6*8.92 | 52 | 48 | 379064
70 | Chandpur 150 MW CCPP |  | PDB | 1*106+1*57 | 163 | 138 | 3252490 | Machine problem
71 | Chandpur 200MW (Desh energy) |  | IPP | 0 | 200 | 197 | 3719040
72 | Feni 22MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 22 | 192780
73 | Feni 11 MW PP (Doreen) |  | SIPP, REB | 4*2.90 | 11 | 8 | 234900
** | Impoprt (Tripura) |  | Imported power | 0 | 160 | 128 | 3036480
74 | Jangalia 33MW PP (Summit) |  | SIPP, PDB | 4*8.73 | 33 | 33 | 802100
75 | Jangalia 52 MW PP (Lakdanavi) |  | IPP | 6*8.92 | 52 | 16 | 318398 | Fuel shortage
76 | Cumilla 25 MW PP (Summit) |  | SIPP, PDB | 3*3.67+2*6.97 | 25 | 20 | 396090 | Engine problem
77 | Daudkandi 200 MW PP (B.Trac) |  | IPP | 154*1.4 | 200 | 0 | 113472 | Reserve.
78 | Feni Lanka Power |  | IPP | 7*18.415+1*9.78 | 114 | 34 | 710220 | Fuel shortage
79 | Chowmuhani 113 MW |  | IPP | 12*9.78+2*3.1 | 113 | 95 | 1571640 | Engine problem
80 | Bhairob 54.5 MW |  | IPP | 3*18.2 | 54 | 17 | 432360 | 33 kV feeder fault.
| Cumilla Area Total |  |  |  | 3034 | 1843 | 41856026
81 | RPCL 210MW CCPP |  | IPP | 4*35+1*70 | 202 | 162 | 4144080 | Gas shortage
82 | Tangail 22 MW PP (Doreen) |  | SIPP, PDB | 8*2.90 | 22 | 14 | 341208
83 | Jamalpur 95 MW PP(Powerpac) |  | IPP | 12*8.924 | 95 | 0 | 0 | Engine problem
84 | Sarishabari 3 MW Solar Plant |  | IPP | 1*3 | 3 | 0 | 14750
85 | Mymensingh 200 MW PP (United) |  | IPP | 200 | 200 | 170 | 3446400 | Engine problem
86 | Jamalpur 115 MW PP (United) |  | IPP | 115 MW | 115 | 115 | 2727600
87 | Sutiakhali 50 MW Solar PP |  | IPP | 50 | 50 | 0 | 421150
88 | Tangail Palli Power Gen 22 MW |  | IPP | 4*6.7 | 22 | 16 | 233040 | Engine problem
| Mymensingh Area Total |  |  |  | 709 | 477 | 11328228
89 | Fenchugonj CCPP Phase-1 |  | PDB | 2*32+1*33 | 70 | 44 | 1026000 | Machine problem
90 | Fenchugonj CCPP Phase-2 |  | PDB | 2*35+1*35 | 90 | 0 | 0 | Under maint.
91 | Kushiara 163 MW CCPP (KP) |  | IPP | 1*109+1*54 | 163 | 163 | 3355281
92 | Shajibazar 330 MW CCPP |  | PDB | 3*110 | 330 | 160 | 3657000 | GT-2 under maint.
93 | Fenchugonj 51 MW PP (Barakatullah) |  | RPP | 19*2.90 | 51 | 50 | 1209000
| Fenchuganj 44MW (Energyprima) |  | RPP | 12*3.3+5*2 | 0 | 0 | 0 | Contract Expired
94 | Hobiganj 11MW PP Cofidence-E |  | SIPP, REB | 4*2.90 | 11 | 8 | 201264
95 | Shahjibazar GTPP Unit- 8 & 9 |  | PDB | 2*35 | 66 | 25 | 594528 | Gas shortage
96 | Shahjibazar 86MW PP (Shahjibazar) |  | RPP | 32*2.90 | 86 | 78 | 1835520
97 | Shahjibazar 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Under Shut down
98 | Sylhet 225 MW CCPP |  | PDB | 1*142+1*89 | 231 | 221 | 3933750
99 | Sylhet 20 MW GTPP |  | PDB | 1*20 | 20 | 18 | 386000
| Sylhet 50MW PP (EPL) |  | RPP | 27*2 | 0 | 0 | 0 | Contract Expired
100 | Shahjahanulla 25 MW PP |  | SIPP, REB | 3*9.34 | 25 | 16 | 480500
101 | Bibiana-II 341 MW CCPP (Summit) |  | IPP | 1*222+1*119 | 341 | 280 | 7037000 | FGMO
102 | Bibiyana-III 400 MW CCPP |  | PDB | 400 MW | 400 | 316 | 7598000 | Gas shortage
103 | Sylhet 10MW PP (Desh) |  | RPP | 6*1.95 | 10 | 8 | 70740 | Gas shortage
104 | Bibiyana South 400 MW |  | PDB | 400 MW | 383 | 320 | 7679700 | Gas shortage
| Sylhet Area Total |  |  |  | 2377 | 1707 | 39064283
105 | Bheramara GTPP Unit-3 |  | PDB | 1*20 | 16 | 0 | 0 | Reserve.
** | Bheramara (HVDC ) |  | Imported power | 2*500 | 1000 | 709 | 17205818
106 | Khulna 115 PP MW (KPCL-2) |  | QRPP | 7*17 | 0 | 0 | 0 | Contract Expired
107 | Faridpur 50 MW Peaking PP |  | PDB | 8*6.89 | 54 | 30 | 167040 | Engine problem
108 | Khulna 225 MW CCPP |  | NWPGCL | 1*150+1*75 | 230 | 170 | 3378240 | Low demand
109 | Gopalganj 100 MW Peaking PP |  | PDB | 16*6.98 | 109 | 0 | 0 | Line O/L
110 | Bheramara 410 MW CCPP |  | NWPGCL | 1*278+1*132 | 410 | 410 | 9704736 | FGMO
| Noapara 40 MW PP (Khanjahan Ali) |  | QRPP | 5*8.5 | 0 | 0 | 0 | Contract Expired
111 | Noapara 100 MW PP (Bangla Trac) |  | IPP | 70*1.4 | 100 | 50 | 230400 | Low demand
112 | Rupsha 105 MW PP (Orion rupsha) |  | IPP | 6*18.445 | 105 | 98 | 1657440
113 | Madhumati 100 MW PP |  | NWPGCL | 100 MW | 105 | 0 | 0 | Line O/L
| Khulna Area Total |  |  |  | 2129 | 1467 | 32343674
114 | Barisal 110 MW PP (Summit ) |  | IPP | 7*17.076 | 110 | 0 | 0 | Line O/L
115 | Bhola 33 MW PP (Venture) |  | RPP | 1*34.50 | 33 | 33 | 594393
116 | Bhola 225 MW CCPP |  | PDB | 2*63+1*68 | 194 | 86 | 2083690 | Machine problem
117 | Bhola 95 MW PP (Aggreko) |  | QRPP | 96*1.10 | 95 | 11 | 501977 | Engine problem
118 | Payra 1320 MW |  | BCPCL | 2*622 | 1244 | 500 | 11915600 | Line O/L
119 | Bhola Nutan Biddut BD LTD |  | IPP | 220 | 220 | 223 | 4476218
120 | United Payra Power Ltd. |  | IPP | 8*18.5+1*9.5 | 150 | 35 | 114000 | Line O/L
| Barisal Area Total |  |  |  | 2046 | 888 | 19685878
121 | Baghabari 71 MW GTPP |  | PDB | 1*71 | 71 | 0 | 0 | Gas shortage
| Baghabari 100 MW GTPP |  | PDB | 1*100 | 100 | 0 | 0 | Gas shortage
122 | Baghabari 50 MW Peaking PP |  | PDB | 6*8.9 | 52 | 50 | 525003
123 | Bera 70 MW Peaking PP |  | PDB | 9*8.29 | 71 | 33 | 142019 | Engine problem
124 | Amnura 50 MW PP(Sinha) |  | QRPP | 7*7.79 | 50 | 27 | 218380 | Fuel shortage
125 | Katakhali 50 MW PP (Northern) |  | QRPP | 6*8.9 | 50 | 50 | 90165
126 | Katakhali 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 35 | 124672 | Engine problem
127 | Sirajgonj Unit-1 225MW |  | NWPGCL | 1*150+1*75 | 210 | 0 | 0 | Gas shortage
128 | Sirajgonj Unit-2 225MW |  | NWPGCL | 1*150+1*75 | 220 | 184 | 4498418 | FGMO
129 | Sirajgonj Unit-3 225MW |  | NWPGCL | 1*141 | 220 | 187 | 4615009 | FGMO
130 | Sirajgonj 400 MW CCPP Unit-4 |  | SNWPGCL | 1*282+1*132 | 414 | 402 | 8910618 | FGMO
131 | Santahar 50 MW Peaking PP |  | PDB | 6*8.7 | 50 | 29 | 177373 | Engine problem
132 | Bogra 22 MW PP (GBB) |  | RPP | 6*4 | 22 | 21 | 463920
133 | Bogura 20 MW PP (Energyprima) |  | RPP | 5*3.3+5*2 | 0 | 0 | 0 | Contract Expired
134 | Ullapara 11 MW PP (Summit) |  | SIPP, REB | 4*2.90 | 11 | 11 | 203526
135 | Natore 52 MW PP (Rajlanka) |  | IPP | 6*8.92 | 52 | 43 | 380160
136 | Chapainawabganj 100 MW Peaking PP |  | PDB | 12*8.924 | 104 | 94 | 615304 | Engine problem
137 | Baghabari 200 MW PP (Paramount) |  | IPP | 200 MW | 200 | 0 | 0 | Reserve.
138 | Bagura 113 MW PP (Confidence)-2 |  | IPP | 113 MW | 113 | 113 | 2226048
139 | Confidence Power Bogura Unit-1 113 MW |  | IPP | 6*18.55 | 113 | 113 | 2158176
140 | Sirajgonj 6.55 MW Solar |  | NWPGCL | 1*6 | 6 | 0 | 38940
| Rajshahi Area Total |  |  |  | 2179 | 1392 | 25387731
141 | Barapukuria TPP Unit-1 |  | PDB | 1*125 | 85 | 72 | 1856727
| Barapukuria TPP Unit-2 |  | PDB | 1*125 | 85 | 0 | 0 | Under maint.
142 | Barapukuria 275 MW TPP Unit-3 |  | PDB | 1*275 | 274 | 0 | 0 | Under maint.
143 | Rangpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
144 | Saidpur 20 MW GTPP |  | PDB | 1*20 | 20 | 0 | 0 | Reserve.
145 | Rangpur 113 MW PP (Confidence) |  | IPP | 113 MW | 113 | 104 | 2414332
146 | Sympa Solar Power 8MW |  | IPP | 8 MW | 8 | 0 | 46535
| Rangpur Area Total |  |  |  | 605 | 176 | 4317594
| Total |  |  |  | 21180 | 12716 | 276366006
| Eastern Grid Total |  |  |  | 14221 | 8793 | 194631129
| Western Grid Total |  |  |  | 6959 | 3923 | 81734877
| National Grid Total |  |  |  | 21180 | 12716 | 276366006
*Data collected from respective power station over telephone.
Executive Engineer
Network Operation Division
Page- 3

## P3
POWER GRID COMPANY OF BANGLADESH LTD.
NATIONAL LOAD DESPATCH CENTER
MAXIMUM LOAD SERVED BY DIFFERENT GRID SUB-STATIONS
QF-LDC-09
Date: | 2021-09-27
(a) ENTIRE EASTERN GRID : |  | 8588 | MW | (b) ENTIRE WESTERN GRID : |  | 3580 | MW
i) Dhaka area |  | 4560 | MW | i) Khulna area |  | 1358 | MW
ii) Chittagong area |  | 1316 | MW | ii) Rajshahi area |  | 1162 | MW
iii) Comilla area |  | 1193 | MW | iii) Barisal area |  | 365 | MW
iv) Mymensingh area |  | 962 | MW | iv) Rangpur area |  | 695 | MW
v) Sylhet area |  | 557 | MW
| SYSTEM TOTAL DEMAND ( a + b ) = |  | 12168 | MW
MAXIMUM LOAD SERVED BY DIFFERENT SUB-STATIONS
Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour | Sub-station | Load (MW) | Hour
Siddhirganj | 130 | 15:00 | Kishoreganj | 140 | 0:00 | Jessore | 105 | 20:00
Munsiganj | 97 | 21:00 | Netrokona | 123 | 19:00 | Benapol | 54 | 21:00
Sonargaon | 72 | 15:00 | Jamalpur | 152 | 1:00 | Jhenida(Old) | 104 | 19:00
Shyampur | 182 | 6:00 | Sherpur | 140 | 21:00 | Bottail | 114 | 20:00
Bhulta | 207 | 15:00 | Srimongal | 61 | 19:30 | G.K Project | 50 | 21:00
Madanganj | 59 | 18:00 | Shahjibazar | 129 | 21:00 | Faridpur | 140 | 20:00
Shitalakhya | 119 | 15:00 | Fenchuganj | 47 | 1:00 | Rajbari | 54 | 19:30
Rahim steel | 18 | 5:00 | Kulawara | 50 | 18:00 | Madaripur | 99 | 21:00
Matuail | 60 | 9:00 | Sylhet | 162 | 18:00 | Sariatpur | 68 | 20:00
Ghorasal | 82 | 19:30 | Chatak | 34 | 19:00 | Gopalganj | 90 | 20:00
Narsingdi | 189 | 21:00 | Sunamganj | 58 | 20:00 | Bagerhat | 90 | 21:00
Haripur (SBU) | 126 | 16:00 | Biani Bazar | 71 | 20:00 | Mongla | 38 | 1:00
Sreenagar | 41 | 21:00 | Comilla (S) | 164 | 18:00 | Satkhira | 97 | 20:00
Ullon | 76 | 13:00 | Comilla(N) | 139 | 22:00 | Gallamari | 35 | 13:00
Hasnabad | 79 | 14:00 | Chandpur | 80 | 22:00 | Magura | 52 | 18:30
Magbazar | 96 | 15:00 | Feni | 117 | 21:00 | Norail | 39 | 19:30
Maniknagar | 76 | 13:00 | Chowmuhani | 222 | 21:00 | Chuadanga | 90 | 1:00
Bangabhaban | 14 | 11:00 | Ashuganj | 48 | 23:00 | Barisal(N) | 44 | 22:00
Motijheel | 31 | 13:00 | Daudkandi | 154 | 21:00 | Barisal (S) | 106 | 18:30
Narinda | 70 | 13:00 | B.Baria | 174 | 21:00 | Patuakhali | 116 | 21:00
Kazla | 82 | 13:00 | Ramganj | 90 | 21:00 | Bhandaria | 50 | 22:00
Dhanmondi | 224 | 13:00 | Chaddagram | 46 | 21:00 | Borguna | 16 | 18:30
Lalbag | 78 | 13:00 | PHP | 9 | 4:00 | Borhan Uddin | 45 | 1:00
Madartek | 75 | 23:00 | Kochua | 60 | 21:00 | Ishurdi | 65 | 18:30
Dhaka University | 36 | 12:00 | Madunaghat | 65 | 19:00 | Ruppur Paromanobik | 4 | 8:00
Aftabnagar | 16 | 13:00 | Hathazari | 102 | 19:00 | Natore | 132 | 18:30
Fatullah | 62 | 10:00 | Khulshi | 209 | 12:00 | Bogra | 170 | 19:00
Nawabganj | 51 | 21:00 | Halishahar | 145 | 18:00 | Noagaon | 100 | 18:30
Keraniganj | 70 | 18:30 | Baraulia | 163 | 12:00 | Rajshahi | 147 | 18:30
Mirpur | 126 | 18:00 | Sikalbaha | 41 | 17:00 | Rajshahi New | 20 | 1:00
Kalyanpur | 96 | 18:30 | Dohazari | 86 | 22:00 | C.Nawabganj | 61 | 15:00
Gulshan | 132 | 13:00 | Cox'sbazar | 105 | 13:00 | Amnura | 44 | 1:00
Uttara | 91 | 13:00 | Chandraghona | 28 | 18:30 | Pabna | 116 | 18:30
Uttara New | 31 | 15:00 | Kaptai | 4.5 | 18:30 | Shahjadpur | 96 | 21:00
Kamrangirchar | 97 | 12:00 | A. Khaer Stl. | 0 | 1:00 | Serajganj | 106 | 19:30
Savar | 162 | 18:30 | Bakulia | 125 | 18:30 | Niyamatpur | 75 | 1:00
Bhasantec | 142 | 18:00 | Julda | 23 | 15:00 | Joypurhat | 69 | 20:00
Agargaon | 96 | 13:00 | TK chemical | 31 | 18:30 | Sherpur(Bogura) | 54 | 21:00
Satmosjid | 107 | 18:00 | Modern Steel | 0 | 1:00 | Mohastangor | 66 | 1:00
Tongi | 131 | 18:00 | Shahmirpur | 28 | 18:00 | Bhangura | 30 | 19:30
Kabirpur | 245 | 15:00 | Khagrachhari | 26 | 13:00 | Rangpur | 116 | 7:00
Basundhara | 209 | 14:00 | Matarbari | 40 | 21:00 | Lalmonirhat | 40 | 1:00
Manikganj | 68 | 21:00 | Baroiar Hat | 60 | 20:00 | Saidpur | 100 | 21:00
Joydevpur | 186 | 16:00 | Rangamati | 14 | 18:30 | Purbasadipur | 104 | 21:00
New Tongi | 93 | 16:00 | Abul Khair 230 | 152 | 15:00 | Thakurgaon | 93 | 20:00
Kodda | 295 | 18:00 | BSRM | 156 | 3:00 | Palashbari | 126 | 21:00
Dhamrai | 104 | 9:00 | GPH Ispat | 22 | 19:30 | Barapukuria | 60 | 21:00
Rajendrapur | 110 | 19:00 | Agrabad | 0 | 1:00 | Panchagar | 49 | 18:30
Valuka | 120 | 15:00 | Goalpara | 30 | 13:00 | Joldhaka | 51 | 4:00
Tangail | 186 | 1:00 | Central S/S | 93 | 18:30 | Kurigram | 57 | 3:00
Mymensing | 230 | 19:30 | Noapara | 46 | 1:00 | Mithapukur | 42 | 21:00
Sub Divisional Engineer |  |  | Executive Engineer |  | Superintendent Engineer

## Voltage
e
MAXIMUM & MINIMUM VOLTAGES OF DIFFERENT GRID SUB-STATIONS:
| Date: | 2021-09-27 | [7 empty] | QF-LDC-10
| Sub-Station | Max Voltage | Hour | Min | Hour | Sub-Station | Maxm | Hour | Min | Hour
|  |  |  | Voltage |  |  | Voltage |  | Voltage
| 400 KV | KV | Hour | KV |  |  | KV |  | KV
| Bibiyana | 410 | 6:00 | 400 | 24:00 | Kaliakoir | 397 | 0.375 | 387 | 0.58333
| Bheramara | 401 | 8:00 | 396 | 19:30 | Bhulta | 390 | 0.25 | 379 | 0.77083
| Ashuganj(N) | 397 | 6:00 | 389 | 15:00 | Gopalganj | 404 | 0.625 | 388 | 0.041667
| Payra | 410 | 6:00 | 400 | 1:00
| 230 KV | KV |  | KV |  | 230 KV | KV |  | KV
| Ghorasal | 235 | 1:00 | 235 | 1:00 | Hathazari | 237 | 8:00 | 228 | 6:00
| Ishurdi | 233 | 11:00 | 224 | 1:00 | Megnaghat | 242 | 7:00 | 230 | 17:00
| Ashuganj | 244 | 6:00 | 238 | 21:00 | Fenchuganj | 244 | 6:00 | 239 | 18:00
| Serajganj | 230 | 11:00 | 224 | 1:00 | Siddhirganj | 234 | 1:00 | 228 | 15:00
| Baghabari | 232 | 13:00 | 224 | 1:00 | Maniknagar | 231 | 1:00 | 226 | 12:00
| Barapukuria | 236 | 18:00 | 224 | 1:00 | Agargaon | 230 | 9:00 | 223 | 12:00
| Bogra | 225 | 18:00 | 213 | 1:00 | Barisal | 240 | 1:00 | 230 | 18:30
| Rajshahi | 230 | 19:30 | 216 | 2:00 | Bhola 225 MW | 246 | 7:00 | 236 | 4:00
| Khulna South | 234 | 16:00 | 222 | 1:00 | AKSML | 235 | 1:00 | 230 | 3:00
| Rampura | 230 | 2:00 | 226 | 12:00 | BSRM | 235 | 17:00 | 230 | 10:00
| Haripur | 230 | 6:00 | 226 | 11:00 | Bibiyana | 245 | 6:00 | 238 | 24:00
| Hasnabad | 230 | 7:00 | 224 | 9:00 | Bhulta | 234 | 6:00 | 228 | 12:00
| Shyampur | 230 | 6:00 | 224 | 12:00 | Ashuganj (S) | 240 | 6:00 | 234 | 23:00
| Aminbazar | 232 | 1:00 | 224 | 2:00 | Kaliakoir | 231 | 6:00 | 225 | 12:00
| Tongi | 227 | 7:00 | 217 | 15:00 | GPH | 236 | 13:00 | 230 | 5:00
| Comilla (N) | 235 | 6:00 | 230 | 10:00 | Jhenaidah | 232 | 13:00 | 221 | 3:00
| 132 kV | KV |  | KV |  | 132 kV | KV |  | KV
| Siddhirganj | 134 | 1:00 | 129 | 15:00 | Madanhat | 140 | 0.5 | 134 | 0.29167
| Munsiganj | 135 | 3:00 | 130 | 12:00 | Hathazari | 139 | 0.875 | 134 | 0.083333
| Sonargaon | 134 | 4:00 | 130 | 10:00 | Khulshi | 136 | 0.875 | 132 | 0.29167
| Shyampur | 138 | 6:00 | 132 | 12:00 | Halishahar | 137 | 0.875 | 130 | 0.41667
| Bhulta | 128 | 4:00 | 123 | 12:00 | Baraulia | 138 | 0.95833 | 132 | 0.33333
| Madanganj | 136 | 6:00 | 129 | 15:00 | Sikalbaha | 138 | 0.54167 | 133 | 0.41667
| Shitalakhya | 136 | 3:00 | 129 | 16:00 | Dohazari | 134 | 0.54167 | 127 | 0.91667
| Rahim steal | 134 | 5:00 | 130 | 9:00 | Cox'sbazar | 126 | 0.58333 | 116 | 0.041667
| Matuail | 134 | 1:00 | 129 | 15:00 | Chandraghona | 137 | 0.45833 | 133 | 0.41667
| Ghorasal | 140 | 13:00 | 138 | 23:00 | Kaptai | 135 | 0.29167 | 134 | 0.041667
| Narsinghdi | 135 | 7:00 | 123 | 21:00 | A. Khaer Stl. | 136 | 0.77083 | 133 | 0.16667
| Haripur (SBU) | 135 | 6:00 | 130 | 12:00 | Bakulia | 137 | 0.58333 | 132 | 0.375
| Sreenagar | 136 | 6:00 | 131 | 12:00 | Julda | 138 | 0.58333 | 133 | 0.41667
| Ullon | 135 | 5:00 | 128 | 12:00 | TK Chemical | 138 | 0.875 | 133 | 0.29167
| Hasnabad | 136 | 4:00 | 135 | 1:00 | Modern Steel | 137 | 0.54167 | 132 | 0.20833
| Magbazar | 135 | 4:00 | 129 | 11:00 | Shahmirpur | 138 | 0.875 | 133 | 0.375
| Maniknagar | 135 | 1:00 | 130 | 13:00 | Khagrachhari | 136 | 0.54167 | 132 | 0.41667
| Bangabhaban | 135 | 1:00 | 130 | 13:00 | Matarbari | 130 | 0.54167 | 120 | 0.041667
| Motijheel | 135 | 1:00 | 130 | 13:00 | Baroiar Hat | 134 | 0.625 | 130 | 0.16667
| Narinda | 135 | 1:00 | 130 | 13:00 | Rangamati | 136 | 18:30 | 133 | 10:00
| Kazla | 135 | 1:00 | 130 | 13:00 | Agrabad | 0 | #N/A | 0 | #N/A
| Dhanmondi | 135 | 5:00 | 128 | 12:00 | Goalpara S/S | 138 | 11:00 | 133 | 0.041667
| Lalbag | 136 | 6:00 | 131 | 10:00 | Khulna Central S/S | 137 | 11:00 | 132 | 0.041667
| Madartek | 136 | 6:00 | 128 | 12:00 | Noapara | 137 | 17:00 | 129 | 0.041667
| Dhaka University | 136 | 6:00 | 129 | 11:00 | Jessore | 135 | 17:00 | 124 | 0.041667
| Aftabnagar | 135 | 3:00 | 128 | 14:00 | Benapol | 135 | 0.70833 | 123 | 0.875
| Fatullah | 138 | 5:00 | 132 | 12:00 | Jhenida(Old) | 133 | 17:00 | 121 | 0.041667
| Nawabganj | 135 | 6:00 | 131 | 10:00 | Bottail | 134 | 0.70833 | 126 | 0.91667
| Keraniganj | 136 | 6:00 | 131 | 12:00 | G.K Project | 139 | 0.41667 | 132 | 0.041667
| Mirpur | 134 | 4:00 | 128 | 12:00 | Faridpur | 135 | 0.25 | 128 | 0.95833
| Kalyanpur | 134 | 2:00 | 129 | 12:00 | Rajbari | 135 | 0.375 | 127 | 0.083333
| Gulshan | 135 | 6:00 | 128 | 12:00 | Madaripur | 138 | 0.33333 | 130 | 0.041667
| Uttara | 135 | 9:00 | 129 | 20:00 | Shariyatpur S/S | 138 | 7:00 | 131 | 0.875
| Uttara New | 136 | 19:00 | 130 | 18:00 | Gopalganj | 142 | 0.33333 | 131 | 0.875
| Kamrangirchar | 135 | 4:00 | 131 | 11:00 | Bagerhat | 138 | 15:00 | 125 | 0.83333
| Savar | 134 | 1:00 | 129 | 10:00 | Mongla | 135 | 12:00 | 128 | 0.79167
| Bhasantec | 137 | 6:00 | 130 | 12:00 | Satkhira | 137 | 16:00 | 129 | 1:00
| Agargaon | 137 | 3:00 | 132 | 11:00 | Gallamari | 138 | 0.45833 | 132 | 1:00
| Satmosjid | 137 | 6:00 | 131 | 12:00 | Magura | 130 | 10:00 | 118 | 0.041667
| Tongi | 138 | 19:00 | 134 | 12:00 | Narail | 132 | 0.70833 | 118 | 0.041667
| Kabirpur | 136 | 2:00 | 130 | 18:00 | Chuadanga | 137 | 18:00 | 124 | 0.041667
| Basundhara | 136 | 18:30 | 131 | 12:00 | Barisal(N) | 139 | 9:00 | 131 | 0.77083
| Manikganj | 141 | 13:00 | 135 | 22:00 | Barisal (S) | 137 | 7:00 | 130 | 1:00
| Joydevpur | 137 | 2:00 | 134 | 10:00 | Patuakhali(S) | 135 | 0.29167 | 125 | 0.083333
| New Tongi | 137 | 21:00 | 132 | 12:00 | Bhandaria | 134 | 0.29167 | 125 | 0.041667
| Kodda | 135 | 13:00 | 130 | 3:00 | Borguna | 134 | 0.16667 | 129 | 0.041667
| Dhamrai | 137 | 6.00 | 133 | 19:00 | Jhenaidah(230kV S/S) | 133 | 17:00 | 122 | 1:00
| Rajendrapur | 134 | 19:30 | 127 | 5.00 | Ishurdi | 135 | 11:00 | 130 | 1:00
| Valuka | 123 | 6:00 | 108 | 19:00 | Ruppur Paromanobik | 135 | 10:00 | 130 | 1:00
| Tangail | 135 | 7:00 | 123 | 21:00 | Natore | 135 | 18:00 | 126 | 1:00
| Mymensing | 129 | 11:00 | 114 | 20:00 | Bogra | 136 | 18:00 | 123 | 4:00
| Kishorganj | 131 | 6:00 | 118 | 20:00 | Noagaon | 129 | 20:00 | 116 | 1:00
| Netrokona | 127 | 11:00 | 109 | 19:00 | Rajshahi | 135 | 18:00 | 126 | 5:00
| Jamalpur | 137 | 11:00 | 123 | 19:00 | Rajshahi New | 136 | 18:00 | 125 | 2:00
| Sherpur | 136 | 11:00 | 118 | 18:00 | C.Nawabganj | 136 | 18:00 | 125 | 1:00
| Srimongal | 140 | 8:00 | 130 | 21:00 | Amnura | 137 | 18:00 | 121 | 2:00
| Shahjibazar | 137 | 7:00 | 128 | 22:00 | Pabna | 134 | 16:00 | 127 | 1:00
| Fenchuganj | 138 | 8:00 | 131 | 19:30 | Shahjadpur | 139 | 5:00 | 135 | 18:00
| Khulawara | 135 | 8:00 | 131 | 18:00 | Serajganj | 132 | 18:00 | 127 | 1:00
| Sylhet | 131 | 2:00 | 129 | 19:30 | Niyamatpur | 129 | 18:00 | 112 | 3:00
| Chatak | 132 | 7:00 | 127 | 19:00 | Joypurhat | 132 | 18:00 | 115 | 1:00
| Sunamganj | 130 | 6:00 | 121 | 20:00 | Sherpur(Bogura) | 136 | 18:00 | 124 | 1:00
| Biani Bazar | 131 | 6:00 | 125 | 19:30 | Mohastangor | 135 | 18:00 | 120 | 1:00
| Comilla(s) | 129 | 6:00 | 122 | 18:00 | Bangura | 135 | 6:00 | 132 | 21:00
| Comilla(n) | 138 | 17:00 | 133 | 20:00 | Rangpur | 131 | 18:00 | 117 | 1:00
| Chandpur | 139 | 17:00 | 135 | 20:00 | Lalmonirhat | 130 | 18:00 | 117 | 1:00
| Feni | 133 | 17:00 | 130 | 19:00 | Saidpur | 130 | 18:00 | 118 | 1:00
| Chowmuhani | 132 | 10:00 | 127 | 15:00 | Purbasadipur | 129 | 18:00 | 109 | 1:00
| Ashuganj | 140 | 6:00 | 134 | 23:00 | Thakurgaon | 130 | 18:00 | 112 | 1:00
| Daudkandi | 133 | 6:00 | 127 | 22:00 | Palashbari | 130 | 18:00 | 120 | 1:00
| B.Baria | 136 | 6:00 | 125 | 22:00 | Barapukuria | 136 | 18:00 | 124 | 1:00
| Ramganj | 134 | 9:00 | 130 | 20:00 | Panchagar | 133 | 0.875 | 112 | 0.083333
| Chaddagram | 136 | 17:00 | 130 | 20:00 | Joldhaka | 127 | 0.75 | 113 | 0.16667
| PHP | 133 | 8:00 | 129 | 20:00 | Kurigram | 127 | 0.45833 | 112 | 0.083333
| Kochua | 138 | 17:00 | 134 | 19:30 | Mithapukur | 131 | 0.75 | 118 | 0.083333
| Sub Assistant Engineer | [5 empty] | Sub Divisional Engineer
| Network Operation Division | [5 empty] | Network Operation Division |  |  | Page 7 of 7

## L-Curve
Date | 2021-09-27
.
TIME | E-W INT.(Export) | EAST GRID | WEST GRID | TOTAL |  |  | DAILY LOAD CURVE
0:00 | 86 | 8624 | 3535 | 12159 |  |  |  | QF-LDC-11
0:30 | 181 | 8394 | 3496 | 11890 | Date: | 2021-09-27
1:00 | 276 | 8164 | 3457 | 11621
1:30 | 286 | 8024 | 3450.5 | 11474.5
2:00 | 296 | 7884 | 3444 | 11328
2:30 | 278 | 7854.5 | 3416.5 | 11271 | [5 empty] | Gen. at Eve. Peak | 12716 | 12716 MW (19:00 )
3:00 | 260 | 7825 | 3389 | 11214 | [6 empty] | 19:00
3:30 | 254 | 7706.5 | 3314 | 11020.5 | [5 empty] | Gen. at Day Peak | 11458 | 11458 MW (12:00 )
4:00 | 248 | 7588 | 3239 | 10827 | [6 empty] | 12:00
4:30 | 256 | 7561.5 | 3169.5 | 10731 | [5 empty] | Highest Generation | 12716
5:00 | 264 | 7535 | 3100 | 10635 | [6 empty] | 19:00
5:30 | 249 | 7359.5 | 3031.5 | 10391
6:00 | 234 | 7184 | 2963 | 10147
6:30 | 228 | 7071 | 2906.5 | 9977.5
7:00 | 222 | 6958 | 2850 | 9808
7:30 | 224 | 6975 | 2831.5 | 9806.5
8:00 | 226 | 6992 | 2813 | 9805
8:30 | 165 | 7213 | 2830 | 10043
9:00 | 104 | 7434 | 2847 | 10281
9:30 | 61 | 7529 | 2901 | 10430
10:00 | 18 | 7624 | 2955 | 10579
10:30 | 21 | 7756 | 3004.5 | 10760.5
11:00 | 24 | 7888 | 3054 | 10942
11:30 | 21 | 8063.5 | 3136.5 | 11200
12:00 | 18 | 8239 | 3219 | 11458
12:30 | 121 | 8311.5 | 3219.5 | 11531
13:00 | 224 | 8384 | 3220 | 11604
13:30 | 144 | 8441 | 3243 | 11684
14:00 | 64 | 8498 | 3266 | 11764
14:30 | 43 | 8558.5 | 3336.5 | 11895
15:00 | 22 | 8619 | 3407 | 12026
15:30 | 53 | 8432 | 3313 | 11745
16:00 | 84 | 8245 | 3219 | 11464
16:30 | 83 | 8109 | 3056.5 | 11165.5
17:00 | 82 | 7973 | 2894 | 10867
17:30 | 193 | 8088.5 | 3089.5 | 11178
18:00 | 304 | 8204 | 3285 | 11489
18:30 | 241 | 8498.5 | 3604 | 12102.5
19:00 | 178 | 8793 | 3923 | 12716
19:30 | 170 | 8815 | 3853 | 12668
20:00 | 236 | 8816 | 3832 | 12648 |  |  |  | Executive Engineer
20:30 | 121 | 8863 | 3796 | 12659 |  |  |  | Network Operation Division
21:00 | 6 | 8910 | 3760 | 12670
21:30 | 13 | 8857.5 | 3756 | 12613.5
22:00 | 20 | 8805 | 3752 | 12557 |  |  |  |  | Page 6 of 7
22:30 | 33 | 8772.5 | 3701.5 | 12474
23:00 | 46 | 8740 | 3651 | 12391
23:30 | 66 | 8682 | 3593 | 12275
24:00 | 86 | 8624 | 3535 | 12159
12716 MW (19:00 )
11458 MW (12:00 )

## En-Curve
DAILY ENERGY CURVE
Date | 2021-09-27 |  | Energy | 276366006
[11 empty] | 2021-09-27 | [5 empty] | QF-LDC-12
TIME | GAS | HVDC | P.GEN(GAS). | P.GEN(OIL). | COAL | HYDRO | OIL | SHORTAGE | TRIPURA | SOLAR
0:00 | 4558 | 717 | 2027 | 3775 | 593 | 119 | 358 | 0 | 128 | 0
0:30 | 4563.5 | 713.5 | 2004.5 | 3502 | 596 | 119 | 323.5 | 0 | 126 | 0 | Date: | 2021-09-27
1:00 | 4569 | 710 | 1982 | 3229 | 599 | 119 | 289 | 0 | 124 | 0
1:30 | 4598.5 | 715 | 1980.5 | 3120 | 589 | 118.5 | 229 | 0 | 124 | 0 | [7 empty] | Total Energy | 276.366 | Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
2:00 | 4628 | 720 | 1979 | 3011 | 579 | 118 | 169 | 0 | 124 | 0 | [7 empty] | Energy not Served | 0
2:30 | 4609 | 717.5 | 1977 | 2988 | 579 | 118 | 160.5 | 0 | 122 | 0 | [7 empty] | Energy Requirement | 276.366
3:00 | 4590 | 715 | 1975 | 2965 | 579 | 118 | 152 | 0 | 120 | 0
3:30 | 4596 | 712.5 | 1988.5 | 2779.5 | 564.5 | 117.5 | 144 | 0 | 118 | 0 | [6 empty] | Shortage
4:00 | 4602 | 710 | 2002 | 2594 | 550 | 117 | 136 | 0 | 116 | 0
4:30 | 4616.5 | 709.5 | 2012 | 2496.5 | 530 | 116.5 | 136 | 0 | 114 | 0
5:00 | 4631 | 709 | 2022 | 2399 | 510 | 116 | 136 | 0 | 112 | 0
5:30 | 4578.5 | 709.5 | 1968.5 | 2274.5 | 499.5 | 115.5 | 136 | 0 | 109 | 0
6:00 | 4526 | 710 | 1915 | 2150 | 489 | 115 | 136 | 0 | 106 | 0
6:30 | 4446.5 | 709.5 | 1887 | 2087 | 485.5 | 115 | 136 | 0 | 102 | 9 |  |  |  |  | Coal
7:00 | 4367 | 709 | 1859 | 2024 | 482 | 115 | 136 | 0 | 98 | 18
7:30 | 4361.5 | 709.5 | 1819 | 2053 | 481 | 115 | 128 | 0 | 101 | 38.5 |  |  |  | Oil |  |  |  | ,
8:00 | 4356 | 710 | 1779 | 2082 | 480 | 115 | 120 | 0 | 104 | 59
8:30 | 4392.5 | 710 | 1802.5 | 2244.5 | 475 | 116 | 120 | 0 | 107 | 75.5
9:00 | 4429 | 710 | 1826 | 2407 | 470 | 117 | 120 | 0 | 110 | 92
9:30 | 4466 | 710 | 1801.5 | 2529 | 480 | 117 | 120 | 0 | 111 | 95.5
10:00 | 4503 | 710 | 1777 | 2651 | 490 | 117 | 120 | 0 | 112 | 99
10:30 | 4473 | 709.5 | 1753 | 2830 | 510 | 117.5 | 144 | 0 | 122 | 101.5
11:00 | 4443 | 709 | 1729 | 3009 | 530 | 118 | 168 | 0 | 132 | 104
11:30 | 4428 | 709 | 1774.5 | 3222.5 | 535 | 118 | 168 | 0 | 136 | 109
12:00 | 4413 | 709 | 1820 | 3436 | 540 | 118 | 168 | 0 | 140 | 114
12:30 | 4351 | 709 | 1775.5 | 3477.5 | 535.5 | 118 | 304.5 | 0 | 140 | 120
13:00 | 4289 | 709 | 1731 | 3519 | 531 | 118 | 441 | 0 | 140 | 126
13:30 | 4289 | 709 | 1731 | 3519 | 531 | 118 | 441 | 0 | 140 | 126
14:00 | 4289 | 709 | 1731 | 3519 | 531 | 118 | 441 | 0 | 140 | 126
14:30 | 4370 | 709 | 1823 | 3558.5 | 529.5 | 116.5 | 460.5 | 0 | 147 | 101
15:00 | 4451 | 709 | 1915 | 3598 | 528 | 115 | 480 | 0 | 154 | 76
15:30 | 4436 | 709 | 1872 | 3425 | 515 | 115 | 467.5 | 0 | 152 | 53.5
16:00 | 4421 | 709 | 1829 | 3252 | 502 | 115 | 455 | 0 | 150 | 31
16:30 | 4393 | 709 | 1825.5 | 3036.5 | 472.5 | 115 | 447 | 0 | 145 | 22
17:00 | 4365 | 709 | 1822 | 2821 | 443 | 115 | 439 | 0 | 140 | 13
17:30 | 4275 | 709.5 | 1873.5 | 3028.5 | 448 | 115 | 570 | 0 | 152 | 6.5
18:00 | 4185 | 710 | 1925 | 3236 | 453 | 115 | 701 | 0 | 164 | 0
18:30 | 4317 | 709.5 | 1959.5 | 3619.5 | 512.5 | 117.5 | 721 | 0 | 146 | 0
19:00 | 4449 | 709 | 1994 | 4003 | 572 | 120 | 741 | 0 | 128 | 0
19:30 | 4460 | 716 | 1933 | 3963 | 602 | 120 | 744 | 0 | 130 | 0
20:00 | 4464 | 716 | 1959 | 3955 | 601 | 120 | 705 | 0 | 128 | 0
20:30 | 4495.5 | 716 | 1960 | 3929.5 | 601.5 | 120 | 707.5 | 0 | 129 | 0
21:00 | 4527 | 716 | 1961 | 3904 | 602 | 120 | 710 | 0 | 130 | 0
21:30 | 4522.5 | 716 | 1989.5 | 3899.5 | 602 | 120 | 633 | 0 | 131 | 0
22:00 | 4518 | 716 | 2018 | 3895 | 602 | 120 | 556 | 0 | 132 | 0
22:30 | 4534.5 | 716 | 1993 | 3835 | 597.5 | 120 | 546 | 0 | 132 | 0
23:00 | 4551 | 716 | 1968 | 3775 | 593 | 120 | 536 | 0 | 132 | 0
23:30 | 4554.5 | 716.5 | 1997.5 | 3775 | 593 | 119.5 | 447 | 0 | 130 | 0 | Max Temp. in Dhaka |  | 35.9° C
24:00 | 4558 | 717 | 2027 | 3775 | 593 | 119 | 358 | 0 | 128 | 0
Executive Engineer
Network Operation Division
Page 5 of 7
00:00
00:30
01:00
01:30
02:00
02:30
03:00
03:30
04:00
04:30
05:00
05:30
06:00
06:30
07:00
07:30
08:00
08:30
09:00
09:30
10:00
10:30
11:00
11:30
12:00
12:30
13:00
13:30
14:00
14:30
15:00
15:30
16:00
16:30
17:00
17:30
18:00
18:30
19:00
19:30
20:00
20:30
21:00
21:30
22:00
22:30
23:00
23:30
24:00
GAS
Oil
HVDC
COAL
HYDRO
Total Energy Gen 184.074 MKWHr Energy Not Served 0.000 MKWHr Energy Requirement 184.074 MKWHr
SOLAR
Note on W13: Author:

## Generation
g | 2021-09-27
Si No | Unit | 1:00 | 2:00 | 3:00 | 4:00 | 5:00 | 6:00 | 7:00 | 8:00 | 9:00 | 10:00 | 11:00 | 12:00 | 13:00 | 14:00 | 15:00 | 16:00 | 17:00 | 18:00 | 18:30 | 19:00 | 19:30 | 20:00 | 21:00 | 22:00 | 23:00 | 24:00 | KWH
1 | Karnaphuli Hydro PP Unit-1, 2 & 3 | 44 | 43 | 43 | 42 | 41 | 40 | 40 | 40 | 42 | 42 | 43 | 43 | 43 | 39 | 40 | 40 | 40 | 40 |  | 45 | 45 | 45 | 45 | 45 | 45 | 44 | 967920
2 | Karnaphuli Hydro PP Unit-4 & 5 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |  | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 1808000
3 | Chattogram TPP-1 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2800000
4 | Chattogram TPP-2
5 | Raozan 25 MW PP | [9 empty] | 2 | 8 | 9 | 24 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 316935
| Teknaf 20MW PP (Solartech) | [5 empty] | 0 | 2 | 10 | 14 | 10 | 11 | 16 | 17 | 8 | 4 | 2 | 1 | [9 empty] | 96795
6 | Sikalbaha 225MW CCPP (Gas)
7 | Sikalbaha 225MW CCPP(Oil)
8
9 | Sikalbaha 150MW GTPP
10 | Sikalbaha 150MW GTPP(Oil)
| Dohazari -Kalaish 100 MW Peaking | 34 | 17 | 0 | [9 empty] | 85 | 102 | 101 | 102 | 102 | 102 |  | 102 | 102 | 102 | 102 | 34 | 34 | 17 | 1053673
12 | Hathazari 100 MW peaking PP
| Sikalbaha 105 MW PP (Baraka Sikalbaha) | 105 | 105 | 105 | 68 | 68 | 17 | 17 | 24 | 34 | 34 | 91 | 105 | 105 | 105 | 105 | 105 | 68 | 84 |  | 105 | 105 | 105 | 105 | 105 | 105 | 105 | 2093418
| Daudkandi 200 MW PP (B.Trac) | [24 empty] | 70 | 70 | 113472
14 | Titas 50 MW Peaking PP | [13 empty] | 48 | 48 | 48 | 48 | 48 |  | 48 | 48 | 41 | 48 |  |  | 0 | 379064
15 | 210 MW Siddhirgonj TPP
16 | Siddhirgonj 2*120 MW GTPP
17 | Siddhirganj 335 MW CCPP | 300 | 300 | 300 | 300 | 300 | 290 | 280 | 280 | 280 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 | 250 |  | 250 | 255 | 250 | 269 | 275 | 275 | 275 | 6614803
18 | Kodda 300 MW PP Unit-2 (Summit) | 245 | 245 | 245 | 195 | 165 | 165 | 165 | 178 | 245 | 262 | 258 | 258 | 245 | 260 | 260 | 260 | 260 | 275 |  | 281 | 281 | 281 | 281 | 281 | 281 | 281 | 5928980
19 | Ashuganj 195MW PP (APSCL-United) | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 |  | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 903272
20 | Ghorasal TPP (Unit-1&2)
21 | Ghorasal Repowered CCPP:Unit-3 (GT
22 | Ghorasal Repowered CCPP Unit-4
23 | Ghorasal TPP Unit-5
24
25 | Ghorasal 365 MW CCPP Unit-7 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 310 | 300 | 300 | 300 |  | 300 | 310 | 310 | 310 | 310 | 310 | 310 | 7382709
26
28 | Ashuganj TPP Unit- 3
29 | Ashuganj TPP Unit- 4
30 | Ashuganj TPP Unit- 5
32 | Ashuganj 50 MW PP | 23 | 23 | 20 | 20 | 20 | 20 | 20 | 23 | 23 | 23 | 20 | 23 | 23 | 23 | 23 | 23 | 23 | 23 |  | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 496368
33 | Ashuganj 225 MW CCPP | 210 | 210 | 210 | 212 | 212 | 212 | 212 | 212 | 212 | 206 | 207 | 205 | 208 | 203 | 202 | 203 | 208 | 204 |  | 208 | 206 | 206 | 208 | 206 | 209 | 207 | 5021000
34 | Ashuganj 450 MW CCPP(South) | 300 | 320 | 305 | 305 | 320 | 305 | 305 | 305 | 305 | 340 | 300 | 305 | 300 | 310 | 310 | 305 | 305 | 290 |  | 295 | 295 | 295 | 295 | 315 | 300 | 300 | 7414000
| Ashuganj 450 MW CCPP(North) | 335 | 355 | 340 | 340 | 355 | 335 | 280 | 265 | 330 | 300 | 315 | 320 | 315 | 320 | 320 | 310 | 315 | 290 |  | 315 | 310 | 310 | 315 | 330 | 340 | 335 | 7896000
35 | Ashuganj 55 MW PP (Precision) | 56 | 56 | 55 | 56 | 56 | 56 | 55 | 52 | 54 | 52 | 52 | 52 | 51 | 53 | 52 | 47 | 48 | 50 |  | 52 | 52 | 54 | 55 | 55 | 56 | 56 | 1277280
36 | Chandpur 150 MW CCPP | 141 | 134 | 137 | 141 | 141 | 138 | 141 | 139 | 138 | 140 | 140 | 139 | 134 | 137 | 142 | 139 | 137 | 140 |  | 138 | 140 | 140 | 138 | 139 | 137 | 140 | 3252490
37 | Tongi 80 MW GTPP
38 | Haripur GTPP
39 | Haripur 412 MW CCPP | 394 | 394 | 394 | 394 | 394 | 394 | 394 | 406 | 413 | 413 | 413 | 411 | 409 | 408 | 406 | 410 | 408 | 339 |  | 378 | 379 | 379 | 398 | 399 | 399 | 399 | 9666560
40 | Meghnaghat 450 MW CCPP(MPL) | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 | 280 |  | 280 | 280 | 280 | 305 | 305 | 305 | 305 | 6795000
41 | Haripur 360MW CCPP(HPL) | 328 | 329 | 329 | 329 | 330 | 330 | 293 | 293 | 314 | 320 | 320 | 320 | 315 | 315 | 314 | 314 | 314 | 320 |  | 320 | 320 | 320 | 321 | 317 | 327 | 327 | 7606000
42 | RPCL 210MW CCPP | 188 | 200 | 202 | 210 | 210 | 212 | 211 | 201 | 183 | 168 | 168 | 152 | 141 | 139 | 154 | 154 | 167 | 165 |  | 162 | 163 | 170 | 171 | 167 | 167 | 171 | 4144080
43 | Sutiakhali 50 MW Solar PP | [5 empty] | 0 | 10 | 25 | 43 | 54 | 57 | 57 | 56 | 45 | 38 | 15 | 8 | 0 | [8 empty] | 421150
44 | Fenchugonj CCPP Phase-1 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 44 | 44 | 44 | 43 | 44 | 44 | 43 | 43 | 44 | 44 |  | 44 | 44 | 44 | 43 | 43 | 44 | 43 | 1026000
45 | Fenchugonj CCPP Phase-2
46 | Shajibazar 330 MW CCPP | 160 | 163 | 160 | 161 | 159 | 160 | 160 | 160 | 161 | 162 | 161 | 162 | 162 | 160 | 160 | 161 | 160 | 161 |  | 160 | 160 | 161 | 161 | 162 | 161 | 160 | 3657000
47 | Shahjibazar GTPP Unit- 8 & 9 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 594528
48 | Shahjibazar 86MW PP (Shahjibazar) | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 75 | 75 | 75 | 71 | 70 | 77 | 76 | 71 | 72 | 77 | 78 |  | 78 | 78 | 78 | 78 | 78 | 78 | 78 | 1835520
Shahjibazar 100 MW GTPP
49 | Shahjibazar 50MW PP (EPL)
50 | Sylhet 225 MW CCPP | 220 | 220 | 220 | 220 | 220 | 159 | 159 | 159 | 187 | 220 | 220 | 220 | 180 | 213 | 221 | 221 | 220 | 195 |  | 221 | 221 | 221 | 221 | 220 | 220 | 220 | 3933750
51 | Sylhet 20 MW GTPP | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 | 18 |  | 18 | 18 | 18 | 18 | 18 | 17 | 18 | 386000
52 | Sylhet 50MW PP (EPL)
53 | Sylhet 10MW PP (Desh) | [15 empty] | 5 | 6 | 8 |  | 8 | 8 | 8 | 8 | 8 | 9 | 9 | 70740
54 | Hobiganj 11MW PP Cofidence-E | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 201264
55 | Fenchugonj 51 MW PP (Barakatullah) | 53 | 53 | 53 | 53 | 53 | 53 | 50 | 47 | 47 | 47 | 50 | 50 | 50 | 49 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 1209000
56 | Shahjahanulla 25 MW PP | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 21 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 16 | 480500
57 | Bibiana-II 341 MW CCPP (Summit) | 280 | 285 | 295 | 280 | 285 | 280 | 280 | 280 | 280 | 290 | 270 | 290 | 260 | 280 | 300 | 280 | 290 | 290 |  | 280 | 280 | 290 | 280 | 290 | 280 | 280 | 7037000
| Bibiyana South 400 MW | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 321 | 320 |  | 320 | 320 | 320 | 320 | 320 | 320 | 320 | 7679700
58 | Nababganj 55 MW PP (Southern power ) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 35 |  | 35 | 35 | 35 | 35 | 35 | 17 | 17 | 523595
59 | Tangail Palli Power Gen 22 MW | [10 empty] | 4 | 19 |  |  | 11 | 24 |  | 1 |  | 16 | 24 | 24 | 24 | 7 | 16 | 24 | 233040
60 | Barabkunda 22 MW PP (Regent) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 |  | 21 | 21 | 21 | 21 | 0 | 21 | 21 | 478176
61 | Narshingdi 22 MW PP (Doreen) | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 19 | 19 | 19 |  | 21 | 21 | 21 | 21 | 21 | 21 | 22 | 461196
62 | Tangail 22 MW PP (Doreen) | 19 | 19 | 19 | 19 | 19 | 19 | 19 | 18 | 18 | 18 | 18 | 18 |  |  | 18 | 18 |  |  |  | 14 | 21 | 21 | 21 |  | 21 | 21 | 341208
63 | Impoprt (Tripura) | 124 | 124 | 120 | 116 | 112 | 106 | 98 | 104 | 110 | 112 | 132 | 140 | 140 | 146 | 154 | 150 | 140 | 164 |  | 128 | 130 | 128 | 130 | 132 | 132 | 128 | 3036480
64 | Malancha, Ctg. EPZ (United) | 36 | 8 | 38 | 39 | 39 | 39 | 37 | 7 | 2 | 2 | 2 | 2 | 6 | 4 | 3 | 3 | 6 | 5 |  | 2 | 5 | 8 | 17 | 32 | 34 | 33 | 409920
65 | Feni 22MW PP (Doreen) | [14 empty] | 19 | 19 | 19 | 19 |  | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 192780
66 | Feni 11 MW PP (Doreen) | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 8 | 11 | 11 | 11 | 11 | 11 | 11 | 234900
67 | Jangalia 33MW PP (Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 802100
68 | Cumilla 25 MW PP (Summit) | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 12 | 12 | 12 | 12 | 12 | 12 | 19 | 20 |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 396090
69 | Summit Ashulia | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |  | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 600000
70 | Summit Madhabdi | 30 | 30 | 30 | 30 | 30 | 30 | 23 | 23 | 23 | 22 | 22 | 21 | 21 | 28 | 28 | 28 | 28 | 17 |  | 29 | 30 | 30 | 30 | 30 | 30 | 30 | 616680
71 | Maona 33 MW PP(Summit) | 30 | 28 | 28 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 805000
72 | Rupganj 33 MW PP(Summit) | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 25 | 33 | 33 | 33 | 33 | 33 | 33 |  | 33 | 33 | 33 | 33 | 33 | 33 | 33 | 791200
73 | Ghorashal 108MW PP (Regent)
| Feni Lanka Power | 34 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 34 | 34 | 34 | 34 | 34 | 34 |  | 34 | 34 | 34 | 52 | 52 | 52 | 52 | 710220
| Chowmuhani 113 MW | 74 | 63 | 58 | 58 | 58 | 58 | 57 | 58 | 58 | 58 | 50 | 47 | 48 | 49 | 48 | 47 | 50 | 95 |  | 95 | 95 | 95 | 96 | 92 | 83 | 60 | 1571640
| Manikgonj 162MW PP(MPGL) | 162 | 126 | 108 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 90 | 108 | 108 | 126 | 139 | 144 | 151 | 162 |  | 162 | 162 | 162 | 162 | 162 | 162 | 162 | 3136320
77 | Siddhirganj 100 PP(Dutch Bangla)
78 | Gazipur 52 MW PP | 16 | 0 | [6 empty] | 8 | 51 | 51 | 51 | 51 | 51 | 51 | 41 | 25 | 51 |  | 51 | 51 | 51 | 51 | 25 | 25 | 25 | 667200
79 | Kodda 150MW PP | 100 | 32 | 32 | 16 | 16 | 16 | 16 |  |  |  | 48 | 48 | 150 | 150 | 150 | 98 | 82 | 150 |  | 150 | 150 | 150 | 150 | 150 | 150 | 150 | 1968000
80 | Jamalpur 95 MW PP(Powerpac) | [25 empty] | 0 | 0
81 | Jangalia 52 MW PP (Lakdanavi) | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 16 | 16 | 16 | 16 | 16 |  | 16 | 16 | 16 | 16 | 16 | 16 | 23 | 318398
| Gazipur 100 MW PP | [7 empty] | 35 | 105 | 105 | 90 | 105 | 105 | 105 | 105 | 70 | 70 | 80 |  | 105 | 105 | 105 | 105 | 105 | 52 | 17 | 1621200
| Kaptai 7 MW Solar PP | [5 empty] | 0 | 1 | 2 | 4 | 2 | 6 | 3 | 6 | 4 | 1 | 0 | 0 | [9 empty] | 26281
| Jodiac Power | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 54 |  | 54 | 54 | 54 | 54 | 54 | 54 | 54 | 1300159
| Karnaphuli Power Ltd. | 68 | 68 | 68 | 68 | 68 | 17 | 17 | 23 | 34 | 34 | 65 | 108 | 110 | 105 | 110 | 110 | 51 | 65 |  | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 1997227
82 | Madanganj 102 PP(Summit)
83 | Pagla (DPA )
84 | B.Baria (Aggreko) 85MW
85 | Keraniganj 100 MW PP (Powerpac) | [10 empty] | 20 | 50 | 45 | 10 | 34 | 50 | 50 | 55 |  | 54 | 50 | 51 | 50 | 51 | 10 | 10 | 591427
86 | Meghnaghat CCPP ( Summit) | 260 | 280 | 260 | 255 | 275 | 235 | 280 | 260 | 260 | 300 | 265 | 265 | 245 | 265 | 280 | 265 | 245 | 285 |  | 285 | 300 | 295 | 270 | 283 | 260 | 260 | 6474124
87 | Meghnaghat 100 MW(IEL)
| Meghnaghat 104 MW PP (OPCL) | 94 | 94 | 94 | 94 | 94 | 94 | 62 | 54 | 62 | 93 | 94 | 94 | 94 | 94 | 94 | 93 | 94 | 94 |  | 94 | 94 | 94 | 94 | 93 | 93 | 94 | 2160000
88 | Ghorashal 78.5 MW PP(MAX)
90 | Ashuganj 53MW PP (United)
91 | Juldah 100 MW Unit-1 (Acorn) | 40 | 10 | 10 | 0 | [6 empty] | 70 | 85 | 92 | 50 | 50 | 10 | 10 | 50 |  | 50 | 50 | 50 | 70 | 100 | 100 | 100 | 935760
92 | Fenchuganj 44MW (Energyprima)
93 | Ashuganj 51 MW PP (Midland) | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 17 | 35 | 35 | 35 | 35 | 35 | 35 | 35 |  | 35 | 35 | 35 | 35 | 35 | 35 | 35 | 790236
94 | Gagnagar 102 MW PP (Digital Power) | 102 | 58 | 58 | 58 | 58 | 58 | 58 | 58 | 72 | 93 | 102 | 102 | 102 | 102 | 102 | 72 | 48 | 72 |  | 102 | 102 | 102 | 102 | 102 | 102 | 102 | 1996704
95 | Patenga 50MW PP (Baraka) | 25 | 25 | 25 | 0 |  |  | 1 | 12 | 12 | 13 | 38 | 50 | 50 | 50 | 50 | 50 | 25 | 30 |  | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 781920
96 | Chattogram 108 MW PP (ECPV) | [10 empty] | 8 | 35 | 70 | 83 | 85 | 50 | 11 | 42 |  | 85 | 85 | 85 | 85 | 85 | 85 | 46 | 866880
97 | katpotti 52 MW | [25 empty] | 0 | 0
98 | Bosila 108MW PP(CLC)
99 | Madanganj-55 MW PP(Summit) | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 40 | 40 | 55 | 55 | 55 | 55 | 55 | 55 |  | 55 | 55 | 55 | 55 | 55 | 55 | 55 | 1323073
100 | Manikganj 55 MW PP (Northern) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 55 | 55 | 55 | 55 | 55 | 17 | 17 | 555036
101 | Kushiara 163 MW CCPP (KP) | 163 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 130 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 |  | 163 | 163 | 163 | 163 | 163 | 163 | 163 | 3355281
102 | Sarishabari 3 MW Solar Plant | [6 empty] | 0 | 1 | 1 | 2 | 1 | 2 | 2 | 2 | 1 | 1 | 0 | [9 empty] | 14750
103 | Kamalaghat 54 MW PP(Banco Energy) | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 436680
104 | Keranigonj 300 MW PP (APR) | [25 empty] | 0 | 68889
105 | Bramhangoan 100 MW PP (Aggreko) | [25 empty] | 0 | 27070
106 | Mymensingh 200 MW PP (United) | 182 | 165 | 164 | 140 | 100 | 60 | 60 | 60 | 60 | 60 | 125 | 168 | 167 | 165 | 167 | 100 | 100 | 108 |  | 170 | 189 | 189 | 190 | 191 | 192 | 192 | 3446400
112 | Aurahati 100MW PP (Aggreko) | [19 empty] | 50 | [5 empty] | 0 | 60336
114 | Kodda 149 MW PP Unit-1 (Summit) | 149 | 123 | 117 | 98 | 85 | 85 | 85 | 105 | 132 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 149 |  | 149 | 149 | 149 | 149 | 149 | 149 | 149 | 3241730
115 | Juldah 100 MW PP Unit-3 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 90 | 90 | 100 | 100 | 90 | 90 | 90 | 55 |  | 100 | 100 | 100 | 100 | 90 | 90 | 100 | 2223360
116 | Chandpur 200MW (Desh energy) | 155 | 155 | 155 | 120 | 100 | 70 | 70 | 70 | 70 | 74 | 121 | 193 | 200 | 200 | 200 | 180 | 136 | 147 |  | 197 | 200 | 200 | 200 | 200 | 200 | 200 | 3719040
117 | Ashuganj 150MW PP (Midland) | 130 | 123 | 127 | 125 | 127 | 127 | 123 | 117 | 117 | 117 | 110 | 110 | 113 | 117 | 118 | 118 | 118 | 118 |  | 123 | 123 | 120 | 122 | 127 | 123 | 128 | 2898836
118 | Bibiyana-III 400 MW CCPP | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 316 | 315 | 318 | 316 | 318 | 316 | 316 | 316 | 316 | 317 |  | 316 | 316 | 316 | 316 | 317 | 316 | 316 | 7598000
| Jamalpur 115 MW PP (United) | 115 | 115 | 115 | 115 | 115 | 112 | 112 | 112 | 111 | 115 | 115 | 115 | 106 | 115 | 115 | 115 | 115 | 115 |  | 115 | 115 | 115 | 115 | 115 | 115 | 115 | 2727600
| Anwara 300 MW PP (United) | 305 | 304 | 304 | 306 | 305 | 305 | 253 | 252 | 303 | 306 | 287 | 304 | 304 | 305 | 304 | 287 | 304 | 304 |  | 305 | 305 | 304 | 304 | 304 | 305 | 303 | 7118291
| Juldah unit-2 (Acorn) | 100 | 100 | 100 | 100 | 100 | 100 | 70 | 70 | 100 | 100 | 90 | 90 | 90 | 100 | 100 | 100 | 100 | 100 |  | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 2292480
| Anlima Energy Ltd. | 108 | 108 | 108 | 108 | 108 | 90 | 72 | 72 | 72 | 105 | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 108 |  | 108 | 108 | 108 | 108 | 108 | 108 | 108 | 2492782
| Bhairob 54.5 MW | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 17 |  | 17 | 17 | 17 | 17 | 17 | 17 | 17 | 432360
| Spectra Solar Plant Ltd. | [5 empty] | 0 | 3 | 18 | 22 | 21 | 18 | 24 | 34 | 29 | 22 | 6 | 1 | [9 empty] | 203103
120 | Eastern Zone Total | 8164 | 7884 | 7825 | 7588 | 7535 | 7184 | 6958 | 6992 | 7434 | 7624 | 7888 | 8239 | 8384 | 8498 | 8619 | 8245 | 7973 | 8204 | 0 | 8793 | 8815 | 8816 | 8910 | 8805 | 8740 | 8624 | 194631129
121
122
123 | Khulna 60MW
124 | Khulna 115 MW PP (KPCL-1 & 3)
125 | Khulna 115 PP MW (KPCL-2)
126
127 | Khulna (Aggreeco) 55MW
128 | Faridpur 50 MW Peaking PP | [12 empty] | 3 | 4 | 4 | 4 | 4 | 23 |  | 30 | 30 | 30 | 30 | 30 | 14 | 4 | 167040
| Khulna 225 MW CCPP | 155 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 120 | 160 | 120 | 120 | 120 | 120 | 150 |  | 170 | 170 | 170 | 170 | 170 | 170 | 140 | 3378240
129 | Rupsha 105 MW PP (Orion rupsha) | 105 | 105 | 105 | 35 | 0 | [5 empty] | 35 | 85 | 105 | 105 | 105 | 35 | 17 | 35 |  | 98 | 105 | 105 | 105 | 105 | 105 | 105 | 1657440
130
131
132 | United Payra Power Ltd. | 17 | 0 | [15 empty] | 1 |  | 35 | 17 | 17 | 17 | 17 |  | 0 | 114000
133 | Bhola Nutan Biddut BD LTD (GAS) | 118 | 193 | 193 | 223 | 226 | 197 | 182 | 182 | 132 | 132 | 132 | 132 | 174 | 176 | 176 | 176 | 199 | 222 |  | 223 | 222 | 221 | 221 | 223 | 225 | 225 | 4476218
Bhola Nutan Biddut BD LTD (OIL)
Barisal 110 MW PP (Summit )
136 | Barisal GT PP Unit-1& 2
137 | Bhola 95 MW PP (Aggreko) | 62 | 32 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 50 |  | 40 | 43 | 41 | 10 | 11 |  | 11 | 11 | 11 | 11 | 11 | 11 | 12 | 501977
| Bhola 225 MW CCPP | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 87 | 86 | 86 | 86 | 86 | 84 | 85 | 86 | 86 | 85 |  | 86 | 87 | 87 | 87 | 87 | 87 | 87 | 2083690
140 | Bhola 33 MW PP (Venture) | 20 | 22 | 26 | 26 | 27 | 27 | 23 | 21 | 18 | 18 | 21 | 21 | 23 | 24 | 20 | 22 | 22 | 26 |  | 33 | 33 | 33 | 34 | 34 | 24 | 32 | 594393
141 | Noapara 100 MW PP (Bangla Trac) | [19 empty] | 50 | 30 | 30 | 30 | 30 | 30 | 0 | 230400
142 | Noapara 40 MW PP (Khanjahan Ali)
143 | Gopalganj 100 MW Peaking PP
144 | Bheramara GTPP Unit-3
145 | Madhumati 100 MW PP
146 | Bheramara HVDC | 710 | 720 | 715 | 710 | 709 | 710 | 709 | 710 | 710 | 710 | 709 | 709 | 709 | 709 | 709 | 709 | 709 | 710 |  | 709 | 716 | 716 | 716 | 716 | 716 | 717 | 17205818
147 | Bheramara 410 MW CCPP | 410 | 410 | 410 | 410 | 410 | 410 | 370 | 370 | 370 | 400 | 370 | 395 | 320 | 320 | 405 | 405 | 340 | 335 |  | 410 | 390 | 390 | 410 | 410 | 410 | 410 | 9704736
148 | Payra 1320 MW | 520 | 500 | 500 | 470 | 430 | 410 | 400 | 400 | 390 | 410 | 450 | 460 | 450 | 420 | 450 | 430 | 370 | 380 |  | 500 | 530 | 530 | 530 | 530 | 520 | 520 | 11915600
149
150 | Barapukuria TPP Unit-1 | 79 | 79 | 79 | 80 | 80 | 79 | 82 | 80 | 80 | 80 | 80 | 80 | 81 | 78 | 78 | 72 | 73 | 73 |  | 72 | 72 | 71 | 72 | 72 | 73 | 73 | 1856727
151 | Barapukuria TPP Unit-2
152 | Barapukuria 275 MW TPP Unit-3
153 | Baghabari 71 MW GTPP
156 | Baghabari 100 MW GTPP
| Baghabari 50 MW Peaking PP | [12 empty] | 43 | 50 | 50 | 50 | 50 | 50 |  | 50 | 50 | 50 | 50 | 50 | 50 |  | 525003
| Sirajgonj 6.55 MW Solar | [5 empty] | 0 | 1 | 1 | 4 | 4 | 4 | 5 | 4 | 4 | 4 | 2 | 0 | [9 empty] | 38940
157 | Sirajgonj 225MW CCPP Unit-1 (Gas)
158 | Sirajgonj 225MW CCPP Unit-1(Oil)
| Sirajgonj 225 MW CCPP Unit-2 (Gas) | 183 | 189 | 184 | 183 | 184 | 186 | 158 | 163 | 168 | 190 | 189 | 170 | 176 | 174 | 177 | 172 | 173 | 161 |  | 184 | 184 | 184 | 183 | 183 | 183 | 187 | 4498418
Sirajgonj 225 MW CCPP Unit-2 (Oil)
159 | Sirajgonj 225MW CCPP Unit-3 (Gas) | 190 | 197 | 195 | 188 | 191 | 190 | 169 | 168 | 173 | 188 | 187 | 173 | 193 | 171 | 169 | 164 | 164 | 148 |  | 187 | 191 | 192 | 193 | 188 | 185 | 188 | 4615009
Sirajgonj 225MW CCPP Unit-3 (Oil)
| Sirajgonj 400 MW CCPP Unit-4 | 415 | 420 | 394 | 404 | 414 | 341 | 347 | 308 | 390 | 383 | 341 | 356 | 295 | 402 | 407 | 340 | 320 | 383 |  | 402 | 339 | 351 | 326 | 360 | 314 | 365 | 8910618
160 | Sirajgonj 400MW CCPP Unit-4 (Oil)
161 | Bera 70 MW Peaking PP | [13 empty] | 5 | 7 | 33 | 33 | 33 |  | 33 | 33 | [5 empty] | 142019
162 | Bogra 22 MW PP (GBB) | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 22 | 21 | 16 | 16 | 19 | 18 | 18 | 18 | 19 | 21 |  | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 463920
163 | Bogura 20 MW PP (Energyprima)
164 | Ullapara 11 MW PP (Summit) | 11 | 11 | 11 | 11 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 | 8 |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 203526
165 | Amnura 50 MW PP(Sinha) | [11 empty] | 27 | 27 | 27 | 27 |  |  | 27 |  | 27 | 27 | 27 | 10 |  |  | 0 | 218380
166 | Katakhali 50 MW PP (Northern) | [19 empty] | 50 | 50 | 50 |  |  |  |  | 90165
167 | Katakhali 50 MW Peaking PP | [17 empty] | 24 |  | 35 | 38 | 40 | 38 |  |  |  | 124672
168 | Santahar 50 MW Peaking PP | [17 empty] | 28 |  | 29 | 29 | 28 | 28 | 28 | 27 |  | 177373
169 | Natore 52 MW PP (Rajlanka) | 16 | 0 | [8 empty] | 4 | 8 | 27 | 8 | 8 |  |  |  |  | 43 | 43 | 43 | 43 | 52 | 52 | 52 | 380160
170 | Chapainawabganj 100 MW Peaking PP | [17 empty] | 93 |  | 94 | 94 | 94 | 94 | 94 | 91 | 47 | 615304
171 | Baghabari 200 MW PP (Paramount)
| Bagura 113 MW PP (Confidence)-2 | 113 | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 38 | 80 | 94 | 94 | 96 | 113 | 113 | 70 | 75 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2226048
172 | Confidence Power Bogura Unit-1 113 MW | 113 | 113 | 113 | 35 | 35 | 35 | 35 | 35 | 35 | 50 | 100 | 113 | 113 | 113 | 113 | 113 | 50 | 95 |  | 113 | 113 | 113 | 113 | 113 | 113 | 113 | 2158176
173 | Rangpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
175 | Saidpur 20 MW GTPP | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
176 | Rangpur 113 MW PP (Confidence) | 111 | 111 | 111 | 111 | 111 | 95 | 90 | 90 | 90 | 100 | 104 | 104 | 103 | 103 | 105 | 101 | 54 | 88 |  | 104 | 104 | 104 | 104 | 104 | 106 | 113 | 2414332
177 | Sympa Solar Power 8MW | [5 empty] | 0 | 1 | 2 | 4 | 6 | 7 | 7 | 7 | 7 | 6 | 5 | 3 | 0 | [8 empty] | 46535
178
178